## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2497-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2497-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2497-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2497-2_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2497-2_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2497-2_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2497-2_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2497-2_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2497-2_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_2497-2_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2497-2_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_2497-2_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2497-2_0_4_node_137 | 0.4 | n |  | TRUE
13 | bus_LV_2497-2_0_4_node_92 | 0.4 | n |  | TRUE
14 | bus_LV_2497-2_0_4_node_154 | 0.4 | n |  | TRUE
15 | bus_LV_2497-2_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2497-2_0_4_node_156 | 0.4 | n |  | TRUE
17 | bus_LV_2497-2_0_4_node_138 | 0.4 | n |  | TRUE
18 | bus_LV_2497-2_0_4_node_89 | 0.4 | n |  | TRUE
19 | bus_LV_2497-2_0_4_node_152 | 0.4 | n |  | TRUE
20 | bus_LV_2497-2_0_4_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_2497-2_0_4_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_2497-2_0_4_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_2497-2_0_4_node_157 | 0.4 | n |  | TRUE
24 | bus_LV_2497-2_0_4_node_155 | 0.4 | n |  | TRUE
25 | bus_LV_2497-2_0_4_node_178 | 0.4 | n |  | TRUE
26 | bus_LV_2497-2_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2497-2_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_2497-2_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_2497-2_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_2497-2_0_4_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_2497-2_0_4_node_109 | 0.4 | n |  | TRUE
32 | bus_LV_2497-2_0_4_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_2497-2_0_4_node_99 | 0.4 | n |  | TRUE
34 | bus_LV_2497-2_0_4_node_100 | 0.4 | n |  | TRUE
35 | bus_LV_2497-2_0_4_node_101 | 0.4 | n |  | TRUE
36 | bus_LV_2497-2_0_4_node_110 | 0.4 | n |  | TRUE
37 | bus_LV_2497-2_0_4_node_128 | 0.4 | n |  | TRUE
38 | bus_LV_2497-2_0_4_node_129 | 0.4 | n |  | TRUE
39 | bus_LV_2497-2_0_4_node_130 | 0.4 | n |  | TRUE
40 | bus_LV_2497-2_0_4_node_131 | 0.4 | n |  | TRUE
41 | bus_LV_2497-2_0_4_node_132 | 0.4 | n |  | TRUE
42 | bus_LV_2497-2_0_4_node_133 | 0.4 | n |  | TRUE
43 | bus_LV_2497-2_0_4_node_134 | 0.4 | n |  | TRUE
44 | bus_LV_2497-2_0_4_node_135 | 0.4 | n |  | TRUE
45 | bus_LV_2497-2_0_4_node_136 | 0.4 | n |  | TRUE
46 | bus_LV_2497-2_0_4_node_164 | 0.4 | n |  | TRUE
47 | bus_LV_2497-2_0_4_node_177 | 0.4 | n |  | TRUE
48 | bus_LV_2497-2_0_4_node_111 | 0.4 | n |  | TRUE
49 | bus_LV_2497-2_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2497-2_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_2497-2_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_2497-2_0_4_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_2497-2_0_4_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_2497-2_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_2497-2_0_4_node_97 | 0.4 | n |  | TRUE
56 | bus_LV_2497-2_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_2497-2_0_4_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_2497-2_0_4_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_2497-2_0_4_node_112 | 0.4 | n |  | TRUE
60 | bus_LV_2497-2_0_4_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_2497-2_0_4_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_2497-2_0_4_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_2497-2_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2497-2_0_4_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_2497-2_0_4_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2497-2_0_4_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_2497-2_0_4_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2497-2_0_4_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2497-2_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2497-2_0_4_node_104 | 0.4 | n |  | TRUE
71 | bus_LV_2497-2_0_4_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_2497-2_0_4_node_150 | 0.4 | n |  | TRUE
73 | bus_LV_2497-2_0_4_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_2497-2_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2497-2_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_2497-2_0_4_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_2497-2_0_4_node_103 | 0.4 | n |  | TRUE
78 | bus_LV_2497-2_0_4_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_2497-2_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_2497-2_0_4_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_2497-2_0_4_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_2497-2_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_2497-2_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_2497-2_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_2497-2_0_4_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_2497-2_0_4_node_142 | 0.4 | n |  | TRUE
87 | bus_LV_2497-2_0_4_node_126 | 0.4 | n |  | TRUE
88 | bus_LV_2497-2_0_4_node_159 | 0.4 | n |  | TRUE
89 | bus_LV_2497-2_0_4_node_160 | 0.4 | n |  | TRUE
90 | bus_LV_2497-2_0_4_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_2497-2_0_4_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_2497-2_0_4_node_96 | 0.4 | n |  | TRUE
93 | bus_LV_2497-2_0_4_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_2497-2_0_4_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_2497-2_0_4_node_106 | 0.4 | n |  | TRUE
96 | bus_LV_2497-2_0_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_2497-2_0_4_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_2497-2_0_4_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_2497-2_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_2497-2_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_2497-2_0_4_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_2497-2_0_4_node_125 | 0.4 | n |  | TRUE
103 | bus_LV_2497-2_0_4_node_180 | 0.4 | n |  | TRUE
104 | bus_LV_2497-2_0_4_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_2497-2_0_4_node_123 | 0.4 | n |  | TRUE
106 | bus_LV_2497-2_0_4_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_2497-2_0_4_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_2497-2_0_4_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_2497-2_0_4_node_151 | 0.4 | n |  | TRUE
110 | bus_LV_2497-2_0_4_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_2497-2_0_4_node_115 | 0.4 | n |  | TRUE
112 | bus_LV_2497-2_0_4_node_116 | 0.4 | n |  | TRUE
113 | bus_LV_2497-2_0_4_node_117 | 0.4 | n |  | TRUE
114 | bus_LV_2497-2_0_4_node_143 | 0.4 | n |  | TRUE
115 | bus_LV_2497-2_0_4_node_179 | 0.4 | n |  | TRUE
116 | bus_LV_2497-2_0_4_node_144 | 0.4 | n |  | TRUE
117 | bus_LV_2497-2_0_4_node_127 | 0.4 | n |  | TRUE
118 | bus_LV_2497-2_0_4_node_153 | 0.4 | n |  | TRUE
119 | bus_LV_2497-2_0_4_node_163 | 0.4 | n |  | TRUE
120 | bus_LV_2497-2_0_4_node_139 | 0.4 | n |  | TRUE
121 | bus_LV_2497-2_0_4_node_140 | 0.4 | n |  | TRUE
122 | bus_LV_2497-2_0_4_node_172 | 0.4 | n |  | TRUE
123 | bus_LV_2497-2_0_4_node_161 | 0.4 | n |  | TRUE
124 | bus_LV_2497-2_0_4_node_162 | 0.4 | n |  | TRUE
125 | bus_LV_2497-2_0_4_node_158 | 0.4 | n |  | TRUE
126 | bus_LV_2497-2_0_4_node_170 | 0.4 | n |  | TRUE
127 | bus_LV_2497-2_0_4_node_169 | 0.4 | n |  | TRUE
128 | bus_LV_2497-2_0_4_node_166 | 0.4 | n |  | TRUE
129 | bus_LV_2497-2_0_4_node_167 | 0.4 | n |  | TRUE
130 | bus_LV_2497-2_0_4_node_168 | 0.4 | n |  | TRUE
131 | bus_LV_2497-2_0_4_node_171 | 0.4 | n |  | TRUE
132 | bus_MV_291_1_node_206 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2497-2_0_4_load_0 | 0 | 0.00066234 | 0.000166 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2497-2_0_4_load_1 | 1 | 0.0018314 | 0.00045899 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2497-2_0_4_load_5 | 4 | 0.0014382 | 0.00036045 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2497-2_0_4_load_6 | 6 | 0.0034276 | 0.00085903 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2497-2_0_4_load_10 | 8 | 0.0011302 | 0.00028325 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2497-2_0_4_load_11 | 9 | 0.0020283 | 0.00050834 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2497-2_0_4_load_137 | 12 | 0.0052025 | 0.0013039 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2497-2_0_4_load_92 | 13 | 0.0021866 | 0.00054802 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2497-2_0_4_load_154 | 14 | 0.0021221 | 0.00053184 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2497-2_0_4_load_9 | 15 | 0.0008022 | 0.00020105 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2497-2_0_4_load_138 | 17 | 0.0046823 | 0.0011735 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2497-2_0_4_load_67 | 22 | 0.004035 | 0.0010113 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2497-2_0_4_load_157 | 23 | 0.0014281 | 0.00035791 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2497-2_0_4_load_155 | 24 | 0.00057395 | 0.00014385 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2497-2_0_4_load_178 | 25 | 0.00074142 | 0.00018582 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2497-2_0_4_load_31 | 26 | 0.0011458 | 0.00028716 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2497-2_0_4_load_32 | 27 | 0.0006028 | 0.00015108 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2497-2_0_4_load_33 | 28 | 0.0005709 | 0.00014308 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2497-2_0_4_load_36 | 30 | 0.0030116 | 0.00075477 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2497-2_0_4_load_109 | 31 | 0.0039715 | 0.00099535 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2497-2_0_4_load_98 | 32 | 0.0005777 | 0.00014478 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2497-2_0_4_load_101 | 35 | 0.006205 | 0.0015551 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2497-2_0_4_load_110 | 36 | 0.013959 | 0.0034985 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2497-2_0_4_load_128 | 37 | 0.00094532 | 0.00023692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2497-2_0_4_load_129 | 38 | 0.0015642 | 0.00039202 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2497-2_0_4_load_131 | 40 | 0.0023463 | 0.00058804 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2497-2_0_4_load_132 | 41 | 0.00074125 | 0.00018577 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2497-2_0_4_load_133 | 42 | 0.002279 | 0.00057118 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2497-2_0_4_load_134 | 43 | 0.0016114 | 0.00040386 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2497-2_0_4_load_135 | 44 | 0.0067827 | 0.0016999 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2497-2_0_4_load_136 | 45 | 0.0041791 | 0.0010474 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2497-2_0_4_load_177 | 47 | 0.0061204 | 0.0015339 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2497-2_0_4_load_38 | 49 | 0.00065138 | 0.00016325 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2497-2_0_4_load_39 | 50 | 0.00081225 | 0.00020357 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2497-2_0_4_load_40 | 51 | 0.00061542 | 0.00015424 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2497-2_0_4_load_41 | 52 | 0.002081 | 0.00052154 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2497-2_0_4_load_42 | 53 | 0.00092254 | 0.00023121 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2497-2_0_4_load_97 | 55 | 0.0071825 | 0.0018001 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2497-2_0_4_load_44 | 56 | 0.001036 | 0.00025964 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2497-2_0_4_load_75 | 57 | 0.0041372 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2497-2_0_4_load_76 | 58 | 0.001353 | 0.0003391 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2497-2_0_4_load_112 | 59 | 0.00067358 | 0.00016881 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2497-2_0_4_load_77 | 60 | 0.002027 | 0.00050801 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2497-2_0_4_load_78 | 61 | 0.0021497 | 0.00053878 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2497-2_0_4_load_52 | 63 | 0.0022247 | 0.00055755 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2497-2_0_4_load_53 | 64 | 0.0017086 | 0.00042823 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2497-2_0_4_load_54 | 65 | 0.0017118 | 0.00042902 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2497-2_0_4_load_55 | 66 | 0.0013877 | 0.00034778 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2497-2_0_4_load_56 | 67 | 0.0046305 | 0.0011605 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2497-2_0_4_load_57 | 68 | 0.0011572 | 0.00029003 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2497-2_0_4_load_58 | 69 | 0.0016008 | 0.00040119 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2497-2_0_4_load_104 | 70 | 0.0017897 | 0.00044855 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2497-2_0_4_load_150 | 72 | 0.0018923 | 0.00047425 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2497-2_0_4_load_102 | 73 | 0.0033151 | 0.00083085 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2497-2_0_4_load_61 | 74 | 0.0020801 | 0.00052132 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2497-2_0_4_load_59 | 75 | 0.00056264 | 0.00014101 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2497-2_0_4_load_60 | 76 | 0.0017214 | 0.00043143 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2497-2_0_4_load_103 | 77 | 0.0022563 | 0.00056549 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2497-2_0_4_load_68 | 78 | 0.0029793 | 0.00074668 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2497-2_0_4_load_69 | 79 | 0.0024607 | 0.00061672 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2497-2_0_4_load_70 | 80 | 0.0023804 | 0.00059659 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2497-2_0_4_load_71 | 81 | 0.00197 | 0.00049374 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2497-2_0_4_load_72 | 82 | 0.0022735 | 0.00056979 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2497-2_0_4_load_73 | 83 | 0.0012518 | 0.00031372 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2497-2_0_4_load_74 | 84 | 0.0022312 | 0.0005592 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2497-2_0_4_load_87 | 85 | 0.0012534 | 0.00031414 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2497-2_0_4_load_126 | 87 | 0.0016748 | 0.00041974 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2497-2_0_4_load_160 | 89 | 0.0017843 | 0.00044719 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2497-2_0_4_load_108 | 90 | 0.0013031 | 0.00032659 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2497-2_0_4_load_105 | 91 | 0.00126 | 0.00031579 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2497-2_0_4_load_96 | 92 | 0.0022303 | 0.00055898 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2497-2_0_4_load_95 | 93 | 0.0024765 | 0.00062068 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2497-2_0_4_load_107 | 94 | 0.0013807 | 0.00034604 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2497-2_0_4_load_106 | 95 | 0.0024692 | 0.00061885 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2497-2_0_4_load_79 | 96 | 0.00148 | 0.00037091 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2497-2_0_4_load_80 | 97 | 0.002461 | 0.00061679 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2497-2_0_4_load_81 | 98 | 0.0019479 | 0.0004882 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2497-2_0_4_load_85 | 100 | 0.0017823 | 0.00044669 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2497-2_0_4_load_86 | 101 | 0.0024925 | 0.00062467 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2497-2_0_4_load_125 | 102 | 0.0023441 | 0.00058749 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2497-2_0_4_load_180 | 103 | 0.0016967 | 0.00042525 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2497-2_0_4_load_123 | 105 | 0.0014461 | 0.00036243 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2497-2_0_4_load_124 | 106 | 0.00075799 | 0.00018997 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2497-2_0_4_load_88 | 107 | 0.017801 | 0.0044614 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2497-2_0_4_load_94 | 108 | 0.00092075 | 0.00023076 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2497-2_0_4_load_151 | 109 | 0.0011849 | 0.00029695 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2497-2_0_4_load_114 | 110 | 0.0014252 | 0.00035718 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2497-2_0_4_load_115 | 111 | 0.00087542 | 0.0002194 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2497-2_0_4_load_116 | 112 | 0.0031781 | 0.0007965 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2497-2_0_4_load_117 | 113 | 0.0012511 | 0.00031356 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2497-2_0_4_load_143 | 114 | 0.0034212 | 0.00085743 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2497-2_0_4_load_179 | 115 | 0.0043861 | 0.0010993 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2497-2_0_4_load_144 | 116 | 0.0040975 | 0.0010269 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2497-2_0_4_load_127 | 117 | 0.0011626 | 0.00029137 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2497-2_0_4_load_153 | 118 | 0.0025018 | 0.00062701 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2497-2_0_4_load_163 | 119 | 0.0020939 | 0.00052477 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2497-2_0_4_load_139 | 120 | 0.0014413 | 0.00036122 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2497-2_0_4_load_140 | 121 | 0.0034217 | 0.00085757 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2497-2_0_4_load_172 | 122 | 0.002489 | 0.00062381 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2497-2_0_4_load_161 | 123 | 0.0025595 | 0.00064146 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2497-2_0_4_load_162 | 124 | 0.0011598 | 0.00029068 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2497-2_0_4_load_158 | 125 | 0.0053156 | 0.0013322 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2497-2_0_4_load_170 | 126 | 0.00093185 | 0.00023354 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2497-2_0_4_load_169 | 127 | 0.0020552 | 0.00051508 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2497-2_0_4_load_166 | 128 | 0.002764 | 0.00069272 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2497-2_0_4_load_167 | 129 | 0.0019036 | 0.00047709 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2497-2_0_4_load_168 | 130 | 0.0010426 | 0.0002613 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2497-2_0_4_load_171 | 131 | 0.0015163 | 0.00038003 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2497-2_0_4_line_0 |  | 0 | 1 | 0.012967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2497-2_0_4_line_1 |  | 0 | 2 | 0.0081039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2497-2_0_4_line_2 |  | 2 | 3 | 0.004528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2497-2_0_4_line_3 |  | 2 | 4 | 0.021559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2497-2_0_4_line_4 |  | 3 | 8 | 0.021229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2497-2_0_4_line_5 |  | 3 | 9 | 0.013501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2497-2_0_4_line_6 |  | 4 | 10 | 0.0087348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2497-2_0_4_line_7 |  | 5 | 6 | 0.022552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2497-2_0_4_line_8 |  | 5 | 7 | 0.015391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2497-2_0_4_line_9 |  | 6 | 9 | 0.024486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2497-2_0_4_line_10 |  | 7 | 11 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2497-2_0_4_line_11 |  | 7 | 12 | 0.0072708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2497-2_0_4_line_12 |  | 8 | 16 | 0.023357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2497-2_0_4_line_13 |  | 10 | 15 | 0.005576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2497-2_0_4_line_14 |  | 11 | 13 | 0.04471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2497-2_0_4_line_15 |  | 11 | 14 | 0.041548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2497-2_0_4_line_16 |  | 12 | 17 | 0.013881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2497-2_0_4_line_17 |  | 13 | 18 | 0.012571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2497-2_0_4_line_18 |  | 14 | 19 | 0.0085613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2497-2_0_4_line_19 |  | 16 | 23 | 0.013603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2497-2_0_4_line_20 |  | 16 | 24 | 0.024193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2497-2_0_4_line_21 |  | 17 | 120 | 0.014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2497-2_0_4_line_22 |  | 18 | 33 | 0.11894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2497-2_0_4_line_23 |  | 18 | 107 | 0.035395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2497-2_0_4_line_24 |  | 19 | 109 | 0.026777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2497-2_0_4_line_25 |  | 19 | 118 | 0.044879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2497-2_0_4_line_26 |  | 20 | 21 | 0.0049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2497-2_0_4_line_27 |  | 20 | 22 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2497-2_0_4_line_28 |  | 21 | 25 | 0.022513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2497-2_0_4_line_29 |  | 22 | 24 | 0.018523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2497-2_0_4_line_30 |  | 23 | 125 | 0.013567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2497-2_0_4_line_31 |  | 26 | 27 | 0.010409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2497-2_0_4_line_32 |  | 26 | 28 | 0.0036572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2497-2_0_4_line_33 |  | 27 | 29 | 0.073826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2497-2_0_4_line_34 |  | 29 | 30 | 0.022239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2497-2_0_4_line_35 |  | 30 | 31 | 0.045604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2497-2_0_4_line_36 |  | 31 | 36 | 0.03086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2497-2_0_4_line_37 |  | 32 | 33 | 0.057918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2497-2_0_4_line_38 |  | 33 | 34 | 0.020985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2497-2_0_4_line_39 |  | 34 | 35 | 0.0072459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2497-2_0_4_line_40 |  | 35 | 46 | 0.029839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2497-2_0_4_line_41 |  | 36 | 48 | 0.021229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2497-2_0_4_line_42 |  | 37 | 38 | 0.021312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2497-2_0_4_line_43 |  | 37 | 39 | 0.025612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2497-2_0_4_line_44 |  | 38 | 40 | 0.00028338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2497-2_0_4_line_45 |  | 39 | 41 | 0.027949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2497-2_0_4_line_46 |  | 39 | 42 | 0.01985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2497-2_0_4_line_47 |  | 40 | 43 | 0.017062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2497-2_0_4_line_48 |  | 41 | 44 | 0.0051063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2497-2_0_4_line_49 |  | 42 | 45 | 0.037403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2497-2_0_4_line_50 |  | 43 | 46 | 0.025368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2497-2_0_4_line_51 |  | 44 | 55 | 0.020489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2497-2_0_4_line_52 |  | 45 | 47 | 0.021178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2497-2_0_4_line_53 |  | 47 | 48 | 0.035577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2497-2_0_4_line_54 |  | 49 | 50 | 0.020553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2497-2_0_4_line_55 |  | 49 | 51 | 0.00043961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2497-2_0_4_line_56 |  | 50 | 52 | 0.022175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2497-2_0_4_line_57 |  | 51 | 53 | 0.018373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2497-2_0_4_line_58 |  | 52 | 54 | 0.00014473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2497-2_0_4_line_59 |  | 53 | 56 | 0.0066662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2497-2_0_4_line_60 |  | 54 | 57 | 0.027626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2497-2_0_4_line_61 |  | 54 | 58 | 0.017471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2497-2_0_4_line_62 |  | 55 | 92 | 0.0050219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2497-2_0_4_line_63 |  | 56 | 59 | 0.031919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2497-2_0_4_line_64 |  | 57 | 60 | 0.016017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2497-2_0_4_line_65 |  | 58 | 61 | 0.0031928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2497-2_0_4_line_66 |  | 59 | 62 | 0.0023127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2497-2_0_4_line_67 |  | 60 | 90 | 0.017786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2497-2_0_4_line_68 |  | 61 | 91 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2497-2_0_4_line_69 |  | 62 | 110 | 0.018626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2497-2_0_4_line_70 |  | 62 | 111 | 0.025945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2497-2_0_4_line_71 |  | 63 | 64 | 0.01312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2497-2_0_4_line_72 |  | 63 | 65 | 0.014996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2497-2_0_4_line_73 |  | 64 | 66 | 0.012042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2497-2_0_4_line_74 |  | 65 | 67 | 0.012166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2497-2_0_4_line_75 |  | 66 | 68 | 0.0043477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2497-2_0_4_line_76 |  | 67 | 69 | 0.032465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2497-2_0_4_line_77 |  | 68 | 70 | 0.0081742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2497-2_0_4_line_78 |  | 69 | 71 | 0.014651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2497-2_0_4_line_79 |  | 70 | 72 | 0.012611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2497-2_0_4_line_80 |  | 71 | 73 | 0.020805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2497-2_0_4_line_81 |  | 71 | 74 | 0.028152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2497-2_0_4_line_82 |  | 72 | 109 | 0.0091288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2497-2_0_4_line_83 |  | 73 | 77 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2497-2_0_4_line_84 |  | 74 | 76 | 0.021758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2497-2_0_4_line_85 |  | 75 | 76 | 0.023751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2497-2_0_4_line_86 |  | 78 | 79 | 0.026417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2497-2_0_4_line_87 |  | 78 | 80 | 0.020864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2497-2_0_4_line_88 |  | 79 | 81 | 0.016714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2497-2_0_4_line_89 |  | 80 | 82 | 0.018922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2497-2_0_4_line_90 |  | 81 | 83 | 0.0087077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2497-2_0_4_line_91 |  | 82 | 84 | 0.0060456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2497-2_0_4_line_92 |  | 83 | 85 | 0.00027302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2497-2_0_4_line_93 |  | 84 | 86 | 0.030254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2497-2_0_4_line_94 |  | 85 | 87 | 0.014507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2497-2_0_4_line_95 |  | 86 | 88 | 0.005135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2497-2_0_4_line_96 |  | 86 | 89 | 0.019229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2497-2_0_4_line_97 |  | 87 | 105 | 0.010798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2497-2_0_4_line_98 |  | 88 | 123 | 0.014988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2497-2_0_4_line_99 |  | 88 | 124 | 0.022242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2497-2_0_4_line_100 |  | 89 | 119 | 0.00031333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2497-2_0_4_line_101 |  | 90 | 94 | 0.01004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2497-2_0_4_line_102 |  | 91 | 95 | 0.021837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2497-2_0_4_line_103 |  | 92 | 93 | 0.014781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2497-2_0_4_line_104 |  | 93 | 108 | 0.026671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2497-2_0_4_line_105 |  | 96 | 97 | 0.028466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2497-2_0_4_line_106 |  | 96 | 98 | 0.023883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2497-2_0_4_line_107 |  | 98 | 99 | 0.037098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2497-2_0_4_line_108 |  | 99 | 100 | 0.021127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2497-2_0_4_line_109 |  | 99 | 101 | 0.029024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2497-2_0_4_line_110 |  | 100 | 102 | 0.003371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2497-2_0_4_line_111 |  | 102 | 103 | 0.0010487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2497-2_0_4_line_112 |  | 103 | 119 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2497-2_0_4_line_113 |  | 104 | 105 | 0.012335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2497-2_0_4_line_114 |  | 104 | 106 | 0.018775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2497-2_0_4_line_115 |  | 106 | 117 | 0.012086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2497-2_0_4_line_116 |  | 110 | 112 | 0.016137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2497-2_0_4_line_117 |  | 111 | 113 | 0.031336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2497-2_0_4_line_118 |  | 112 | 114 | 0.018743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2497-2_0_4_line_119 |  | 113 | 115 | 0.0078213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2497-2_0_4_line_120 |  | 114 | 116 | 0.0014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2497-2_0_4_line_121 |  | 116 | 122 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2497-2_0_4_line_122 |  | 117 | 118 | 0.00031486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2497-2_0_4_line_123 |  | 120 | 121 | 0.0029075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2497-2_0_4_line_124 |  | 121 | 122 | 0.0089693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2497-2_0_4_line_125 |  | 124 | 126 | 0.0024713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2497-2_0_4_line_126 |  | 126 | 127 | 0.022367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2497-2_0_4_line_127 |  | 127 | 131 | 0.0035555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2497-2_0_4_line_128 |  | 128 | 129 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2497-2_0_4_line_129 |  | 129 | 130 | 0.0004008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2497-2_0_4_line_130 |  | 130 | 131 | 0.019558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2497-2_0_4_trafo_89 | 0.63 MVA 20/0.4 kV | 132 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2638973.3762 | 1245003.7637 | 2638973.8285 | 1245004.3824 | 2638978.6755 | 1245010.685 | 2638981.2713 | 1245014.0497
1 | 2638968.5942 | 1244997.2212 | 2638973.3762 | 1245003.7637
2 | 2638968.5942 | 1244997.2212 | 2638965.2046 | 1245000.2342
3 | 2638968.5942 | 1244997.2212 | 2638963.6003 | 1244990.2616 | 2638955.6252 | 1244980.0034
4 | 2638965.2046 | 1245000.2342 | 2638953.2525 | 1245009.3284 | 2638947.6216 | 1245011.9487
5 | 2638965.2046 | 1245000.2342 | 2638974.0133 | 1245010.4664
6 | 2638950.2641 | 1244973.1074 | 2638955.6252 | 1244980.0034
7 | 2638998.3412 | 1245036.1752 | 2638998.4113 | 1245042.7466 | 2638988.8084 | 1245029.973
8 | 2638998.3412 | 1245036.1752 | 2639003.8456 | 1245039.0132 | 2639012.6675 | 1245041.7507
9 | 2638974.0133 | 1245010.4664 | 2638975.0424 | 1245011.6618 | 2638988.8084 | 1245029.973
10 | 2639009.3017 | 1245051.5017 | 2639005.8998 | 1245047.1987 | 2639012.6675 | 1245041.7507
11 | 2639012.6675 | 1245041.7507 | 2639019.2188 | 1245038.5972
12 | 2638930.7427 | 1244996.9616 | 2638940.6614 | 1245008.7343 | 2638943.9756 | 1245011.4467 | 2638947.6216 | 1245011.9487
13 | 2638945.5598 | 1244976.1229 | 2638950.2641 | 1244973.1074
14 | 2639009.3017 | 1245051.5017 | 2639024.2013 | 1245071.0012 | 2639035.9997 | 1245087.3597
15 | 2639009.3017 | 1245051.5017 | 2638998.1022 | 1245059.9003 | 2638989.8999 | 1245065.2054 | 2638979.8042 | 1245071.1986 | 2638975.3038 | 1245073.1037 | 2638974.1859 | 1245073.3872
16 | 2639032.1569 | 1245033.574 | 2639019.868 | 1245038.2847 | 2639019.2188 | 1245038.5972
17 | 2639043.3534 | 1245097.5556 | 2639035.9997 | 1245087.3597
18 | 2638965.804 | 1245073.4971 | 2638970.604 | 1245074.2958 | 2638974.1859 | 1245073.3872
19 | 2638930.7427 | 1244996.9616 | 2638919.7243 | 1245004.9384
20 | 2638930.7427 | 1244996.9616 | 2638914.9109 | 1244978.6685
21 | 2639032.1569 | 1245033.574 | 2639045.7234 | 1245028.3735
22 | 2639043.3534 | 1245097.5556 | 2639137.4064 | 1245170.3668
23 | 2639043.3534 | 1245097.5556 | 2639034.0912 | 1245108.9243 | 2639020.9976 | 1245124.9962
24 | 2638965.804 | 1245073.4971 | 2638961.797 | 1245071.6029 | 2638956.8994 | 1245068.402 | 2638951.7981 | 1245066.3005 | 2638945.6013 | 1245064.203 | 2638941.3316 | 1245063.0038
25 | 2638965.804 | 1245073.4971 | 2638961.2008 | 1245078.4035 | 2638952.8025 | 1245087.0985 | 2638935.4086 | 1245106.5083
26 | 2638925.2227 | 1244943.5016 | 2638921.9798 | 1244947.1828
27 | 2638921.9798 | 1244947.1828 | 2638909.19 | 1244963.0426
28 | 2638925.2227 | 1244943.5016 | 2638910.1526 | 1244926.7766
29 | 2638914.9109 | 1244978.6685 | 2638909.7912 | 1244972.7529 | 2638907.4985 | 1244968.6574 | 2638907.6217 | 1244966.0121 | 2638909.19 | 1244963.0426 | 2638909.19 | 1244963.0426
30 | 2638908.7347 | 1245012.8944 | 2638919.7243 | 1245004.9384
31 | 2639050.7836 | 1245274.6252 | 2639058.6914 | 1245267.8559
32 | 2639050.7836 | 1245274.6252 | 2639048.0053 | 1245277.0035
33 | 2639058.6914 | 1245267.8559 | 2639125.7029 | 1245236.8776
34 | 2639125.7029 | 1245236.8776 | 2639135.2232 | 1245247.0803 | 2639141.7469 | 1245252.1861
35 | 2639183.2497 | 1245270.6197 | 2639164.2364 | 1245264.0827 | 2639144.2204 | 1245254.122 | 2639141.7469 | 1245252.1861
36 | 2639212.9879 | 1245278.8052 | 2639200.4012 | 1245275.7957 | 2639186.0968 | 1245271.5985 | 2639183.2497 | 1245270.6197
37 | 2639137.4064 | 1245170.3668 | 2639083.6376 | 1245191.8936
38 | 2639137.4064 | 1245170.3668 | 2639151.5985 | 1245171.0274 | 2639154.3503 | 1245173.058 | 2639157.0946 | 1245175.0885
39 | 2639157.0946 | 1245175.0885 | 2639163.8094 | 1245172.3657
40 | 2639192.3891 | 1245165.3817 | 2639184.6697 | 1245165.0639 | 2639179.8225 | 1245166.8442 | 2639168.7231 | 1245170.3733 | 2639163.8094 | 1245172.3657
41 | 2639233.6995 | 1245283.3984 | 2639230.099 | 1245282.8965 | 2639212.9879 | 1245278.8052
42 | 2639234.4907 | 1245172.1602 | 2639255.2675 | 1245176.9054
43 | 2639280.2341 | 1245182.6179 | 2639260.7784 | 1245178.164 | 2639255.2675 | 1245176.9054
44 | 2639234.4907 | 1245172.1602 | 2639234.2145 | 1245172.0971
45 | 2639280.2341 | 1245182.6179 | 2639297.7181 | 1245188.1705 | 2639306.9422 | 1245190.8454
46 | 2639280.2341 | 1245182.6179 | 2639277.4017 | 1245193.9065 | 2639275.1241 | 1245201.7961
47 | 2639217.556 | 1245168.4097 | 2639230.7989 | 1245171.317 | 2639234.2145 | 1245172.0971
48 | 2639306.9422 | 1245190.8454 | 2639311.8464 | 1245192.2675
49 | 2639263.4396 | 1245237.2821 | 2639268.6175 | 1245224.335 | 2639275.1241 | 1245201.7961
50 | 2639192.3891 | 1245165.3817 | 2639203.4815 | 1245166.3444 | 2639214.8728 | 1245167.8206 | 2639217.556 | 1245168.4097
51 | 2639331.5528 | 1245197.8776 | 2639316.4343 | 1245193.5979 | 2639311.8464 | 1245192.2675
52 | 2639263.4396 | 1245237.2821 | 2639260.8123 | 1245243.8517 | 2639254.8678 | 1245256.6398
53 | 2639233.6995 | 1245283.3984 | 2639237.4301 | 1245282.5113 | 2639240.2589 | 1245280.8845 | 2639243.4532 | 1245277.6924 | 2639246.8899 | 1245272.1226 | 2639254.3819 | 1245257.6849 | 2639254.8678 | 1245256.6398
54 | 2639174.9712 | 1244966.4297 | 2639191.2982 | 1244957.6053 | 2639193.0848 | 1244956.7203
55 | 2639174.9712 | 1244966.4297 | 2639174.5844 | 1244966.6387
56 | 2639213.0283 | 1244947.0274 | 2639201.7971 | 1244952.4045 | 2639193.0848 | 1244956.7203
57 | 2639158.2617 | 1244975.0715 | 2639172.8042 | 1244967.6009 | 2639174.5844 | 1244966.6387
58 | 2639213.1589 | 1244946.9649 | 2639213.0283 | 1244947.0274
59 | 2639158.2617 | 1244975.0715 | 2639152.3321 | 1244978.1176
60 | 2639213.1589 | 1244946.9649 | 2639202.6041 | 1244928.6054 | 2639200.0744 | 1244922.6737 | 2639200.0744 | 1244922.6737
61 | 2639213.1589 | 1244946.9649 | 2639220.7185 | 1244944.0685 | 2639229.291 | 1244940.2712
62 | 2639336.3849 | 1245199.2454 | 2639331.5528 | 1245197.8776
63 | 2639123.7043 | 1244992.2086 | 2639132.5023 | 1244988.3043 | 2639152.3321 | 1244978.1176
64 | 2639200.0744 | 1244922.6737 | 2639214.5934 | 1244915.9105
65 | 2639229.291 | 1244940.2712 | 2639232.2102 | 1244938.9782
66 | 2639121.5903 | 1244993.1467 | 2639123.7043 | 1244992.2086
67 | 2639230.7161 | 1244908.4002 | 2639214.5934 | 1244915.9105
68 | 2639249.7611 | 1244932.6466 | 2639246.2335 | 1244933.8192 | 2639236.1014 | 1244937.2545 | 2639232.2102 | 1244938.9782
69 | 2639121.5903 | 1244993.1467 | 2639104.5667 | 1245000.7036
70 | 2639121.5903 | 1244993.1467 | 2639107.3446 | 1244971.463
71 | 2638896.2324 | 1245052.5609 | 2638887.4009 | 1245050.5015 | 2638883.5851 | 1245049.1401
72 | 2638869.3938 | 1245044.3003 | 2638869.9039 | 1245044.5052 | 2638878.7022 | 1245047.3981 | 2638883.5851 | 1245049.1401
73 | 2638896.2324 | 1245052.5609 | 2638907.9596 | 1245055.2955
74 | 2638869.3938 | 1245044.3003 | 2638858.2011 | 1245039.8034 | 2638858.1071 | 1245039.7598
75 | 2638912.1938 | 1245056.2829 | 2638907.9596 | 1245055.2955
76 | 2638858.1071 | 1245039.7598 | 2638845.6969 | 1245034.0067 | 2638837.7035 | 1245030.4965 | 2638828.7946 | 1245025.8321
77 | 2638912.1938 | 1245056.2829 | 2638918.7006 | 1245057.8002 | 2638920.1616 | 1245058.1066
78 | 2638815.9982 | 1245018.7025 | 2638821.2007 | 1245021.505 | 2638827.4029 | 1245025.1034 | 2638828.7946 | 1245025.8321
79 | 2638932.5037 | 1245060.695 | 2638920.1616 | 1245058.1066
80 | 2638815.9982 | 1245018.7025 | 2638813.1027 | 1245025.8993 | 2638808.9038 | 1245038.2524
81 | 2638815.9982 | 1245018.7025 | 2638821.6993 | 1245006.4984 | 2638830.2375 | 1244994.5548
82 | 2638932.5037 | 1245060.695 | 2638934.8999 | 1245061.1975 | 2638941.3316 | 1245063.0038
83 | 2638804.0997 | 1245054.3035 | 2638807.9027 | 1245041.1976 | 2638808.9038 | 1245038.2524
84 | 2638842.7086 | 1244976.7285 | 2638839.0012 | 1244982.2957 | 2638830.2375 | 1244994.5548
85 | 2638842.7086 | 1244976.7285 | 2638855.8729 | 1244956.96
86 | 2638830.0146 | 1245099.4151 | 2638846.897 | 1245104.6051 | 2638855.1993 | 1245107.3844
87 | 2638830.0146 | 1245099.4151 | 2638823.8013 | 1245097.505 | 2638818.5616 | 1245110.8789
88 | 2638871.0489 | 1245112.6904 | 2638855.1993 | 1245107.3844
89 | 2638811.7406 | 1245128.529 | 2638816.2021 | 1245116.9013 | 2638818.5616 | 1245110.8789
90 | 2638871.0489 | 1245112.6904 | 2638879.3062 | 1245115.4547
91 | 2638811.7406 | 1245128.529 | 2638809.5748 | 1245134.1734
92 | 2638879.3062 | 1245115.4547 | 2638879.5651 | 1245115.5414
93 | 2638798.701 | 1245162.4055 | 2638802.1976 | 1245153.4003 | 2638809.5748 | 1245134.1734
94 | 2638879.5651 | 1245115.5414 | 2638892.899 | 1245120.0052 | 2638893.3134 | 1245120.169
95 | 2638796.6831 | 1245167.1288 | 2638798.701 | 1245162.4055
96 | 2638798.701 | 1245162.4055 | 2638805.8005 | 1245165.0981 | 2638816.6313 | 1245169.3523
97 | 2638893.3134 | 1245120.169 | 2638903.3555 | 1245124.1391
98 | 2638796.6831 | 1245167.1288 | 2638783.3181 | 1245160.3457
99 | 2638796.6831 | 1245167.1288 | 2638790.8978 | 1245174.8961 | 2638787.502 | 1245178.8987 | 2638781.9133 | 1245183.6078
100 | 2638816.6313 | 1245169.3523 | 2638816.9229 | 1245169.4669
101 | 2639230.7161 | 1244908.4002 | 2639239.8171 | 1244904.1608
102 | 2639249.7611 | 1244932.6466 | 2639266.9589 | 1244926.9295 | 2639270.4822 | 1244925.7546
103 | 2639350.6153 | 1245203.2414 | 2639348.2881 | 1245202.6148 | 2639336.3849 | 1245199.2454
104 | 2639376.369 | 1245210.175 | 2639350.6153 | 1245203.2414
105 | 2638822.719 | 1245229.5539 | 2638813.7009 | 1245237.0968 | 2638799.7671 | 1245246.3185
106 | 2638822.719 | 1245229.5539 | 2638827.8005 | 1245225.3035 | 2638836.7031 | 1245218.0014 | 2638840.8731 | 1245214.0518
107 | 2638862.7972 | 1245184.806 | 2638861.6019 | 1245188.5006 | 2638860.9976 | 1245190.7981 | 2638857.7029 | 1245195.5019 | 2638853.3968 | 1245201.1996 | 2638846.0996 | 1245209.1015 | 2638840.8731 | 1245214.0518
108 | 2638862.7972 | 1245184.806 | 2638857.8019 | 1245184.9956 | 2638850.1036 | 1245182.5993 | 2638842.611 | 1245179.6132
109 | 2638862.7972 | 1245184.806 | 2638865.6974 | 1245183.8021 | 2638869.1985 | 1245182.2017 | 2638873.2043 | 1245178.5033 | 2638883.8167 | 1245165.669
110 | 2638839.4796 | 1245178.3652 | 2638842.611 | 1245179.6132
111 | 2638838.5054 | 1245177.9769 | 2638839.4796 | 1245178.3652
112 | 2638816.9229 | 1245169.4669 | 2638832.8018 | 1245175.7038 | 2638838.5054 | 1245177.9769
113 | 2638914.3998 | 1245129.4967 | 2638910.6007 | 1245127.0035 | 2638903.3555 | 1245124.1391
114 | 2638914.3998 | 1245129.4967 | 2638917.7001 | 1245125.1043 | 2638926.9284 | 1245115.553
115 | 2638935.1984 | 1245106.7428 | 2638932.1002 | 1245110.2001 | 2638926.9284 | 1245115.553
116 | 2639104.5667 | 1245000.7036 | 2639099.4028 | 1245002.9959 | 2639090.041 | 1245007.723
117 | 2639088.0996 | 1244955.6029 | 2639094.1892 | 1244951.439 | 2639107.3446 | 1244971.463
118 | 2639073.3103 | 1245016.1711 | 2639090.041 | 1245007.723
119 | 2639081.6433 | 1244960.0175 | 2639088.0996 | 1244955.6029
120 | 2639073.3103 | 1245016.1711 | 2639072.0401 | 1245016.8124
121 | 2639072.0401 | 1245016.8124 | 2639068.2991 | 1245018.7014 | 2639056.7341 | 1245023.9327
122 | 2638935.4086 | 1245106.5083 | 2638935.1984 | 1245106.7428
123 | 2639045.7234 | 1245028.3735 | 2639048.4383 | 1245027.3328
124 | 2639048.4383 | 1245027.3328 | 2639053.5446 | 1245025.3754 | 2639056.7341 | 1245023.9327
125 | 2638781.9133 | 1245183.6078 | 2638781.204 | 1245184.2055 | 2638780.0325 | 1245185.2108
126 | 2638763.0851 | 1245199.807 | 2638764.8989 | 1245198.1971 | 2638780.0325 | 1245185.2108
127 | 2638760.4259 | 1245202.1671 | 2638763.0851 | 1245199.807
128 | 2638724.4067 | 1245234.0145 | 2638740.1024 | 1245220.2052 | 2638745.4986 | 1245215.4158
129 | 2638745.7983 | 1245215.1498 | 2638745.4986 | 1245215.4158
130 | 2638760.4259 | 1245202.1671 | 2638745.7983 | 1245215.1498

## bus_geodata
| x | y | coords
0 | 2638973.3762 | 1245003.7637
1 | 2638981.2713 | 1245014.0497
2 | 2638968.5942 | 1244997.2212
3 | 2638965.2046 | 1245000.2342
4 | 2638955.6252 | 1244980.0034
5 | 2638998.3412 | 1245036.1752
6 | 2638988.8084 | 1245029.973
7 | 2639012.6675 | 1245041.7507
8 | 2638947.6216 | 1245011.9487
9 | 2638974.0133 | 1245010.4664
10 | 2638950.2641 | 1244973.1074
11 | 2639009.3017 | 1245051.5017
12 | 2639019.2188 | 1245038.5972
13 | 2639035.9997 | 1245087.3597
14 | 2638974.1859 | 1245073.3872
15 | 2638945.5598 | 1244976.1229
16 | 2638930.7427 | 1244996.9616
17 | 2639032.1569 | 1245033.574
18 | 2639043.3534 | 1245097.5556
19 | 2638965.804 | 1245073.4971
20 | 2638921.9798 | 1244947.1828
21 | 2638925.2227 | 1244943.5016
22 | 2638909.19 | 1244963.0426
23 | 2638919.7243 | 1245004.9384
24 | 2638914.9109 | 1244978.6685
25 | 2638910.1526 | 1244926.7766
26 | 2639050.7836 | 1245274.6252
27 | 2639058.6914 | 1245267.8559
28 | 2639048.0053 | 1245277.0035
29 | 2639125.7029 | 1245236.8776
30 | 2639141.7469 | 1245252.1861
31 | 2639183.2497 | 1245270.6197
32 | 2639083.6376 | 1245191.8936
33 | 2639137.4064 | 1245170.3668
34 | 2639157.0946 | 1245175.0885
35 | 2639163.8094 | 1245172.3657
36 | 2639212.9879 | 1245278.8052
37 | 2639255.2675 | 1245176.9054
38 | 2639234.4907 | 1245172.1602
39 | 2639280.2341 | 1245182.6179
40 | 2639234.2145 | 1245172.0971
41 | 2639306.9422 | 1245190.8454
42 | 2639275.1241 | 1245201.7961
43 | 2639217.556 | 1245168.4097
44 | 2639311.8464 | 1245192.2675
45 | 2639263.4396 | 1245237.2821
46 | 2639192.3891 | 1245165.3817
47 | 2639254.8678 | 1245256.6398
48 | 2639233.6995 | 1245283.3984
49 | 2639174.9712 | 1244966.4297
50 | 2639193.0848 | 1244956.7203
51 | 2639174.5844 | 1244966.6387
52 | 2639213.0283 | 1244947.0274
53 | 2639158.2617 | 1244975.0715
54 | 2639213.1589 | 1244946.9649
55 | 2639331.5528 | 1245197.8776
56 | 2639152.3321 | 1244978.1176
57 | 2639200.0744 | 1244922.6737
58 | 2639229.291 | 1244940.2712
59 | 2639123.7043 | 1244992.2086
60 | 2639214.5934 | 1244915.9105
61 | 2639232.2102 | 1244938.9782
62 | 2639121.5903 | 1244993.1467
63 | 2638883.5851 | 1245049.1401
64 | 2638896.2324 | 1245052.5609
65 | 2638869.3938 | 1245044.3003
66 | 2638907.9596 | 1245055.2955
67 | 2638858.1071 | 1245039.7598
68 | 2638912.1938 | 1245056.2829
69 | 2638828.7946 | 1245025.8321
70 | 2638920.1616 | 1245058.1066
71 | 2638815.9982 | 1245018.7025
72 | 2638932.5037 | 1245060.695
73 | 2638808.9038 | 1245038.2524
74 | 2638830.2375 | 1244994.5548
75 | 2638855.8729 | 1244956.96
76 | 2638842.7086 | 1244976.7285
77 | 2638804.0997 | 1245054.3035
78 | 2638830.0146 | 1245099.4151
79 | 2638855.1993 | 1245107.3844
80 | 2638818.5616 | 1245110.8789
81 | 2638871.0489 | 1245112.6904
82 | 2638811.7406 | 1245128.529
83 | 2638879.3062 | 1245115.4547
84 | 2638809.5748 | 1245134.1734
85 | 2638879.5651 | 1245115.5414
86 | 2638798.701 | 1245162.4055
87 | 2638893.3134 | 1245120.169
88 | 2638796.6831 | 1245167.1288
89 | 2638816.6313 | 1245169.3523
90 | 2639230.7161 | 1244908.4002
91 | 2639249.7611 | 1244932.6466
92 | 2639336.3849 | 1245199.2454
93 | 2639350.6153 | 1245203.2414
94 | 2639239.8171 | 1244904.1608
95 | 2639270.4822 | 1244925.7546
96 | 2638822.719 | 1245229.5539
97 | 2638799.7671 | 1245246.3185
98 | 2638840.8731 | 1245214.0518
99 | 2638862.7972 | 1245184.806
100 | 2638842.611 | 1245179.6132
101 | 2638883.8167 | 1245165.669
102 | 2638839.4796 | 1245178.3652
103 | 2638838.5054 | 1245177.9769
104 | 2638914.3998 | 1245129.4967
105 | 2638903.3555 | 1245124.1391
106 | 2638926.9284 | 1245115.553
107 | 2639020.9976 | 1245124.9962
108 | 2639376.369 | 1245210.175
109 | 2638941.3316 | 1245063.0038
110 | 2639104.5667 | 1245000.7036
111 | 2639107.3446 | 1244971.463
112 | 2639090.041 | 1245007.723
113 | 2639088.0996 | 1244955.6029
114 | 2639073.3103 | 1245016.1711
115 | 2639081.6433 | 1244960.0175
116 | 2639072.0401 | 1245016.8124
117 | 2638935.1984 | 1245106.7428
118 | 2638935.4086 | 1245106.5083
119 | 2638816.9229 | 1245169.4669
120 | 2639045.7234 | 1245028.3735
121 | 2639048.4383 | 1245027.3328
122 | 2639056.7341 | 1245023.9327
123 | 2638783.3181 | 1245160.3457
124 | 2638781.9133 | 1245183.6078
125 | 2638908.7347 | 1245012.8944
126 | 2638780.0325 | 1245185.2108
127 | 2638763.0851 | 1245199.807
128 | 2638724.4067 | 1245234.0145
129 | 2638745.4986 | 1245215.4158
130 | 2638745.7983 | 1245215.1498
131 | 2638760.4259 | 1245202.1671
132 | 2639009.3017 | 1245051.5017

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99294 | -0.1353 | 0.00066234 | 0.000166
1 | 0.99291 | -0.13572 | 0.0018314 | 0.00045899
2 | 0.99295 | -0.13494 | 0 | 0
3 | 0.99297 | -0.13456 | 0 | 0
4 | 0.99291 | -0.13579 | 0.0014382 | 0.00036045
5 | 0.99412 | -0.11231 | 0 | 0
6 | 0.99364 | -0.12163 | 0.0034276 | 0.00085903
7 | 0.99445 | -0.10595 | 0 | 0
8 | 0.99272 | -0.13953 | 0.0011302 | 0.00028325
9 | 0.99319 | -0.13027 | 0.0020283 | 0.00050834
10 | 0.9929 | -0.13592 | 0 | 0
11 | 0.99552 | -0.085443 | 0 | 0
12 | 0.99406 | -0.11348 | 0.0052025 | 0.0013039
13 | 0.99901 | -0.018873 | 0.0021866 | 0.00054802
14 | 0.99216 | -0.14977 | 0.0021221 | 0.00053184
15 | 0.9929 | -0.136 | 0.0008022 | 0.00020105
16 | 0.99246 | -0.14453 | 0 | 0
17 | 0.99338 | -0.1266 | 0.0046823 | 0.0011735
18 | 1 | 0 | -0.26393 | -0.06687
19 | 0.99149 | -0.16275 | 0 | 0
20 | 0.99225 | -0.14865 | 0 | 0
21 | 0.99224 | -0.14872 | 0 | 0
22 | 0.99226 | -0.14838 | 0.004035 | 0.0010113
23 | 0.99238 | -0.14615 | 0.0014281 | 0.00035791
24 | 0.99234 | -0.14682 | 0.00057395 | 0.00014385
25 | 0.99223 | -0.14901 | 0.00074142 | 0.00018582
26 | 0.97963 | -0.39251 | 0.0011458 | 0.00028716
27 | 0.97964 | -0.39219 | 0.0006028 | 0.00015108
28 | 0.97962 | -0.39255 | 0.0005709 | 0.00014308
29 | 0.9798 | -0.38907 | 0 | 0
30 | 0.97985 | -0.38814 | 0.0030116 | 0.00075477
31 | 0.98007 | -0.38372 | 0.0039715 | 0.00099535
32 | 0.99234 | -0.14567 | 0.0005777 | 0.00014478
33 | 0.99237 | -0.14508 | 0 | 0
34 | 0.99104 | -0.17069 | 0 | 0
35 | 0.99058 | -0.17955 | 0.006205 | 0.0015551
36 | 0.98034 | -0.37851 | 0.013959 | 0.0034985
37 | 0.98528 | -0.28196 | 0.00094532 | 0.00023692
38 | 0.98641 | -0.26012 | 0.0015642 | 0.00039202
39 | 0.98395 | -0.30783 | 0 | 0
40 | 0.98642 | -0.25983 | 0.0023463 | 0.00058804
41 | 0.98343 | -0.31807 | 0.00074125 | 0.00018577
42 | 0.9833 | -0.32065 | 0.002279 | 0.00057118
43 | 0.98739 | -0.24119 | 0.0016114 | 0.00040386
44 | 0.98334 | -0.31987 | 0.0067827 | 0.0016999
45 | 0.98214 | -0.34331 | 0.0041791 | 0.0010474
46 | 0.98885 | -0.21281 | 0 | 0
47 | 0.98156 | -0.35457 | 0.0061204 | 0.0015339
48 | 0.9808 | -0.36956 | 0 | 0
49 | 0.98883 | -0.21466 | 0.00065138 | 0.00016325
50 | 0.98847 | -0.22161 | 0.00081225 | 0.00020357
51 | 0.98884 | -0.2145 | 0.00061542 | 0.00015424
52 | 0.98811 | -0.2288 | 0.002081 | 0.00052154
53 | 0.98918 | -0.20787 | 0.00092254 | 0.00023121
54 | 0.9881 | -0.22884 | 0 | 0
55 | 0.9831 | -0.32461 | 0.0071825 | 0.0018001
56 | 0.98931 | -0.20536 | 0.001036 | 0.00025964
57 | 0.98788 | -0.23321 | 0.0041372 | 0.0010369
58 | 0.98799 | -0.2311 | 0.001353 | 0.0003391
59 | 0.98996 | -0.19275 | 0.00067358 | 0.00016881
60 | 0.98781 | -0.23455 | 0.002027 | 0.00050801
61 | 0.98797 | -0.23143 | 0.0021497 | 0.00053878
62 | 0.99001 | -0.19181 | 0 | 0
63 | 0.98948 | -0.20175 | 0.0022247 | 0.00055755
64 | 0.98972 | -0.19706 | 0.0017086 | 0.00042823
65 | 0.98923 | -0.20653 | 0.0017118 | 0.00042902
66 | 0.98996 | -0.19238 | 0.0013877 | 0.00034778
67 | 0.98905 | -0.21003 | 0.0046305 | 0.0011605
68 | 0.99005 | -0.19059 | 0.0011572 | 0.00029003
69 | 0.98871 | -0.21671 | 0.0016008 | 0.00040119
70 | 0.99023 | -0.18705 | 0.0017897 | 0.00044855
71 | 0.98857 | -0.21931 | 0 | 0
72 | 0.99054 | -0.18119 | 0.0018923 | 0.00047425
73 | 0.98847 | -0.22138 | 0.0033151 | 0.00083085
74 | 0.98846 | -0.2215 | 0.0020801 | 0.00052132
75 | 0.9884 | -0.22263 | 0.00056264 | 0.00014101
76 | 0.98841 | -0.22239 | 0.0017214 | 0.00043143
77 | 0.98843 | -0.22205 | 0.0022563 | 0.00056549
78 | 0.98381 | -0.31139 | 0.0029793 | 0.00074668
79 | 0.98483 | -0.29148 | 0.0024607 | 0.00061672
80 | 0.98306 | -0.32602 | 0.0023804 | 0.00059659
81 | 0.98551 | -0.27817 | 0.00197 | 0.00049374
82 | 0.98242 | -0.3385 | 0.0022735 | 0.00056979
83 | 0.98589 | -0.27093 | 0.0012518 | 0.00031372
84 | 0.98223 | -0.34224 | 0.0022312 | 0.0005592
85 | 0.9859 | -0.2707 | 0.0012534 | 0.00031414
86 | 0.98133 | -0.35976 | 0 | 0
87 | 0.98655 | -0.25801 | 0.0016748 | 0.00041974
88 | 0.98126 | -0.36105 | 0 | 0
89 | 0.98101 | -0.36606 | 0.0017843 | 0.00044719
90 | 0.98777 | -0.23541 | 0.0013031 | 0.00032659
91 | 0.98791 | -0.23268 | 0.00126 | 0.00031579
92 | 0.98307 | -0.32512 | 0.0022303 | 0.00055898
93 | 0.98302 | -0.32602 | 0.0024765 | 0.00062068
94 | 0.98775 | -0.23565 | 0.0013807 | 0.00034604
95 | 0.98786 | -0.23364 | 0.0024692 | 0.00061885
96 | 0.9802 | -0.38186 | 0.00148 | 0.00037091
97 | 0.98014 | -0.38313 | 0.002461 | 0.00061679
98 | 0.98029 | -0.38015 | 0.0019479 | 0.0004882
99 | 0.98049 | -0.37619 | 0 | 0
100 | 0.98066 | -0.37298 | 0.0017823 | 0.00044669
101 | 0.98042 | -0.3775 | 0.0024925 | 0.00062467
102 | 0.98069 | -0.37236 | 0.0023441 | 0.00058749
103 | 0.9807 | -0.37212 | 0.0016967 | 0.00042525
104 | 0.98765 | -0.23679 | 0 | 0
105 | 0.98706 | -0.24824 | 0.0014461 | 0.00036243
106 | 0.98855 | -0.21937 | 0.00075799 | 0.00018997
107 | 0.99943 | -0.010988 | 0.017801 | 0.0044614
108 | 0.983 | -0.32647 | 0.00092075 | 0.00023076
109 | 0.99077 | -0.17664 | 0.0011849 | 0.00029695
110 | 0.99051 | -0.18207 | 0.0014252 | 0.00035718
111 | 0.98986 | -0.19481 | 0.00087542 | 0.0002194
112 | 0.99097 | -0.17324 | 0.0031781 | 0.0007965
113 | 0.98969 | -0.19795 | 0.0012511 | 0.00031356
114 | 0.99155 | -0.16194 | 0.0034212 | 0.00085743
115 | 0.98966 | -0.19856 | 0.0043861 | 0.0010993
116 | 0.9916 | -0.161 | 0.0040975 | 0.0010269
117 | 0.98914 | -0.20802 | 0.0011626 | 0.00029137
118 | 0.98915 | -0.20772 | 0.0025018 | 0.00062701
119 | 0.981 | -0.36615 | 0.0020939 | 0.00052477
120 | 0.99273 | -0.13915 | 0.0014413 | 0.00036122
121 | 0.9926 | -0.14159 | 0.0034217 | 0.00085757
122 | 0.99224 | -0.14858 | 0.002489 | 0.00062381
123 | 0.98123 | -0.36175 | 0.0025595 | 0.00064146
124 | 0.98103 | -0.36564 | 0.0011598 | 0.00029068
125 | 0.99231 | -0.14743 | 0.0053156 | 0.0013322
126 | 0.98101 | -0.36609 | 0.00093185 | 0.00023354
127 | 0.98081 | -0.36985 | 0.0020552 | 0.00051508
128 | 0.98061 | -0.37379 | 0.002764 | 0.00069272
129 | 0.98069 | -0.37238 | 0.0019036 | 0.00047709
130 | 0.98069 | -0.37234 | 0.0010426 | 0.0002613
131 | 0.98079 | -0.37032 | 0.0015163 | 0.00038003
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0018314 | 0.00045885 | -0.0018314 | -0.00045899 | 3.6628e-08 | -1.4428e-07 | 0.0027445 | 0.0027446 | 0.0027446 | 0.99294 | -0.1353 | 0.99291 | -0.13572 | 0.75401
1 | -0.0024938 | -0.00062484 | 0.0024938 | 0.00062477 | 4.2442e-08 | -7.766e-08 | 0.0037371 | 0.0037371 | 0.0037371 | 0.99294 | -0.1353 | 0.99295 | -0.13494 | 1.0267
2 | -0.0047343 | -0.0011859 | 0.0047344 | 0.0011859 | 8.5463e-08 | -3.8746e-09 | 0.0070945 | 0.0070945 | 0.0070945 | 0.99295 | -0.13494 | 0.99297 | -0.13456 | 1.949
3 | 0.0022405 | 0.0005611 | -0.0022404 | -0.00056132 | 9.1136e-08 | -2.2053e-07 | 0.0033574 | 0.0033575 | 0.0033575 | 0.99295 | -0.13494 | 0.99291 | -0.13579 | 0.92239
4 | 0.013232 | 0.0033172 | -0.013229 | -0.0033155 | 3.1303e-06 | 1.7288e-06 | 0.019829 | 0.019829 | 0.019829 | 0.99297 | -0.13456 | 0.99272 | -0.13953 | 5.4476
5 | -0.017966 | -0.0045031 | 0.01797 | 0.0045053 | 3.6701e-06 | 2.1742e-06 | 0.026924 | 0.026924 | 0.026924 | 0.99297 | -0.13456 | 0.99319 | -0.13027 | 7.3966
6 | 0.00080221 | 0.00020087 | -0.0008022 | -0.00020098 | 4.734e-09 | -1.0995e-07 | 0.0012022 | 0.0012022 | 0.0012022 | 0.99291 | -0.13579 | 0.9929 | -0.13592 | 0.33027
7 | 0.023445 | 0.005884 | -0.023434 | -0.0058776 | 1.0416e-05 | 6.3743e-06 | 0.035095 | 0.035095 | 0.035095 | 0.99412 | -0.11231 | 0.99364 | -0.12163 | 9.6416
8 | -0.023445 | -0.005884 | 0.023452 | 0.0058883 | 7.1087e-06 | 4.35e-06 | 0.035095 | 0.035095 | 0.035095 | 0.99412 | -0.11231 | 0.99445 | -0.10595 | 9.6415
9 | 0.020007 | 0.0050186 | -0.019998 | -0.0050136 | 8.2433e-06 | 4.9587e-06 | 0.029962 | 0.029962 | 0.029962 | 0.99364 | -0.12163 | 0.99319 | -0.13027 | 8.2314
10 | -0.082413 | -0.020745 | 0.082494 | 0.020796 | 8.0866e-05 | 5.157e-05 | 0.12335 | 0.12335 | 0.12335 | 0.99445 | -0.10595 | 0.99552 | -0.085443 | 33.8867
11 | 0.058961 | 0.014856 | -0.05894 | -0.014843 | 2.1236e-05 | 1.3497e-05 | 0.088252 | 0.088252 | 0.088252 | 0.99445 | -0.10595 | 0.99406 | -0.11348 | 24.2452
12 | 0.012099 | 0.0030322 | -0.012096 | -0.0030307 | 2.8807e-06 | 1.5417e-06 | 0.018135 | 0.018135 | 0.018135 | 0.99272 | -0.13953 | 0.99246 | -0.14453 | 4.9822
13 | 0.0008022 | 0.00020098 | -0.0008022 | -0.00020105 | 3.0222e-09 | -7.0184e-08 | 0.0012022 | 0.0012022 | 0.0012022 | 0.9929 | -0.13592 | 0.9929 | -0.136 | 0.33028
14 | -0.17105 | -0.043312 | 0.1716 | 0.043662 | 0.00054866 | 0.00034997 | 0.25583 | 0.25583 | 0.25583 | 0.99552 | -0.085443 | 0.99901 | -0.018873 | 35.1414
15 | 0.088557 | 0.022515 | -0.088284 | -0.022341 | 0.00027346 | 0.00017448 | 0.13248 | 0.13248 | 0.13248 | 0.99552 | -0.085443 | 0.99216 | -0.14977 | 36.3961
16 | 0.053737 | 0.013539 | -0.053704 | -0.013518 | 3.3703e-05 | 2.139e-05 | 0.080465 | 0.080465 | 0.080465 | 0.99406 | -0.11348 | 0.99338 | -0.1266 | 22.1057
17 | -0.17379 | -0.04421 | 0.17394 | 0.04431 | 0.00015822 | 0.00010093 | 0.25909 | 0.25909 | 0.25909 | 0.99901 | -0.018873 | 1 | 0 | 35.5887
18 | 0.086162 | 0.021809 | -0.086108 | -0.021775 | 5.3674e-05 | 3.4241e-05 | 0.1293 | 0.1293 | 0.1293 | 0.99216 | -0.14977 | 0.99149 | -0.16275 | 35.5218
19 | 0.0067446 | 0.0016903 | -0.006744 | -0.0016902 | 5.2162e-07 | 1.5808e-07 | 0.010112 | 0.010112 | 0.010112 | 0.99246 | -0.14453 | 0.99238 | -0.14615 | 2.7781
20 | 0.0053513 | 0.0013404 | -0.0053507 | -0.0013403 | 5.8398e-07 | 6.1164e-08 | 0.008023 | 0.0080232 | 0.0080232 | 0.99246 | -0.14453 | 0.99234 | -0.14682 | 2.2042
21 | 0.049021 | 0.012344 | -0.048992 | -0.012325 | 2.9395e-05 | 1.8625e-05 | 0.073451 | 0.073451 | 0.073451 | 0.99338 | -0.1266 | 0.99273 | -0.13915 | 20.1789
22 | 0.070523 | 0.018093 | -0.07003 | -0.017779 | 0.00049258 | 0.0003137 | 0.10509 | 0.10509 | 0.10509 | 1 | 0 | 0.99237 | -0.14508 | 28.8703
23 | 0.01781 | 0.0044669 | -0.017801 | -0.0044614 | 9.3233e-06 | 5.5028e-06 | 0.026503 | 0.026503 | 0.026503 | 1 | 0 | 0.99943 | -0.010988 | 7.2812
24 | 0.029285 | 0.0073598 | -0.029266 | -0.0073477 | 1.9403e-05 | 1.2073e-05 | 0.043958 | 0.043958 | 0.043958 | 0.99149 | -0.16275 | 0.99077 | -0.17664 | 12.0763
25 | 0.056823 | 0.014415 | -0.056701 | -0.014337 | 0.00012258 | 7.7871e-05 | 0.085342 | 0.085342 | 0.085342 | 0.99149 | -0.16275 | 0.98915 | -0.20772 | 23.4456
26 | 0.00074144 | 0.00018547 | -0.00074143 | -0.00018553 | 2.2712e-09 | -6.1838e-08 | 0.0011118 | 0.0011118 | 0.0011118 | 0.99225 | -0.14865 | 0.99224 | -0.14872 | 0.30544
27 | -0.00074144 | -0.00018547 | 0.00074144 | 0.00018521 | 9.4429e-09 | -2.5713e-07 | 0.0011118 | 0.0011117 | 0.0011118 | 0.99225 | -0.14865 | 0.99226 | -0.14838 | 0.30543
28 | 0.00074143 | 0.00018553 | -0.00074142 | -0.00018582 | 1.0436e-08 | -2.8411e-07 | 0.0011118 | 0.0011119 | 0.0011119 | 0.99224 | -0.14872 | 0.99223 | -0.14901 | 0.30546
29 | -0.0047764 | -0.0011965 | 0.0047768 | 0.0011965 | 3.5636e-07 | -1.1216e-08 | 0.0071626 | 0.0071625 | 0.0071626 | 0.99226 | -0.14838 | 0.99234 | -0.14682 | 1.9677
30 | 0.005316 | 0.0013323 | -0.0053156 | -0.0013322 | 3.2326e-07 | 3.161e-08 | 0.007971 | 0.0079711 | 0.0079711 | 0.99238 | -0.14615 | 0.99231 | -0.14743 | 2.1899
31 | -0.0017167 | -0.0004302 | 0.0017167 | 0.00043008 | 2.6541e-08 | -1.1407e-07 | 0.0026076 | 0.0026075 | 0.0026076 | 0.97963 | -0.39251 | 0.97964 | -0.39219 | 0.71636
32 | 0.0005709 | 0.00014304 | -0.0005709 | -0.00014308 | 1.0313e-09 | -4.5385e-08 | 0.00086716 | 0.00086718 | 0.00086718 | 0.97963 | -0.39251 | 0.97962 | -0.39255 | 0.23823
33 | -0.0023195 | -0.00058116 | 0.0023199 | 0.00058045 | 3.436e-07 | -7.0975e-07 | 0.0035231 | 0.0035228 | 0.0035231 | 0.97964 | -0.39219 | 0.9798 | -0.38907 | 0.96789
34 | -0.0023199 | -0.00058045 | 0.00232 | 0.00058023 | 1.0349e-07 | -2.1387e-07 | 0.0035228 | 0.0035227 | 0.0035228 | 0.9798 | -0.38907 | 0.97985 | -0.38814 | 0.9678
35 | -0.0053315 | -0.001335 | 0.0053326 | 0.0013351 | 1.1209e-06 | 1.4284e-07 | 0.0080961 | 0.0080959 | 0.0080961 | 0.97985 | -0.38814 | 0.98007 | -0.38372 | 2.2242
36 | -0.0093041 | -0.0023305 | 0.0093064 | 0.0023316 | 2.3091e-06 | 1.0888e-06 | 0.014126 | 0.014126 | 0.014126 | 0.98007 | -0.38372 | 0.98034 | -0.37851 | 3.8807
37 | -0.0005777 | -0.00014478 | 0.00057771 | 0.00014405 | 1.6293e-08 | -7.3785e-07 | 0.00086626 | 0.00086599 | 0.00086626 | 0.99234 | -0.14567 | 0.99237 | -0.14508 | 0.23798
38 | 0.069452 | 0.017635 | -0.069367 | -0.017581 | 8.5479e-05 | 5.4436e-05 | 0.10422 | 0.10422 | 0.10422 | 0.99237 | -0.14508 | 0.99104 | -0.17069 | 28.6324
39 | 0.069367 | 0.017581 | -0.069337 | -0.017562 | 2.9515e-05 | 1.8796e-05 | 0.10422 | 0.10422 | 0.10422 | 0.99104 | -0.17069 | 0.99058 | -0.17955 | 28.6324
40 | 0.063132 | 0.016007 | -0.063032 | -0.015943 | 0.00010078 | 6.4113e-05 | 0.094901 | 0.094901 | 0.094901 | 0.99058 | -0.17955 | 0.98885 | -0.21281 | 26.0718
41 | -0.023266 | -0.0058301 | 0.023276 | 0.0058362 | 9.9275e-06 | 6.0858e-06 | 0.035314 | 0.035314 | 0.035314 | 0.98034 | -0.37851 | 0.9808 | -0.36956 | 9.7015
42 | -0.057309 | -0.014431 | 0.057369 | 0.014469 | 5.99e-05 | 3.8064e-05 | 0.086574 | 0.086574 | 0.086574 | 0.98528 | -0.28196 | 0.98641 | -0.26012 | 23.7841
43 | 0.056363 | 0.014194 | -0.056294 | -0.01415 | 6.9631e-05 | 4.4238e-05 | 0.085146 | 0.085147 | 0.085147 | 0.98528 | -0.28196 | 0.98395 | -0.30783 | 23.3919
44 | -0.058933 | -0.014861 | 0.058934 | 0.014861 | 8.4048e-07 | 5.3429e-07 | 0.088934 | 0.088934 | 0.088934 | 0.98641 | -0.26012 | 0.98642 | -0.25983 | 24.4323
45 | 0.020349 | 0.0051044 | -0.020339 | -0.0050984 | 9.9262e-06 | 5.998e-06 | 0.030775 | 0.030775 | 0.030775 | 0.98395 | -0.30783 | 0.98343 | -0.31807 | 8.4547
46 | 0.035945 | 0.0090453 | -0.035923 | -0.0090315 | 2.2006e-05 | 1.3832e-05 | 0.054372 | 0.054372 | 0.054372 | 0.98395 | -0.30783 | 0.9833 | -0.32065 | 14.9373
47 | -0.06128 | -0.01545 | 0.061335 | 0.015484 | 5.4712e-05 | 3.4798e-05 | 0.092473 | 0.092473 | 0.092473 | 0.98642 | -0.25983 | 0.98739 | -0.24119 | 25.4047
48 | 0.019598 | 0.0049126 | -0.019596 | -0.0049116 | 1.6838e-06 | 1.0128e-06 | 0.029653 | 0.029653 | 0.029653 | 0.98343 | -0.31807 | 0.98334 | -0.31987 | 8.1465
49 | 0.033644 | 0.0084603 | -0.033607 | -0.0084375 | 3.6372e-05 | 2.2804e-05 | 0.050923 | 0.050923 | 0.050923 | 0.9833 | -0.32065 | 0.98214 | -0.34331 | 13.9899
50 | -0.062946 | -0.015888 | 0.063032 | 0.015943 | 8.5676e-05 | 5.4508e-05 | 0.094901 | 0.094901 | 0.094901 | 0.98739 | -0.24119 | 0.98885 | -0.21281 | 26.0718
51 | 0.012813 | 0.0032117 | -0.01281 | -0.0032101 | 2.8887e-06 | 1.5889e-06 | 0.01939 | 0.01939 | 0.01939 | 0.98334 | -0.31987 | 0.9831 | -0.32461 | 5.3269
52 | 0.029428 | 0.0073901 | -0.029413 | -0.0073803 | 1.5791e-05 | 9.8385e-06 | 0.044592 | 0.044592 | 0.044592 | 0.98214 | -0.34331 | 0.98156 | -0.35457 | 12.2505
53 | 0.023292 | 0.0058464 | -0.023276 | -0.0058362 | 1.6637e-05 | 1.0198e-05 | 0.035313 | 0.035314 | 0.035314 | 0.98156 | -0.35457 | 0.9808 | -0.36956 | 9.7015
54 | 0.018989 | 0.0047631 | -0.018983 | -0.0047594 | 6.2941e-06 | 3.7647e-06 | 0.028577 | 0.028577 | 0.028577 | 0.98883 | -0.21466 | 0.98847 | -0.22161 | 7.8508
55 | -0.019641 | -0.0049264 | 0.019641 | 0.0049265 | 1.4402e-07 | 8.6532e-08 | 0.029557 | 0.029557 | 0.029557 | 0.98883 | -0.21466 | 0.98884 | -0.2145 | 8.1201
56 | 0.018171 | 0.0045558 | -0.018164 | -0.0045521 | 6.2221e-06 | 3.698e-06 | 0.027354 | 0.027354 | 0.027354 | 0.98847 | -0.22161 | 0.98811 | -0.2288 | 7.5149
57 | -0.020256 | -0.0050807 | 0.020263 | 0.0050846 | 6.4021e-06 | 3.8616e-06 | 0.030483 | 0.030483 | 0.030483 | 0.98884 | -0.2145 | 0.98918 | -0.20787 | 8.3745
58 | 0.016084 | 0.0040306 | -0.016083 | -0.0040306 | 3.184e-08 | 1.8523e-08 | 0.02422 | 0.02422 | 0.02422 | 0.98811 | -0.2288 | 0.9881 | -0.22884 | 6.654
59 | -0.021185 | -0.0053158 | 0.021188 | 0.0053173 | 2.5392e-06 | 1.5395e-06 | 0.031871 | 0.031871 | 0.031871 | 0.98918 | -0.20787 | 0.98931 | -0.20536 | 8.7557
60 | 0.0088503 | 0.002218 | -0.0088484 | -0.0022172 | 1.8402e-06 | 8.2397e-07 | 0.013328 | 0.013328 | 0.013328 | 0.9881 | -0.22884 | 0.98788 | -0.23321 | 3.6615
61 | 0.0072332 | 0.0018125 | -0.0072324 | -0.0018122 | 7.7737e-07 | 2.7375e-07 | 0.010893 | 0.010893 | 0.010893 | 0.9881 | -0.22884 | 0.98799 | -0.2311 | 2.9925
62 | 0.0056279 | 0.00141 | -0.0056278 | -0.00141 | 1.3665e-07 | 2.3781e-08 | 0.0085183 | 0.0085183 | 0.0085183 | 0.9831 | -0.32461 | 0.98307 | -0.32512 | 2.3402
63 | -0.022224 | -0.005577 | 0.022237 | 0.0055851 | 1.3376e-05 | 8.1504e-06 | 0.033429 | 0.033429 | 0.033429 | 0.98931 | -0.20536 | 0.98996 | -0.19275 | 9.1838
64 | 0.0047112 | 0.0011804 | -0.0047109 | -0.0011804 | 3.0247e-07 | -1.1475e-08 | 0.0070963 | 0.0070963 | 0.0070963 | 0.98788 | -0.23321 | 0.98781 | -0.23455 | 1.9495
65 | 0.0058794 | 0.0014731 | -0.0058793 | -0.0014731 | 9.3878e-08 | 1.9196e-08 | 0.0088549 | 0.0088549 | 0.0088549 | 0.98799 | -0.2311 | 0.98797 | -0.23143 | 2.4327
66 | -0.022911 | -0.0057539 | 0.022912 | 0.0057546 | 1.0288e-06 | 6.2867e-07 | 0.034441 | 0.034441 | 0.034441 | 0.98996 | -0.19275 | 0.99001 | -0.19181 | 9.4619
67 | 0.002684 | 0.00067236 | -0.0026838 | -0.00067251 | 1.0902e-07 | -1.579e-07 | 0.0040429 | 0.004043 | 0.004043 | 0.98781 | -0.23455 | 0.98777 | -0.23541 | 1.1107
68 | 0.0037296 | 0.00093433 | -0.0037294 | -0.00093443 | 2.2093e-07 | -9.7694e-08 | 0.0056171 | 0.0056172 | 0.0056172 | 0.98797 | -0.23143 | 0.98791 | -0.23268 | 1.5432
69 | -0.029426 | -0.0073872 | 0.02944 | 0.0073957 | 1.3666e-05 | 8.5064e-06 | 0.044233 | 0.044233 | 0.044233 | 0.99001 | -0.19181 | 0.99051 | -0.18207 | 12.1519
70 | 0.0065146 | 0.0016326 | -0.0065136 | -0.0016323 | 9.328e-07 | 2.6343e-07 | 0.0097916 | 0.0097917 | 0.0097917 | 0.99001 | -0.19181 | 0.98986 | -0.19481 | 2.69
71 | -0.020116 | -0.0050442 | 0.020121 | 0.0050469 | 4.5028e-06 | 2.7132e-06 | 0.030253 | 0.030253 | 0.030253 | 0.98948 | -0.20175 | 0.98972 | -0.19706 | 8.3112
72 | 0.017892 | 0.0044867 | -0.017888 | -0.0044843 | 4.0713e-06 | 2.4131e-06 | 0.026907 | 0.026907 | 0.026907 | 0.98948 | -0.20175 | 0.98923 | -0.20653 | 7.3921
73 | -0.021829 | -0.0054752 | 0.021834 | 0.0054781 | 4.8645e-06 | 2.9585e-06 | 0.032821 | 0.032821 | 0.032821 | 0.98972 | -0.19706 | 0.98996 | -0.19238 | 9.0169
74 | 0.016176 | 0.0040552 | -0.016173 | -0.0040537 | 2.7011e-06 | 1.5725e-06 | 0.024332 | 0.024332 | 0.024332 | 0.98923 | -0.20653 | 0.98905 | -0.21003 | 6.6847
75 | -0.023222 | -0.0058259 | 0.023224 | 0.0058271 | 1.9867e-06 | 1.2156e-06 | 0.034907 | 0.034907 | 0.034907 | 0.98996 | -0.19238 | 0.99005 | -0.19059 | 9.5899
76 | 0.011542 | 0.0028932 | -0.011539 | -0.0028912 | 3.6714e-06 | 1.9332e-06 | 0.017366 | 0.017366 | 0.017366 | 0.98905 | -0.21003 | 0.98871 | -0.21671 | 4.7708
77 | -0.024381 | -0.0061172 | 0.024385 | 0.0061197 | 4.1166e-06 | 2.5295e-06 | 0.036646 | 0.036646 | 0.036646 | 0.99005 | -0.19059 | 0.99023 | -0.18705 | 10.0677
78 | 0.009938 | 0.00249 | -0.0099368 | -0.0024894 | 1.229e-06 | 5.9871e-07 | 0.014957 | 0.014957 | 0.014957 | 0.98871 | -0.21671 | 0.98857 | -0.21931 | 4.109
79 | -0.026175 | -0.0065682 | 0.026182 | 0.0065728 | 7.3172e-06 | 4.5207e-06 | 0.039336 | 0.039336 | 0.039336 | 0.99023 | -0.18705 | 0.99054 | -0.18119 | 10.8066
80 | 0.0055721 | 0.0013963 | -0.0055715 | -0.0013962 | 5.4881e-07 | 8.4524e-08 | 0.0083871 | 0.0083872 | 0.0083872 | 0.98857 | -0.21931 | 0.98847 | -0.22138 | 2.3042
81 | 0.0043647 | 0.0010932 | -0.0043643 | -0.0010932 | 4.5564e-07 | -6.9287e-08 | 0.0065696 | 0.0065697 | 0.0065697 | 0.98857 | -0.21931 | 0.98846 | -0.2215 | 1.8049
82 | -0.028075 | -0.007047 | 0.028081 | 0.0070508 | 6.0901e-06 | 3.7801e-06 | 0.042178 | 0.042178 | 0.042178 | 0.99054 | -0.18119 | 0.99077 | -0.17664 | 11.5875
83 | 0.0022564 | 0.00056532 | -0.0022563 | -0.00056549 | 7.2501e-08 | -1.6839e-07 | 0.0033967 | 0.0033967 | 0.0033967 | 0.98847 | -0.22138 | 0.98843 | -0.22205 | 0.93317
84 | 0.0022842 | 0.00057193 | -0.0022841 | -0.00057214 | 9.6466e-08 | -2.1715e-07 | 0.0034384 | 0.0034385 | 0.0034385 | 0.98846 | -0.2215 | 0.98841 | -0.22239 | 0.94464
85 | -0.00056264 | -0.00014101 | 0.00056264 | 0.00014071 | 6.3894e-09 | -3.0032e-07 | 0.00084704 | 0.00084693 | 0.00084704 | 0.9884 | -0.22263 | 0.98841 | -0.22239 | 0.2327
86 | -0.041981 | -0.010556 | 0.042021 | 0.010581 | 3.9957e-05 | 2.5237e-05 | 0.063509 | 0.063509 | 0.063509 | 0.98381 | -0.31139 | 0.98483 | -0.29148 | 17.4476
87 | 0.039002 | 0.0098094 | -0.038975 | -0.0097922 | 2.7238e-05 | 1.7168e-05 | 0.059003 | 0.059003 | 0.059003 | 0.98381 | -0.31139 | 0.98306 | -0.32602 | 16.2097
88 | -0.044482 | -0.011198 | 0.04451 | 0.011216 | 2.8327e-05 | 1.7917e-05 | 0.067227 | 0.067227 | 0.067227 | 0.98483 | -0.29148 | 0.98551 | -0.27817 | 18.469
89 | 0.036594 | 0.0091956 | -0.036572 | -0.0091819 | 2.1779e-05 | 1.3699e-05 | 0.0554 | 0.0554 | 0.0554 | 0.98306 | -0.32602 | 0.98242 | -0.3385 | 15.2198
90 | -0.04648 | -0.01171 | 0.046496 | 0.01172 | 1.6093e-05 | 1.0188e-05 | 0.070202 | 0.070202 | 0.070202 | 0.98551 | -0.27817 | 0.98589 | -0.27093 | 19.2862
91 | 0.034299 | 0.0086121 | -0.034293 | -0.0086083 | 6.12e-06 | 3.8403e-06 | 0.051957 | 0.051957 | 0.051957 | 0.98242 | -0.3385 | 0.98223 | -0.34224 | 14.2738
92 | -0.047748 | -0.012034 | 0.047749 | 0.012034 | 5.321e-07 | 3.3706e-07 | 0.072091 | 0.072091 | 0.072091 | 0.98589 | -0.27093 | 0.9859 | -0.2707 | 19.8052
93 | 0.032062 | 0.0080491 | -0.032035 | -0.0080323 | 2.6771e-05 | 1.6751e-05 | 0.048576 | 0.048577 | 0.048577 | 0.98223 | -0.34224 | 0.98133 | -0.35976 | 13.3452
94 | -0.049002 | -0.012348 | 0.049032 | 0.012367 | 2.9776e-05 | 1.8871e-05 | 0.073983 | 0.073983 | 0.073983 | 0.9859 | -0.2707 | 0.98655 | -0.25801 | 20.3249
95 | 0.013939 | 0.0034944 | -0.013938 | -0.0034939 | 8.6028e-07 | 4.8571e-07 | 0.021137 | 0.021137 | 0.021137 | 0.98133 | -0.35976 | 0.98126 | -0.36105 | 5.8067
96 | 0.018096 | 0.0045379 | -0.01809 | -0.0045347 | 5.4296e-06 | 3.2321e-06 | 0.02744 | 0.02744 | 0.02744 | 0.98133 | -0.35976 | 0.98101 | -0.36606 | 7.5385
97 | -0.050707 | -0.012787 | 0.05073 | 0.012802 | 2.3704e-05 | 1.5032e-05 | 0.076509 | 0.076509 | 0.076509 | 0.98655 | -0.25801 | 0.98706 | -0.24824 | 21.0189
98 | 0.0025595 | 0.00064133 | -0.0025595 | -0.00064146 | 8.4671e-08 | -1.3513e-07 | 0.0038813 | 0.0038814 | 0.0038814 | 0.98126 | -0.36105 | 0.98123 | -0.36175 | 1.0663
99 | 0.011379 | 0.0028526 | -0.011376 | -0.0028513 | 2.4834e-06 | 1.3085e-06 | 0.017255 | 0.017255 | 0.017255 | 0.98126 | -0.36105 | 0.98103 | -0.36564 | 4.7405
100 | 0.016306 | 0.0040875 | -0.016306 | -0.0040875 | 7.1881e-08 | 4.2048e-08 | 0.024734 | 0.024734 | 0.024734 | 0.98101 | -0.36606 | 0.981 | -0.36615 | 6.795
101 | 0.0013807 | 0.00034592 | -0.0013807 | -0.00034604 | 1.6288e-08 | -1.1809e-07 | 0.00208 | 0.00208 | 0.00208 | 0.98777 | -0.23541 | 0.98775 | -0.23565 | 0.57143
102 | 0.0024693 | 0.00061864 | -0.0024692 | -0.00061885 | 1.1328e-07 | -2.0709e-07 | 0.0037193 | 0.0037194 | 0.0037194 | 0.98791 | -0.23268 | 0.98786 | -0.23364 | 1.0218
103 | 0.0033975 | 0.00085102 | -0.0033973 | -0.00085111 | 1.4658e-07 | -9.3588e-08 | 0.0051424 | 0.0051424 | 0.0051424 | 0.98307 | -0.32512 | 0.98302 | -0.32602 | 1.4128
104 | 0.00092077 | 0.00023044 | -0.00092075 | -0.00023076 | 1.9428e-08 | -3.2568e-07 | 0.0013937 | 0.0013938 | 0.0013938 | 0.98302 | -0.32602 | 0.983 | -0.32647 | 0.38291
105 | 0.0024612 | 0.00061653 | -0.002461 | -0.00061679 | 1.4901e-07 | -2.6342e-07 | 0.0037361 | 0.0037363 | 0.0037363 | 0.9802 | -0.38186 | 0.98014 | -0.38313 | 1.0264
106 | -0.0039411 | -0.00098744 | 0.0039415 | 0.00098735 | 3.2057e-07 | -9.5904e-08 | 0.0059828 | 0.0059827 | 0.0059828 | 0.9802 | -0.38186 | 0.98029 | -0.38015 | 1.6436
107 | -0.0058894 | -0.0014755 | 0.0058905 | 0.0014758 | 1.1118e-06 | 2.4372e-07 | 0.0089396 | 0.0089394 | 0.0089396 | 0.98029 | -0.38015 | 0.98049 | -0.37619 | 2.4559
108 | -0.0083831 | -0.0021002 | 0.0083844 | 0.0021008 | 1.2823e-06 | 5.5417e-07 | 0.012722 | 0.012722 | 0.012722 | 0.98049 | -0.37619 | 0.98066 | -0.37298 | 3.4951
109 | 0.0024926 | 0.0006244 | -0.0024925 | -0.00062467 | 1.5575e-07 | -2.6636e-07 | 0.0037827 | 0.0037829 | 0.0037829 | 0.98049 | -0.37619 | 0.98042 | -0.3775 | 1.0393
110 | -0.010167 | -0.0025474 | 0.010167 | 0.0025476 | 3.0083e-07 | 1.5e-07 | 0.015426 | 0.015426 | 0.015426 | 0.98066 | -0.37298 | 0.98069 | -0.37236 | 4.238
111 | -0.012511 | -0.0031351 | 0.012511 | 0.0031352 | 1.4171e-07 | 7.7465e-08 | 0.018983 | 0.018983 | 0.018983 | 0.98069 | -0.37236 | 0.9807 | -0.37212 | 5.2152
112 | -0.014208 | -0.0035604 | 0.014212 | 0.0035627 | 4.0431e-06 | 2.2948e-06 | 0.021558 | 0.021558 | 0.021558 | 0.9807 | -0.37212 | 0.981 | -0.36615 | 5.9224
113 | 0.052205 | 0.013182 | -0.052176 | -0.013164 | 2.8641e-05 | 1.8173e-05 | 0.078689 | 0.078689 | 0.078689 | 0.98765 | -0.23679 | 0.98706 | -0.24824 | 21.6178
114 | -0.052205 | -0.013182 | 0.052249 | 0.01321 | 4.3595e-05 | 2.766e-05 | 0.078689 | 0.078689 | 0.078689 | 0.98765 | -0.23679 | 0.98855 | -0.21937 | 21.6178
115 | -0.053007 | -0.0134 | 0.053035 | 0.013418 | 2.8882e-05 | 1.8329e-05 | 0.079829 | 0.079829 | 0.079829 | 0.98855 | -0.21937 | 0.98914 | -0.20802 | 21.9312
116 | -0.030865 | -0.0077529 | 0.030878 | 0.007761 | 1.3014e-05 | 8.1211e-06 | 0.046374 | 0.046374 | 0.046374 | 0.99051 | -0.18207 | 0.99097 | -0.17324 | 12.74
117 | 0.0056382 | 0.0014129 | -0.0056374 | -0.0014128 | 8.4417e-07 | 1.3753e-07 | 0.0084757 | 0.0084758 | 0.0084758 | 0.98986 | -0.19481 | 0.98969 | -0.19795 | 2.3285
118 | -0.034056 | -0.0085575 | 0.034074 | 0.008569 | 1.8386e-05 | 1.1525e-05 | 0.051146 | 0.051146 | 0.051146 | 0.99097 | -0.17324 | 0.99155 | -0.16194 | 14.051
119 | 0.0043862 | 0.0010992 | -0.0043861 | -0.0010993 | 1.2756e-07 | -1.8865e-08 | 0.0065947 | 0.0065948 | 0.0065948 | 0.98969 | -0.19795 | 0.98966 | -0.19856 | 1.8118
120 | -0.037496 | -0.0094264 | 0.037497 | 0.0094275 | 1.6901e-06 | 1.0633e-06 | 0.05628 | 0.05628 | 0.05628 | 0.99155 | -0.16194 | 0.9916 | -0.161 | 15.4615
121 | -0.041595 | -0.010454 | 0.04162 | 0.01047 | 2.4676e-05 | 1.5575e-05 | 0.062429 | 0.062429 | 0.062429 | 0.9916 | -0.161 | 0.99224 | -0.14858 | 17.1507
122 | -0.054198 | -0.01371 | 0.054199 | 0.01371 | 7.8576e-07 | 4.9885e-07 | 0.081578 | 0.081578 | 0.081578 | 0.98914 | -0.20802 | 0.98915 | -0.20772 | 22.4116
123 | 0.047551 | 0.011964 | -0.047545 | -0.011961 | 5.5413e-06 | 3.5089e-06 | 0.071291 | 0.071291 | 0.071291 | 0.99273 | -0.13915 | 0.9926 | -0.14159 | 19.5854
124 | 0.044123 | 0.011103 | -0.044109 | -0.011094 | 1.4723e-05 | 9.3068e-06 | 0.066161 | 0.066161 | 0.066161 | 0.9926 | -0.14159 | 0.99224 | -0.14858 | 18.1762
125 | 0.010216 | 0.0025606 | -0.010216 | -0.0025605 | 2.2253e-07 | 1.1122e-07 | 0.015496 | 0.015496 | 0.015496 | 0.98103 | -0.36564 | 0.98101 | -0.36609 | 4.2572
126 | 0.0092843 | 0.0023269 | -0.0092826 | -0.0023261 | 1.6634e-06 | 7.8226e-07 | 0.014083 | 0.014083 | 0.014083 | 0.98101 | -0.36609 | 0.98081 | -0.36985 | 3.8689
127 | 0.0072274 | 0.0018111 | -0.0072273 | -0.001811 | 1.603e-07 | 5.772e-08 | 0.010965 | 0.010965 | 0.010965 | 0.98081 | -0.36985 | 0.98079 | -0.37032 | 3.0123
128 | -0.002764 | -0.00069272 | 0.0027642 | 0.00069248 | 1.8549e-07 | -2.3607e-07 | 0.0041941 | 0.004194 | 0.0041941 | 0.98061 | -0.37379 | 0.98069 | -0.37238 | 1.1522
129 | -0.0046678 | -0.0011696 | 0.0046678 | 0.0011696 | 7.5392e-09 | -2.3215e-10 | 0.0070824 | 0.0070824 | 0.0070824 | 0.98069 | -0.37238 | 0.98069 | -0.37234 | 1.9457
130 | -0.0057104 | -0.0014309 | 0.0057109 | 0.001431 | 5.5058e-07 | 1.0557e-07 | 0.0086643 | 0.0086642 | 0.0086643 | 0.98069 | -0.37234 | 0.98079 | -0.37032 | 2.3803

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26393 | 0.06687

## res_load
| p_mw | q_mvar
0 | 0.00066234 | 0.000166
1 | 0.0018314 | 0.00045899
2 | 0.0014382 | 0.00036045
3 | 0.0034276 | 0.00085903
4 | 0.0011302 | 0.00028325
5 | 0.0020283 | 0.00050834
6 | 0.0052025 | 0.0013039
7 | 0.0021866 | 0.00054802
8 | 0.0021221 | 0.00053184
9 | 0.0008022 | 0.00020105
10 | 0.0046823 | 0.0011735
11 | 0.004035 | 0.0010113
12 | 0.0014281 | 0.00035791
13 | 0.00057395 | 0.00014385
14 | 0.00074142 | 0.00018582
15 | 0.0011458 | 0.00028716
16 | 0.0006028 | 0.00015108
17 | 0.0005709 | 0.00014308
18 | 0.0030116 | 0.00075477
19 | 0.0039715 | 0.00099535
20 | 0.0005777 | 0.00014478
21 | 0.006205 | 0.0015551
22 | 0.013959 | 0.0034985
23 | 0.00094532 | 0.00023692
24 | 0.0015642 | 0.00039202
25 | 0.0023463 | 0.00058804
26 | 0.00074125 | 0.00018577
27 | 0.002279 | 0.00057118
28 | 0.0016114 | 0.00040386
29 | 0.0067827 | 0.0016999
30 | 0.0041791 | 0.0010474
31 | 0.0061204 | 0.0015339
32 | 0.00065138 | 0.00016325
33 | 0.00081225 | 0.00020357
34 | 0.00061542 | 0.00015424
35 | 0.002081 | 0.00052154
36 | 0.00092254 | 0.00023121
37 | 0.0071825 | 0.0018001
38 | 0.001036 | 0.00025964
39 | 0.0041372 | 0.0010369
40 | 0.001353 | 0.0003391
41 | 0.00067358 | 0.00016881
42 | 0.002027 | 0.00050801
43 | 0.0021497 | 0.00053878
44 | 0.0022247 | 0.00055755
45 | 0.0017086 | 0.00042823
46 | 0.0017118 | 0.00042902
47 | 0.0013877 | 0.00034778
48 | 0.0046305 | 0.0011605
49 | 0.0011572 | 0.00029003
50 | 0.0016008 | 0.00040119
51 | 0.0017897 | 0.00044855
52 | 0.0018923 | 0.00047425
53 | 0.0033151 | 0.00083085
54 | 0.0020801 | 0.00052132
55 | 0.00056264 | 0.00014101
56 | 0.0017214 | 0.00043143
57 | 0.0022563 | 0.00056549
58 | 0.0029793 | 0.00074668
59 | 0.0024607 | 0.00061672
60 | 0.0023804 | 0.00059659
61 | 0.00197 | 0.00049374
62 | 0.0022735 | 0.00056979
63 | 0.0012518 | 0.00031372
64 | 0.0022312 | 0.0005592
65 | 0.0012534 | 0.00031414
66 | 0.0016748 | 0.00041974
67 | 0.0017843 | 0.00044719
68 | 0.0013031 | 0.00032659
69 | 0.00126 | 0.00031579
70 | 0.0022303 | 0.00055898
71 | 0.0024765 | 0.00062068
72 | 0.0013807 | 0.00034604
73 | 0.0024692 | 0.00061885
74 | 0.00148 | 0.00037091
75 | 0.002461 | 0.00061679
76 | 0.0019479 | 0.0004882
77 | 0.0017823 | 0.00044669
78 | 0.0024925 | 0.00062467
79 | 0.0023441 | 0.00058749
80 | 0.0016967 | 0.00042525
81 | 0.0014461 | 0.00036243
82 | 0.00075799 | 0.00018997
83 | 0.017801 | 0.0044614
84 | 0.00092075 | 0.00023076
85 | 0.0011849 | 0.00029695
86 | 0.0014252 | 0.00035718
87 | 0.00087542 | 0.0002194
88 | 0.0031781 | 0.0007965
89 | 0.0012511 | 0.00031356
90 | 0.0034212 | 0.00085743
91 | 0.0043861 | 0.0010993
92 | 0.0040975 | 0.0010269
93 | 0.0011626 | 0.00029137
94 | 0.0025018 | 0.00062701
95 | 0.0020939 | 0.00052477
96 | 0.0014413 | 0.00036122
97 | 0.0034217 | 0.00085757
98 | 0.002489 | 0.00062381
99 | 0.0025595 | 0.00064146
100 | 0.0011598 | 0.00029068
101 | 0.0053156 | 0.0013322
102 | 0.00093185 | 0.00023354
103 | 0.0020552 | 0.00051508
104 | 0.002764 | 0.00069272
105 | 0.0019036 | 0.00047709
106 | 0.0010426 | 0.0002613
107 | 0.0015163 | 0.00038003

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1