## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2500-3_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2500-3_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2500-3_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2500-3_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2500-3_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2500-3_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2500-3_0_8_node_92 | 0.4 | n |  | TRUE
7 | bus_LV_2500-3_0_8_node_90 | 0.4 | n |  | TRUE
8 | bus_LV_2500-3_0_8_node_114 | 0.4 | n |  | TRUE
9 | bus_LV_2500-3_0_8_node_112 | 0.4 | n |  | TRUE
10 | bus_LV_2500-3_0_8_node_91 | 0.4 | n |  | TRUE
11 | bus_LV_2500-3_0_8_node_124 | 0.4 | n |  | TRUE
12 | bus_LV_2500-3_0_8_node_122 | 0.4 | n |  | TRUE
13 | bus_LV_2500-3_0_8_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_2500-3_0_8_node_66 | 0.4 | n |  | TRUE
15 | bus_LV_2500-3_0_8_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_2500-3_0_8_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_2500-3_0_8_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_2500-3_0_8_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2500-3_0_8_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2500-3_0_8_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2500-3_0_8_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_2500-3_0_8_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_2500-3_0_8_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_2500-3_0_8_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2500-3_0_8_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_2500-3_0_8_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2500-3_0_8_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2500-3_0_8_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2500-3_0_8_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_2500-3_0_8_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2500-3_0_8_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2500-3_0_8_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2500-3_0_8_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2500-3_0_8_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2500-3_0_8_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_2500-3_0_8_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_2500-3_0_8_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_2500-3_0_8_node_102 | 0.4 | n |  | TRUE
39 | bus_LV_2500-3_0_8_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_2500-3_0_8_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2500-3_0_8_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2500-3_0_8_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2500-3_0_8_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_2500-3_0_8_node_89 | 0.4 | n |  | TRUE
45 | bus_LV_2500-3_0_8_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_2500-3_0_8_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_2500-3_0_8_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_2500-3_0_8_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_2500-3_0_8_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_2500-3_0_8_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_2500-3_0_8_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_2500-3_0_8_node_72 | 0.4 | n |  | TRUE
53 | bus_LV_2500-3_0_8_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2500-3_0_8_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2500-3_0_8_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_2500-3_0_8_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_2500-3_0_8_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_2500-3_0_8_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_2500-3_0_8_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_2500-3_0_8_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_2500-3_0_8_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_2500-3_0_8_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2500-3_0_8_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_2500-3_0_8_node_98 | 0.4 | n |  | TRUE
65 | bus_LV_2500-3_0_8_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_2500-3_0_8_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_2500-3_0_8_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_2500-3_0_8_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_2500-3_0_8_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_2500-3_0_8_node_42 | 0.4 | n |  | TRUE
71 | bus_LV_2500-3_0_8_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_2500-3_0_8_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_2500-3_0_8_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_2500-3_0_8_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_2500-3_0_8_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_2500-3_0_8_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_2500-3_0_8_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_2500-3_0_8_node_108 | 0.4 | n |  | TRUE
79 | bus_LV_2500-3_0_8_node_116 | 0.4 | n |  | TRUE
80 | bus_LV_2500-3_0_8_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_2500-3_0_8_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_2500-3_0_8_node_97 | 0.4 | n |  | TRUE
83 | bus_LV_2500-3_0_8_node_93 | 0.4 | n |  | TRUE
84 | bus_LV_2500-3_0_8_node_111 | 0.4 | n |  | TRUE
85 | bus_LV_2500-3_0_8_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_2500-3_0_8_node_121 | 0.4 | n |  | TRUE
87 | bus_LV_2500-3_0_8_node_128 | 0.4 | n |  | TRUE
88 | bus_LV_2500-3_0_8_node_52 | 0.4 | n |  | TRUE
89 | bus_LV_2500-3_0_8_node_127 | 0.4 | n |  | TRUE
90 | bus_LV_2500-3_0_8_node_126 | 0.4 | n |  | TRUE
91 | bus_LV_2500-3_0_8_node_123 | 0.4 | n |  | TRUE
92 | bus_LV_2500-3_0_8_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_2500-3_0_8_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_2500-3_0_8_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_2500-3_0_8_node_119 | 0.4 | n |  | TRUE
96 | bus_LV_2500-3_0_8_node_55 | 0.4 | n |  | TRUE
97 | bus_LV_2500-3_0_8_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_2500-3_0_8_node_57 | 0.4 | n |  | TRUE
99 | bus_LV_2500-3_0_8_node_58 | 0.4 | n |  | TRUE
100 | bus_LV_2500-3_0_8_node_59 | 0.4 | n |  | TRUE
101 | bus_LV_2500-3_0_8_node_60 | 0.4 | n |  | TRUE
102 | bus_LV_2500-3_0_8_node_61 | 0.4 | n |  | TRUE
103 | bus_LV_2500-3_0_8_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_2500-3_0_8_node_78 | 0.4 | n |  | TRUE
105 | bus_LV_2500-3_0_8_node_125 | 0.4 | n |  | TRUE
106 | bus_LV_2500-3_0_8_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_2500-3_0_8_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2500-3_0_8_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_2500-3_0_8_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_2500-3_0_8_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_2500-3_0_8_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_2500-3_0_8_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_2500-3_0_8_node_73 | 0.4 | n |  | TRUE
114 | bus_LV_2500-3_0_8_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_2500-3_0_8_node_79 | 0.4 | n |  | TRUE
116 | bus_LV_2500-3_0_8_node_80 | 0.4 | n |  | TRUE
117 | bus_LV_2500-3_0_8_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_2500-3_0_8_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_2500-3_0_8_node_87 | 0.4 | n |  | TRUE
120 | bus_LV_2500-3_0_8_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2500-3_0_8_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_2500-3_0_8_node_118 | 0.4 | n |  | TRUE
123 | bus_MV_290_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2500-3_0_8_load_0 | 0 | 0.00066526 | 0.00016673 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2500-3_0_8_load_1 | 1 | 0.0013908 | 0.00034856 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2500-3_0_8_load_3 | 3 | 0.0004994 | 0.00012516 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2500-3_0_8_load_92 | 6 | 0.0024965 | 0.00062568 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2500-3_0_8_load_90 | 7 | 0.0082882 | 0.0020772 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2500-3_0_8_load_112 | 9 | 0.008358 | 0.0020947 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2500-3_0_8_load_91 | 10 | 0.0076863 | 0.0019264 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2500-3_0_8_load_124 | 11 | 0.0037028 | 0.00092801 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2500-3_0_8_load_122 | 12 | 0.0089379 | 0.0022401 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2500-3_0_8_load_66 | 14 | 0.006853 | 0.0017175 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2500-3_0_8_load_64 | 15 | 0.001876 | 0.00047018 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2500-3_0_8_load_6 | 16 | 0.001991 | 0.00049898 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2500-3_0_8_load_7 | 17 | 0.0019892 | 0.00049854 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2500-3_0_8_load_8 | 18 | 0.0013205 | 0.00033095 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2500-3_0_8_load_9 | 19 | 0.0017117 | 0.00042899 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2500-3_0_8_load_10 | 20 | 0.0018935 | 0.00047455 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2500-3_0_8_load_75 | 21 | 0.0022298 | 0.00055884 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2500-3_0_8_load_37 | 22 | 0.0018245 | 0.00045726 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2500-3_0_8_load_14 | 24 | 0.0016106 | 0.00040365 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2500-3_0_8_load_11 | 25 | 0.0015204 | 0.00038104 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2500-3_0_8_load_12 | 26 | 0.0010246 | 0.00025679 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2500-3_0_8_load_13 | 27 | 0.0011881 | 0.00029776 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2500-3_0_8_load_15 | 28 | 0.0016215 | 0.00040639 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2500-3_0_8_load_28 | 29 | 0.00049858 | 0.00012496 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2500-3_0_8_load_26 | 30 | 0.0013714 | 0.00034371 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2500-3_0_8_load_16 | 31 | 0.001664 | 0.00041703 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2500-3_0_8_load_17 | 32 | 0.0024612 | 0.00061682 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2500-3_0_8_load_18 | 33 | 0.002363 | 0.00059222 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2500-3_0_8_load_56 | 35 | 0.0034693 | 0.00086949 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2500-3_0_8_load_102 | 38 | 0.0061131 | 0.0015321 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2500-3_0_8_load_20 | 39 | 0.0014205 | 0.00035602 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2500-3_0_8_load_22 | 41 | 0.0016632 | 0.00041683 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2500-3_0_8_load_53 | 43 | 0.0018432 | 0.00046196 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2500-3_0_8_load_89 | 44 | 0.00035791 | 8.97e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2500-3_0_8_load_84 | 45 | 0.00074625 | 0.00018703 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2500-3_0_8_load_110 | 46 | 0.00032811 | 8.2231e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2500-3_0_8_load_83 | 47 | 0.00044582 | 0.00011173 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2500-3_0_8_load_24 | 48 | 0.00050053 | 0.00012544 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2500-3_0_8_load_25 | 49 | 0.00055661 | 0.0001395 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2500-3_0_8_load_27 | 50 | 0.00066942 | 0.00016777 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2500-3_0_8_load_72 | 52 | 0.0013256 | 0.00033222 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2500-3_0_8_load_32 | 53 | 0.00071231 | 0.00017852 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2500-3_0_8_load_29 | 54 | 0.00055275 | 0.00013853 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2500-3_0_8_load_30 | 55 | 0.00049808 | 0.00012483 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2500-3_0_8_load_31 | 56 | 0.000734 | 0.00018396 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2500-3_0_8_load_33 | 57 | 0.00072236 | 0.00018104 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2500-3_0_8_load_34 | 58 | 0.003494 | 0.00087569 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2500-3_0_8_load_35 | 59 | 0.01502 | 0.0037643 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2500-3_0_8_load_98 | 64 | 0.0029911 | 0.00074964 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2500-3_0_8_load_115 | 66 | 0.0007372 | 0.00018476 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2500-3_0_8_load_38 | 67 | 7.9368e-05 | 1.9892e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2500-3_0_8_load_39 | 68 | 0.0013262 | 0.00033237 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2500-3_0_8_load_95 | 71 | 0.0042134 | 0.001056 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2500-3_0_8_load_68 | 75 | 0.00055709 | 0.00013962 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2500-3_0_8_load_116 | 79 | 0.01042 | 0.0026114 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2500-3_0_8_load_97 | 82 | 0.014933 | 0.0037426 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2500-3_0_8_load_93 | 83 | 0.0023216 | 0.00058184 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2500-3_0_8_load_111 | 84 | 0.00046992 | 0.00011777 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2500-3_0_8_load_88 | 85 | 0.00097968 | 0.00024553 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2500-3_0_8_load_121 | 86 | 0.0008907 | 0.00022323 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2500-3_0_8_load_128 | 87 | 0.0019989 | 0.00050097 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2500-3_0_8_load_127 | 89 | 0.0008064 | 0.0002021 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2500-3_0_8_load_126 | 90 | 0.0052378 | 0.0013127 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2500-3_0_8_load_123 | 91 | 0.0043286 | 0.0010848 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2500-3_0_8_load_96 | 93 | 0.014923 | 0.0037401 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2500-3_0_8_load_94 | 94 | 0.0013272 | 0.00033262 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2500-3_0_8_load_119 | 95 | 0.0075054 | 0.001881 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2500-3_0_8_load_55 | 96 | 0.0022643 | 0.0005675 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2500-3_0_8_load_69 | 97 | 0.0017851 | 0.00044739 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2500-3_0_8_load_57 | 98 | 0.0028311 | 0.00070955 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2500-3_0_8_load_58 | 99 | 0.0021327 | 0.00053449 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2500-3_0_8_load_62 | 103 | 0.0038246 | 0.00095853 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2500-3_0_8_load_78 | 104 | 0.00098246 | 0.00024623 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2500-3_0_8_load_125 | 105 | 0.0036148 | 0.00090594 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2500-3_0_8_load_100 | 107 | 0.043778 | 0.010972 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2500-3_0_8_load_103 | 108 | 0.019201 | 0.0048123 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2500-3_0_8_load_105 | 110 | 0.066493 | 0.016665 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2500-3_0_8_load_85 | 111 | 0.0039741 | 0.00099601 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2500-3_0_8_load_86 | 112 | 0.0021587 | 0.00054103 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2500-3_0_8_load_73 | 113 | 0.0016351 | 0.0004098 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2500-3_0_8_load_81 | 114 | 0.0494 | 0.012381 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2500-3_0_8_load_79 | 115 | 0.027024 | 0.0067728 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2500-3_0_8_load_117 | 117 | 0.010441 | 0.0026168 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2500-3_0_8_load_120 | 118 | 0.0039438 | 0.00098842 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2500-3_0_8_load_87 | 119 | 0.0045098 | 0.0011303 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2500-3_0_8_load_101 | 120 | 0.0058889 | 0.0014759 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2500-3_0_8_load_106 | 121 | 0.002887 | 0.00072356 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2500-3_0_8_load_118 | 122 | 0.0039121 | 0.00098047 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2500-3_0_8_line_0 |  | 0 | 1 | 0.004162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2500-3_0_8_line_1 |  | 0 | 2 | 0.056337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2500-3_0_8_line_2 |  | 1 | 3 | 0.0015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2500-3_0_8_line_3 |  | 2 | 4 | 0.007478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2500-3_0_8_line_4 |  | 2 | 5 | 0.067321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2500-3_0_8_line_5 |  | 4 | 6 | 0.033276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2500-3_0_8_line_6 |  | 4 | 7 | 0.050456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2500-3_0_8_line_7 |  | 5 | 8 | 0.10934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2500-3_0_8_line_8 |  | 5 | 9 | 0.04823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2500-3_0_8_line_9 |  | 7 | 10 | 0.0022898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2500-3_0_8_line_10 |  | 8 | 11 | 0.022812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2500-3_0_8_line_11 |  | 8 | 12 | 0.013594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2500-3_0_8_line_12 |  | 11 | 102 | 0.019601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2500-3_0_8_line_13 |  | 12 | 91 | 0.013619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2500-3_0_8_line_14 |  | 13 | 14 | 0.01255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2500-3_0_8_line_15 |  | 13 | 15 | 0.11595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2500-3_0_8_line_16 |  | 14 | 108 | 0.043323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2500-3_0_8_line_17 |  | 15 | 80 | 0.033883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2500-3_0_8_line_18 |  | 16 | 17 | 0.016051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2500-3_0_8_line_19 |  | 16 | 18 | 0.0057229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2500-3_0_8_line_20 |  | 17 | 19 | 0.0019651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2500-3_0_8_line_21 |  | 18 | 20 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2500-3_0_8_line_22 |  | 19 | 21 | 0.019075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2500-3_0_8_line_23 |  | 20 | 22 | 0.011259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2500-3_0_8_line_24 |  | 21 | 23 | 0.045984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2500-3_0_8_line_25 |  | 22 | 24 | 0.0074452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2500-3_0_8_line_26 |  | 23 | 113 | 0.15321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2500-3_0_8_line_27 |  | 24 | 26 | 0.016904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2500-3_0_8_line_28 |  | 25 | 26 | 0.0037758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2500-3_0_8_line_29 |  | 25 | 27 | 0.0146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2500-3_0_8_line_30 |  | 27 | 28 | 0.012285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2500-3_0_8_line_31 |  | 28 | 29 | 0.0073169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2500-3_0_8_line_32 |  | 29 | 30 | 0.013685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2500-3_0_8_line_33 |  | 30 | 48 | 0.0064733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2500-3_0_8_line_34 |  | 31 | 32 | 0.021853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2500-3_0_8_line_35 |  | 31 | 33 | 0.041572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2500-3_0_8_line_36 |  | 33 | 34 | 0.022691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2500-3_0_8_line_37 |  | 34 | 35 | 0.10313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2500-3_0_8_line_38 |  | 34 | 36 | 0.009157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2500-3_0_8_line_39 |  | 35 | 37 | 0.0031119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2500-3_0_8_line_40 |  | 36 | 38 | 0.018937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2500-3_0_8_line_41 |  | 37 | 96 | 0.030323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2500-3_0_8_line_42 |  | 37 | 43 | 0.016398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2500-3_0_8_line_43 |  | 38 | 120 | 0.021479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2500-3_0_8_line_44 |  | 39 | 40 | 0.0068794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2500-3_0_8_line_45 |  | 40 | 41 | 0.027056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2500-3_0_8_line_46 |  | 40 | 42 | 0.30212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2500-3_0_8_line_47 |  | 41 | 43 | 0.033252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2500-3_0_8_line_48 |  | 42 | 44 | 0.042486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2500-3_0_8_line_49 |  | 42 | 45 | 0.065291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2500-3_0_8_line_50 |  | 44 | 46 | 0.0020183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2500-3_0_8_line_51 |  | 45 | 47 | 0.013798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2500-3_0_8_line_52 |  | 47 | 57 | 0.01821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2500-3_0_8_line_53 |  | 48 | 49 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2500-3_0_8_line_54 |  | 49 | 50 | 0.0061293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2500-3_0_8_line_55 |  | 50 | 51 | 0.010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2500-3_0_8_line_56 |  | 51 | 52 | 0.035022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2500-3_0_8_line_57 |  | 51 | 53 | 0.0059592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2500-3_0_8_line_58 |  | 52 | 85 | 0.0037083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2500-3_0_8_line_59 |  | 53 | 55 | 0.0038929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2500-3_0_8_line_60 |  | 54 | 55 | 0.018878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2500-3_0_8_line_61 |  | 54 | 56 | 0.0030827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2500-3_0_8_line_62 |  | 56 | 57 | 0.015118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2500-3_0_8_line_63 |  | 58 | 59 | 0.049275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2500-3_0_8_line_64 |  | 59 | 60 | 0.028672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2500-3_0_8_line_65 |  | 60 | 61 | 0.035143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2500-3_0_8_line_66 |  | 61 | 66 | 0.00043811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2500-3_0_8_line_67 |  | 61 | 62 | 0.03371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2500-3_0_8_line_68 |  | 62 | 63 | 0.10714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2500-3_0_8_line_69 |  | 62 | 64 | 0.08951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2500-3_0_8_line_70 |  | 62 | 65 | 0.079826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2500-3_0_8_line_71 |  | 63 | 87 | 0.009811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2500-3_0_8_line_72 |  | 63 | 88 | 0.027975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2500-3_0_8_line_73 |  | 65 | 67 | 0.011937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2500-3_0_8_line_74 |  | 67 | 68 | 0.027141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2500-3_0_8_line_75 |  | 68 | 69 | 0.011623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2500-3_0_8_line_76 |  | 69 | 70 | 0.014775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2500-3_0_8_line_77 |  | 70 | 71 | 0.016046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2500-3_0_8_line_78 |  | 71 | 74 | 0.016708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2500-3_0_8_line_79 |  | 72 | 73 | 0.010835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2500-3_0_8_line_80 |  | 72 | 74 | 0.03377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2500-3_0_8_line_81 |  | 72 | 75 | 0.020326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2500-3_0_8_line_82 |  | 73 | 76 | 0.08217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2500-3_0_8_line_83 |  | 74 | 83 | 0.011171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2500-3_0_8_line_84 |  | 75 | 80 | 0.0072164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2500-3_0_8_line_85 |  | 76 | 84 | 0.034455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2500-3_0_8_line_86 |  | 76 | 85 | 0.012752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2500-3_0_8_line_87 |  | 76 | 86 | 0.03318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2500-3_0_8_line_88 |  | 77 | 78 | 0.063332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2500-3_0_8_line_89 |  | 77 | 79 | 0.041592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2500-3_0_8_line_90 |  | 78 | 90 | 0.010572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2500-3_0_8_line_91 |  | 78 | 91 | 0.051872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2500-3_0_8_line_92 |  | 78 | 81 | 0.006134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2500-3_0_8_line_93 |  | 79 | 92 | 0.029094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2500-3_0_8_line_94 |  | 81 | 82 | 0.014267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2500-3_0_8_line_95 |  | 82 | 93 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2500-3_0_8_line_96 |  | 83 | 94 | 0.016901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2500-3_0_8_line_97 |  | 86 | 95 | 0.029107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2500-3_0_8_line_98 |  | 88 | 89 | 0.0045214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2500-3_0_8_line_99 |  | 92 | 117 | 0.042658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2500-3_0_8_line_100 |  | 92 | 116 | 0.027177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2500-3_0_8_line_101 |  | 95 | 122 | 0.018767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2500-3_0_8_line_102 |  | 96 | 97 | 0.045075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2500-3_0_8_line_103 |  | 98 | 99 | 0.00042418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2500-3_0_8_line_104 |  | 98 | 100 | 0.018738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2500-3_0_8_line_105 |  | 99 | 101 | 0.01905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2500-3_0_8_line_106 |  | 100 | 102 | 0.026777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2500-3_0_8_line_107 |  | 100 | 103 | 0.021638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2500-3_0_8_line_108 |  | 101 | 104 | 0.010532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2500-3_0_8_line_109 |  | 102 | 105 | 0.0011726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2500-3_0_8_line_110 |  | 105 | 106 | 0.030365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2500-3_0_8_line_111 |  | 106 | 107 | 0.042808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2500-3_0_8_line_112 |  | 107 | 114 | 0.021494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2500-3_0_8_line_113 |  | 108 | 109 | 0.094288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2500-3_0_8_line_114 |  | 109 | 121 | 0.11709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2500-3_0_8_line_115 |  | 109 | 110 | 0.10462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
116 | LV_2500-3_0_8_line_116 |  | 111 | 112 | 0.06329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2500-3_0_8_line_117 |  | 112 | 119 | 0.027548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2500-3_0_8_line_118 |  | 115 | 116 | 0.029452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2500-3_0_8_line_119 |  | 117 | 118 | 0.0080155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2500-3_0_8_line_120 |  | 118 | 122 | 0.009982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2500-3_0_8_line_121 |  | 119 | 120 | 0.023742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2500-3_0_8_trafo_46 | 0.63 MVA 20/0.4 kV | 123 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58
0 | 2636172.3382 | 1246729.8845 | 2636175.98 | 1246731.8994
1 | 2636148.0001 | 1246679.3031 | 2636152.9034 | 1246691.4965 | 2636159.5994 | 1246707.003 | 2636168.1035 | 1246724.4996 | 2636172.3382 | 1246729.8845
2 | 2636175.98 | 1246731.8994 | 2636177.3368 | 1246732.6501
3 | 2636148.0001 | 1246679.3031 | 2636145.8006 | 1246678.3002 | 2636140.8913 | 1246676.9917
4 | 2636135.0892 | 1246613.9262 | 2636133.6915 | 1246621.4226 | 2636135.9036 | 1246633.9998 | 2636146.1032 | 1246674.4995 | 2636148.0001 | 1246679.3031
5 | 2636120.1029 | 1246651.2038 | 2636126.6025 | 1246656.8026 | 2636132.6022 | 1246665.1001 | 2636140.8913 | 1246676.9917
6 | 2636140.8913 | 1246676.9917 | 2636127.6678 | 1246684.038 | 2636110.1359 | 1246714.8753
7 | 2636135.0892 | 1246613.9262 | 2636107.0027 | 1246605.7055 | 2636028.8557 | 1246586.9074
8 | 2636135.0892 | 1246613.9262 | 2636167.1082 | 1246625.0729 | 2636179.9971 | 1246631.3274
9 | 2636110.1359 | 1246714.8753 | 2636109.0041 | 1246716.8659
10 | 2636028.8557 | 1246586.9074 | 2636027.282 | 1246596.0482 | 2636024.5325 | 1246609.3028
11 | 2636028.8557 | 1246586.9074 | 2636015.712 | 1246583.4364
12 | 2636020.5513 | 1246628.4953 | 2636024.5325 | 1246609.3028
13 | 2636015.712 | 1246583.4364 | 2636002.5446 | 1246579.9592
14 | 2635878.2983 | 1246361.1036 | 2635879.4042 | 1246353.105 | 2635879.7202 | 1246348.6411
15 | 2635878.2983 | 1246361.1036 | 2635874.3988 | 1246368.8962 | 2635870.2022 | 1246377.0984 | 2635865.201 | 1246384.7065 | 2635830.7013 | 1246418.7983 | 2635803.5209 | 1246448.7108
16 | 2635866.9353 | 1246308.1103 | 2635870.6036 | 1246313.2035 | 2635875.497 | 1246324.6962 | 2635878.9006 | 1246335.2014 | 2635879.9989 | 1246344.7031 | 2635879.7202 | 1246348.6411
17 | 2635781.1403 | 1246474.1468 | 2635794.901 | 1246458.1971 | 2635803.5209 | 1246448.7108
18 | 2635835.9481 | 1246663.0245 | 2635839.9018 | 1246666.4048 | 2635848.451 | 1246673.0836
19 | 2635835.9481 | 1246663.0245 | 2635831.5982 | 1246659.3056 | 2635831.5982 | 1246659.3056
20 | 2635848.451 | 1246673.0836 | 2635849.9996 | 1246674.2934
21 | 2635820.4084 | 1246646.4501 | 2635824.3001 | 1246650.8004 | 2635831.5982 | 1246659.3056
22 | 2635849.9996 | 1246674.2934 | 2635853.5993 | 1246677.1056 | 2635864.9945 | 1246686.0838
23 | 2635813.1928 | 1246637.8156 | 2635816.7899 | 1246642.4051 | 2635820.4084 | 1246646.4501
24 | 2635898.7976 | 1246717.2049 | 2635891.0991 | 1246709.9981 | 2635880.0982 | 1246699.3024 | 2635872.4984 | 1246691.9961 | 2635864.9945 | 1246686.0838
25 | 2635813.1928 | 1246637.8156 | 2635809.4966 | 1246633.0995 | 2635808.5457 | 1246632.0005
26 | 2635898.7976 | 1246717.2049 | 2635897.3005 | 1246726.2018 | 2635899.6024 | 1246733.9986 | 2635901.8988 | 1246740.2054 | 2635903.4989 | 1246745.3963 | 2635904.0995 | 1246748.5019 | 2635903.0988 | 1246751.5979 | 2635900.7011 | 1246753.3957 | 2635896.5005 | 1246754.8045 | 2635888.5993 | 1246752.3997 | 2635881.1977 | 1246749.7977 | 2635876.5981 | 1246748.5024 | 2635866.6016 | 1246746.5963 | 2635861.6034 | 1246744.9984 | 2635857.7005 | 1246743.396 | 2635851.5002 | 1246739.5004 | 2635841.9969 | 1246732.2049 | 2635831.403 | 1246722.9016 | 2635828.4028 | 1246719.4034 | 2635823.5983 | 1246714.5045 | 2635811.3969 | 1246703.7016 | 2635804.728 | 1246698.6345
27 | 2635796.7358 | 1246619.9495 | 2635803.1432 | 1246625.7564 | 2635808.5457 | 1246632.0005
28 | 2635793.7986 | 1246617.5789 | 2635796.2393 | 1246619.4996 | 2635796.7358 | 1246619.9495
29 | 2635793.7986 | 1246617.5789 | 2635784.2937 | 1246610.0992 | 2635782.1895 | 1246608.74
30 | 2635771.8707 | 1246602.0742 | 2635782.1895 | 1246608.74
31 | 2635765.7107 | 1246598.1257 | 2635769.7345 | 1246600.6942 | 2635771.8707 | 1246602.0742
32 | 2635754.1759 | 1246590.7624 | 2635765.7107 | 1246598.1257
33 | 2635754.1759 | 1246590.7624 | 2635749.6892 | 1246587.8984 | 2635748.7335 | 1246587.258
34 | 2635723.3152 | 1246737.1568 | 2635730.804 | 1246741.1962 | 2635739.0042 | 1246745.4039 | 2635742.3676 | 1246747.7964
35 | 2635723.3152 | 1246737.1568 | 2635720.7982 | 1246735.7991 | 2635709.3034 | 1246726.8019 | 2635699.2038 | 1246714.3997 | 2635695.0576 | 1246707.417
36 | 2635681.1018 | 1246689.9971 | 2635684.602 | 1246691.9973 | 2635690.5971 | 1246699.9051 | 2635695.0576 | 1246707.417
37 | 2635681.1018 | 1246689.9971 | 2635681.4994 | 1246689.199 | 2635681.9017 | 1246685.0987 | 2635681.1969 | 1246679.2018 | 2635679.0988 | 1246673.8968 | 2635675.5038 | 1246668.8052 | 2635671.6028 | 1246665.6019 | 2635647.602 | 1246649.903 | 2635625.1969 | 1246635.1033 | 2635608.5335 | 1246624.6636
38 | 2635676.1992 | 1246697.606 | 2635679.5003 | 1246693.8011 | 2635681.1018 | 1246689.9971
39 | 2635605.9026 | 1246623.0019 | 2635606.2035 | 1246623.2038 | 2635608.5335 | 1246624.6636
40 | 2635676.1992 | 1246697.606 | 2635676.0017 | 1246697.8049 | 2635671.3976 | 1246701.0016 | 2635662.2989 | 1246703.0038 | 2635658.6257 | 1246702.3235
41 | 2635605.9026 | 1246623.0019 | 2635602.0983 | 1246627.6043 | 2635599.2003 | 1246629.6994 | 2635594.1003 | 1246631.2032 | 2635587.2013 | 1246630.4057 | 2635579.4042 | 1246626.9858
42 | 2635605.9026 | 1246623.0019 | 2635591.8147 | 1246614.6097
43 | 2635638.9623 | 1246694.2194 | 2635652.0001 | 1246701.0963 | 2635658.6257 | 1246702.3235
44 | 2635544.7757 | 1246577.139 | 2635539.7021 | 1246572.4932
45 | 2635544.7757 | 1246577.139 | 2635565.2333 | 1246594.8451
46 | 2635544.7757 | 1246577.139 | 2635542.665 | 1246567.5979 | 2635538.7834 | 1246563.6721 | 2635533.8925 | 1246555.4819 | 2635528.7349 | 1246543.8768 | 2635529.6726 | 1246542.437 | 2635530.7636 | 1246541.8876 | 2635531.645 | 1246542.282 | 2635534.6134 | 1246544.8237 | 2635536.5575 | 1246546.8811 | 2635539.1359 | 1246548.9535 | 2635541.8839 | 1246550.4598 | 2635545.4497 | 1246551.6263 | 2635549.4177 | 1246552.4951 | 2635553.0409 | 1246552.906 | 2635562.7348 | 1246553.6979 | 2635565.4455 | 1246553.8698 | 2635567.1036 | 1246554.4801 | 2635568.8118 | 1246554.2902 | 2635569.9265 | 1246553.5631 | 2635570.8175 | 1246552.3676 | 2635571.0295 | 1246551.0236 | 2635571.1286 | 1246544.5755 | 2635570.7603 | 1246543.0056 | 2635569.9339 | 1246540.9882 | 2635568.6783 | 1246538.757 | 2635567.5684 | 1246537.4273 | 2635564.9979 | 1246535.2883 | 2635561.1084 | 1246531.418 | 2635556.7585 | 1246527.4782 | 2635553.8891 | 1246524.8038 | 2635551.9099 | 1246522.3014 | 2635550.3909 | 1246519.9018 | 2635548.6963 | 1246516.5562 | 2635548.0497 | 1246513.5392 | 2635548.0308 | 1246509.1251 | 2635548.4587 | 1246507.0485 | 2635549.3123 | 1246504.5187 | 2635549.3939 | 1246499.716 | 2635548.7956 | 1246497.4665 | 2635547.267 | 1246494.1441 | 2635546.5168 | 1246492.0271 | 2635545.4667 | 1246488.2628 | 2635544.2784 | 1246483.6193 | 2635542.8335 | 1246478.9298 | 2635540.249 | 1246474.0889 | 2635537.6333 | 1246470.6599 | 2635535.0365 | 1246467.8648 | 2635531.5272 | 1246464.8307 | 2635528.8541 | 1246462.1574 | 2635525.9221 | 1246458.5708 | 2635524.1623 | 1246456.0142 | 2635522.9137 | 1246453.872 | 2635521.8329 | 1246451.4528 | 2635522.1175 | 1246448.0746 | 2635567.2375 | 1246470.3926 | 2635578.325 | 1246476.8855 | 2635593.8827 | 1246489.9206 | 2635603.81 | 1246497.1626
47 | 2635591.8147 | 1246614.6097 | 2635579.6576 | 1246607.3677 | 2635566.7405 | 1246596.1496 | 2635565.2333 | 1246594.8451
48 | 2635603.81 | 1246497.1626 | 2635614.076 | 1246497.0463 | 2635621.082 | 1246496.399 | 2635627.9473 | 1246499.0642 | 2635640.0557 | 1246504.0957 | 2635644.6825 | 1246504.9613
49 | 2635603.81 | 1246497.1626 | 2635607.5224 | 1246506.6355 | 2635609.8827 | 1246509.8073 | 2635612.7795 | 1246512.96 | 2635616.6765 | 1246516.8304 | 2635625.1118 | 1246522.1956 | 2635630.8084 | 1246524.5091 | 2635640.0588 | 1246526.2213 | 2635650.1276 | 1246527.4825 | 2635655.4872 | 1246529.3889
50 | 2635644.6825 | 1246504.9613 | 2635646.6665 | 1246505.3325
51 | 2635655.4872 | 1246529.3889 | 2635659.1574 | 1246530.6944 | 2635666.7637 | 1246534.487 | 2635667.9635 | 1246535.214
52 | 2635683.4559 | 1246544.7826 | 2635677.1798 | 1246540.7982 | 2635667.9635 | 1246535.214
53 | 2635737.1472 | 1246579.4936 | 2635748.7335 | 1246587.258
54 | 2635737.1472 | 1246579.4936 | 2635732.0555 | 1246576.0814
55 | 2635723.0198 | 1246570.0262 | 2635732.0555 | 1246576.0814
56 | 2635723.0198 | 1246570.0262 | 2635741.6095 | 1246540.3456
57 | 2635723.0198 | 1246570.0262 | 2635718.0017 | 1246566.8122
58 | 2635741.6095 | 1246540.3456 | 2635743.5779 | 1246537.2028
59 | 2635714.7236 | 1246564.7125 | 2635718.0017 | 1246566.8122
60 | 2635714.7236 | 1246564.7125 | 2635700.5894 | 1246555.6597 | 2635698.822 | 1246554.5377
61 | 2635696.2195 | 1246552.8855 | 2635698.822 | 1246554.5377
62 | 2635683.4559 | 1246544.7826 | 2635696.2195 | 1246552.8855
63 | 2635644.0117 | 1246419.7771 | 2635633.7005 | 1246432.8443 | 2635605.408 | 1246416.5891
64 | 2635580.5473 | 1246402.3056 | 2635605.408 | 1246416.5891
65 | 2635580.5473 | 1246402.3056 | 2635594.3417 | 1246384.4432 | 2635584.2648 | 1246376.9224
66 | 2635584.2648 | 1246376.9224 | 2635584.0024 | 1246377.2732
67 | 2635584.2648 | 1246376.9224 | 2635594.3417 | 1246384.4432 | 2635607.2532 | 1246367.7097
68 | 2635604.14 | 1246291.0854 | 2635593.2851 | 1246304.9516 | 2635582.5291 | 1246318.6961 | 2635588.687 | 1246323.4806 | 2635582.3301 | 1246331.7257 | 2635578.7368 | 1246336.385 | 2635611.0748 | 1246362.7627 | 2635607.2532 | 1246367.7097
69 | 2635607.2532 | 1246367.7097 | 2635623.086 | 1246380.2573 | 2635678.0274 | 1246422.5065
70 | 2635607.2532 | 1246367.7097 | 2635611.0748 | 1246362.7627 | 2635653.3516 | 1246395.7046 | 2635655.5362 | 1246392.9159 | 2635668.5666 | 1246402.934
71 | 2635610.1917 | 1246283.35 | 2635604.14 | 1246291.0854
72 | 2635604.14 | 1246291.0854 | 2635626.2677 | 1246308.2849
73 | 2635668.5666 | 1246402.934 | 2635671.2994 | 1246399.4371 | 2635677.2173 | 1246404.0426
74 | 2635677.2173 | 1246404.0426 | 2635698.6367 | 1246420.7119
75 | 2635701.9129 | 1246428.5734 | 2635704.501 | 1246425.2757 | 2635698.6367 | 1246420.7119
76 | 2635712.7059 | 1246427.5154 | 2635707.725 | 1246433.0446 | 2635701.9129 | 1246428.5734
77 | 2635712.7059 | 1246427.5154 | 2635725.2156 | 1246437.5636
78 | 2635738.2421 | 1246448.0269 | 2635725.2156 | 1246437.5636
79 | 2635749.298 | 1246477.3126 | 2635752.5493 | 1246472.996 | 2635755.816 | 1246468.6573
80 | 2635755.816 | 1246468.6573 | 2635743.5822 | 1246460.6229 | 2635733.7627 | 1246453.0699 | 2635738.2421 | 1246448.0269
81 | 2635755.816 | 1246468.6573 | 2635761.0282 | 1246471.1237 | 2635767.058 | 1246472.0383 | 2635771.6154 | 1246471.61 | 2635775.1824 | 1246470.0749
82 | 2635749.298 | 1246477.3126 | 2635761.0144 | 1246485.9555 | 2635780.1184 | 1246499.5684 | 2635774.4937 | 1246511.6535 | 2635756.0293 | 1246515.9896 | 2635750.3468 | 1246526.3955
83 | 2635738.2421 | 1246448.0269 | 2635745.6599 | 1246439.674
84 | 2635781.1403 | 1246474.1468 | 2635775.1824 | 1246470.0749
85 | 2635750.3468 | 1246526.3955 | 2635738.6272 | 1246523.3007 | 2635716.8862 | 1246518.1903
86 | 2635750.3468 | 1246526.3955 | 2635743.5779 | 1246537.2028
87 | 2635750.3468 | 1246526.3955 | 2635765.8964 | 1246531.915 | 2635779.1942 | 1246541.9845
88 | 2635893.508 | 1246542.7699 | 2635927.2333 | 1246556.6829 | 2635952.7404 | 1246565.5765
89 | 2635893.508 | 1246542.7699 | 2635877.0679 | 1246580.9747
90 | 2635956.1849 | 1246555.5797 | 2635952.7404 | 1246565.5765
91 | 2635952.7404 | 1246565.5765 | 2635967.1898 | 1246570.6229 | 2636002.5446 | 1246579.9592
92 | 2635950.7489 | 1246571.3793 | 2635952.7404 | 1246565.5765
93 | 2635865.5679 | 1246607.6991 | 2635877.0679 | 1246580.9747
94 | 2635950.7489 | 1246571.3793 | 2635956.6216 | 1246573.2717 | 2635964.3814 | 1246575.5824
95 | 2635980.4497 | 1246580.013 | 2635971.9049 | 1246577.8228 | 2635964.3814 | 1246575.5824
96 | 2635756.8826 | 1246427.0365 | 2635745.6599 | 1246439.674
97 | 2635802.3993 | 1246559.5562 | 2635779.1942 | 1246541.9845
98 | 2635626.2677 | 1246308.2849 | 2635629.8367 | 1246311.0608
99 | 2635865.5679 | 1246607.6991 | 2635831.6573 | 1246581.8185
100 | 2635865.5679 | 1246607.6991 | 2635886.6206 | 1246624.9598
101 | 2635817.3505 | 1246570.8995 | 2635813.6882 | 1246568.1045 | 2635802.3993 | 1246559.5562
102 | 2635538.7392 | 1246607.5638 | 2635566.8983 | 1246621.5005 | 2635579.4042 | 1246626.9858
103 | 2636042.4399 | 1246652.7705 | 2636042.5366 | 1246652.3576
104 | 2636046.8106 | 1246634.1139 | 2636042.5366 | 1246652.3576
105 | 2636038.0946 | 1246671.3187 | 2636042.4399 | 1246652.7705
106 | 2636046.8106 | 1246634.1139 | 2636020.5513 | 1246628.4953
107 | 2636046.8106 | 1246634.1139 | 2636051.1777 | 1246612.9212
108 | 2636038.0946 | 1246671.3187 | 2636035.768 | 1246681.5904
109 | 2636020.5513 | 1246628.4953 | 2636020.1518 | 1246629.5978
110 | 2636005.7389 | 1246655.9123 | 2636011.7771 | 1246649.189 | 2636017.271 | 1246637.548 | 2636020.1518 | 1246629.5978
111 | 2636005.7389 | 1246655.9123 | 2635996.7314 | 1246661.528 | 2635987.5849 | 1246665.1639 | 2635976.0715 | 1246666.7618 | 2635965.3975 | 1246665.6965
112 | 2635944.4054 | 1246661.1359 | 2635955.4002 | 1246663.9014 | 2635965.3975 | 1246665.6965
113 | 2635812.3979 | 1246231.1986 | 2635839.5978 | 1246268.9985 | 2635863.3973 | 1246303.1979 | 2635866.9353 | 1246308.1103
114 | 2635812.3979 | 1246231.1986 | 2635777.4036 | 1246268.3008 | 2635732.4258 | 1246316.7225
115 | 2635812.3979 | 1246231.1986 | 2635796.8009 | 1246209.6016 | 2635767.6971 | 1246167.999 | 2635751.2775 | 1246146.2985
116 | 2635532.8668 | 1246653.898 | 2635536.3986 | 1246655.3956 | 2635552.4998 | 1246659.6058 | 2635594.0327 | 1246669.9891
117 | 2635619.0811 | 1246681.2524 | 2635619.0811 | 1246681.2524 | 2635606.8696 | 1246674.5859 | 2635594.1017 | 1246670.0063 | 2635594.0327 | 1246669.9891
118 | 2635886.6206 | 1246624.9598 | 2635890.7008 | 1246621.0041 | 2635894.0989 | 1246617.4001 | 2635897.3022 | 1246614.8066 | 2635902.8005 | 1246612.405 | 2635907.5997 | 1246610.6995 | 2635911.0758 | 1246609.7595
119 | 2635831.6573 | 1246581.8185 | 2635825.2855 | 1246576.9556
120 | 2635817.3505 | 1246570.8995 | 2635825.2855 | 1246576.9556
121 | 2635619.0811 | 1246681.2524 | 2635637.7996 | 1246693.6061 | 2635638.9623 | 1246694.2194

## bus_geodata
| x | y | coords
0 | 2636172.3382 | 1246729.8845
1 | 2636175.98 | 1246731.8994
2 | 2636148.0001 | 1246679.3031
3 | 2636177.3368 | 1246732.6501
4 | 2636140.8913 | 1246676.9917
5 | 2636135.0892 | 1246613.9262
6 | 2636120.1029 | 1246651.2038
7 | 2636110.1359 | 1246714.8753
8 | 2636028.8557 | 1246586.9074
9 | 2636179.9971 | 1246631.3274
10 | 2636109.0041 | 1246716.8659
11 | 2636024.5325 | 1246609.3028
12 | 2636015.712 | 1246583.4364
13 | 2635878.2983 | 1246361.1036
14 | 2635879.7202 | 1246348.6411
15 | 2635803.5209 | 1246448.7108
16 | 2635835.9481 | 1246663.0245
17 | 2635848.451 | 1246673.0836
18 | 2635831.5982 | 1246659.3056
19 | 2635849.9996 | 1246674.2934
20 | 2635820.4084 | 1246646.4501
21 | 2635864.9945 | 1246686.0838
22 | 2635813.1928 | 1246637.8156
23 | 2635898.7976 | 1246717.2049
24 | 2635808.5457 | 1246632.0005
25 | 2635793.7986 | 1246617.5789
26 | 2635796.7358 | 1246619.9495
27 | 2635782.1895 | 1246608.74
28 | 2635771.8707 | 1246602.0742
29 | 2635765.7107 | 1246598.1257
30 | 2635754.1759 | 1246590.7624
31 | 2635723.3152 | 1246737.1568
32 | 2635742.3676 | 1246747.7964
33 | 2635695.0576 | 1246707.417
34 | 2635681.1018 | 1246689.9971
35 | 2635608.5335 | 1246624.6636
36 | 2635676.1992 | 1246697.606
37 | 2635605.9026 | 1246623.0019
38 | 2635658.6257 | 1246702.3235
39 | 2635539.7021 | 1246572.4932
40 | 2635544.7757 | 1246577.139
41 | 2635565.2333 | 1246594.8451
42 | 2635603.81 | 1246497.1626
43 | 2635591.8147 | 1246614.6097
44 | 2635644.6825 | 1246504.9613
45 | 2635655.4872 | 1246529.3889
46 | 2635646.6665 | 1246505.3325
47 | 2635667.9635 | 1246535.214
48 | 2635748.7335 | 1246587.258
49 | 2635737.1472 | 1246579.4936
50 | 2635732.0555 | 1246576.0814
51 | 2635723.0198 | 1246570.0262
52 | 2635741.6095 | 1246540.3456
53 | 2635718.0017 | 1246566.8122
54 | 2635698.822 | 1246554.5377
55 | 2635714.7236 | 1246564.7125
56 | 2635696.2195 | 1246552.8855
57 | 2635683.4559 | 1246544.7826
58 | 2635644.0117 | 1246419.7771
59 | 2635605.408 | 1246416.5891
60 | 2635580.5473 | 1246402.3056
61 | 2635584.2648 | 1246376.9224
62 | 2635607.2532 | 1246367.7097
63 | 2635604.14 | 1246291.0854
64 | 2635678.0274 | 1246422.5065
65 | 2635668.5666 | 1246402.934
66 | 2635584.0024 | 1246377.2732
67 | 2635677.2173 | 1246404.0426
68 | 2635698.6367 | 1246420.7119
69 | 2635701.9129 | 1246428.5734
70 | 2635712.7059 | 1246427.5154
71 | 2635725.2156 | 1246437.5636
72 | 2635755.816 | 1246468.6573
73 | 2635749.298 | 1246477.3126
74 | 2635738.2421 | 1246448.0269
75 | 2635775.1824 | 1246470.0749
76 | 2635750.3468 | 1246526.3955
77 | 2635893.508 | 1246542.7699
78 | 2635952.7404 | 1246565.5765
79 | 2635877.0679 | 1246580.9747
80 | 2635781.1403 | 1246474.1468
81 | 2635950.7489 | 1246571.3793
82 | 2635964.3814 | 1246575.5824
83 | 2635745.6599 | 1246439.674
84 | 2635716.8862 | 1246518.1903
85 | 2635743.5779 | 1246537.2028
86 | 2635779.1942 | 1246541.9845
87 | 2635610.1917 | 1246283.35
88 | 2635626.2677 | 1246308.2849
89 | 2635629.8367 | 1246311.0608
90 | 2635956.1849 | 1246555.5797
91 | 2636002.5446 | 1246579.9592
92 | 2635865.5679 | 1246607.6991
93 | 2635980.4497 | 1246580.013
94 | 2635756.8826 | 1246427.0365
95 | 2635802.3993 | 1246559.5562
96 | 2635579.4042 | 1246626.9858
97 | 2635538.7392 | 1246607.5638
98 | 2636042.5366 | 1246652.3576
99 | 2636042.4399 | 1246652.7705
100 | 2636046.8106 | 1246634.1139
101 | 2636038.0946 | 1246671.3187
102 | 2636020.5513 | 1246628.4953
103 | 2636051.1777 | 1246612.9212
104 | 2636035.768 | 1246681.5904
105 | 2636020.1518 | 1246629.5978
106 | 2636005.7389 | 1246655.9123
107 | 2635965.3975 | 1246665.6965
108 | 2635866.9353 | 1246308.1103
109 | 2635812.3979 | 1246231.1986
110 | 2635751.2775 | 1246146.2985
111 | 2635532.8668 | 1246653.898
112 | 2635594.0327 | 1246669.9891
113 | 2635804.728 | 1246698.6345
114 | 2635944.4054 | 1246661.1359
115 | 2635911.0758 | 1246609.7595
116 | 2635886.6206 | 1246624.9598
117 | 2635831.6573 | 1246581.8185
118 | 2635825.2855 | 1246576.9556
119 | 2635619.0811 | 1246681.2524
120 | 2635638.9623 | 1246694.2194
121 | 2635732.4258 | 1246316.7225
122 | 2635817.3505 | 1246570.8995
123 | 2635952.7404 | 1246565.5765

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98837 | -0.22299 | 0.00066526 | 0.00016673
1 | 0.98836 | -0.22313 | 0.0013908 | 0.00034856
2 | 0.9885 | -0.22042 | 0 | 0
3 | 0.98836 | -0.22315 | 0.0004994 | 0.00012516
4 | 0.98838 | -0.22289 | 0 | 0
5 | 0.9898 | -0.1952 | 0 | 0
6 | 0.9883 | -0.22437 | 0.0024965 | 0.00062568
7 | 0.98764 | -0.23728 | 0.0082882 | 0.0020772
8 | 0.99275 | -0.13819 | 0 | 0
9 | 0.98943 | -0.20238 | 0.008358 | 0.0020947
10 | 0.98762 | -0.2376 | 0.0076863 | 0.0019264
11 | 0.99043 | -0.18279 | 0.0037028 | 0.00092801
12 | 0.9945 | -0.10467 | 0.0089379 | 0.0022401
13 | 0.98168 | -0.35121 | 0 | 0
14 | 0.9814 | -0.35663 | 0.006853 | 0.0017175
15 | 0.98425 | -0.30129 | 0.001876 | 0.00047018
16 | 0.98512 | -0.28478 | 0.001991 | 0.00049898
17 | 0.98501 | -0.28696 | 0.0019892 | 0.00049854
18 | 0.98517 | -0.28379 | 0.0013205 | 0.00033095
19 | 0.985 | -0.28716 | 0.0017117 | 0.00042899
20 | 0.98534 | -0.28046 | 0.0018935 | 0.00047455
21 | 0.98493 | -0.28849 | 0.0022298 | 0.00055884
22 | 0.98548 | -0.27788 | 0.0018245 | 0.00045726
23 | 0.98486 | -0.28984 | 0 | 0
24 | 0.98558 | -0.27593 | 0.0016106 | 0.00040365
25 | 0.98589 | -0.26985 | 0.0015204 | 0.00038104
26 | 0.98583 | -0.27101 | 0.0010246 | 0.00025679
27 | 0.98614 | -0.26494 | 0.0011881 | 0.00029776
28 | 0.98637 | -0.26054 | 0.0016215 | 0.00040639
29 | 0.98651 | -0.25772 | 0.00049858 | 0.00012496
30 | 0.98679 | -0.25231 | 0.0013714 | 0.00034371
31 | 0.97437 | -0.49409 | 0.001664 | 0.00041703
32 | 0.97432 | -0.49508 | 0.0024612 | 0.00061682
33 | 0.97453 | -0.49094 | 0.002363 | 0.00059222
34 | 0.97467 | -0.48824 | 0 | 0
35 | 0.97747 | -0.43326 | 0.0034693 | 0.00086949
36 | 0.97448 | -0.49205 | 0 | 0
37 | 0.97756 | -0.4314 | 0 | 0
38 | 0.97408 | -0.49992 | 0.0061131 | 0.0015321
39 | 0.98031 | -0.37759 | 0.0014205 | 0.00035602
40 | 0.98032 | -0.37741 | 0 | 0
41 | 0.97931 | -0.39714 | 0.0016632 | 0.00041683
42 | 0.98617 | -0.26411 | 0 | 0
43 | 0.97812 | -0.42045 | 0.0018432 | 0.00046196
44 | 0.98614 | -0.26463 | 0.00035791 | 8.97e-05
45 | 0.98681 | -0.25174 | 0.00074625 | 0.00018703
46 | 0.98614 | -0.26464 | 0.00032811 | 8.2231e-05
47 | 0.98695 | -0.24908 | 0.00044582 | 0.00011173
48 | 0.98693 | -0.24959 | 0.00050053 | 0.00012544
49 | 0.98724 | -0.24362 | 0.00055661 | 0.0001395
50 | 0.98737 | -0.24093 | 0.00066942 | 0.00016777
51 | 0.98763 | -0.23604 | 0 | 0
52 | 0.98821 | -0.2248 | 0.0013256 | 0.00033222
53 | 0.98756 | -0.23729 | 0.00071231 | 0.00017852
54 | 0.98732 | -0.24193 | 0.00055275 | 0.00013853
55 | 0.98752 | -0.23809 | 0.00049808 | 0.00012483
56 | 0.98729 | -0.24255 | 0.000734 | 0.00018396
57 | 0.98713 | -0.24554 | 0.00072236 | 0.00018104
58 | 0.97844 | -0.415 | 0.003494 | 0.00087569
59 | 0.9786 | -0.41186 | 0.01502 | 0.0037643
60 | 0.97909 | -0.40221 | 0 | 0
61 | 0.97969 | -0.39038 | 0 | 0
62 | 0.98029 | -0.3786 | 0 | 0
63 | 0.98001 | -0.38406 | 0 | 0
64 | 0.98004 | -0.38346 | 0.0029911 | 0.00074964
65 | 0.98214 | -0.34239 | 0 | 0
66 | 0.97969 | -0.39039 | 0.0007372 | 0.00018476
67 | 0.98242 | -0.33698 | 7.9368e-05 | 1.9892e-05
68 | 0.98305 | -0.32467 | 0.0013262 | 0.00033237
69 | 0.98334 | -0.31912 | 0 | 0
70 | 0.9837 | -0.31207 | 0 | 0
71 | 0.98409 | -0.30443 | 0.0042134 | 0.001056
72 | 0.98564 | -0.27438 | 0 | 0
73 | 0.98597 | -0.26795 | 0 | 0
74 | 0.98457 | -0.2952 | 0 | 0
75 | 0.98518 | -0.28331 | 0.00055709 | 0.00013962
76 | 0.98849 | -0.21937 | 0 | 0
77 | 1 | 0 | -0.46731 | -0.11923
78 | 0.99726 | -0.052035 | 0 | 0
79 | 0.9974 | -0.049263 | 0.01042 | 0.0026114
80 | 0.98501 | -0.28647 | 0 | 0
81 | 0.9971 | -0.055246 | 0 | 0
82 | 0.99671 | -0.062716 | 0.014933 | 0.0037426
83 | 0.98453 | -0.29594 | 0.0023216 | 0.00058184
84 | 0.98847 | -0.21966 | 0.00046992 | 0.00011777
85 | 0.98827 | -0.22359 | 0.00097968 | 0.00024553
86 | 0.99008 | -0.18879 | 0.0008907 | 0.00022323
87 | 0.98 | -0.38442 | 0.0019989 | 0.00050097
88 | 0.97999 | -0.38447 | 0 | 0
89 | 0.97999 | -0.38454 | 0.0008064 | 0.0002021
90 | 0.99721 | -0.053006 | 0.0052378 | 0.0013127
91 | 0.99543 | -0.086858 | 0.0043286 | 0.0010848
92 | 0.99564 | -0.082542 | 0 | 0
93 | 0.99648 | -0.067082 | 0.014923 | 0.0037401
94 | 0.98451 | -0.29634 | 0.0013272 | 0.00033262
95 | 0.99148 | -0.16194 | 0.0075054 | 0.001881
96 | 0.97745 | -0.43365 | 0.0022643 | 0.0005675
97 | 0.97737 | -0.43511 | 0.0017851 | 0.00044739
98 | 0.98816 | -0.22663 | 0.0028311 | 0.00070955
99 | 0.98816 | -0.22665 | 0.0021327 | 0.00053449
100 | 0.98826 | -0.22464 | 0 | 0
101 | 0.98814 | -0.22699 | 0 | 0
102 | 0.9885 | -0.21997 | 0 | 0
103 | 0.98818 | -0.22612 | 0.0038246 | 0.00095853
104 | 0.98813 | -0.22717 | 0.00098246 | 0.00024623
105 | 0.98839 | -0.222 | 0.0036148 | 0.00090594
106 | 0.98578 | -0.27261 | 0 | 0
107 | 0.98209 | -0.34442 | 0.043778 | 0.010972
108 | 0.98051 | -0.37402 | 0.019201 | 0.0048123
109 | 0.97899 | -0.40372 | 0 | 0
110 | 0.97576 | -0.46719 | 0.066493 | 0.016665
111 | 0.97312 | -0.51883 | 0.0039741 | 0.00099601
112 | 0.97336 | -0.5142 | 0.0021587 | 0.00054103
113 | 0.98463 | -0.29435 | 0.0016351 | 0.0004098
114 | 0.98111 | -0.36363 | 0.0494 | 0.012381
115 | 0.99425 | -0.10949 | 0.027024 | 0.0067728
116 | 0.99497 | -0.095465 | 0 | 0
117 | 0.99334 | -0.12646 | 0.010441 | 0.0026168
118 | 0.99292 | -0.13436 | 0.0039438 | 0.00098842
119 | 0.97351 | -0.51109 | 0.0045098 | 0.0011303
120 | 0.97375 | -0.50645 | 0.0058889 | 0.0014759
121 | 0.97868 | -0.40987 | 0.002887 | 0.00072356
122 | 0.99242 | -0.14404 | 0.0039121 | 0.00098047
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0018902 | 0.00047366 | -0.0018902 | -0.0004737 | 1.2639e-08 | -4.5251e-08 | 0.0028457 | 0.0028457 | 0.0028457 | 0.98837 | -0.22299 | 0.98836 | -0.22313 | 0.78179
1 | -0.0025555 | -0.00064039 | 0.0025558 | 0.00063987 | 3.1268e-07 | -5.2199e-07 | 0.0038473 | 0.003847 | 0.0038473 | 0.98837 | -0.22299 | 0.9885 | -0.22042 | 1.0569
2 | 0.0004994 | 0.00012514 | -0.0004994 | -0.00012516 | 3.2873e-10 | -1.9661e-08 | 0.00075186 | 0.00075187 | 0.00075187 | 0.98836 | -0.22313 | 0.98836 | -0.22315 | 0.20656
3 | 0.018484 | 0.0046367 | -0.018482 | -0.0046354 | 2.1714e-06 | 1.2938e-06 | 0.027826 | 0.027826 | 0.027826 | 0.9885 | -0.22042 | 0.98838 | -0.22289 | 7.6446
4 | -0.02104 | -0.0052765 | 0.021066 | 0.0052919 | 2.5326e-05 | 1.5345e-05 | 0.031673 | 0.031673 | 0.031673 | 0.9885 | -0.22042 | 0.9898 | -0.1952 | 8.7015
5 | 0.0024967 | 0.00062536 | -0.0024965 | -0.00062568 | 1.763e-07 | -3.1361e-07 | 0.0037586 | 0.0037588 | 0.0037588 | 0.98838 | -0.22289 | 0.9883 | -0.22437 | 1.0326
6 | 0.015986 | 0.00401 | -0.015975 | -0.0040036 | 1.096e-05 | 6.3685e-06 | 0.024068 | 0.024068 | 0.024068 | 0.98838 | -0.22289 | 0.98764 | -0.23728 | 6.6121
7 | -0.029426 | -0.0073878 | 0.029507 | 0.0074377 | 8.0255e-05 | 4.9953e-05 | 0.044243 | 0.044242 | 0.044243 | 0.9898 | -0.1952 | 0.99275 | -0.13819 | 12.1545
8 | 0.0083608 | 0.0020959 | -0.008358 | -0.0020947 | 2.8575e-06 | 1.2091e-06 | 0.012569 | 0.01257 | 0.01257 | 0.9898 | -0.1952 | 0.98943 | -0.20238 | 3.4532
9 | 0.0076864 | 0.0019264 | -0.0076863 | -0.0019264 | 1.1516e-07 | 4.44e-08 | 0.011581 | 0.011581 | 0.011581 | 0.98764 | -0.23728 | 0.98762 | -0.2376 | 3.1815
10 | 0.1113 | 0.028295 | -0.11106 | -0.028142 | 0.00023849 | 0.00015234 | 0.16697 | 0.16697 | 0.16697 | 0.99275 | -0.13819 | 0.99043 | -0.18279 | 45.8707
11 | -0.14081 | -0.035732 | 0.14103 | 0.035878 | 0.00022742 | 0.00014537 | 0.21121 | 0.21121 | 0.21121 | 0.99275 | -0.13819 | 0.9945 | -0.10467 | 58.0251
12 | 0.10736 | 0.027214 | -0.10717 | -0.027092 | 0.00019149 | 0.0001223 | 0.16141 | 0.16141 | 0.16141 | 0.99043 | -0.18279 | 0.9885 | -0.21997 | 44.3424
13 | -0.14997 | -0.038118 | 0.1501 | 0.0382 | 0.00012879 | 8.2075e-05 | 0.22458 | 0.22458 | 0.22458 | 0.9945 | -0.10467 | 0.99543 | -0.086858 | 30.8495
14 | 0.095834 | 0.024162 | -0.095809 | -0.024147 | 2.4844e-05 | 1.5266e-05 | 0.14532 | 0.14532 | 0.14532 | 0.98168 | -0.35121 | 0.9814 | -0.35663 | 9.9805
15 | -0.095834 | -0.024162 | 0.096063 | 0.024303 | 0.00022954 | 0.00014103 | 0.14532 | 0.14531 | 0.14532 | 0.98168 | -0.35121 | 0.98425 | -0.30129 | 9.9804
16 | 0.088956 | 0.02243 | -0.088882 | -0.022385 | 7.394e-05 | 4.5134e-05 | 0.13492 | 0.13493 | 0.13493 | 0.9814 | -0.35663 | 0.98051 | -0.37402 | 9.2669
17 | -0.09794 | -0.024774 | 0.098009 | 0.024817 | 6.9719e-05 | 4.2896e-05 | 0.14815 | 0.14815 | 0.14815 | 0.98425 | -0.30129 | 0.98501 | -0.28647 | 10.1751
18 | 0.0075673 | 0.0018941 | -0.0075666 | -0.0018939 | 7.8629e-07 | 2.9889e-07 | 0.01143 | 0.01143 | 0.01143 | 0.98512 | -0.28478 | 0.98501 | -0.28696 | 3.14
19 | -0.0095583 | -0.0023931 | 0.0095588 | 0.0023933 | 4.473e-07 | 2.134e-07 | 0.014437 | 0.014437 | 0.014437 | 0.98512 | -0.28478 | 0.98517 | -0.28379 | 3.9662
20 | 0.0055774 | 0.0013953 | -0.0055773 | -0.0013953 | 5.2301e-08 | 8.4594e-09 | 0.0084246 | 0.0084246 | 0.0084246 | 0.98501 | -0.28696 | 0.985 | -0.28716 | 2.3144
21 | -0.010879 | -0.0027243 | 0.010881 | 0.0027252 | 1.7256e-06 | 8.8734e-07 | 0.016431 | 0.016431 | 0.016431 | 0.98517 | -0.28379 | 0.98534 | -0.28046 | 4.5141
22 | 0.0038656 | 0.00096631 | -0.0038654 | -0.0009664 | 2.4387e-07 | -8.6711e-08 | 0.0058388 | 0.0058389 | 0.0058389 | 0.985 | -0.28716 | 0.98493 | -0.28849 | 1.6041
23 | -0.012774 | -0.0031997 | 0.012776 | 0.0032006 | 1.5711e-06 | 8.6209e-07 | 0.019291 | 0.019291 | 0.019291 | 0.98534 | -0.28046 | 0.98548 | -0.27788 | 5.2996
24 | 0.0016356 | 0.00040755 | -0.0016355 | -0.00040807 | 1.0522e-07 | -5.1785e-07 | 0.0024701 | 0.0024703 | 0.0024703 | 0.98493 | -0.28849 | 0.98486 | -0.28984 | 0.67866
25 | -0.014601 | -0.0036579 | 0.014602 | 0.0036586 | 1.3569e-06 | 7.7355e-07 | 0.022046 | 0.022045 | 0.022046 | 0.98548 | -0.27788 | 0.98558 | -0.27593 | 6.0565
26 | 0.0016355 | 0.00040807 | -0.0016351 | -0.0004098 | 3.5073e-07 | -1.7248e-06 | 0.0024703 | 0.002471 | 0.002471 | 0.98486 | -0.28984 | 0.98463 | -0.29435 | 0.67885
27 | -0.016212 | -0.0040623 | 0.016216 | 0.0040645 | 3.7979e-06 | 2.2152e-06 | 0.024477 | 0.024477 | 0.024477 | 0.98558 | -0.27593 | 0.98583 | -0.27101 | 6.7245
28 | 0.017242 | 0.0043219 | -0.017241 | -0.0043213 | 9.5892e-07 | 5.6556e-07 | 0.026024 | 0.026024 | 0.026024 | 0.98589 | -0.26985 | 0.98583 | -0.27101 | 7.1493
29 | -0.018762 | -0.0047029 | 0.018767 | 0.0047055 | 4.3905e-06 | 2.6237e-06 | 0.028318 | 0.028318 | 0.028318 | 0.98589 | -0.26985 | 0.98614 | -0.26494 | 7.7798
30 | -0.019955 | -0.0050033 | 0.019959 | 0.0050058 | 4.1767e-06 | 2.5164e-06 | 0.030111 | 0.030111 | 0.030111 | 0.98614 | -0.26494 | 0.98637 | -0.26054 | 8.2722
31 | -0.02158 | -0.0054122 | 0.021583 | 0.0054139 | 2.9084e-06 | 1.7679e-06 | 0.032557 | 0.032557 | 0.032557 | 0.98637 | -0.26054 | 0.98651 | -0.25772 | 8.9442
32 | -0.022082 | -0.0055389 | 0.022088 | 0.0055424 | 5.6936e-06 | 3.4692e-06 | 0.033309 | 0.033309 | 0.033309 | 0.98651 | -0.25772 | 0.98679 | -0.25231 | 9.1508
33 | -0.023459 | -0.0058861 | 0.023462 | 0.0058879 | 3.0381e-06 | 1.8617e-06 | 0.035377 | 0.035377 | 0.035377 | 0.98679 | -0.25231 | 0.98693 | -0.24959 | 9.719
34 | 0.0024613 | 0.00061663 | -0.0024612 | -0.00061682 | 1.1578e-07 | -1.9808e-07 | 0.0037587 | 0.0037588 | 0.0037588 | 0.97437 | -0.49409 | 0.97432 | -0.49508 | 1.0326
35 | -0.0041253 | -0.0010337 | 0.0041259 | 0.0010335 | 6.1869e-07 | -1.2192e-07 | 0.0062998 | 0.0062996 | 0.0062998 | 0.97437 | -0.49409 | 0.97453 | -0.49094 | 1.7307
36 | -0.0064889 | -0.0016258 | 0.0064897 | 0.001626 | 8.3527e-07 | 2.5181e-07 | 0.0099076 | 0.0099075 | 0.0099076 | 0.97453 | -0.49094 | 0.97467 | -0.48824 | 2.7219
37 | -0.029156 | -0.0073133 | 0.029233 | 0.007361 | 7.6634e-05 | 4.7756e-05 | 0.044515 | 0.044514 | 0.044515 | 0.97467 | -0.48824 | 0.97747 | -0.43326 | 12.2293
38 | 0.022667 | 0.0056873 | -0.022662 | -0.0056847 | 4.1126e-06 | 2.518e-06 | 0.034607 | 0.034607 | 0.034607 | 0.97467 | -0.48824 | 0.97448 | -0.49205 | 9.5074
39 | -0.032702 | -0.0082305 | 0.032705 | 0.0082323 | 2.8936e-06 | 1.8129e-06 | 0.049796 | 0.049795 | 0.049796 | 0.97747 | -0.43326 | 0.97756 | -0.4314 | 13.6801
40 | 0.022662 | 0.0056847 | -0.022654 | -0.0056795 | 8.5052e-06 | 5.2075e-06 | 0.034607 | 0.034607 | 0.034607 | 0.97448 | -0.49205 | 0.97408 | -0.49992 | 9.5075
41 | 0.00405 | 0.0010143 | -0.0040496 | -0.0010144 | 4.3213e-07 | -1.0356e-07 | 0.0061645 | 0.0061647 | 0.0061647 | 0.97756 | -0.4314 | 0.97745 | -0.43365 | 1.6936
42 | -0.036755 | -0.0092466 | 0.036774 | 0.0092587 | 1.9257e-05 | 1.2119e-05 | 0.05596 | 0.05596 | 0.05596 | 0.97756 | -0.4314 | 0.97812 | -0.42045 | 15.3736
43 | 0.016541 | 0.0041474 | -0.016536 | -0.0041444 | 5.1429e-06 | 3.0242e-06 | 0.025269 | 0.025269 | 0.025269 | 0.97408 | -0.49992 | 0.97375 | -0.50645 | 6.942
44 | -0.0014205 | -0.00035602 | 0.0014205 | 0.00035594 | 1.1994e-08 | -7.9059e-08 | 0.0021562 | 0.0021562 | 0.0021562 | 0.98031 | -0.37759 | 0.98032 | -0.37741 | 0.59237
45 | 0.040362 | 0.010189 | -0.040324 | -0.010165 | 3.8114e-05 | 2.4052e-05 | 0.061291 | 0.061291 | 0.061291 | 0.98032 | -0.37741 | 0.97931 | -0.39714 | 16.8382
46 | -0.041782 | -0.010545 | 0.042011 | 0.010683 | 0.00022803 | 0.00013827 | 0.063447 | 0.063444 | 0.063447 | 0.98032 | -0.37741 | 0.98617 | -0.26411 | 8.7153
47 | 0.038661 | 0.0097478 | -0.038618 | -0.0097207 | 4.306e-05 | 2.7141e-05 | 0.058764 | 0.058764 | 0.058764 | 0.97931 | -0.39714 | 0.97812 | -0.42045 | 16.144
48 | 0.00068603 | 0.00017137 | -0.00068601 | -0.00017191 | 1.7068e-08 | -5.3114e-07 | 0.0010349 | 0.0010351 | 0.0010351 | 0.98617 | -0.26411 | 0.98614 | -0.26463 | 0.28438
49 | -0.042697 | -0.010854 | 0.042722 | 0.010867 | 2.5448e-05 | 1.2952e-05 | 0.064479 | 0.064478 | 0.064479 | 0.98617 | -0.26411 | 0.98681 | -0.25174 | 4.4285
50 | 0.00032811 | 8.2206e-05 | -0.00032811 | -8.2231e-05 | 1.8548e-10 | -2.5632e-08 | 0.00049508 | 0.00049509 | 0.00049509 | 0.98614 | -0.26463 | 0.98614 | -0.26464 | 0.13601
51 | -0.043468 | -0.011054 | 0.043474 | 0.011057 | 5.5671e-06 | 2.8578e-06 | 0.065603 | 0.065603 | 0.065603 | 0.98681 | -0.25174 | 0.98695 | -0.24908 | 4.5057
52 | -0.04392 | -0.011169 | 0.043927 | 0.011173 | 7.4987e-06 | 3.8682e-06 | 0.066275 | 0.066275 | 0.066275 | 0.98695 | -0.24908 | 0.98713 | -0.24554 | 4.5519
53 | -0.023963 | -0.0060134 | 0.023969 | 0.0060176 | 6.8281e-06 | 4.1917e-06 | 0.036132 | 0.036132 | 0.036132 | 0.98693 | -0.24959 | 0.98724 | -0.24362 | 9.9263
54 | -0.024526 | -0.0061571 | 0.024529 | 0.006159 | 3.1416e-06 | 1.9322e-06 | 0.036971 | 0.036971 | 0.036971 | 0.98724 | -0.24362 | 0.98737 | -0.24093 | 10.1567
55 | -0.025199 | -0.0063268 | 0.025204 | 0.0063304 | 5.8835e-06 | 3.6263e-06 | 0.037979 | 0.037979 | 0.037979 | 0.98737 | -0.24093 | 0.98763 | -0.23604 | 10.4339
56 | -0.072372 | -0.018321 | 0.072411 | 0.018344 | 3.9084e-05 | 2.322e-05 | 0.10911 | 0.1091 | 0.10911 | 0.98763 | -0.23604 | 0.98821 | -0.2248 | 7.4935
57 | 0.047168 | 0.011991 | -0.047165 | -0.011989 | 2.8263e-06 | 1.5038e-06 | 0.071126 | 0.071126 | 0.071126 | 0.98763 | -0.23604 | 0.98756 | -0.23729 | 4.885
58 | -0.073737 | -0.018676 | 0.073741 | 0.018679 | 4.2912e-06 | 2.5563e-06 | 0.1111 | 0.1111 | 0.1111 | 0.98821 | -0.2248 | 0.98827 | -0.22359 | 7.6305
59 | 0.046452 | 0.011811 | -0.046451 | -0.01181 | 1.791e-06 | 9.4701e-07 | 0.070053 | 0.070053 | 0.070053 | 0.98756 | -0.23729 | 0.98752 | -0.23809 | 4.8113
60 | -0.045944 | -0.01168 | 0.045953 | 0.011685 | 8.5003e-06 | 4.4743e-06 | 0.069303 | 0.069302 | 0.069303 | 0.98732 | -0.24193 | 0.98752 | -0.23809 | 4.7598
61 | 0.045391 | 0.011542 | -0.04539 | -0.011541 | 1.3549e-06 | 7.0942e-07 | 0.06847 | 0.06847 | 0.06847 | 0.98732 | -0.24193 | 0.98729 | -0.24255 | 4.7026
62 | 0.044656 | 0.011357 | -0.044649 | -0.011354 | 6.4317e-06 | 3.3431e-06 | 0.067364 | 0.067364 | 0.067364 | 0.98729 | -0.24255 | 0.98713 | -0.24554 | 4.6266
63 | -0.003494 | -0.00087569 | 0.0034946 | 0.0008754 | 5.2173e-07 | -2.8507e-07 | 0.0053138 | 0.0053136 | 0.0053138 | 0.97844 | -0.415 | 0.9786 | -0.41186 | 1.4598
64 | -0.018514 | -0.0046397 | 0.018523 | 0.0046448 | 8.5212e-06 | 5.0931e-06 | 0.028152 | 0.028152 | 0.028152 | 0.9786 | -0.41186 | 0.97909 | -0.40221 | 7.734
65 | -0.018523 | -0.0046448 | 0.018533 | 0.004651 | 1.0444e-05 | 6.242e-06 | 0.028152 | 0.028152 | 0.028152 | 0.97909 | -0.40221 | 0.97969 | -0.39038 | 7.734
66 | 0.0007372 | 0.00018476 | -0.0007372 | -0.00018476 | 2.0581e-10 | -5.3848e-09 | 0.0011197 | 0.0011197 | 0.0011197 | 0.97969 | -0.39038 | 0.97969 | -0.39039 | 0.30761
67 | -0.01927 | -0.0048358 | 0.019281 | 0.0048423 | 1.0831e-05 | 6.5071e-06 | 0.029271 | 0.029271 | 0.029271 | 0.97969 | -0.39038 | 0.98029 | -0.3786 | 8.0416
68 | 0.0028061 | 0.00070169 | -0.0028053 | -0.00070257 | 7.2881e-07 | -8.839e-07 | 0.0042589 | 0.0042593 | 0.0042593 | 0.98029 | -0.3786 | 0.98001 | -0.38406 | 1.1702
69 | 0.0029918 | 0.00074895 | -0.0029911 | -0.00074964 | 6.9222e-07 | -6.8517e-07 | 0.004541 | 0.0045414 | 0.0045414 | 0.98029 | -0.3786 | 0.98004 | -0.38346 | 1.2476
70 | -0.025079 | -0.0062929 | 0.025122 | 0.0063197 | 4.3387e-05 | 2.6759e-05 | 0.038071 | 0.038071 | 0.038071 | 0.98029 | -0.3786 | 0.98214 | -0.34239 | 10.4591
71 | 0.0019989 | 0.00050087 | -0.0019989 | -0.00050097 | 3.3891e-08 | -1.0193e-07 | 0.0030351 | 0.0030351 | 0.0030351 | 0.98001 | -0.38406 | 0.98 | -0.38442 | 0.83382
72 | 0.00080642 | 0.00020171 | -0.0008064 | -0.00020205 | 1.5726e-08 | -3.4242e-07 | 0.0012243 | 0.0012244 | 0.0012244 | 0.98001 | -0.38406 | 0.97999 | -0.38447 | 0.33638
73 | -0.025122 | -0.0063197 | 0.025129 | 0.0063237 | 6.4879e-06 | 4.0012e-06 | 0.038071 | 0.038071 | 0.038071 | 0.98214 | -0.34239 | 0.98242 | -0.33698 | 10.459
74 | -0.025208 | -0.0063436 | 0.025223 | 0.0063527 | 1.4845e-05 | 9.1569e-06 | 0.038191 | 0.038191 | 0.038191 | 0.98242 | -0.33698 | 0.98305 | -0.32467 | 10.492
75 | -0.026549 | -0.0066851 | 0.026556 | 0.0066895 | 7.043e-06 | 4.3601e-06 | 0.040198 | 0.040198 | 0.040198 | 0.98305 | -0.32467 | 0.98334 | -0.31912 | 11.0434
76 | -0.026556 | -0.0066895 | 0.026565 | 0.006695 | 8.9529e-06 | 5.5423e-06 | 0.040198 | 0.040198 | 0.040198 | 0.98334 | -0.31912 | 0.9837 | -0.31207 | 11.0434
77 | -0.026565 | -0.006695 | 0.026575 | 0.006701 | 9.7228e-06 | 6.0188e-06 | 0.040198 | 0.040198 | 0.040198 | 0.9837 | -0.31207 | 0.98409 | -0.30443 | 11.0434
78 | -0.030788 | -0.007757 | 0.030802 | 0.0077655 | 1.3588e-05 | 8.4839e-06 | 0.046569 | 0.046569 | 0.046569 | 0.98409 | -0.30443 | 0.98457 | -0.2952 | 12.7936
79 | -0.13311 | -0.033693 | 0.13315 | 0.033718 | 4.1069e-05 | 2.5731e-05 | 0.20107 | 0.20107 | 0.20107 | 0.98564 | -0.27438 | 0.98597 | -0.26795 | 13.8099
80 | 0.034485 | 0.0087012 | -0.034451 | -0.0086797 | 3.4352e-05 | 2.1555e-05 | 0.052083 | 0.052083 | 0.052083 | 0.98564 | -0.27438 | 0.98457 | -0.2952 | 14.3086
81 | 0.098623 | 0.024991 | -0.098581 | -0.024965 | 4.2299e-05 | 2.6036e-05 | 0.14899 | 0.14899 | 0.14899 | 0.98564 | -0.27438 | 0.98518 | -0.28331 | 10.2328
82 | -0.13315 | -0.033718 | 0.13346 | 0.033913 | 0.00031145 | 0.00019513 | 0.20107 | 0.20107 | 0.20107 | 0.98597 | -0.26795 | 0.98849 | -0.21937 | 13.8099
83 | 0.0036489 | 0.0009142 | -0.0036488 | -0.00091426 | 1.274e-07 | -6.0528e-08 | 0.0055146 | 0.0055147 | 0.0055147 | 0.98457 | -0.2952 | 0.98453 | -0.29594 | 1.515
84 | 0.098024 | 0.024826 | -0.098009 | -0.024817 | 1.4849e-05 | 9.1357e-06 | 0.14815 | 0.14815 | 0.14815 | 0.98518 | -0.28331 | 0.98501 | -0.28647 | 10.1751
85 | 0.00046992 | 0.00011734 | -0.00046992 | -0.00011777 | 6.4642e-09 | -4.3753e-07 | 0.00070724 | 0.0007074 | 0.0007074 | 0.98849 | -0.21937 | 0.98847 | -0.21966 | 0.19434
86 | 0.074736 | 0.018934 | -0.074721 | -0.018925 | 1.5151e-05 | 9.0429e-06 | 0.11258 | 0.11258 | 0.11258 | 0.98849 | -0.21937 | 0.98827 | -0.22359 | 7.7318
87 | -0.20867 | -0.052964 | 0.20897 | 0.053159 | 0.00030739 | 0.00019502 | 0.31435 | 0.31435 | 0.31435 | 0.98849 | -0.21937 | 0.99008 | -0.18879 | 21.5902
88 | 0.19028 | 0.048557 | -0.1898 | -0.048255 | 0.00047702 | 0.00030198 | 0.28345 | 0.28345 | 0.28345 | 1 | 0 | 0.99726 | -0.052035 | 19.4676
89 | 0.27538 | 0.070675 | -0.27472 | -0.070257 | 0.00065661 | 0.00041805 | 0.41036 | 0.41036 | 0.41036 | 1 | 0 | 0.9974 | -0.049263 | 28.184
90 | 0.0052381 | 0.0013127 | -0.0052378 | -0.0013127 | 2.4218e-07 | 1.7061e-08 | 0.0078157 | 0.0078158 | 0.0078158 | 0.99726 | -0.052035 | 0.99721 | -0.053006 | 2.1472
91 | 0.15469 | 0.039448 | -0.15443 | -0.039285 | 0.00025962 | 0.00016345 | 0.23105 | 0.23105 | 0.23105 | 0.99726 | -0.052035 | 0.99543 | -0.086858 | 15.8691
92 | 0.029875 | 0.007494 | -0.02987 | -0.0074912 | 4.5712e-06 | 2.8455e-06 | 0.044579 | 0.044579 | 0.044579 | 0.99726 | -0.052035 | 0.9971 | -0.055246 | 12.2469
93 | 0.2643 | 0.067646 | -0.26388 | -0.067375 | 0.00042516 | 0.00027059 | 0.39481 | 0.39481 | 0.39481 | 0.9974 | -0.049263 | 0.99564 | -0.082542 | 27.1164
94 | 0.02987 | 0.0074912 | -0.02986 | -0.0074845 | 1.0632e-05 | 6.6184e-06 | 0.044579 | 0.044579 | 0.044579 | 0.9971 | -0.055246 | 0.99671 | -0.062716 | 12.2469
95 | 0.014926 | 0.0037419 | -0.014923 | -0.0037401 | 3.1045e-06 | 1.7697e-06 | 0.022284 | 0.022284 | 0.022284 | 0.99671 | -0.062716 | 0.99648 | -0.067082 | 6.1221
96 | 0.0013272 | 0.00033243 | -0.0013272 | -0.00033262 | 2.5502e-08 | -1.986e-07 | 0.0020059 | 0.002006 | 0.002006 | 0.98453 | -0.29594 | 0.98451 | -0.29634 | 0.55109
97 | -0.20986 | -0.053383 | 0.21014 | 0.053555 | 0.00027196 | 0.00017255 | 0.31569 | 0.31569 | 0.31569 | 0.99008 | -0.18879 | 0.99148 | -0.16194 | 21.6821
98 | 0.0008064 | 0.00020205 | -0.0008064 | -0.0002021 | 2.542e-09 | -5.5341e-08 | 0.0012244 | 0.0012244 | 0.0012244 | 0.97999 | -0.38447 | 0.97999 | -0.38454 | 0.33638
99 | 0.23682 | 0.060581 | -0.23632 | -0.060262 | 0.00050222 | 0.0003192 | 0.35437 | 0.35437 | 0.35437 | 0.99564 | -0.082542 | 0.99334 | -0.12646 | 24.3387
100 | 0.027058 | 0.0067943 | -0.027042 | -0.0067839 | 1.667e-05 | 1.0316e-05 | 0.040444 | 0.040444 | 0.040444 | 0.99564 | -0.082542 | 0.99497 | -0.095465 | 11.111
101 | -0.21764 | -0.055436 | 0.21783 | 0.055556 | 0.00018808 | 0.0001194 | 0.32696 | 0.32695 | 0.32696 | 0.99148 | -0.16194 | 0.99242 | -0.14404 | 22.4557
102 | 0.0017852 | 0.00044691 | -0.0017851 | -0.00044739 | 1.2484e-07 | -4.8504e-07 | 0.0027176 | 0.0027178 | 0.0027178 | 0.97745 | -0.43365 | 0.97737 | -0.43511 | 0.74664
103 | 0.0031151 | 0.00078035 | -0.0031151 | -0.00078036 | 3.5001e-09 | -3.1937e-09 | 0.0046908 | 0.0046908 | 0.0046908 | 0.98816 | -0.22663 | 0.98816 | -0.22665 | 1.2887
104 | -0.0059463 | -0.0014899 | 0.0059468 | 0.00149 | 5.6335e-07 | 1.2049e-07 | 0.0089541 | 0.008954 | 0.0089541 | 0.98816 | -0.22663 | 0.98826 | -0.22464 | 2.4599
105 | 0.00098248 | 0.00024586 | -0.00098247 | -0.0002461 | 1.5635e-08 | -2.3403e-07 | 0.0014793 | 0.0014794 | 0.0014794 | 0.98816 | -0.22665 | 0.98814 | -0.22699 | 0.40644
106 | -0.0097717 | -0.0024484 | 0.0097738 | 0.0024495 | 2.1736e-06 | 1.048e-06 | 0.014713 | 0.014713 | 0.014713 | 0.98826 | -0.22464 | 0.9885 | -0.21997 | 4.042
107 | 0.0038248 | 0.00095842 | -0.0038246 | -0.00095853 | 2.6912e-07 | -1.0499e-07 | 0.005759 | 0.0057591 | 0.0057591 | 0.98826 | -0.22464 | 0.98818 | -0.22612 | 1.5822
108 | 0.00098247 | 0.0002461 | -0.00098246 | -0.00024623 | 8.6445e-09 | -1.2938e-07 | 0.0014794 | 0.0014795 | 0.0014795 | 0.98814 | -0.22699 | 0.98813 | -0.22717 | 0.40645
109 | 0.097394 | 0.024643 | -0.097385 | -0.024637 | 9.4622e-06 | 6.0408e-06 | 0.14669 | 0.14669 | 0.14669 | 0.9885 | -0.21997 | 0.98839 | -0.222 | 40.3005
110 | 0.09377 | 0.023731 | -0.093543 | -0.023586 | 0.00022719 | 0.00014502 | 0.14125 | 0.14125 | 0.14125 | 0.98839 | -0.222 | 0.98578 | -0.27261 | 38.8055
111 | 0.093543 | 0.023586 | -0.093223 | -0.023381 | 0.00032029 | 0.00020444 | 0.14125 | 0.14125 | 0.14125 | 0.98578 | -0.27261 | 0.98209 | -0.34442 | 38.8055
112 | 0.049445 | 0.012409 | -0.0494 | -0.012381 | 4.5246e-05 | 2.8686e-05 | 0.074923 | 0.074923 | 0.074923 | 0.98209 | -0.34442 | 0.98111 | -0.36363 | 20.5832
113 | 0.069681 | 0.017572 | -0.069582 | -0.017514 | 9.8923e-05 | 5.8561e-05 | 0.10579 | 0.10579 | 0.10579 | 0.98051 | -0.37402 | 0.97899 | -0.40372 | 7.2657
114 | 0.0028879 | 0.00072262 | -0.002887 | -0.00072356 | 8.4593e-07 | -9.3041e-07 | 0.004389 | 0.0043895 | 0.0043895 | 0.97899 | -0.40372 | 0.97868 | -0.40987 | 1.2059
115 | 0.066694 | 0.016791 | -0.066493 | -0.016665 | 0.0002017 | 0.00012647 | 0.1014 | 0.1014 | 0.1014 | 0.97899 | -0.40372 | 0.97576 | -0.46719 | 13.9286
116 | -0.0039741 | -0.00099601 | 0.003975 | 0.00099579 | 8.7642e-07 | -2.2556e-07 | 0.0060769 | 0.0060766 | 0.0060769 | 0.97312 | -0.51883 | 0.97336 | -0.5142 | 1.6695
117 | -0.0061337 | -0.0015368 | 0.0061347 | 0.0015371 | 9.0829e-07 | 2.3884e-07 | 0.0093768 | 0.0093767 | 0.0093768 | 0.97336 | -0.5142 | 0.97351 | -0.51109 | 2.576
118 | -0.027024 | -0.0067728 | 0.027042 | 0.0067839 | 1.8066e-05 | 1.118e-05 | 0.040444 | 0.040444 | 0.040444 | 0.99425 | -0.10949 | 0.99497 | -0.095465 | 11.1111
119 | 0.22588 | 0.057645 | -0.22579 | -0.05759 | 8.6221e-05 | 5.4766e-05 | 0.33873 | 0.33873 | 0.33873 | 0.99334 | -0.12646 | 0.99292 | -0.13436 | 23.2645
120 | 0.22185 | 0.056602 | -0.22174 | -0.056536 | 0.00010366 | 6.5826e-05 | 0.33282 | 0.33282 | 0.33282 | 0.99292 | -0.13436 | 0.99242 | -0.14404 | 22.8586
121 | -0.010644 | -0.0026673 | 0.010647 | 0.0026685 | 2.3568e-06 | 1.2131e-06 | 0.01627 | 0.01627 | 0.01627 | 0.97351 | -0.51109 | 0.97375 | -0.50645 | 4.4697

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46731 | 0.11923

## res_load
| p_mw | q_mvar
0 | 0.00066526 | 0.00016673
1 | 0.0013908 | 0.00034856
2 | 0.0004994 | 0.00012516
3 | 0.0024965 | 0.00062568
4 | 0.0082882 | 0.0020772
5 | 0.008358 | 0.0020947
6 | 0.0076863 | 0.0019264
7 | 0.0037028 | 0.00092801
8 | 0.0089379 | 0.0022401
9 | 0.006853 | 0.0017175
10 | 0.001876 | 0.00047018
11 | 0.001991 | 0.00049898
12 | 0.0019892 | 0.00049854
13 | 0.0013205 | 0.00033095
14 | 0.0017117 | 0.00042899
15 | 0.0018935 | 0.00047455
16 | 0.0022298 | 0.00055884
17 | 0.0018245 | 0.00045726
18 | 0.0016106 | 0.00040365
19 | 0.0015204 | 0.00038104
20 | 0.0010246 | 0.00025679
21 | 0.0011881 | 0.00029776
22 | 0.0016215 | 0.00040639
23 | 0.00049858 | 0.00012496
24 | 0.0013714 | 0.00034371
25 | 0.001664 | 0.00041703
26 | 0.0024612 | 0.00061682
27 | 0.002363 | 0.00059222
28 | 0.0034693 | 0.00086949
29 | 0.0061131 | 0.0015321
30 | 0.0014205 | 0.00035602
31 | 0.0016632 | 0.00041683
32 | 0.0018432 | 0.00046196
33 | 0.00035791 | 8.97e-05
34 | 0.00074625 | 0.00018703
35 | 0.00032811 | 8.2231e-05
36 | 0.00044582 | 0.00011173
37 | 0.00050053 | 0.00012544
38 | 0.00055661 | 0.0001395
39 | 0.00066942 | 0.00016777
40 | 0.0013256 | 0.00033222
41 | 0.00071231 | 0.00017852
42 | 0.00055275 | 0.00013853
43 | 0.00049808 | 0.00012483
44 | 0.000734 | 0.00018396
45 | 0.00072236 | 0.00018104
46 | 0.003494 | 0.00087569
47 | 0.01502 | 0.0037643
48 | 0.0029911 | 0.00074964
49 | 0.0007372 | 0.00018476
50 | 7.9368e-05 | 1.9892e-05
51 | 0.0013262 | 0.00033237
52 | 0.0042134 | 0.001056
53 | 0.00055709 | 0.00013962
54 | 0.01042 | 0.0026114
55 | 0.014933 | 0.0037426
56 | 0.0023216 | 0.00058184
57 | 0.00046992 | 0.00011777
58 | 0.00097968 | 0.00024553
59 | 0.0008907 | 0.00022323
60 | 0.0019989 | 0.00050097
61 | 0.0008064 | 0.0002021
62 | 0.0052378 | 0.0013127
63 | 0.0043286 | 0.0010848
64 | 0.014923 | 0.0037401
65 | 0.0013272 | 0.00033262
66 | 0.0075054 | 0.001881
67 | 0.0022643 | 0.0005675
68 | 0.0017851 | 0.00044739
69 | 0.0028311 | 0.00070955
70 | 0.0021327 | 0.00053449
71 | 0.0038246 | 0.00095853
72 | 0.00098246 | 0.00024623
73 | 0.0036148 | 0.00090594
74 | 0.043778 | 0.010972
75 | 0.019201 | 0.0048123
76 | 0.066493 | 0.016665
77 | 0.0039741 | 0.00099601
78 | 0.0021587 | 0.00054103
79 | 0.0016351 | 0.0004098
80 | 0.0494 | 0.012381
81 | 0.027024 | 0.0067728
82 | 0.010441 | 0.0026168
83 | 0.0039438 | 0.00098842
84 | 0.0045098 | 0.0011303
85 | 0.0058889 | 0.0014759
86 | 0.002887 | 0.00072356
87 | 0.0039121 | 0.00098047

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1