## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2501-3_1_4_node_9 | 0.4 | n |  | TRUE
1 | bus_LV_2501-3_1_4_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_2501-3_1_4_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_2501-3_1_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_2501-3_1_4_node_210 | 0.4 | n |  | TRUE
5 | bus_LV_2501-3_1_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_2501-3_1_4_node_266 | 0.4 | n |  | TRUE
7 | bus_LV_2501-3_1_4_node_267 | 0.4 | n |  | TRUE
8 | bus_LV_2501-3_1_4_node_255 | 0.4 | n |  | TRUE
9 | bus_LV_2501-3_1_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2501-3_1_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_2501-3_1_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_2501-3_1_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_2501-3_1_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2501-3_1_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_2501-3_1_4_node_98 | 0.4 | n |  | TRUE
16 | bus_LV_2501-3_1_4_node_205 | 0.4 | n |  | TRUE
17 | bus_LV_2501-3_1_4_node_172 | 0.4 | n |  | TRUE
18 | bus_LV_2501-3_1_4_node_142 | 0.4 | n |  | TRUE
19 | bus_LV_2501-3_1_4_node_273 | 0.4 | n |  | TRUE
20 | bus_LV_2501-3_1_4_node_95 | 0.4 | n |  | TRUE
21 | bus_LV_2501-3_1_4_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_2501-3_1_4_node_84 | 0.4 | n |  | TRUE
23 | bus_LV_2501-3_1_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2501-3_1_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2501-3_1_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2501-3_1_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2501-3_1_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2501-3_1_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2501-3_1_4_node_150 | 0.4 | n |  | TRUE
30 | bus_LV_2501-3_1_4_node_141 | 0.4 | n |  | TRUE
31 | bus_LV_2501-3_1_4_node_138 | 0.4 | n |  | TRUE
32 | bus_LV_2501-3_1_4_node_235 | 0.4 | n |  | TRUE
33 | bus_LV_2501-3_1_4_node_149 | 0.4 | n |  | TRUE
34 | bus_LV_2501-3_1_4_node_242 | 0.4 | n |  | TRUE
35 | bus_LV_2501-3_1_4_node_241 | 0.4 | n |  | TRUE
36 | bus_LV_2501-3_1_4_node_139 | 0.4 | n |  | TRUE
37 | bus_LV_2501-3_1_4_node_236 | 0.4 | n |  | TRUE
38 | bus_LV_2501-3_1_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_2501-3_1_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2501-3_1_4_node_233 | 0.4 | n |  | TRUE
41 | bus_LV_2501-3_1_4_node_92 | 0.4 | n |  | TRUE
42 | bus_LV_2501-3_1_4_node_94 | 0.4 | n |  | TRUE
43 | bus_LV_2501-3_1_4_node_90 | 0.4 | n |  | TRUE
44 | bus_LV_2501-3_1_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2501-3_1_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_2501-3_1_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_2501-3_1_4_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_2501-3_1_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_2501-3_1_4_node_128 | 0.4 | n |  | TRUE
50 | bus_LV_2501-3_1_4_node_127 | 0.4 | n |  | TRUE
51 | bus_LV_2501-3_1_4_node_88 | 0.4 | n |  | TRUE
52 | bus_LV_2501-3_1_4_node_178 | 0.4 | n |  | TRUE
53 | bus_LV_2501-3_1_4_node_102 | 0.4 | n |  | TRUE
54 | bus_LV_2501-3_1_4_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_2501-3_1_4_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_2501-3_1_4_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_2501-3_1_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_2501-3_1_4_node_140 | 0.4 | n |  | TRUE
59 | bus_LV_2501-3_1_4_node_256 | 0.4 | n |  | TRUE
60 | bus_LV_2501-3_1_4_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_2501-3_1_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_2501-3_1_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_2501-3_1_4_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_2501-3_1_4_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_2501-3_1_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_2501-3_1_4_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_2501-3_1_4_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_2501-3_1_4_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_2501-3_1_4_node_143 | 0.4 | n |  | TRUE
70 | bus_LV_2501-3_1_4_node_211 | 0.4 | n |  | TRUE
71 | bus_LV_2501-3_1_4_node_238 | 0.4 | n |  | TRUE
72 | bus_LV_2501-3_1_4_node_243 | 0.4 | n |  | TRUE
73 | bus_LV_2501-3_1_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_2501-3_1_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_2501-3_1_4_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_2501-3_1_4_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_2501-3_1_4_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_2501-3_1_4_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_2501-3_1_4_node_118 | 0.4 | n |  | TRUE
80 | bus_LV_2501-3_1_4_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_2501-3_1_4_node_85 | 0.4 | n |  | TRUE
82 | bus_LV_2501-3_1_4_node_213 | 0.4 | n |  | TRUE
83 | bus_LV_2501-3_1_4_node_253 | 0.4 | n |  | TRUE
84 | bus_LV_2501-3_1_4_node_263 | 0.4 | n |  | TRUE
85 | bus_LV_2501-3_1_4_node_227 | 0.4 | n |  | TRUE
86 | bus_LV_2501-3_1_4_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_2501-3_1_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_2501-3_1_4_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_2501-3_1_4_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_2501-3_1_4_node_170 | 0.4 | n |  | TRUE
91 | bus_LV_2501-3_1_4_node_228 | 0.4 | n |  | TRUE
92 | bus_LV_2501-3_1_4_node_169 | 0.4 | n |  | TRUE
93 | bus_LV_2501-3_1_4_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_2501-3_1_4_node_171 | 0.4 | n |  | TRUE
95 | bus_LV_2501-3_1_4_node_137 | 0.4 | n |  | TRUE
96 | bus_LV_2501-3_1_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_2501-3_1_4_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_2501-3_1_4_node_167 | 0.4 | n |  | TRUE
99 | bus_LV_2501-3_1_4_node_173 | 0.4 | n |  | TRUE
100 | bus_LV_2501-3_1_4_node_168 | 0.4 | n |  | TRUE
101 | bus_LV_2501-3_1_4_node_174 | 0.4 | n |  | TRUE
102 | bus_LV_2501-3_1_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_2501-3_1_4_node_262 | 0.4 | n |  | TRUE
104 | bus_LV_2501-3_1_4_node_251 | 0.4 | n |  | TRUE
105 | bus_LV_2501-3_1_4_node_274 | 0.4 | n |  | TRUE
106 | bus_LV_2501-3_1_4_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_2501-3_1_4_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2501-3_1_4_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_2501-3_1_4_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_2501-3_1_4_node_129 | 0.4 | n |  | TRUE
111 | bus_LV_2501-3_1_4_node_184 | 0.4 | n |  | TRUE
112 | bus_LV_2501-3_1_4_node_239 | 0.4 | n |  | TRUE
113 | bus_LV_2501-3_1_4_node_220 | 0.4 | n |  | TRUE
114 | bus_LV_2501-3_1_4_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_2501-3_1_4_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_2501-3_1_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_2501-3_1_4_node_115 | 0.4 | n |  | TRUE
118 | bus_LV_2501-3_1_4_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_2501-3_1_4_node_194 | 0.4 | n |  | TRUE
120 | bus_LV_2501-3_1_4_node_215 | 0.4 | n |  | TRUE
121 | bus_LV_2501-3_1_4_node_244 | 0.4 | n |  | TRUE
122 | bus_LV_2501-3_1_4_node_183 | 0.4 | n |  | TRUE
123 | bus_LV_2501-3_1_4_node_214 | 0.4 | n |  | TRUE
124 | bus_LV_2501-3_1_4_node_212 | 0.4 | n |  | TRUE
125 | bus_LV_2501-3_1_4_node_254 | 0.4 | n |  | TRUE
126 | bus_LV_2501-3_1_4_node_264 | 0.4 | n |  | TRUE
127 | bus_LV_2501-3_1_4_node_176 | 0.4 | n |  | TRUE
128 | bus_LV_2501-3_1_4_node_135 | 0.4 | n |  | TRUE
129 | bus_LV_2501-3_1_4_node_136 | 0.4 | n |  | TRUE
130 | bus_LV_2501-3_1_4_node_232 | 0.4 | n |  | TRUE
131 | bus_LV_2501-3_1_4_node_234 | 0.4 | n |  | TRUE
132 | bus_LV_2501-3_1_4_node_277 | 0.4 | n |  | TRUE
133 | bus_LV_2501-3_1_4_node_151 | 0.4 | n |  | TRUE
134 | bus_LV_2501-3_1_4_node_152 | 0.4 | n |  | TRUE
135 | bus_LV_2501-3_1_4_node_191 | 0.4 | n |  | TRUE
136 | bus_LV_2501-3_1_4_node_190 | 0.4 | n |  | TRUE
137 | bus_LV_2501-3_1_4_node_175 | 0.4 | n |  | TRUE
138 | bus_LV_2501-3_1_4_node_177 | 0.4 | n |  | TRUE
139 | bus_LV_2501-3_1_4_node_179 | 0.4 | n |  | TRUE
140 | bus_LV_2501-3_1_4_node_180 | 0.4 | n |  | TRUE
141 | bus_LV_2501-3_1_4_node_181 | 0.4 | n |  | TRUE
142 | bus_LV_2501-3_1_4_node_182 | 0.4 | n |  | TRUE
143 | bus_LV_2501-3_1_4_node_218 | 0.4 | n |  | TRUE
144 | bus_LV_2501-3_1_4_node_192 | 0.4 | n |  | TRUE
145 | bus_LV_2501-3_1_4_node_217 | 0.4 | n |  | TRUE
146 | bus_LV_2501-3_1_4_node_219 | 0.4 | n |  | TRUE
147 | bus_LV_2501-3_1_4_node_221 | 0.4 | n |  | TRUE
148 | bus_LV_2501-3_1_4_node_229 | 0.4 | n |  | TRUE
149 | bus_LV_2501-3_1_4_node_250 | 0.4 | n |  | TRUE
150 | bus_LV_2501-3_1_4_node_249 | 0.4 | n |  | TRUE
151 | bus_LV_2501-3_1_4_node_237 | 0.4 | n |  | TRUE
152 | bus_LV_2501-3_1_4_node_268 | 0.4 | n |  | TRUE
153 | bus_LV_2501-3_1_4_node_252 | 0.4 | n |  | TRUE
154 | bus_LV_2501-3_1_4_node_276 | 0.4 | n |  | TRUE
155 | bus_MV_398_1_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2501-3_1_4_load_9 | 0 | 0.0031525 | 0.00079009 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2501-3_1_4_load_11 | 2 | 0.00045697 | 0.00011453 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2501-3_1_4_load_210 | 4 | 0.00098123 | 0.00024592 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2501-3_1_4_load_266 | 6 | 0.0015959 | 0.00039998 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2501-3_1_4_load_14 | 9 | 0.0028323 | 0.00070984 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2501-3_1_4_load_15 | 10 | 0.0025506 | 0.00063923 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2501-3_1_4_load_18 | 13 | 0.0035183 | 0.00088177 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2501-3_1_4_load_19 | 14 | 0.0014748 | 0.00036961 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2501-3_1_4_load_205 | 16 | 0.0034327 | 0.00086032 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2501-3_1_4_load_172 | 17 | 0.0024753 | 0.00062038 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2501-3_1_4_load_273 | 19 | 0.0013159 | 0.0003298 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2501-3_1_4_load_95 | 20 | 0.0028535 | 0.00071515 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2501-3_1_4_load_96 | 21 | 0.0021441 | 0.00053736 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2501-3_1_4_load_84 | 22 | 0.0027322 | 0.00068476 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2501-3_1_4_load_20 | 23 | 0.0009282 | 0.00023263 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2501-3_1_4_load_21 | 24 | 0.0013985 | 0.0003505 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2501-3_1_4_load_23 | 26 | 0.00094389 | 0.00023656 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2501-3_1_4_load_25 | 28 | 0.0011678 | 0.00029268 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2501-3_1_4_load_150 | 29 | 0.0036643 | 0.00091837 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2501-3_1_4_load_138 | 31 | 0.0015338 | 0.0003844 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2501-3_1_4_load_235 | 32 | 0.0024423 | 0.00061209 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2501-3_1_4_load_149 | 33 | 0.00063154 | 0.00015828 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2501-3_1_4_load_242 | 34 | 0.0016053 | 0.00040233 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2501-3_1_4_load_241 | 35 | 0.0018075 | 0.00045301 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2501-3_1_4_load_139 | 36 | 0.0013707 | 0.00034353 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2501-3_1_4_load_236 | 37 | 0.0017456 | 0.00043748 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2501-3_1_4_load_27 | 38 | 0.0044707 | 0.0011205 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2501-3_1_4_load_233 | 40 | 0.0011634 | 0.00029158 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2501-3_1_4_load_94 | 42 | 0.0051027 | 0.0012789 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2501-3_1_4_load_90 | 43 | 0.0028699 | 0.00071927 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2501-3_1_4_load_31 | 44 | 0.0010662 | 0.00026721 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2501-3_1_4_load_32 | 45 | 0.0013689 | 0.00034307 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2501-3_1_4_load_34 | 46 | 0.0009527 | 0.00023877 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2501-3_1_4_load_87 | 47 | 0.0012663 | 0.00031737 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2501-3_1_4_load_128 | 49 | 0.0012534 | 0.00031413 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2501-3_1_4_load_127 | 50 | 0.00060021 | 0.00015043 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2501-3_1_4_load_88 | 51 | 0.001174 | 0.00029423 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2501-3_1_4_load_178 | 52 | 0.0042381 | 0.0010622 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2501-3_1_4_load_36 | 54 | 0.0016908 | 0.00042375 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2501-3_1_4_load_37 | 55 | 0.00083377 | 0.00020896 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2501-3_1_4_load_38 | 56 | 0.00070921 | 0.00017775 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2501-3_1_4_load_40 | 57 | 0.0021757 | 0.00054527 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2501-3_1_4_load_256 | 59 | 0.001657 | 0.00041527 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2501-3_1_4_load_41 | 60 | 0.0010636 | 0.00026657 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2501-3_1_4_load_42 | 61 | 0.00094128 | 0.00023591 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2501-3_1_4_load_43 | 62 | 0.00081573 | 0.00020444 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2501-3_1_4_load_44 | 63 | 0.0011909 | 0.00029846 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2501-3_1_4_load_45 | 64 | 0.0013135 | 0.0003292 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2501-3_1_4_load_46 | 65 | 0.0020614 | 0.00051663 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2501-3_1_4_load_47 | 66 | 0.0012537 | 0.00031421 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2501-3_1_4_load_48 | 67 | 0.0016799 | 0.00042101 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2501-3_1_4_load_49 | 68 | 0.0010587 | 0.00026532 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2501-3_1_4_load_143 | 69 | 0.0027547 | 0.00069039 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2501-3_1_4_load_238 | 71 | 0.0015429 | 0.00038669 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2501-3_1_4_load_243 | 72 | 0.0012002 | 0.00030079 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2501-3_1_4_load_65 | 73 | 0.0016729 | 0.00041926 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2501-3_1_4_load_66 | 74 | 0.0022158 | 0.00055532 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2501-3_1_4_load_68 | 76 | 0.0036863 | 0.00092387 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2501-3_1_4_load_70 | 78 | 0.0042303 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2501-3_1_4_load_117 | 80 | 0.0018488 | 0.00046336 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2501-3_1_4_load_263 | 84 | 0.0011261 | 0.00028223 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2501-3_1_4_load_227 | 85 | 0.0076269 | 0.0019115 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2501-3_1_4_load_81 | 87 | 0.0035324 | 0.00088531 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2501-3_1_4_load_82 | 88 | 0.002299 | 0.00057618 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2501-3_1_4_load_86 | 89 | 0.0025834 | 0.00064746 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2501-3_1_4_load_170 | 90 | 0.0022723 | 0.00056949 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2501-3_1_4_load_228 | 91 | 0.0076298 | 0.0019122 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2501-3_1_4_load_169 | 92 | 0.010026 | 0.0025128 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2501-3_1_4_load_89 | 93 | 0.0018498 | 0.0004636 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2501-3_1_4_load_91 | 96 | 0.017058 | 0.0042752 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2501-3_1_4_load_93 | 97 | 0.0050837 | 0.0012741 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2501-3_1_4_load_167 | 98 | 0.010194 | 0.0025548 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2501-3_1_4_load_173 | 99 | 0.0040752 | 0.0010213 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2501-3_1_4_load_168 | 100 | 0.0086469 | 0.0021671 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2501-3_1_4_load_174 | 101 | 0.017164 | 0.0043018 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2501-3_1_4_load_262 | 103 | 0.0022352 | 0.0005602 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2501-3_1_4_load_251 | 104 | 0.0019465 | 0.00048783 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2501-3_1_4_load_274 | 105 | 0.00087443 | 0.00021915 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2501-3_1_4_load_99 | 106 | 0.0015765 | 0.00039511 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2501-3_1_4_load_100 | 107 | 0.00108 | 0.00027066 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2501-3_1_4_load_101 | 108 | 0.00069413 | 0.00017397 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2501-3_1_4_load_103 | 109 | 0.0010431 | 0.00026144 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2501-3_1_4_load_129 | 110 | 0.0015649 | 0.0003922 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2501-3_1_4_load_184 | 111 | 0.00072432 | 0.00018153 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2501-3_1_4_load_239 | 112 | 0.00073684 | 0.00018467 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2501-3_1_4_load_112 | 114 | 0.00059161 | 0.00014827 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2501-3_1_4_load_113 | 115 | 0.00065405 | 0.00016392 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2501-3_1_4_load_114 | 116 | 0.00058893 | 0.0001476 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2501-3_1_4_load_115 | 117 | 0.0010028 | 0.00025132 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2501-3_1_4_load_116 | 118 | 0.00078139 | 0.00019583 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2501-3_1_4_load_194 | 119 | 0.00056952 | 0.00014273 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2501-3_1_4_load_215 | 120 | 0.00079864 | 0.00020016 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2501-3_1_4_load_244 | 121 | 0.00080976 | 0.00020294 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2501-3_1_4_load_214 | 123 | 0.00091264 | 0.00022873 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2501-3_1_4_load_212 | 124 | 0.00085532 | 0.00021436 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2501-3_1_4_load_264 | 126 | 0.001422 | 0.0003564 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2501-3_1_4_load_176 | 127 | 0.0014639 | 0.00036689 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2501-3_1_4_load_135 | 128 | 0.001259 | 0.00031553 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2501-3_1_4_load_136 | 129 | 0.0017903 | 0.00044869 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2501-3_1_4_load_232 | 130 | 0.0015211 | 0.00038123 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2501-3_1_4_load_234 | 131 | 0.0019023 | 0.00047676 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2501-3_1_4_load_277 | 132 | 0.0017728 | 0.0004443 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2501-3_1_4_load_151 | 133 | 0.0014214 | 0.00035623 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2501-3_1_4_load_152 | 134 | 0.00083954 | 0.00021041 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2501-3_1_4_load_191 | 135 | 0.0012086 | 0.00030292 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2501-3_1_4_load_190 | 136 | 0.0030064 | 0.00075349 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2501-3_1_4_load_175 | 137 | 0.0068262 | 0.0017108 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2501-3_1_4_load_177 | 138 | 0.0012919 | 0.00032378 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2501-3_1_4_load_179 | 139 | 0.00067427 | 0.00016899 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2501-3_1_4_load_180 | 140 | 0.0010521 | 0.00026369 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2501-3_1_4_load_181 | 141 | 0.00075729 | 0.0001898 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2501-3_1_4_load_182 | 142 | 0.00068786 | 0.00017239 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2501-3_1_4_load_218 | 143 | 0.00094112 | 0.00023587 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2501-3_1_4_load_192 | 144 | 0.00067018 | 0.00016796 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2501-3_1_4_load_217 | 145 | 0.0012461 | 0.00031231 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2501-3_1_4_load_219 | 146 | 0.0011434 | 0.00028657 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2501-3_1_4_load_221 | 147 | 0.0010257 | 0.00025708 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2501-3_1_4_load_229 | 148 | 0.007643 | 0.0019155 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2501-3_1_4_load_249 | 150 | 0.0033572 | 0.00084139 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2501-3_1_4_load_237 | 151 | 0.00087248 | 0.00021866 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2501-3_1_4_load_268 | 152 | 0.00090225 | 0.00022613 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2501-3_1_4_load_252 | 153 | 0.0029665 | 0.00074347 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2501-3_1_4_load_276 | 154 | 0.0012682 | 0.00031783 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2501-3_1_4_line_0 |  | 0 | 1 | 0.0042096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2501-3_1_4_line_1 |  | 1 | 2 | 0.018451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2501-3_1_4_line_2 |  | 2 | 3 | 0.0031871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2501-3_1_4_line_3 |  | 3 | 4 | 0.028855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2501-3_1_4_line_4 |  | 3 | 5 | 0.096904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2501-3_1_4_line_5 |  | 5 | 6 | 0.026371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2501-3_1_4_line_6 |  | 5 | 7 | 0.020106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2501-3_1_4_line_7 |  | 7 | 8 | 0.038271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2501-3_1_4_line_8 |  | 8 | 154 | 0.016175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2501-3_1_4_line_9 |  | 8 | 125 | 0.035656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2501-3_1_4_line_10 |  | 9 | 10 | 0.010311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2501-3_1_4_line_11 |  | 9 | 11 | 0.018878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2501-3_1_4_line_12 |  | 10 | 12 | 0.023535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2501-3_1_4_line_13 |  | 11 | 13 | 0.014049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2501-3_1_4_line_14 |  | 11 | 14 | 0.0061044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2501-3_1_4_line_15 |  | 12 | 15 | 0.001348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2501-3_1_4_line_16 |  | 13 | 16 | 0.012566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2501-3_1_4_line_17 |  | 14 | 17 | 0.0057103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2501-3_1_4_line_18 |  | 15 | 18 | 0.040129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2501-3_1_4_line_19 |  | 15 | 19 | 0.018307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2501-3_1_4_line_20 |  | 17 | 22 | 0.021834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2501-3_1_4_line_21 |  | 18 | 40 | 0.0264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2501-3_1_4_line_22 |  | 18 | 63 | 0.02891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2501-3_1_4_line_23 |  | 19 | 105 | 0.023854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2501-3_1_4_line_24 |  | 20 | 21 | 0.020526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2501-3_1_4_line_25 |  | 21 | 102 | 0.01818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2501-3_1_4_line_26 |  | 22 | 88 | 0.011838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2501-3_1_4_line_27 |  | 23 | 24 | 0.003151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2501-3_1_4_line_28 |  | 23 | 25 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2501-3_1_4_line_29 |  | 24 | 26 | 0.034997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2501-3_1_4_line_30 |  | 25 | 27 | 0.030289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2501-3_1_4_line_31 |  | 25 | 28 | 0.034464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2501-3_1_4_line_32 |  | 26 | 29 | 0.0017901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2501-3_1_4_line_33 |  | 27 | 30 | 0.003925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2501-3_1_4_line_34 |  | 27 | 31 | 0.018493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2501-3_1_4_line_35 |  | 28 | 32 | 0.022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2501-3_1_4_line_36 |  | 29 | 33 | 0.018631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2501-3_1_4_line_37 |  | 30 | 34 | 0.036552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2501-3_1_4_line_38 |  | 30 | 35 | 0.020858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2501-3_1_4_line_39 |  | 31 | 36 | 0.00079263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2501-3_1_4_line_40 |  | 32 | 37 | 0.028192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2501-3_1_4_line_41 |  | 33 | 133 | 0.011496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2501-3_1_4_line_42 |  | 34 | 132 | 0.0037312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2501-3_1_4_line_43 |  | 36 | 58 | 0.026436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2501-3_1_4_line_44 |  | 37 | 151 | 0.023097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2501-3_1_4_line_45 |  | 38 | 39 | 0.07353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2501-3_1_4_line_46 |  | 39 | 40 | 0.059123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2501-3_1_4_line_47 |  | 39 | 41 | 0.030147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2501-3_1_4_line_48 |  | 41 | 42 | 0.018306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2501-3_1_4_line_49 |  | 41 | 43 | 0.010045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2501-3_1_4_line_50 |  | 42 | 99 | 0.019898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2501-3_1_4_line_51 |  | 43 | 96 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2501-3_1_4_line_52 |  | 44 | 45 | 0.027576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2501-3_1_4_line_53 |  | 45 | 46 | 0.0084332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2501-3_1_4_line_54 |  | 46 | 47 | 0.025678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2501-3_1_4_line_55 |  | 47 | 51 | 0.01976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2501-3_1_4_line_56 |  | 48 | 49 | 0.020046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2501-3_1_4_line_57 |  | 48 | 50 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2501-3_1_4_line_58 |  | 49 | 52 | 0.012534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2501-3_1_4_line_59 |  | 50 | 53 | 0.035843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2501-3_1_4_line_60 |  | 51 | 93 | 0.020028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2501-3_1_4_line_61 |  | 52 | 127 | 0.0035237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2501-3_1_4_line_62 |  | 53 | 110 | 0.025449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2501-3_1_4_line_63 |  | 53 | 107 | 0.013715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2501-3_1_4_line_64 |  | 54 | 55 | 0.02892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2501-3_1_4_line_65 |  | 54 | 56 | 0.0024816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2501-3_1_4_line_66 |  | 56 | 57 | 0.029395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2501-3_1_4_line_67 |  | 57 | 58 | 0.013711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2501-3_1_4_line_68 |  | 58 | 59 | 0.0066315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2501-3_1_4_line_69 |  | 59 | 131 | 0.01236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2501-3_1_4_line_70 |  | 60 | 61 | 0.015512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2501-3_1_4_line_71 |  | 60 | 62 | 0.003469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2501-3_1_4_line_72 |  | 61 | 63 | 0.0032207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2501-3_1_4_line_73 |  | 64 | 65 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2501-3_1_4_line_74 |  | 64 | 66 | 0.013184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2501-3_1_4_line_75 |  | 65 | 67 | 0.0036499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2501-3_1_4_line_76 |  | 66 | 68 | 0.021159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2501-3_1_4_line_77 |  | 67 | 69 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2501-3_1_4_line_78 |  | 68 | 70 | 0.013296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2501-3_1_4_line_79 |  | 69 | 71 | 0.0021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2501-3_1_4_line_80 |  | 70 | 72 | 0.018378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2501-3_1_4_line_81 |  | 71 | 112 | 0.014974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2501-3_1_4_line_82 |  | 73 | 74 | 0.0007607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2501-3_1_4_line_83 |  | 73 | 75 | 0.015017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2501-3_1_4_line_84 |  | 74 | 76 | 0.013902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2501-3_1_4_line_85 |  | 75 | 77 | 0.035895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2501-3_1_4_line_86 |  | 75 | 78 | 0.036072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2501-3_1_4_line_87 |  | 77 | 79 | 0.13628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2501-3_1_4_line_88 |  | 77 | 80 | 0.039116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2501-3_1_4_line_89 |  | 78 | 81 | 0.015747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2501-3_1_4_line_90 |  | 79 | 82 | 0.040271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2501-3_1_4_line_91 |  | 79 | 83 | 0.17811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2501-3_1_4_line_92 |  | 79 | 84 | 0.055979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2501-3_1_4_line_93 |  | 81 | 85 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2501-3_1_4_line_94 |  | 81 | 86 | 0.005365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2501-3_1_4_line_95 |  | 82 | 123 | 0.021487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2501-3_1_4_line_96 |  | 82 | 124 | 0.017526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2501-3_1_4_line_97 |  | 83 | 125 | 0.055414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2501-3_1_4_line_98 |  | 84 | 126 | 0.03827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2501-3_1_4_line_99 |  | 85 | 91 | 0.020811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2501-3_1_4_line_100 |  | 86 | 89 | 0.033292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2501-3_1_4_line_101 |  | 86 | 87 | 0.019453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2501-3_1_4_line_102 |  | 87 | 88 | 0.016498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2501-3_1_4_line_103 |  | 89 | 90 | 0.028316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2501-3_1_4_line_104 |  | 90 | 92 | 0.007858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2501-3_1_4_line_105 |  | 91 | 148 | 0.028005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2501-3_1_4_line_106 |  | 92 | 94 | 0.014037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2501-3_1_4_line_107 |  | 93 | 94 | 0.061368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2501-3_1_4_line_108 |  | 94 | 95 | 0.013305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_2501-3_1_4_line_109 |  | 95 | 130 | 0.0307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2501-3_1_4_line_110 |  | 95 | 129 | 0.04035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2501-3_1_4_line_111 |  | 96 | 97 | 0.0034726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2501-3_1_4_line_112 |  | 97 | 98 | 0.035096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2501-3_1_4_line_113 |  | 98 | 100 | 0.013499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2501-3_1_4_line_114 |  | 99 | 101 | 0.041928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2501-3_1_4_line_115 |  | 101 | 137 | 0.0086229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2501-3_1_4_line_116 |  | 102 | 103 | 0.012408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2501-3_1_4_line_117 |  | 103 | 104 | 0.028165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2501-3_1_4_line_118 |  | 104 | 147 | 0.021313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2501-3_1_4_line_119 |  | 106 | 107 | 0.012474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2501-3_1_4_line_120 |  | 106 | 108 | 0.0071337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2501-3_1_4_line_121 |  | 108 | 109 | 0.0016626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2501-3_1_4_line_122 |  | 109 | 111 | 0.010215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2501-3_1_4_line_123 |  | 110 | 112 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2501-3_1_4_line_124 |  | 111 | 113 | 0.020742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2501-3_1_4_line_125 |  | 113 | 143 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2501-3_1_4_line_126 |  | 113 | 130 | 0.0060023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2501-3_1_4_line_127 |  | 114 | 115 | 0.0075183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2501-3_1_4_line_128 |  | 114 | 116 | 0.0096097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2501-3_1_4_line_129 |  | 115 | 117 | 0.018102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2501-3_1_4_line_130 |  | 116 | 118 | 0.0063002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2501-3_1_4_line_131 |  | 117 | 119 | 0.017321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2501-3_1_4_line_132 |  | 118 | 120 | 0.017468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2501-3_1_4_line_133 |  | 119 | 121 | 0.025989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2501-3_1_4_line_134 |  | 120 | 122 | 0.020487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2501-3_1_4_line_135 |  | 122 | 124 | 0.019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2501-3_1_4_line_136 |  | 122 | 141 | 0.0071323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2501-3_1_4_line_137 |  | 125 | 153 | 0.04442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2501-3_1_4_line_138 |  | 127 | 138 | 0.027656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2501-3_1_4_line_139 |  | 128 | 129 | 0.0076583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2501-3_1_4_line_140 |  | 131 | 139 | 0.0047248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2501-3_1_4_line_141 |  | 133 | 134 | 0.019109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2501-3_1_4_line_142 |  | 134 | 135 | 0.033002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2501-3_1_4_line_143 |  | 135 | 136 | 0.067392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2501-3_1_4_line_144 |  | 136 | 144 | 0.010775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2501-3_1_4_line_145 |  | 138 | 139 | 0.012302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2501-3_1_4_line_146 |  | 140 | 141 | 0.0094348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2501-3_1_4_line_147 |  | 140 | 142 | 0.01677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2501-3_1_4_line_148 |  | 143 | 145 | 0.022682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_2501-3_1_4_line_149 |  | 145 | 146 | 0.024707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_2501-3_1_4_line_150 |  | 146 | 147 | 0.018811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_2501-3_1_4_line_151 |  | 148 | 149 | 0.099205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2501-3_1_4_line_152 |  | 149 | 150 | 0.1151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2501-3_1_4_line_153 |  | 151 | 152 | 0.011843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2501-3_1_4_trafo_95 | 0.63 MVA 20/0.4 kV | 155 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2636691.0716 | 1246918.5134 | 2636687.8962 | 1246915.7497
1 | 2636691.0716 | 1246918.5134 | 2636704.2917 | 1246931.3847
2 | 2636706.5752 | 1246933.608 | 2636704.2917 | 1246931.3847
3 | 2636706.5752 | 1246933.608 | 2636725.3279 | 1246935.0694 | 2636733.8784 | 1246929.7968
4 | 2636706.5752 | 1246933.608 | 2636692.6144 | 1246946.2856 | 2636707.5104 | 1246964.3562 | 2636712.8142 | 1246966.546 | 2636725.3538 | 1246967.4908 | 2636739.464 | 1246968.5232 | 2636761.4168 | 1246965.4571
5 | 2636761.4168 | 1246965.4571 | 2636765.8886 | 1246991.4458
6 | 2636781.1483 | 1246961.3099 | 2636761.4168 | 1246965.4571
7 | 2636781.1483 | 1246961.3099 | 2636800.9856 | 1246955.9293 | 2636816.2766 | 1246946.7959
8 | 2636816.2766 | 1246946.7959 | 2636820.1009 | 1246953.7019 | 2636824.4385 | 1246960.7556
9 | 2636838.2116 | 1246918.6579 | 2636819.1968 | 1246943.6008 | 2636816.2766 | 1246946.7959
10 | 2637040.1755 | 1246498.3013 | 2637047.9837 | 1246505.0347
11 | 2637062.4011 | 1246517.201 | 2637062.1015 | 1246516.7988 | 2637048.2974 | 1246505.3051 | 2637047.9837 | 1246505.0347
12 | 2637022.3999 | 1246482.9067 | 2637025.5978 | 1246486.1065 | 2637031.5031 | 1246491.2022 | 2637035.9984 | 1246494.6992 | 2637040.1755 | 1246498.3013
13 | 2637062.4011 | 1246517.201 | 2637067.1041 | 1246509.2029 | 2637069.7996 | 1246505.2668
14 | 2637062.4011 | 1246517.201 | 2637067.284 | 1246520.8646
15 | 2637022.3999 | 1246482.9067 | 2637021.4998 | 1246481.9004
16 | 2637076.8998 | 1246494.8991 | 2637069.7996 | 1246505.2668
17 | 2637067.284 | 1246520.8646 | 2637071.8515 | 1246524.2916
18 | 2636995.0994 | 1246451.705 | 2637002.5976 | 1246461.8028 | 2637011.1035 | 1246471.4065 | 2637019 | 1246479.4054 | 2637021.4998 | 1246481.9004
19 | 2637021.4998 | 1246481.9004 | 2637008.3301 | 1246494.6169
20 | 2637071.8515 | 1246524.2916 | 2637079.197 | 1246529.803 | 2637089.4804 | 1246537.1709
21 | 2636995.0994 | 1246451.705 | 2636994.9036 | 1246451.6037 | 2636985.5041 | 1246437.5026 | 2636980.8984 | 1246429.5011
22 | 2636995.0994 | 1246451.705 | 2636987.903 | 1246457.3972 | 2636973.3002 | 1246470.6718
23 | 2637008.3301 | 1246494.6169 | 2637006.9014 | 1246495.9964 | 2636990.5031 | 1246510.4633
24 | 2637048.8979 | 1246432.1054 | 2637045.1028 | 1246443.5003 | 2637041.7003 | 1246451.3064
25 | 2637051.797 | 1246414.2006 | 2637051.6983 | 1246415.5008 | 2637050.7979 | 1246424.2009 | 2637048.8979 | 1246432.1054
26 | 2637099.1697 | 1246543.9673 | 2637097.1996 | 1246542.7017 | 2637089.4804 | 1246537.1709
27 | 2637089.8843 | 1246240.7783 | 2637089.0763 | 1246243.824
28 | 2637082.1041 | 1246270.1065 | 2637089.0763 | 1246243.824
29 | 2637089.8843 | 1246240.7783 | 2637094.2034 | 1246224.4967 | 2637094.8013 | 1246220.6979 | 2637094.6034 | 1246217.3056 | 2637094.0984 | 1246213.5 | 2637092.6007 | 1246208.9988 | 2637091.5851 | 1246206.9066
30 | 2637082.1041 | 1246270.1065 | 2637074.7971 | 1246299.5024
31 | 2637082.1041 | 1246270.1065 | 2637079.0019 | 1246268.4972 | 2637073.3986 | 1246264.6041 | 2637064.3978 | 1246255.5976 | 2637057.0497 | 1246246.8647
32 | 2637090.8033 | 1246205.2962 | 2637091.5851 | 1246206.9066
33 | 2637074.7971 | 1246299.5024 | 2637073.7989 | 1246303.2986
34 | 2637074.7971 | 1246299.5024 | 2637080.3983 | 1246300.1044 | 2637083.7981 | 1246300.0034 | 2637088.0012 | 1246299.496 | 2637093.1431 | 1246298.572
35 | 2637057.0497 | 1246246.8647 | 2637050.601 | 1246239.2008 | 2637042.8017 | 1246230.1017
36 | 2637090.8033 | 1246205.2962 | 2637090.8033 | 1246205.2962 | 2637088.3034 | 1246201.6004 | 2637084.802 | 1246197.398 | 2637077.8381 | 1246192.1841
37 | 2637073.7989 | 1246303.2986 | 2637070.8982 | 1246302.102 | 2637066.7357 | 1246298.5292 | 2637051.355 | 1246275.2175
38 | 2637073.7989 | 1246303.2986 | 2637071.6037 | 1246312.5021 | 2637068.3634 | 1246323.4284
39 | 2637093.1431 | 1246298.572 | 2637093.9233 | 1246298.4318
40 | 2637022.486 | 1246210.5587 | 2637028.9042 | 1246216.5061 | 2637042.8017 | 1246230.1017 | 2637042.8017 | 1246230.1017
41 | 2637068.2682 | 1246185.8154 | 2637077.599 | 1246192.0051 | 2637077.8381 | 1246192.1841
42 | 2637049.3002 | 1246272.1031 | 2637051.355 | 1246275.2175
43 | 2637120.16 | 1246295.5499 | 2637112.0984 | 1246295.7997 | 2637100.1993 | 1246297.3041 | 2637093.9233 | 1246298.4318
44 | 2637022.486 | 1246210.5587 | 2637009.9026 | 1246198.8983 | 2637005.4579 | 1246194.9557
45 | 2636950.5034 | 1246378.8017 | 2636945.1038 | 1246370.0958 | 2636930.1004 | 1246347.2986 | 2636919.0991 | 1246330.7972 | 2636911.2039 | 1246320.0966 | 2636909.3855 | 1246317.8846
46 | 2636950.5034 | 1246378.8017 | 2636965.2977 | 1246402.3982 | 2636980.8984 | 1246429.5011
47 | 2636950.5034 | 1246378.8017 | 2636922.4767 | 1246390.1126
48 | 2636922.4767 | 1246390.1126 | 2636915.763 | 1246373.0823
49 | 2636922.4767 | 1246390.1126 | 2636913.2419 | 1246394.0643
50 | 2636915.763 | 1246373.0823 | 2636910.1694 | 1246358.8934 | 2636907.7711 | 1246354.914
51 | 2636913.2419 | 1246394.0643 | 2636900.3301 | 1246399.5895
52 | 2637245.9526 | 1246376.9499 | 2637255.0115 | 1246353.2545 | 2637255.2688 | 1246351.0615
53 | 2637245.9526 | 1246376.9499 | 2637242.9411 | 1246384.8271
54 | 2637233.7717 | 1246408.8118 | 2637242.9411 | 1246384.8271
55 | 2637226.2861 | 1246427.0674 | 2637227.8557 | 1246424.2863 | 2637233.7717 | 1246408.8118
56 | 2637216.2004 | 1246318.2993 | 2637205.9032 | 1246317.3008 | 2637196.3035 | 1246315.9064
57 | 2637216.2004 | 1246318.2993 | 2637213.9093 | 1246345.107
58 | 2637184.2376 | 1246312.6092 | 2637189.303 | 1246314.406 | 2637196.3035 | 1246315.9064
59 | 2637209.1549 | 1246380.5849 | 2637212.263 | 1246364.3715 | 2637213.9093 | 1246345.107
60 | 2637226.2861 | 1246427.0674 | 2637222.2031 | 1246434.3018 | 2637216.3383 | 1246444.4497
61 | 2637184.2376 | 1246312.6092 | 2637181.1027 | 1246311.4972 | 2637180.9254 | 1246311.4103
62 | 2637209.1549 | 1246380.5849 | 2637183.7683 | 1246378.7981
63 | 2637209.1549 | 1246380.5849 | 2637205.8596 | 1246393.8986
64 | 2637139.7476 | 1246224.1133 | 2637132.5829 | 1246252.1314
65 | 2637131.9681 | 1246254.5356 | 2637132.5829 | 1246252.1314
66 | 2637123.3186 | 1246282.2081 | 2637125.9714 | 1246271.0035 | 2637128.4354 | 1246268.3505 | 2637131.9681 | 1246254.5356
67 | 2637120.16 | 1246295.5499 | 2637123.3186 | 1246282.2081
68 | 2637120.16 | 1246295.5499 | 2637124.7989 | 1246295.401 | 2637126.7849 | 1246295.5301
69 | 2637126.7849 | 1246295.5301 | 2637137.0992 | 1246296.2007 | 2637139.1029 | 1246296.4832
70 | 2636970.917 | 1246472.8382 | 2636961.6034 | 1246481.3047 | 2636959.4947 | 1246483.3325
71 | 2636956.9943 | 1246485.7371 | 2636959.4947 | 1246483.3325
72 | 2636970.917 | 1246472.8382 | 2636973.3002 | 1246470.6718
73 | 2637105.857 | 1246368.9993 | 2637124.8086 | 1246371.4058
74 | 2637105.857 | 1246368.9993 | 2637092.7779 | 1246367.3385
75 | 2637128.4294 | 1246371.8655 | 2637124.8086 | 1246371.4058
76 | 2637071.7876 | 1246364.6732 | 2637092.7779 | 1246367.3385
77 | 2637128.4294 | 1246371.8655 | 2637148.4628 | 1246374.4094
78 | 2637058.5979 | 1246362.9984 | 2637071.7876 | 1246364.6732
79 | 2637148.4628 | 1246374.4094 | 2637150.615 | 1246374.6826
80 | 2637058.5979 | 1246362.9984 | 2637058.3984 | 1246363.4975 | 2637055.6004 | 1246377.3002 | 2637055.1223 | 1246381.0272
81 | 2637165.4694 | 1246376.5688 | 2637150.615 | 1246374.6826
82 | 2637086.9008 | 1246602.1238 | 2637086.3272 | 1246601.6241
83 | 2637100.1017 | 1246608.8965 | 2637090.2008 | 1246604.9988 | 2637086.9008 | 1246602.1238
84 | 2637075.7983 | 1246592.6007 | 2637078.6039 | 1246594.4972 | 2637081.7041 | 1246597.5964 | 2637086.3272 | 1246601.6241
85 | 2637076.9 | 1246636.3029 | 2637086.1009 | 1246626.4984 | 2637100.1017 | 1246608.8965
86 | 2637100.1017 | 1246608.8965 | 2637120.3772 | 1246579.0618
87 | 2636987.6565 | 1246739.2805 | 2637003.4722 | 1246717.6204 | 2637017.7975 | 1246699.9981 | 2637036.1 | 1246679.2987 | 2637055.1039 | 1246660.0046 | 2637076.9 | 1246636.3029
88 | 2637076.9 | 1246636.3029 | 2637066.0983 | 1246629.0974 | 2637054.0023 | 1246621.1056 | 2637044.4612 | 1246614.449
89 | 2637128.2007 | 1246565.3992 | 2637120.8303 | 1246578.395 | 2637120.3772 | 1246579.0618
90 | 2636987.6565 | 1246739.2805 | 2636980.9438 | 1246755.9051 | 2636969.434 | 1246775.0794
91 | 2636987.6565 | 1246739.2805 | 2636971.0039 | 1246758.3004 | 2636951.5978 | 1246779.2044 | 2636914.1996 | 1246818.3974 | 2636899.7435 | 1246837.7203 | 2636872.0655 | 1246874.717
92 | 2636987.6565 | 1246739.2805 | 2637001.7652 | 1246755.1566 | 2637019.2038 | 1246776.0345 | 2637024.5033 | 1246781.394
93 | 2637128.2007 | 1246565.3992 | 2637131.6024 | 1246567.3996 | 2637135.6978 | 1246570.8052 | 2637141.0061 | 1246576.2337
94 | 2637130.7983 | 1246560.7013 | 2637128.2007 | 1246565.3992
95 | 2636969.434 | 1246775.0794 | 2636953.0999 | 1246789.0392
96 | 2636969.434 | 1246775.0794 | 2636968.0739 | 1246778.7956 | 2636968.7038 | 1246783.169 | 2636975.9855 | 1246788.7097
97 | 2636872.0655 | 1246874.717 | 2636838.2116 | 1246918.6579
98 | 2637024.5033 | 1246781.394 | 2637034.4032 | 1246791.4061 | 2637047.9029 | 1246808.0012 | 2637049.6864 | 1246810.1565
99 | 2637155.5561 | 1246591.113 | 2637141.0061 | 1246576.2337
100 | 2637130.7983 | 1246560.7013 | 2637147.8898 | 1246532.1318
101 | 2637130.7983 | 1246560.7013 | 2637123.9006 | 1246558.5011 | 2637116.5969 | 1246554.7975 | 2637113.1292 | 1246552.7561
102 | 2637113.1292 | 1246552.7561 | 2637109.8011 | 1246550.7968 | 2637099.1697 | 1246543.9673
103 | 2637164.6206 | 1246509.3278 | 2637150.8971 | 1246527.105 | 2637147.8898 | 1246532.1318
104 | 2637164.6206 | 1246509.3278 | 2637169.4224 | 1246503.1076
105 | 2637155.5561 | 1246591.113 | 2637175.1357 | 1246611.1358
106 | 2637178.0001 | 1246491.996 | 2637169.4224 | 1246503.1076
107 | 2637178.0001 | 1246491.996 | 2637185.9004 | 1246484.8964 | 2637195.0997 | 1246474.2026 | 2637205.0998 | 1246462.3019 | 2637215.903 | 1246445.2028 | 2637216.3383 | 1246444.4497
108 | 2637180.2276 | 1246478.8792 | 2637178.0001 | 1246491.996
109 | 2637180.2276 | 1246478.8792 | 2637187.2197 | 1246448.986
110 | 2637180.2276 | 1246478.8792 | 2637160.9553 | 1246474.5334 | 2637141.2883 | 1246468.4251
111 | 2636897.1376 | 1246400.9556 | 2636900.3301 | 1246399.5895
112 | 2636897.1376 | 1246400.9556 | 2636879.5025 | 1246408.502 | 2636864.9839 | 1246415.0187
113 | 2636864.9839 | 1246415.0187 | 2636852.6682 | 1246420.5466
114 | 2636907.7711 | 1246354.914 | 2636904.876 | 1246350.1103 | 2636897.3085 | 1246342.6028 | 2636887.8753 | 1246336.2845 | 2636875.1075 | 1246329.8314
115 | 2636867.4117 | 1246325.9418 | 2636875.1075 | 1246329.8314
116 | 2637051.797 | 1246414.2006 | 2637063.9938 | 1246416.4778
117 | 2637091.6804 | 1246421.6469 | 2637063.9938 | 1246416.4778
118 | 2637091.6804 | 1246421.6469 | 2637112.6318 | 1246425.5586
119 | 2637202.4057 | 1246405.8667 | 2637203.8848 | 1246401.8769 | 2637205.8596 | 1246393.8986
120 | 2637202.4057 | 1246405.8667 | 2637199.9259 | 1246412.5555
121 | 2637199.9259 | 1246412.5555 | 2637199.348 | 1246414.1144
122 | 2637195.797 | 1246423.6928 | 2637199.348 | 1246414.1144
123 | 2637183.7683 | 1246378.7981 | 2637182.1018 | 1246378.6808 | 2637165.4694 | 1246376.5688
124 | 2637188.5868 | 1246443.1414 | 2637195.797 | 1246423.6928
125 | 2637188.5868 | 1246443.1414 | 2637177.0473 | 1246440.5188
126 | 2637188.5868 | 1246443.1414 | 2637187.2197 | 1246448.986
127 | 2636961.3837 | 1246845.1411 | 2636957.1026 | 1246850.9969 | 2636956.9187 | 1246851.187
128 | 2636967.0462 | 1246837.3771 | 2636966.6023 | 1246838.003 | 2636961.3837 | 1246845.1411
129 | 2636944.3327 | 1246864.198 | 2636956.9187 | 1246851.187
130 | 2636967.0462 | 1246837.3771 | 2636970.6909 | 1246832.2382
131 | 2636930.5255 | 1246860.0325 | 2636935.8031 | 1246865.496 | 2636939.2148 | 1246867.0739 | 2636943.1832 | 1246865.3863 | 2636944.3327 | 1246864.198
132 | 2636980.3837 | 1246817.7128 | 2636974.9006 | 1246826.3026 | 2636970.6909 | 1246832.2382
133 | 2636930.5255 | 1246860.0325 | 2636912.4693 | 1246841.3398
134 | 2636991.4068 | 1246800.444 | 2636980.3837 | 1246817.7128
135 | 2636991.4068 | 1246800.444 | 2636975.9855 | 1246788.7097
136 | 2636991.4068 | 1246800.444 | 2636996.9356 | 1246804.9498
137 | 2636838.2116 | 1246918.6579 | 2636849.8865 | 1246932.3616 | 2636855.4065 | 1246932.5738 | 2636862.1648 | 1246930.4143 | 2636872.1611 | 1246920.9027
138 | 2637180.9254 | 1246311.4103 | 2637170.8985 | 1246306.4967 | 2637163.2999 | 1246302.8023 | 2637155.6169 | 1246300.43
139 | 2637141.2883 | 1246468.4251 | 2637133.9746 | 1246466.1536
140 | 2637143.7814 | 1246297.143 | 2637139.1029 | 1246296.4832
141 | 2637052.2484 | 1246175.4001 | 2637057.7011 | 1246178.8055 | 2637068.2682 | 1246185.8154
142 | 2637024.5394 | 1246157.4803 | 2637040.4019 | 1246168.0016 | 2637052.2484 | 1246175.4001
143 | 2637024.5394 | 1246157.4803 | 2637019.3003 | 1246154.0053 | 2637013.1014 | 1246149.8973 | 2637008.7991 | 1246145.7011 | 2637005.6022 | 1246141.1004 | 2637003.2023 | 1246137.105 | 2637001.7976 | 1246133.405 | 2637000.9017 | 1246129.2967 | 2637000.1988 | 1246124.5003 | 2637000.8003 | 1246118.9004 | 2637003.1007 | 1246112.1992 | 2637007.2996 | 1246102.6969 | 2637007.8222 | 1246101.5288
144 | 2637012.2132 | 1246091.6894 | 2637012.0264 | 1246092.1306 | 2637007.8222 | 1246101.5288
145 | 2637143.7814 | 1246297.143 | 2637145.5973 | 1246297.3991 | 2637153.5968 | 1246299.8062 | 2637155.6169 | 1246300.43
146 | 2636996.9356 | 1246804.9498 | 2637004.2492 | 1246810.9103
147 | 2637017.2487 | 1246821.5047 | 2637004.2492 | 1246810.9103
148 | 2637155.0925 | 1246434.8666 | 2637164.6908 | 1246437.7105 | 2637177.0473 | 1246440.5188
149 | 2637131.1228 | 1246429.0109 | 2637142.494 | 1246431.1339 | 2637155.0925 | 1246434.8666
150 | 2637131.1228 | 1246429.0109 | 2637112.6318 | 1246425.5586
151 | 2637246.8375 | 1246679.4838 | 2637220.5585 | 1246657.9382 | 2637208.6021 | 1246645.7997 | 2637197.0017 | 1246633.4967 | 2637175.1357 | 1246611.1358
152 | 2637246.8375 | 1246679.4838 | 2637254.2796 | 1246669.5239 | 2637272.9862 | 1246619.5197 | 2637285.3852 | 1246590.0671 | 2637289.5011 | 1246573.2449
153 | 2636996.5981 | 1246187.0966 | 2637005.4579 | 1246194.9557

## bus_geodata
| x | y | coords
0 | 2636687.8962 | 1246915.7497
1 | 2636691.0716 | 1246918.5134
2 | 2636704.2917 | 1246931.3847
3 | 2636706.5752 | 1246933.608
4 | 2636733.8784 | 1246929.7968
5 | 2636761.4168 | 1246965.4571
6 | 2636765.8886 | 1246991.4458
7 | 2636781.1483 | 1246961.3099
8 | 2636816.2766 | 1246946.7959
9 | 2637047.9837 | 1246505.0347
10 | 2637040.1755 | 1246498.3013
11 | 2637062.4011 | 1246517.201
12 | 2637022.3999 | 1246482.9067
13 | 2637069.7996 | 1246505.2668
14 | 2637067.284 | 1246520.8646
15 | 2637021.4998 | 1246481.9004
16 | 2637076.8998 | 1246494.8991
17 | 2637071.8515 | 1246524.2916
18 | 2636995.0994 | 1246451.705
19 | 2637008.3301 | 1246494.6169
20 | 2637041.7003 | 1246451.3064
21 | 2637048.8979 | 1246432.1054
22 | 2637089.4804 | 1246537.1709
23 | 2637089.0763 | 1246243.824
24 | 2637089.8843 | 1246240.7783
25 | 2637082.1041 | 1246270.1065
26 | 2637091.5851 | 1246206.9066
27 | 2637074.7971 | 1246299.5024
28 | 2637057.0497 | 1246246.8647
29 | 2637090.8033 | 1246205.2962
30 | 2637073.7989 | 1246303.2986
31 | 2637093.1431 | 1246298.572
32 | 2637042.8017 | 1246230.1017
33 | 2637077.8381 | 1246192.1841
34 | 2637051.355 | 1246275.2175
35 | 2637068.3634 | 1246323.4284
36 | 2637093.9233 | 1246298.4318
37 | 2637022.486 | 1246210.5587
38 | 2636909.3855 | 1246317.8846
39 | 2636950.5034 | 1246378.8017
40 | 2636980.8984 | 1246429.5011
41 | 2636922.4767 | 1246390.1126
42 | 2636915.763 | 1246373.0823
43 | 2636913.2419 | 1246394.0643
44 | 2637255.2688 | 1246351.0615
45 | 2637245.9526 | 1246376.9499
46 | 2637242.9411 | 1246384.8271
47 | 2637233.7717 | 1246408.8118
48 | 2637216.2004 | 1246318.2993
49 | 2637196.3035 | 1246315.9064
50 | 2637213.9093 | 1246345.107
51 | 2637226.2861 | 1246427.0674
52 | 2637184.2376 | 1246312.6092
53 | 2637209.1549 | 1246380.5849
54 | 2637132.5829 | 1246252.1314
55 | 2637139.7476 | 1246224.1133
56 | 2637131.9681 | 1246254.5356
57 | 2637123.3186 | 1246282.2081
58 | 2637120.16 | 1246295.5499
59 | 2637126.7849 | 1246295.5301
60 | 2636959.4947 | 1246483.3325
61 | 2636970.917 | 1246472.8382
62 | 2636956.9943 | 1246485.7371
63 | 2636973.3002 | 1246470.6718
64 | 2637105.857 | 1246368.9993
65 | 2637124.8086 | 1246371.4058
66 | 2637092.7779 | 1246367.3385
67 | 2637128.4294 | 1246371.8655
68 | 2637071.7876 | 1246364.6732
69 | 2637148.4628 | 1246374.4094
70 | 2637058.5979 | 1246362.9984
71 | 2637150.615 | 1246374.6826
72 | 2637055.1223 | 1246381.0272
73 | 2637086.9008 | 1246602.1238
74 | 2637086.3272 | 1246601.6241
75 | 2637100.1017 | 1246608.8965
76 | 2637075.7983 | 1246592.6007
77 | 2637076.9 | 1246636.3029
78 | 2637120.3772 | 1246579.0618
79 | 2636987.6565 | 1246739.2805
80 | 2637044.4612 | 1246614.449
81 | 2637128.2007 | 1246565.3992
82 | 2636969.434 | 1246775.0794
83 | 2636872.0655 | 1246874.717
84 | 2637024.5033 | 1246781.394
85 | 2637141.0061 | 1246576.2337
86 | 2637130.7983 | 1246560.7013
87 | 2637113.1292 | 1246552.7561
88 | 2637099.1697 | 1246543.9673
89 | 2637147.8898 | 1246532.1318
90 | 2637164.6206 | 1246509.3278
91 | 2637155.5561 | 1246591.113
92 | 2637169.4224 | 1246503.1076
93 | 2637216.3383 | 1246444.4497
94 | 2637178.0001 | 1246491.996
95 | 2637180.2276 | 1246478.8792
96 | 2636900.3301 | 1246399.5895
97 | 2636897.1376 | 1246400.9557
98 | 2636864.9839 | 1246415.0187
99 | 2636907.7711 | 1246354.914
100 | 2636852.6682 | 1246420.5466
101 | 2636875.1075 | 1246329.8314
102 | 2637051.797 | 1246414.2006
103 | 2637063.9938 | 1246416.4778
104 | 2637091.6804 | 1246421.6469
105 | 2636990.5031 | 1246510.4633
106 | 2637202.4057 | 1246405.8667
107 | 2637205.8596 | 1246393.8986
108 | 2637199.9259 | 1246412.5555
109 | 2637199.348 | 1246414.1144
110 | 2637183.7683 | 1246378.7981
111 | 2637195.797 | 1246423.6928
112 | 2637165.4694 | 1246376.5688
113 | 2637188.5868 | 1246443.1414
114 | 2636961.3837 | 1246845.1411
115 | 2636956.9187 | 1246851.187
116 | 2636967.0462 | 1246837.3771
117 | 2636944.3327 | 1246864.198
118 | 2636970.6909 | 1246832.2382
119 | 2636930.5255 | 1246860.0325
120 | 2636980.3837 | 1246817.7128
121 | 2636912.4693 | 1246841.3398
122 | 2636991.4068 | 1246800.444
123 | 2636953.0999 | 1246789.0392
124 | 2636975.9855 | 1246788.7097
125 | 2636838.2116 | 1246918.6579
126 | 2637049.6864 | 1246810.1565
127 | 2637180.9254 | 1246311.4103
128 | 2637133.9746 | 1246466.1536
129 | 2637141.2883 | 1246468.4251
130 | 2637187.2197 | 1246448.986
131 | 2637139.1029 | 1246296.4832
132 | 2637049.3002 | 1246272.1031
133 | 2637068.2682 | 1246185.8154
134 | 2637052.2484 | 1246175.4001
135 | 2637024.5394 | 1246157.4803
136 | 2637007.8222 | 1246101.5288
137 | 2636867.4116 | 1246325.9418
138 | 2637155.6169 | 1246300.43
139 | 2637143.7814 | 1246297.143
140 | 2637004.2492 | 1246810.9103
141 | 2636996.9356 | 1246804.9498
142 | 2637017.2487 | 1246821.5047
143 | 2637177.0473 | 1246440.5188
144 | 2637012.2132 | 1246091.6894
145 | 2637155.0925 | 1246434.8666
146 | 2637131.1228 | 1246429.0109
147 | 2637112.6318 | 1246425.5586
148 | 2637175.1357 | 1246611.1358
149 | 2637246.8375 | 1246679.4838
150 | 2637289.5011 | 1246573.2449
151 | 2637005.4579 | 1246194.9557
152 | 2636996.5981 | 1246187.0966
153 | 2636872.1611 | 1246920.9027
154 | 2636824.4385 | 1246960.7556
155 | 2637022.3999 | 1246482.9067

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97364 | -0.50853 | 0.0031525 | 0.00079009
1 | 0.97365 | -0.50829 | 0 | 0
2 | 0.9737 | -0.50722 | 0.00045697 | 0.00011453
3 | 0.97371 | -0.50701 | 0 | 0
4 | 0.97369 | -0.50753 | 0.00098123 | 0.00024592
5 | 0.97413 | -0.49883 | 0 | 0
6 | 0.97409 | -0.4996 | 0.0015959 | 0.00039998
7 | 0.97424 | -0.49654 | 0 | 0
8 | 0.97446 | -0.49219 | 0 | 0
9 | 0.9802 | -0.37939 | 0.0028323 | 0.00070984
10 | 0.97998 | -0.38367 | 0.0025506 | 0.00063923
11 | 0.98061 | -0.37133 | 0 | 0
12 | 0.97949 | -0.39317 | 0 | 0
13 | 0.98052 | -0.3731 | 0.0035183 | 0.00088177
14 | 0.98075 | -0.36853 | 0.0014748 | 0.00036961
15 | 0.97946 | -0.39371 | 0 | 0
16 | 0.98048 | -0.37388 | 0.0034327 | 0.00086032
17 | 0.98089 | -0.36587 | 0.0024753 | 0.00062038
18 | 0.97865 | -0.40952 | 0 | 0
19 | 0.97942 | -0.39444 | 0.0013159 | 0.0003298
20 | 1 | 0 | -0.29046 | -0.074515
21 | 0.99865 | -0.025375 | 0.0021441 | 0.00053736
22 | 0.98143 | -0.35548 | 0.0027322 | 0.00068476
23 | 0.97554 | -0.47111 | 0.0009282 | 0.00023263
24 | 0.9755 | -0.4719 | 0.0013985 | 0.0003505
25 | 0.97591 | -0.46378 | 0 | 0
26 | 0.97509 | -0.47985 | 0.00094389 | 0.00023656
27 | 0.97652 | -0.45167 | 0 | 0
28 | 0.97568 | -0.46828 | 0.0011678 | 0.00029268
29 | 0.97507 | -0.48023 | 0.0036643 | 0.00091837
30 | 0.9765 | -0.45205 | 0 | 0
31 | 0.97699 | -0.44254 | 0.0015338 | 0.0003844
32 | 0.97556 | -0.47068 | 0.0024423 | 0.00061209
33 | 0.97494 | -0.48289 | 0.00063154 | 0.00015828
34 | 0.97639 | -0.4543 | 0.0016053 | 0.00040233
35 | 0.97647 | -0.45274 | 0.0018075 | 0.00045301
36 | 0.97701 | -0.44213 | 0.0013707 | 0.00034353
37 | 0.97547 | -0.4725 | 0.0017456 | 0.00043748
38 | 0.97617 | -0.4581 | 0.0044707 | 0.0011205
39 | 0.97648 | -0.45209 | 0 | 0
40 | 0.97797 | -0.42277 | 0.0011634 | 0.00029158
41 | 0.97431 | -0.49463 | 0 | 0
42 | 0.97375 | -0.50578 | 0.0051027 | 0.0012789
43 | 0.9739 | -0.50272 | 0.0028699 | 0.00071927
44 | 0.98541 | -0.27835 | 0.0010662 | 0.00026721
45 | 0.98544 | -0.27782 | 0.0013689 | 0.00034307
46 | 0.98545 | -0.27745 | 0.0009527 | 0.00023877
47 | 0.98553 | -0.27589 | 0.0012663 | 0.00031737
48 | 0.98163 | -0.35166 | 0 | 0
49 | 0.98074 | -0.36903 | 0.0012534 | 0.00031413
50 | 0.98283 | -0.32841 | 0.00060021 | 0.00015043
51 | 0.98562 | -0.27424 | 0.001174 | 0.00029423
52 | 0.9802 | -0.37961 | 0.0042381 | 0.0010622
53 | 0.98444 | -0.29712 | 0 | 0
54 | 0.97758 | -0.43088 | 0.0016908 | 0.00042375
55 | 0.97756 | -0.43132 | 0.00083377 | 0.00020896
56 | 0.97759 | -0.43077 | 0.00070921 | 0.00017775
57 | 0.97768 | -0.42903 | 0.0021757 | 0.00054527
58 | 0.97774 | -0.42768 | 0 | 0
59 | 0.97796 | -0.42341 | 0.001657 | 0.00041527
60 | 0.97851 | -0.41233 | 0.0010636 | 0.00026657
61 | 0.97854 | -0.4118 | 0.00094128 | 0.00023591
62 | 0.97851 | -0.41238 | 0.00081573 | 0.00020444
63 | 0.97854 | -0.41164 | 0.0011909 | 0.00029846
64 | 0.98338 | -0.31773 | 0.0013135 | 0.0003292
65 | 0.98347 | -0.31607 | 0.0020614 | 0.00051663
66 | 0.98334 | -0.31857 | 0.0012537 | 0.00031421
67 | 0.98349 | -0.31562 | 0.0016799 | 0.00042101
68 | 0.9833 | -0.31943 | 0.0010587 | 0.00026532
69 | 0.98365 | -0.3125 | 0.0027547 | 0.00069039
70 | 0.98328 | -0.31972 | 0 | 0
71 | 0.98367 | -0.31206 | 0.0015429 | 0.00038669
72 | 0.98326 | -0.32012 | 0.0012002 | 0.00030079
73 | 0.98062 | -0.37132 | 0.0016729 | 0.00041926
74 | 0.98061 | -0.3714 | 0.0022158 | 0.00055532
75 | 0.98072 | -0.36926 | 0 | 0
76 | 0.98057 | -0.37233 | 0.0036863 | 0.00092387
77 | 0.97989 | -0.38548 | 0 | 0
78 | 0.98181 | -0.34804 | 0.0042303 | 0.0010602
79 | 0.97698 | -0.4427 | 0 | 0
80 | 0.97983 | -0.38679 | 0.0018488 | 0.00046336
81 | 0.98235 | -0.33759 | 0 | 0
82 | 0.9766 | -0.45011 | 0 | 0
83 | 0.97525 | -0.47671 | 0 | 0
84 | 0.97684 | -0.44531 | 0.0011261 | 0.00028223
85 | 0.98194 | -0.3456 | 0.0076269 | 0.0019115
86 | 0.98266 | -0.33149 | 0 | 0
87 | 0.98215 | -0.34148 | 0.0035324 | 0.00088531
88 | 0.98172 | -0.3497 | 0.002299 | 0.00057618
89 | 0.98403 | -0.30498 | 0.0025834 | 0.00064746
90 | 0.9852 | -0.28215 | 0.0022723 | 0.00056949
91 | 0.98158 | -0.35261 | 0.0076298 | 0.0019122
92 | 0.98554 | -0.27575 | 0.010026 | 0.0025128
93 | 0.98573 | -0.27214 | 0.0018498 | 0.0004636
94 | 0.98616 | -0.26369 | 0 | 0
95 | 0.98677 | -0.25182 | 0 | 0
96 | 0.97337 | -0.5133 | 0.017058 | 0.0042752
97 | 0.97329 | -0.51483 | 0.0050837 | 0.0012741
98 | 0.97267 | -0.52701 | 0.010194 | 0.0025548
99 | 0.97323 | -0.51606 | 0.0040752 | 0.0010213
100 | 0.97256 | -0.52916 | 0.0086469 | 0.0021671
101 | 0.97229 | -0.53458 | 0.017164 | 0.0043018
102 | 0.99747 | -0.047737 | 0 | 0
103 | 0.99666 | -0.063029 | 0.0022352 | 0.0005602
104 | 0.99483 | -0.097556 | 0.0019465 | 0.00048783
105 | 0.97941 | -0.39482 | 0.00087443 | 0.00021915
106 | 0.98599 | -0.26696 | 0.0015765 | 0.00039511
107 | 0.98525 | -0.28144 | 0.00108 | 0.00027066
108 | 0.98643 | -0.25849 | 0.00069413 | 0.00017397
109 | 0.98653 | -0.2565 | 0.0010431 | 0.00026144
110 | 0.98408 | -0.30407 | 0.0015649 | 0.0003922
111 | 0.98718 | -0.24406 | 0.00072432 | 0.00018153
112 | 0.98385 | -0.30859 | 0.00073684 | 0.00018467
113 | 0.9885 | -0.2186 | 0 | 0
114 | 0.97605 | -0.46088 | 0.00059161 | 0.00014827
115 | 0.97603 | -0.4613 | 0.00065405 | 0.00016392
116 | 0.97609 | -0.46024 | 0.00058893 | 0.0001476
117 | 0.97599 | -0.46209 | 0.0010028 | 0.00025132
118 | 0.97611 | -0.45975 | 0.00078139 | 0.00019583
119 | 0.97597 | -0.46252 | 0.00056952 | 0.00014273
120 | 0.97619 | -0.45816 | 0.00079864 | 0.00020016
121 | 0.97595 | -0.46291 | 0.00080976 | 0.00020294
122 | 0.9763 | -0.45598 | 0 | 0
123 | 0.97658 | -0.45047 | 0.00091264 | 0.00022873
124 | 0.97645 | -0.45304 | 0.00085532 | 0.00021436
125 | 0.97471 | -0.48731 | 0 | 0
126 | 0.97679 | -0.4463 | 0.001422 | 0.0003564
127 | 0.98006 | -0.38232 | 0.0014639 | 0.00036689
128 | 0.98665 | -0.25419 | 0.001259 | 0.00031553
129 | 0.98666 | -0.25402 | 0.0017903 | 0.00044869
130 | 0.98822 | -0.22405 | 0.0015211 | 0.00038123
131 | 0.97839 | -0.41507 | 0.0019023 | 0.00047676
132 | 0.97638 | -0.45443 | 0.0017728 | 0.0004443
133 | 0.97486 | -0.48439 | 0.0014214 | 0.00035623
134 | 0.97476 | -0.4864 | 0.00083954 | 0.00021041
135 | 0.97461 | -0.48936 | 0.0012086 | 0.00030292
136 | 0.97438 | -0.49391 | 0.0030064 | 0.00075349
137 | 0.97223 | -0.53567 | 0.0068262 | 0.0017108
138 | 0.97901 | -0.40286 | 0.0012919 | 0.00032378
139 | 0.97856 | -0.41172 | 0.00067427 | 0.00016899
140 | 0.97627 | -0.45661 | 0.0010521 | 0.00026369
141 | 0.97629 | -0.45631 | 0.00075729 | 0.0001898
142 | 0.97626 | -0.45682 | 0.00068786 | 0.00017239
143 | 0.98925 | -0.20422 | 0.00094112 | 0.00023587
144 | 0.97437 | -0.49404 | 0.00067018 | 0.00016796
145 | 0.99069 | -0.17663 | 0.0012461 | 0.00031231
146 | 0.99226 | -0.14653 | 0.0011434 | 0.00028657
147 | 0.99346 | -0.12359 | 0.0010257 | 0.00025708
148 | 0.9813 | -0.35819 | 0.007643 | 0.0019155
149 | 0.98099 | -0.36423 | 0 | 0
150 | 0.98063 | -0.37123 | 0.0033572 | 0.00084139
151 | 0.97543 | -0.47325 | 0.00087248 | 0.00021866
152 | 0.97542 | -0.47345 | 0.00090225 | 0.00022613
153 | 0.97459 | -0.48972 | 0.0029665 | 0.00074347
154 | 0.97445 | -0.49257 | 0.0012682 | 0.00031783
155 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0031525 | -0.00079009 | 0.0031526 | 0.00079007 | 3.6645e-08 | -2.8902e-08 | 0.004818 | 0.004818 | 0.004818 | 0.97364 | -0.50853 | 0.97365 | -0.50829 | 1.3236
1 | -0.0031526 | -0.00079007 | 0.0031527 | 0.00078994 | 1.6061e-07 | -1.267e-07 | 0.004818 | 0.0048179 | 0.004818 | 0.97365 | -0.50829 | 0.9737 | -0.50722 | 1.3236
2 | -0.0036097 | -0.00090447 | 0.0036097 | 0.00090445 | 3.6367e-08 | -1.6367e-08 | 0.0055162 | 0.0055162 | 0.0055162 | 0.9737 | -0.50722 | 0.97371 | -0.50701 | 1.5155
3 | 0.00098125 | 0.00024557 | -0.00098123 | -0.00024592 | 2.4329e-08 | -3.4334e-07 | 0.0014994 | 0.0014995 | 0.0014995 | 0.97371 | -0.50701 | 0.97369 | -0.50753 | 0.41196
4 | -0.004591 | -0.00115 | 0.0045928 | 0.00115 | 1.7885e-06 | -6.1249e-08 | 0.0070156 | 0.0070152 | 0.0070156 | 0.97371 | -0.50701 | 0.97413 | -0.49883 | 1.9274
5 | 0.001596 | 0.00039969 | -0.0015959 | -0.00039998 | 5.8773e-08 | -2.9067e-07 | 0.0024378 | 0.0024379 | 0.0024379 | 0.97413 | -0.49883 | 0.97409 | -0.4996 | 0.66976
6 | -0.0061887 | -0.0015497 | 0.0061894 | 0.0015498 | 6.7374e-07 | 1.8086e-07 | 0.009453 | 0.0094529 | 0.009453 | 0.97413 | -0.49883 | 0.97424 | -0.49654 | 2.597
7 | -0.0061894 | -0.0015498 | 0.0061907 | 0.0015502 | 1.2824e-06 | 3.4408e-07 | 0.0094529 | 0.0094528 | 0.0094529 | 0.97424 | -0.49654 | 0.97446 | -0.49219 | 2.597
8 | 0.0012682 | 0.00031765 | -0.0012682 | -0.00031783 | 2.2746e-08 | -1.8694e-07 | 0.0019365 | 0.0019365 | 0.0019365 | 0.97446 | -0.49219 | 0.97445 | -0.49257 | 0.53202
9 | -0.0074589 | -0.0018678 | 0.0074606 | 0.0018685 | 1.7344e-06 | 6.657e-07 | 0.011389 | 0.011389 | 0.011389 | 0.97446 | -0.49219 | 0.97471 | -0.48731 | 3.1289
10 | 0.091966 | 0.023255 | -0.091947 | -0.023243 | 1.8861e-05 | 1.1551e-05 | 0.13969 | 0.13969 | 0.13969 | 0.9802 | -0.37939 | 0.97998 | -0.38367 | 9.5938
11 | -0.094798 | -0.023965 | 0.094835 | 0.023987 | 3.6692e-05 | 2.253e-05 | 0.14398 | 0.14398 | 0.14398 | 0.9802 | -0.37939 | 0.98061 | -0.37133 | 9.8891
12 | 0.089396 | 0.022604 | -0.089356 | -0.022579 | 4.0697e-05 | 2.4861e-05 | 0.13581 | 0.13581 | 0.13581 | 0.97998 | -0.38367 | 0.97949 | -0.39317 | 9.3278
13 | 0.0069517 | 0.0017422 | -0.0069512 | -0.001742 | 5.8625e-07 | 1.9798e-07 | 0.010549 | 0.010549 | 0.010549 | 0.98061 | -0.37133 | 0.98052 | -0.3731 | 2.898
14 | -0.10179 | -0.025729 | 0.1018 | 0.025738 | 1.3667e-05 | 8.4386e-06 | 0.15453 | 0.15453 | 0.15453 | 0.98061 | -0.37133 | 0.98075 | -0.36853 | 10.6136
15 | 0.089356 | 0.022579 | -0.089353 | -0.022578 | 2.331e-06 | 1.424e-06 | 0.13581 | 0.13581 | 0.13581 | 0.97949 | -0.39317 | 0.97946 | -0.39371 | 9.3278
16 | 0.0034329 | 0.00086025 | -0.0034327 | -0.00086032 | 1.2789e-07 | -7.664e-08 | 0.0052096 | 0.0052096 | 0.0052096 | 0.98052 | -0.3731 | 0.98048 | -0.37388 | 1.4312
17 | -0.10327 | -0.026107 | 0.10329 | 0.026115 | 1.3157e-05 | 8.1322e-06 | 0.15677 | 0.15677 | 0.15677 | 0.98075 | -0.36853 | 0.98089 | -0.36587 | 10.7672
18 | 0.087163 | 0.022029 | -0.087097 | -0.021989 | 6.6034e-05 | 4.0243e-05 | 0.13249 | 0.13249 | 0.13249 | 0.97946 | -0.39371 | 0.97865 | -0.40952 | 9.0993
19 | 0.0021905 | 0.00054848 | -0.0021904 | -0.00054867 | 7.6019e-08 | -1.8175e-07 | 0.0033276 | 0.0033277 | 0.0033277 | 0.97946 | -0.39371 | 0.97942 | -0.39444 | 0.9142
20 | -0.10576 | -0.026736 | 0.10582 | 0.026768 | 5.2746e-05 | 3.2654e-05 | 0.16053 | 0.16053 | 0.16053 | 0.98089 | -0.36587 | 0.98143 | -0.35548 | 11.0251
21 | 0.083085 | 0.020984 | -0.083032 | -0.020951 | 5.2712e-05 | 3.2741e-05 | 0.12639 | 0.12639 | 0.12639 | 0.97865 | -0.40952 | 0.97797 | -0.42277 | 11.5739
22 | 0.004012 | 0.001005 | -0.0040116 | -0.0010051 | 4.0341e-07 | -1.0504e-07 | 0.0061 | 0.0061001 | 0.0061001 | 0.97865 | -0.40952 | 0.97854 | -0.41164 | 1.6759
23 | 0.00087444 | 0.00021886 | -0.00087443 | -0.00021915 | 1.5787e-08 | -2.9009e-07 | 0.0013284 | 0.0013285 | 0.0013285 | 0.97942 | -0.39444 | 0.97941 | -0.39482 | 0.36498
24 | 0.28881 | 0.074515 | -0.28846 | -0.074288 | 0.00035666 | 0.00022718 | 0.43052 | 0.43052 | 0.43052 | 1 | 0 | 0.99865 | -0.025375 | 29.5685
25 | 0.28631 | 0.073751 | -0.286 | -0.073552 | 0.00031123 | 0.00019824 | 0.42732 | 0.42732 | 0.42732 | 0.99865 | -0.025375 | 0.99747 | -0.047737 | 29.3491
26 | -0.10855 | -0.027453 | 0.10858 | 0.027472 | 3.0092e-05 | 1.8661e-05 | 0.16467 | 0.16467 | 0.16467 | 0.98143 | -0.35548 | 0.98172 | -0.3497 | 11.3096
27 | 0.013793 | 0.003458 | -0.013793 | -0.0034577 | 5.2308e-07 | 2.9543e-07 | 0.02104 | 0.02104 | 0.02104 | 0.97554 | -0.47111 | 0.9755 | -0.4719 | 5.7802
28 | -0.014722 | -0.0036906 | 0.014727 | 0.0036935 | 5.1419e-06 | 2.9512e-06 | 0.022456 | 0.022456 | 0.022456 | 0.97554 | -0.47111 | 0.97591 | -0.46378 | 6.1692
29 | 0.012394 | 0.0031072 | -0.01239 | -0.0031046 | 4.6913e-06 | 2.5657e-06 | 0.018907 | 0.018907 | 0.018907 | 0.9755 | -0.4719 | 0.97509 | -0.47985 | 5.1942
30 | -0.02186 | -0.0054807 | 0.021872 | 0.0054884 | 1.2619e-05 | 7.6974e-06 | 0.033331 | 0.033331 | 0.033331 | 0.97591 | -0.46378 | 0.97652 | -0.45167 | 9.157
31 | 0.0071329 | 0.0017872 | -0.0071314 | -0.0017867 | 1.5287e-06 | 5.4785e-07 | 0.010876 | 0.010876 | 0.010876 | 0.97591 | -0.46378 | 0.97568 | -0.46828 | 2.9879
32 | 0.011446 | 0.002868 | -0.011446 | -0.0028679 | 2.048e-07 | 1.0874e-07 | 0.017466 | 0.017466 | 0.017466 | 0.97509 | -0.47985 | 0.97507 | -0.48023 | 4.7985
33 | 0.0051861 | 0.0012992 | -0.005186 | -0.0012991 | 9.1914e-08 | 9.7224e-09 | 0.0079023 | 0.0079024 | 0.0079024 | 0.97652 | -0.45167 | 0.9765 | -0.45205 | 2.171
34 | -0.027058 | -0.0067876 | 0.02707 | 0.0067949 | 1.1791e-05 | 7.3145e-06 | 0.041234 | 0.041234 | 0.041234 | 0.97652 | -0.45167 | 0.97699 | -0.44254 | 11.3279
35 | 0.0059636 | 0.001494 | -0.0059629 | -0.0014938 | 6.8244e-07 | 1.6203e-07 | 0.0090949 | 0.009095 | 0.009095 | 0.97568 | -0.46828 | 0.97556 | -0.47068 | 2.4986
36 | 0.0077813 | 0.0019495 | -0.0077803 | -0.0019492 | 9.8515e-07 | 3.9813e-07 | 0.011874 | 0.011875 | 0.011875 | 0.97507 | -0.48023 | 0.97494 | -0.48289 | 3.2622
37 | 0.0033784 | 0.00084636 | -0.0033781 | -0.00084658 | 3.6327e-07 | -2.2472e-07 | 0.005148 | 0.0051482 | 0.0051482 | 0.9765 | -0.45205 | 0.97639 | -0.4543 | 1.4143
38 | 0.0018076 | 0.00045279 | -0.0018075 | -0.00045301 | 5.9342e-08 | -2.2295e-07 | 0.0027544 | 0.0027544 | 0.0027544 | 0.9765 | -0.45205 | 0.97647 | -0.45274 | 0.75672
39 | -0.028604 | -0.0071793 | 0.028605 | 0.0071797 | 5.6425e-07 | 3.5119e-07 | 0.04357 | 0.04357 | 0.04357 | 0.97699 | -0.44254 | 0.97701 | -0.44213 | 11.9697
40 | 0.0035207 | 0.00088172 | -0.0035204 | -0.00088188 | 3.0485e-07 | -1.5686e-07 | 0.0053698 | 0.00537 | 0.00537 | 0.97556 | -0.47068 | 0.97547 | -0.4725 | 1.4753
41 | 0.0071487 | 0.0017909 | -0.0071482 | -0.0017907 | 5.1318e-07 | 1.851e-07 | 0.010911 | 0.010911 | 0.010911 | 0.97494 | -0.48289 | 0.97486 | -0.48439 | 2.9974
42 | 0.0017728 | 0.00044426 | -0.0017728 | -0.0004443 | 1.0213e-08 | -4.013e-08 | 0.0027017 | 0.0027017 | 0.0027017 | 0.97639 | -0.4543 | 0.97638 | -0.45443 | 0.74223
43 | -0.029975 | -0.0075232 | 0.029996 | 0.0075361 | 2.0665e-05 | 1.2894e-05 | 0.045657 | 0.045657 | 0.045657 | 0.97701 | -0.44213 | 0.97774 | -0.42768 | 12.5432
44 | 0.0017748 | 0.0004444 | -0.0017747 | -0.00044465 | 6.3481e-08 | -2.4769e-07 | 0.0027072 | 0.0027073 | 0.0027073 | 0.97547 | -0.4725 | 0.97543 | -0.47325 | 0.74377
45 | -0.0044707 | -0.0011205 | 0.004472 | 0.0011204 | 1.2805e-06 | -9.9981e-08 | 0.0068149 | 0.0068146 | 0.0068149 | 0.97617 | -0.4581 | 0.97648 | -0.45209 | 1.8722
46 | -0.081754 | -0.020588 | 0.081869 | 0.020659 | 0.00011477 | 7.1229e-05 | 0.12462 | 0.12462 | 0.12462 | 0.97648 | -0.45209 | 0.97797 | -0.42277 | 11.4118
47 | 0.077282 | 0.019468 | -0.077125 | -0.019368 | 0.00015689 | 0.00010003 | 0.1178 | 0.1178 | 0.1178 | 0.97648 | -0.45209 | 0.97431 | -0.49463 | 32.3634
48 | 0.033221 | 0.0083456 | -0.033204 | -0.0083345 | 1.7677e-05 | 1.1085e-05 | 0.050744 | 0.050744 | 0.050744 | 0.97431 | -0.49463 | 0.97375 | -0.50578 | 13.9408
49 | 0.043904 | 0.011022 | -0.043887 | -0.011012 | 1.6939e-05 | 1.0716e-05 | 0.067059 | 0.067059 | 0.067059 | 0.97431 | -0.49463 | 0.9739 | -0.50272 | 18.4227
50 | 0.028101 | 0.0070557 | -0.028087 | -0.0070471 | 1.3763e-05 | 8.5607e-06 | 0.042947 | 0.042947 | 0.042947 | 0.97375 | -0.50578 | 0.97323 | -0.51606 | 11.7986
51 | 0.041017 | 0.010292 | -0.040996 | -0.010279 | 2.0687e-05 | 1.3065e-05 | 0.062674 | 0.062674 | 0.062674 | 0.9739 | -0.50272 | 0.97337 | -0.5133 | 17.218
52 | -0.0010662 | -0.00026721 | 0.0010662 | 0.00026688 | 2.6803e-08 | -3.3415e-07 | 0.00161 | 0.0016099 | 0.00161 | 0.98541 | -0.27835 | 0.98544 | -0.27782 | 0.44231
53 | -0.0024351 | -0.00060995 | 0.0024351 | 0.00060987 | 4.2754e-08 | -8.0078e-08 | 0.0036769 | 0.0036768 | 0.0036769 | 0.98544 | -0.27782 | 0.98545 | -0.27745 | 1.0101
54 | -0.0033878 | -0.00084863 | 0.0033881 | 0.00084847 | 2.5196e-07 | -1.6592e-07 | 0.0051154 | 0.0051153 | 0.0051154 | 0.98545 | -0.27745 | 0.98553 | -0.27589 | 1.4053
55 | -0.0046544 | -0.0011658 | 0.0046547 | 0.0011658 | 3.6592e-07 | -1.7628e-08 | 0.0070272 | 0.0070271 | 0.0070272 | 0.98553 | -0.27589 | 0.98562 | -0.27424 | 1.9306
56 | 0.048041 | 0.012117 | -0.048001 | -0.012091 | 3.9896e-05 | 2.528e-05 | 0.072851 | 0.072851 | 0.072851 | 0.98163 | -0.35166 | 0.98074 | -0.36903 | 20.0141
57 | -0.048041 | -0.012117 | 0.048095 | 0.012151 | 5.3548e-05 | 3.393e-05 | 0.072851 | 0.072851 | 0.072851 | 0.98163 | -0.35166 | 0.98283 | -0.32841 | 20.0141
58 | 0.046748 | 0.011777 | -0.046724 | -0.011762 | 2.3661e-05 | 1.4985e-05 | 0.07095 | 0.07095 | 0.07095 | 0.98074 | -0.36903 | 0.9802 | -0.37961 | 19.4917
59 | -0.048695 | -0.012301 | 0.048768 | 0.012347 | 7.3127e-05 | 4.6346e-05 | 0.07376 | 0.07376 | 0.07376 | 0.98283 | -0.32841 | 0.98444 | -0.29712 | 20.2637
60 | -0.0058287 | -0.00146 | 0.0058293 | 0.0014602 | 5.8154e-07 | 1.1691e-07 | 0.0087995 | 0.0087994 | 0.0087995 | 0.98562 | -0.27424 | 0.98573 | -0.27214 | 2.4175
61 | 0.042486 | 0.0107 | -0.042481 | -0.010697 | 5.5e-06 | 3.4756e-06 | 0.064516 | 0.064516 | 0.064516 | 0.9802 | -0.37961 | 0.98006 | -0.38232 | 17.7242
62 | 0.015179 | 0.0038069 | -0.015174 | -0.003804 | 5.0243e-06 | 2.8921e-06 | 0.022945 | 0.022945 | 0.022945 | 0.98444 | -0.29712 | 0.98408 | -0.30407 | 6.3035
63 | -0.063947 | -0.016154 | 0.063995 | 0.016185 | 4.8099e-05 | 3.0609e-05 | 0.096704 | 0.096704 | 0.096704 | 0.98444 | -0.29712 | 0.98525 | -0.28144 | 26.5671
64 | 0.00083379 | 0.00020861 | -0.00083377 | -0.00020896 | 1.7467e-08 | -3.514e-07 | 0.001269 | 0.0012692 | 0.0012692 | 0.97758 | -0.43088 | 0.97756 | -0.43132 | 0.34867
65 | -0.0025246 | -0.00063236 | 0.0025246 | 0.00063234 | 1.3741e-08 | -2.232e-08 | 0.0038426 | 0.0038426 | 0.0038426 | 0.97758 | -0.43088 | 0.97759 | -0.43077 | 1.0557
66 | -0.0032338 | -0.00081009 | 0.0032341 | 0.00080989 | 2.6705e-07 | -1.9766e-07 | 0.0049221 | 0.004922 | 0.0049221 | 0.97759 | -0.43077 | 0.97768 | -0.42903 | 1.3522
67 | -0.0054097 | -0.0013552 | 0.0054101 | 0.0013552 | 3.4853e-07 | 5.1113e-08 | 0.0082333 | 0.0082333 | 0.0082333 | 0.97768 | -0.42903 | 0.97774 | -0.42768 | 2.2619
68 | -0.035406 | -0.0088913 | 0.035413 | 0.0088958 | 7.2221e-06 | 4.539e-06 | 0.05389 | 0.05389 | 0.05389 | 0.97774 | -0.42768 | 0.97796 | -0.42341 | 14.805
69 | -0.03707 | -0.0093111 | 0.037085 | 0.0093204 | 1.4749e-05 | 9.2844e-06 | 0.056411 | 0.056411 | 0.056411 | 0.97796 | -0.42341 | 0.97839 | -0.41507 | 15.4977
70 | -0.0018794 | -0.00047097 | 0.0018794 | 0.00047081 | 4.7511e-08 | -1.6445e-07 | 0.0028579 | 0.0028579 | 0.0028579 | 0.97851 | -0.41233 | 0.97854 | -0.4118 | 0.78515
71 | 0.00081573 | 0.0002044 | -0.00081573 | -0.00020444 | 2.0017e-09 | -4.2294e-08 | 0.0012405 | 0.0012405 | 0.0012405 | 0.97851 | -0.41233 | 0.97851 | -0.41238 | 0.34079
72 | -0.0028207 | -0.00070671 | 0.0028207 | 0.00070669 | 2.222e-08 | -2.6239e-08 | 0.0042892 | 0.0042892 | 0.0042892 | 0.97854 | -0.4118 | 0.97854 | -0.41164 | 1.1784
73 | -0.0048264 | -0.0012089 | 0.0048268 | 0.0012089 | 3.8206e-07 | 2.1272e-09 | 0.0073028 | 0.0073027 | 0.0073028 | 0.98338 | -0.31773 | 0.98347 | -0.31607 | 2.0063
74 | 0.0035128 | 0.00087967 | -0.0035127 | -0.00087975 | 1.3968e-07 | -7.7863e-08 | 0.0053152 | 0.0053153 | 0.0053153 | 0.98338 | -0.31773 | 0.98334 | -0.31857 | 1.4602
75 | -0.0068881 | -0.0017255 | 0.0068883 | 0.0017256 | 1.4866e-07 | 4.8826e-08 | 0.010422 | 0.010422 | 0.010422 | 0.98347 | -0.31607 | 0.98349 | -0.31562 | 2.8631
76 | 0.002259 | 0.00056553 | -0.0022589 | -0.00056574 | 9.2706e-08 | -2.0907e-07 | 0.0034181 | 0.0034182 | 0.0034182 | 0.98334 | -0.31857 | 0.9833 | -0.31943 | 0.93907
77 | -0.0085681 | -0.0021466 | 0.0085694 | 0.0021471 | 1.2726e-06 | 5.5815e-07 | 0.012963 | 0.012963 | 0.012963 | 0.98349 | -0.31562 | 0.98365 | -0.3125 | 3.5613
78 | 0.0012002 | 0.00030042 | -0.0012002 | -0.00030058 | 1.6446e-08 | -1.5812e-07 | 0.0018162 | 0.0018162 | 0.0018162 | 0.9833 | -0.31943 | 0.98328 | -0.31972 | 0.49896
79 | -0.011324 | -0.0028375 | 0.011324 | 0.0028376 | 2.3873e-07 | 1.2525e-07 | 0.01713 | 0.01713 | 0.01713 | 0.98365 | -0.3125 | 0.98367 | -0.31206 | 4.7061
80 | 0.0012002 | 0.00030058 | -0.0012002 | -0.00030079 | 2.2735e-08 | -2.1856e-07 | 0.0018162 | 0.0018163 | 0.0018163 | 0.98328 | -0.31972 | 0.98326 | -0.32012 | 0.49898
81 | -0.012867 | -0.0032243 | 0.012869 | 0.0032255 | 2.1273e-06 | 1.1714e-06 | 0.019464 | 0.019464 | 0.019464 | 0.98367 | -0.31206 | 0.98385 | -0.30859 | 5.3473
82 | 0.0059022 | 0.0014791 | -0.0059022 | -0.0014791 | 2.2882e-08 | 5.0475e-09 | 0.0089561 | 0.0089561 | 0.0089561 | 0.98062 | -0.37132 | 0.98061 | -0.3714 | 2.4605
83 | -0.0075751 | -0.0018984 | 0.0075758 | 0.0018987 | 7.4405e-07 | 2.8672e-07 | 0.011495 | 0.011495 | 0.011495 | 0.98062 | -0.37132 | 0.98072 | -0.36926 | 3.1579
84 | 0.0036865 | 0.0009238 | -0.0036863 | -0.00092387 | 1.6313e-07 | -7.0966e-08 | 0.0055939 | 0.005594 | 0.005594 | 0.98061 | -0.3714 | 0.98057 | -0.37233 | 1.5368
85 | 0.024999 | 0.0062975 | -0.02498 | -0.0062855 | 1.9377e-05 | 1.1949e-05 | 0.037942 | 0.037942 | 0.037942 | 0.98072 | -0.36926 | 0.97989 | -0.38548 | 10.4235
86 | -0.032575 | -0.0081962 | 0.032608 | 0.0082169 | 3.3059e-05 | 2.0702e-05 | 0.049436 | 0.049436 | 0.049436 | 0.98072 | -0.36926 | 0.98181 | -0.34804 | 13.5813
87 | 0.023131 | 0.0058226 | -0.023068 | -0.0057839 | 6.3086e-05 | 3.8663e-05 | 0.035134 | 0.035135 | 0.035135 | 0.97989 | -0.38548 | 0.97698 | -0.4427 | 9.6524
88 | 0.0018489 | 0.00046294 | -0.0018488 | -0.00046336 | 1.1563e-07 | -4.1871e-07 | 0.0028075 | 0.0028077 | 0.0028077 | 0.97989 | -0.38548 | 0.97983 | -0.38679 | 0.77135
89 | -0.036838 | -0.0092771 | 0.036857 | 0.0092887 | 1.8417e-05 | 1.1588e-05 | 0.055847 | 0.055847 | 0.055847 | 0.98181 | -0.34804 | 0.98235 | -0.33759 | 15.3426
90 | 0.010069 | 0.0025233 | -0.010066 | -0.0025216 | 3.552e-06 | 1.7692e-06 | 0.015336 | 0.015337 | 0.015337 | 0.97698 | -0.4427 | 0.9766 | -0.45011 | 4.2134
91 | 0.01045 | 0.0026229 | -0.010433 | -0.0026143 | 1.6922e-05 | 8.6039e-06 | 0.015917 | 0.015918 | 0.015918 | 0.97698 | -0.4427 | 0.97525 | -0.47671 | 4.3731
92 | 0.0025485 | 0.00063769 | -0.0025482 | -0.00063819 | 3.1625e-07 | -4.9849e-07 | 0.0038812 | 0.0038815 | 0.0038815 | 0.97698 | -0.4427 | 0.97684 | -0.44531 | 1.0663
93 | 0.026278 | 0.0065907 | -0.026268 | -0.0065845 | 1.0022e-05 | 6.2004e-06 | 0.039807 | 0.039807 | 0.039807 | 0.98235 | -0.33759 | 0.98194 | -0.3456 | 10.9359
94 | -0.063135 | -0.015879 | 0.063153 | 0.015891 | 1.8408e-05 | 1.1713e-05 | 0.095654 | 0.095654 | 0.095654 | 0.98235 | -0.33759 | 0.98266 | -0.33149 | 26.2785
95 | 0.00091265 | 0.00022847 | -0.00091264 | -0.00022873 | 1.558e-08 | -2.5888e-07 | 0.0013905 | 0.0013906 | 0.0013906 | 0.9766 | -0.45011 | 0.97658 | -0.45047 | 0.38203
96 | 0.0091532 | 0.0022931 | -0.0091519 | -0.0022925 | 1.2783e-06 | 5.9883e-07 | 0.013946 | 0.013946 | 0.013946 | 0.9766 | -0.45011 | 0.97645 | -0.45304 | 3.8314
97 | 0.010433 | 0.0026143 | -0.010427 | -0.0026116 | 5.2654e-06 | 2.6788e-06 | 0.015918 | 0.015918 | 0.015918 | 0.97525 | -0.47671 | 0.97471 | -0.48731 | 4.3731
98 | 0.0014221 | 0.00035596 | -0.001422 | -0.0003564 | 6.7343e-08 | -4.3597e-07 | 0.0021661 | 0.0021663 | 0.0021663 | 0.97684 | -0.44531 | 0.97679 | -0.4463 | 0.59514
99 | 0.018641 | 0.004673 | -0.018635 | -0.0046693 | 6.2278e-06 | 3.7226e-06 | 0.028249 | 0.028249 | 0.028249 | 0.98194 | -0.3456 | 0.98158 | -0.35261 | 7.7607
100 | -0.17766 | -0.044886 | 0.17789 | 0.045029 | 0.00022611 | 0.00014302 | 0.26916 | 0.26916 | 0.26916 | 0.98266 | -0.33149 | 0.98403 | -0.30498 | 18.4861
101 | 0.11451 | 0.028995 | -0.11445 | -0.028961 | 5.4901e-05 | 3.4151e-05 | 0.1735 | 0.1735 | 0.1735 | 0.98266 | -0.33149 | 0.98215 | -0.34148 | 11.9165
102 | 0.11092 | 0.028075 | -0.11088 | -0.028048 | 4.3733e-05 | 2.7154e-05 | 0.16815 | 0.16815 | 0.16815 | 0.98215 | -0.34148 | 0.98172 | -0.3497 | 11.5489
103 | -0.18047 | -0.045676 | 0.18067 | 0.045801 | 0.00019794 | 0.00012524 | 0.27306 | 0.27306 | 0.27306 | 0.98403 | -0.30498 | 0.9852 | -0.28215 | 18.7543
104 | -0.18294 | -0.046371 | 0.183 | 0.046407 | 5.6319e-05 | 3.5644e-05 | 0.27649 | 0.27649 | 0.27649 | 0.9852 | -0.28215 | 0.98554 | -0.27575 | 18.99
105 | 0.011005 | 0.0027571 | -0.011002 | -0.0027555 | 2.9229e-06 | 1.5167e-06 | 0.016683 | 0.016683 | 0.016683 | 0.98158 | -0.35261 | 0.9813 | -0.35819 | 4.5832
106 | -0.19302 | -0.048919 | 0.19314 | 0.04899 | 0.00011192 | 7.0916e-05 | 0.29163 | 0.29163 | 0.29163 | 0.98554 | -0.27575 | 0.98616 | -0.26369 | 20.0297
107 | -0.0076791 | -0.0019238 | 0.0076822 | 0.001925 | 3.0922e-06 | 1.1964e-06 | 0.011592 | 0.011592 | 0.011592 | 0.98573 | -0.27214 | 0.98616 | -0.26369 | 3.1846
108 | -0.20082 | -0.050915 | 0.20093 | 0.050988 | 0.00011469 | 7.272e-05 | 0.30322 | 0.30322 | 0.30322 | 0.98616 | -0.26369 | 0.98677 | -0.25182 | 20.8258
109 | -0.20398 | -0.051752 | 0.20426 | 0.051925 | 0.00027272 | 0.00017297 | 0.30782 | 0.30782 | 0.30782 | 0.98677 | -0.25182 | 0.98822 | -0.22405 | 21.1416
110 | 0.0030496 | 0.00076382 | -0.0030493 | -0.00076413 | 3.1998e-07 | -3.106e-07 | 0.0045985 | 0.0045987 | 0.0045987 | 0.98677 | -0.25182 | 0.98666 | -0.25402 | 1.2634
111 | 0.023938 | 0.006004 | -0.023936 | -0.006003 | 1.744e-06 | 1.073e-06 | 0.036596 | 0.036596 | 0.036596 | 0.97337 | -0.5133 | 0.97329 | -0.51483 | 10.0539
112 | 0.018852 | 0.0047289 | -0.018841 | -0.0047223 | 1.0934e-05 | 6.5622e-06 | 0.028824 | 0.028824 | 0.028824 | 0.97329 | -0.51483 | 0.97267 | -0.52701 | 7.9187
113 | 0.0086478 | 0.0021675 | -0.0086469 | -0.0021671 | 8.8603e-07 | 3.9952e-07 | 0.01323 | 0.01323 | 0.01323 | 0.97267 | -0.52701 | 0.97256 | -0.52916 | 3.6345
114 | 0.024012 | 0.0060258 | -0.023991 | -0.0060127 | 2.1196e-05 | 1.3045e-05 | 0.036716 | 0.036716 | 0.036716 | 0.97323 | -0.51606 | 0.97229 | -0.53458 | 10.0869
115 | 0.0068265 | 0.0017109 | -0.0068262 | -0.0017108 | 3.5295e-07 | 1.1895e-07 | 0.010448 | 0.010448 | 0.010448 | 0.97229 | -0.53458 | 0.97223 | -0.53567 | 2.8702
116 | 0.286 | 0.073552 | -0.28579 | -0.073417 | 0.00021241 | 0.00013529 | 0.42732 | 0.42732 | 0.42732 | 0.99747 | -0.047737 | 0.99666 | -0.063029 | 29.3491
117 | 0.28355 | 0.072857 | -0.28308 | -0.072555 | 0.00047466 | 0.00030232 | 0.42399 | 0.42399 | 0.42399 | 0.99666 | -0.063029 | 0.99483 | -0.097556 | 29.12
118 | 0.28113 | 0.072067 | -0.28078 | -0.071841 | 0.00035428 | 0.00022563 | 0.42108 | 0.42108 | 0.42108 | 0.99483 | -0.097556 | 0.99346 | -0.12359 | 28.92
119 | 0.06512 | 0.016484 | -0.065075 | -0.016456 | 4.5234e-05 | 2.8791e-05 | 0.098335 | 0.098335 | 0.098335 | 0.98599 | -0.26696 | 0.98525 | -0.28144 | 27.0152
120 | -0.066697 | -0.01688 | 0.066724 | 0.016897 | 2.7135e-05 | 1.7275e-05 | 0.10071 | 0.10071 | 0.10071 | 0.98599 | -0.26696 | 0.98643 | -0.25849 | 27.6688
121 | -0.067418 | -0.017071 | 0.067425 | 0.017075 | 6.4562e-06 | 4.1107e-06 | 0.10176 | 0.10176 | 0.10176 | 0.98643 | -0.25849 | 0.98653 | -0.2565 | 27.9565
122 | -0.068468 | -0.017336 | 0.068509 | 0.017362 | 4.0905e-05 | 2.6049e-05 | 0.10333 | 0.10333 | 0.10333 | 0.98653 | -0.2565 | 0.98718 | -0.24406 | 28.3887
123 | 0.013609 | 0.0034118 | -0.013606 | -0.0034102 | 2.9278e-06 | 1.6396e-06 | 0.020579 | 0.020579 | 0.020579 | 0.98408 | -0.30407 | 0.98385 | -0.30859 | 5.6535
124 | -0.069233 | -0.017544 | 0.069318 | 0.017598 | 8.4822e-05 | 5.4021e-05 | 0.10443 | 0.10443 | 0.10443 | 0.98718 | -0.24406 | 0.9885 | -0.2186 | 28.6886
125 | -0.27515 | -0.069938 | 0.27534 | 0.07006 | 0.00019064 | 0.00012141 | 0.41454 | 0.41454 | 0.41454 | 0.9885 | -0.2186 | 0.98925 | -0.20422 | 28.4711
126 | 0.20583 | 0.05234 | -0.20578 | -0.052306 | 5.4116e-05 | 3.4326e-05 | 0.31011 | 0.31011 | 0.31011 | 0.9885 | -0.2186 | 0.98822 | -0.22405 | 21.2989
127 | 0.0030363 | 0.00076018 | -0.0030362 | -0.00076024 | 6.0403e-08 | -5.5307e-08 | 0.0046286 | 0.0046287 | 0.0046287 | 0.97605 | -0.46088 | 0.97603 | -0.4613 | 1.2716
128 | -0.0036279 | -0.00090846 | 0.003628 | 0.00090841 | 1.1022e-07 | -4.9567e-08 | 0.0055306 | 0.0055305 | 0.0055306 | 0.97605 | -0.46088 | 0.97609 | -0.46024 | 1.5194
129 | 0.0023822 | 0.00059632 | -0.0023821 | -0.00059649 | 8.9528e-08 | -1.6894e-07 | 0.0036315 | 0.0036316 | 0.0036316 | 0.97603 | -0.4613 | 0.97599 | -0.46209 | 0.9977
130 | -0.004217 | -0.001056 | 0.0042171 | 0.001056 | 9.7629e-08 | -1.6267e-08 | 0.0064283 | 0.0064283 | 0.0064283 | 0.97609 | -0.46024 | 0.97611 | -0.45975 | 1.766
131 | 0.0013793 | 0.00034517 | -0.0013793 | -0.00034536 | 2.872e-08 | -1.9807e-07 | 0.0021027 | 0.0021028 | 0.0021028 | 0.97599 | -0.46209 | 0.97597 | -0.46252 | 0.5777
132 | -0.0049985 | -0.0012518 | 0.0049988 | 0.0012519 | 3.8029e-07 | 2.5021e-08 | 0.0076195 | 0.0076194 | 0.0076195 | 0.97611 | -0.45975 | 0.97619 | -0.45816 | 2.0933
133 | 0.00080977 | 0.00020263 | -0.00080976 | -0.00020294 | 1.4854e-08 | -3.1526e-07 | 0.0012345 | 0.0012346 | 0.0012346 | 0.97597 | -0.46252 | 0.97595 | -0.46291 | 0.33918
134 | -0.0057975 | -0.001452 | 0.0057981 | 0.0014521 | 5.9992e-07 | 1.2779e-07 | 0.0088368 | 0.0088367 | 0.0088368 | 0.97619 | -0.45816 | 0.9763 | -0.45598 | 2.4277
135 | -0.0082954 | -0.0020776 | 0.0082966 | 0.0020781 | 1.1615e-06 | 5.0102e-07 | 0.012643 | 0.012643 | 0.012643 | 0.9763 | -0.45598 | 0.97645 | -0.45304 | 3.4733
136 | 0.0024974 | 0.00062551 | -0.0024973 | -0.00062557 | 3.8748e-08 | -6.4389e-08 | 0.0038062 | 0.0038062 | 0.0038062 | 0.9763 | -0.45598 | 0.97629 | -0.45631 | 1.0457
137 | 0.0029668 | 0.00074314 | -0.0029665 | -0.00074347 | 3.4171e-07 | -3.349e-07 | 0.0045291 | 0.0045293 | 0.0045293 | 0.97471 | -0.48731 | 0.97459 | -0.48972 | 1.2443
138 | 0.041017 | 0.01033 | -0.040976 | -0.010304 | 4.0244e-05 | 2.5408e-05 | 0.062293 | 0.062293 | 0.062293 | 0.98006 | -0.38232 | 0.97901 | -0.40286 | 17.1136
139 | -0.001259 | -0.00031553 | 0.001259 | 0.00031544 | 1.0354e-08 | -9.1182e-08 | 0.0018988 | 0.0018987 | 0.0018988 | 0.98665 | -0.25419 | 0.98666 | -0.25402 | 0.52164
140 | -0.038987 | -0.0097971 | 0.038993 | 0.0098011 | 6.2315e-06 | 3.9288e-06 | 0.059305 | 0.059305 | 0.059305 | 0.97839 | -0.41507 | 0.97856 | -0.41172 | 16.2925
141 | 0.0057269 | 0.0014345 | -0.0057263 | -0.0014343 | 5.4754e-07 | 1.1219e-07 | 0.0087411 | 0.0087412 | 0.0087412 | 0.97486 | -0.48439 | 0.97476 | -0.4864 | 2.4014
142 | 0.0048868 | 0.0012239 | -0.0048861 | -0.0012239 | 6.8866e-07 | 2.9426e-08 | 0.0074596 | 0.0074597 | 0.0074597 | 0.97476 | -0.4864 | 0.97461 | -0.48936 | 2.0494
143 | 0.0036774 | 0.00092099 | -0.0036766 | -0.00092132 | 7.9665e-07 | -3.2975e-07 | 0.0056144 | 0.0056147 | 0.0056147 | 0.97461 | -0.48936 | 0.97438 | -0.49391 | 1.5425
144 | 0.00067018 | 0.00016783 | -0.00067018 | -0.00016796 | 4.2322e-09 | -1.315e-07 | 0.0010234 | 0.0010235 | 0.0010235 | 0.97438 | -0.49391 | 0.97437 | -0.49404 | 0.28117
145 | 0.039685 | 0.0099806 | -0.039668 | -0.0099701 | 1.6791e-05 | 1.0591e-05 | 0.06033 | 0.06033 | 0.06033 | 0.97901 | -0.40286 | 0.97856 | -0.41172 | 16.5741
146 | -0.00174 | -0.00043588 | 0.00174 | 0.00043578 | 2.4883e-08 | -1.0205e-07 | 0.002652 | 0.002652 | 0.002652 | 0.97627 | -0.45661 | 0.97629 | -0.45631 | 0.72858
147 | 0.00068787 | 0.00017219 | -0.00068786 | -0.00017239 | 6.9122e-09 | -2.0526e-07 | 0.0010484 | 0.0010484 | 0.0010484 | 0.97627 | -0.45661 | 0.97626 | -0.45682 | 0.28803
148 | -0.27628 | -0.070296 | 0.27665 | 0.07053 | 0.00036792 | 0.0002343 | 0.41595 | 0.41595 | 0.41595 | 0.98925 | -0.20422 | 0.99069 | -0.17663 | 28.5683
149 | -0.27789 | -0.070842 | 0.2783 | 0.0711 | 0.00040438 | 0.00025753 | 0.41783 | 0.41782 | 0.41783 | 0.99069 | -0.17663 | 0.99226 | -0.14653 | 28.6968
150 | -0.27944 | -0.071386 | 0.27975 | 0.071584 | 0.0003104 | 0.00019768 | 0.41954 | 0.41954 | 0.41954 | 0.99226 | -0.14653 | 0.99346 | -0.12359 | 28.8145
151 | 0.0033593 | 0.00084002 | -0.0033583 | -0.00084066 | 9.6515e-07 | -6.3518e-07 | 0.0050933 | 0.0050937 | 0.0050937 | 0.9813 | -0.35819 | 0.98099 | -0.36423 | 1.3994
152 | 0.0033583 | 0.00084066 | -0.0033572 | -0.00084139 | 1.12e-06 | -7.358e-07 | 0.0050937 | 0.0050942 | 0.0050942 | 0.98099 | -0.36423 | 0.98063 | -0.37123 | 1.3995
153 | 0.00090226 | 0.00022598 | -0.00090225 | -0.00022613 | 8.4135e-09 | -1.4245e-07 | 0.0013764 | 0.0013764 | 0.0013764 | 0.97543 | -0.47325 | 0.97542 | -0.47345 | 0.37813

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29332 | 0.07523

## res_load
| p_mw | q_mvar
0 | 0.0031525 | 0.00079009
1 | 0.00045697 | 0.00011453
2 | 0.00098123 | 0.00024592
3 | 0.0015959 | 0.00039998
4 | 0.0028323 | 0.00070984
5 | 0.0025506 | 0.00063923
6 | 0.0035183 | 0.00088177
7 | 0.0014748 | 0.00036961
8 | 0.0034327 | 0.00086032
9 | 0.0024753 | 0.00062038
10 | 0.0013159 | 0.0003298
11 | 0.0028535 | 0.00071515
12 | 0.0021441 | 0.00053736
13 | 0.0027322 | 0.00068476
14 | 0.0009282 | 0.00023263
15 | 0.0013985 | 0.0003505
16 | 0.00094389 | 0.00023656
17 | 0.0011678 | 0.00029268
18 | 0.0036643 | 0.00091837
19 | 0.0015338 | 0.0003844
20 | 0.0024423 | 0.00061209
21 | 0.00063154 | 0.00015828
22 | 0.0016053 | 0.00040233
23 | 0.0018075 | 0.00045301
24 | 0.0013707 | 0.00034353
25 | 0.0017456 | 0.00043748
26 | 0.0044707 | 0.0011205
27 | 0.0011634 | 0.00029158
28 | 0.0051027 | 0.0012789
29 | 0.0028699 | 0.00071927
30 | 0.0010662 | 0.00026721
31 | 0.0013689 | 0.00034307
32 | 0.0009527 | 0.00023877
33 | 0.0012663 | 0.00031737
34 | 0.0012534 | 0.00031413
35 | 0.00060021 | 0.00015043
36 | 0.001174 | 0.00029423
37 | 0.0042381 | 0.0010622
38 | 0.0016908 | 0.00042375
39 | 0.00083377 | 0.00020896
40 | 0.00070921 | 0.00017775
41 | 0.0021757 | 0.00054527
42 | 0.001657 | 0.00041527
43 | 0.0010636 | 0.00026657
44 | 0.00094128 | 0.00023591
45 | 0.00081573 | 0.00020444
46 | 0.0011909 | 0.00029846
47 | 0.0013135 | 0.0003292
48 | 0.0020614 | 0.00051663
49 | 0.0012537 | 0.00031421
50 | 0.0016799 | 0.00042101
51 | 0.0010587 | 0.00026532
52 | 0.0027547 | 0.00069039
53 | 0.0015429 | 0.00038669
54 | 0.0012002 | 0.00030079
55 | 0.0016729 | 0.00041926
56 | 0.0022158 | 0.00055532
57 | 0.0036863 | 0.00092387
58 | 0.0042303 | 0.0010602
59 | 0.0018488 | 0.00046336
60 | 0.0011261 | 0.00028223
61 | 0.0076269 | 0.0019115
62 | 0.0035324 | 0.00088531
63 | 0.002299 | 0.00057618
64 | 0.0025834 | 0.00064746
65 | 0.0022723 | 0.00056949
66 | 0.0076298 | 0.0019122
67 | 0.010026 | 0.0025128
68 | 0.0018498 | 0.0004636
69 | 0.017058 | 0.0042752
70 | 0.0050837 | 0.0012741
71 | 0.010194 | 0.0025548
72 | 0.0040752 | 0.0010213
73 | 0.0086469 | 0.0021671
74 | 0.017164 | 0.0043018
75 | 0.0022352 | 0.0005602
76 | 0.0019465 | 0.00048783
77 | 0.00087443 | 0.00021915
78 | 0.0015765 | 0.00039511
79 | 0.00108 | 0.00027066
80 | 0.00069413 | 0.00017397
81 | 0.0010431 | 0.00026144
82 | 0.0015649 | 0.0003922
83 | 0.00072432 | 0.00018153
84 | 0.00073684 | 0.00018467
85 | 0.00059161 | 0.00014827
86 | 0.00065405 | 0.00016392
87 | 0.00058893 | 0.0001476
88 | 0.0010028 | 0.00025132
89 | 0.00078139 | 0.00019583
90 | 0.00056952 | 0.00014273
91 | 0.00079864 | 0.00020016
92 | 0.00080976 | 0.00020294
93 | 0.00091264 | 0.00022873
94 | 0.00085532 | 0.00021436
95 | 0.001422 | 0.0003564
96 | 0.0014639 | 0.00036689
97 | 0.001259 | 0.00031553
98 | 0.0017903 | 0.00044869
99 | 0.0015211 | 0.00038123
100 | 0.0019023 | 0.00047676
101 | 0.0017728 | 0.0004443
102 | 0.0014214 | 0.00035623
103 | 0.00083954 | 0.00021041
104 | 0.0012086 | 0.00030292
105 | 0.0030064 | 0.00075349
106 | 0.0068262 | 0.0017108
107 | 0.0012919 | 0.00032378
108 | 0.00067427 | 0.00016899
109 | 0.0010521 | 0.00026369
110 | 0.00075729 | 0.0001898
111 | 0.00068786 | 0.00017239
112 | 0.00094112 | 0.00023587
113 | 0.00067018 | 0.00016796
114 | 0.0012461 | 0.00031231
115 | 0.0011434 | 0.00028657
116 | 0.0010257 | 0.00025708
117 | 0.007643 | 0.0019155
118 | 0.0033572 | 0.00084139
119 | 0.00087248 | 0.00021866
120 | 0.00090225 | 0.00022613
121 | 0.0029665 | 0.00074347
122 | 0.0012682 | 0.00031783

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1