## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_251-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_251-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_251-7_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_251-7_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_251-7_0_6_node_31 | 0.4 | n |  | TRUE
5 | bus_LV_251-7_0_6_node_74 | 0.4 | n |  | TRUE
6 | bus_LV_251-7_0_6_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_251-7_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_251-7_0_6_node_75 | 0.4 | n |  | TRUE
9 | bus_LV_251-7_0_6_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_251-7_0_6_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_251-7_0_6_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_251-7_0_6_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_251-7_0_6_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_251-7_0_6_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_251-7_0_6_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_251-7_0_6_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_251-7_0_6_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_251-7_0_6_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_251-7_0_6_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_251-7_0_6_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_251-7_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_251-7_0_6_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_251-7_0_6_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_251-7_0_6_node_58 | 0.4 | n |  | TRUE
25 | bus_LV_251-7_0_6_node_60 | 0.4 | n |  | TRUE
26 | bus_LV_251-7_0_6_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_251-7_0_6_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_251-7_0_6_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_251-7_0_6_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_251-7_0_6_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_251-7_0_6_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_251-7_0_6_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_251-7_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_251-7_0_6_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_251-7_0_6_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_251-7_0_6_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_251-7_0_6_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_251-7_0_6_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_251-7_0_6_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_251-7_0_6_node_51 | 0.4 | n |  | TRUE
41 | bus_LV_251-7_0_6_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_251-7_0_6_node_57 | 0.4 | n |  | TRUE
43 | bus_LV_251-7_0_6_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_251-7_0_6_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_251-7_0_6_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_251-7_0_6_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_251-7_0_6_node_68 | 0.4 | n |  | TRUE
48 | bus_LV_251-7_0_6_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_251-7_0_6_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_251-7_0_6_node_63 | 0.4 | n |  | TRUE
51 | bus_LV_251-7_0_6_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_251-7_0_6_node_25 | 0.4 | n |  | TRUE
53 | bus_LV_251-7_0_6_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_251-7_0_6_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_251-7_0_6_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_251-7_0_6_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_251-7_0_6_node_59 | 0.4 | n |  | TRUE
58 | bus_LV_251-7_0_6_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_251-7_0_6_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_251-7_0_6_node_72 | 0.4 | n |  | TRUE
61 | bus_LV_251-7_0_6_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_251-7_0_6_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_251-7_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_251-7_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_251-7_0_6_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_251-7_0_6_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_251-7_0_6_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_251-7_0_6_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_251-7_0_6_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_251-7_0_6_node_69 | 0.4 | n |  | TRUE
71 | bus_MV_514_0_node_102 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_251-7_0_6_load_0 | 0 | 0.014968 | 0.0037513 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_251-7_0_6_load_3 | 2 | 0.00147 | 0.00036842 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_251-7_0_6_load_74 | 5 | 0.010808 | 0.0027087 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_251-7_0_6_load_75 | 8 | 0.022698 | 0.0056886 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_251-7_0_6_load_26 | 9 | 0.025792 | 0.006464 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_251-7_0_6_load_30 | 11 | 0.0043595 | 0.0010926 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_251-7_0_6_load_43 | 13 | 0.011823 | 0.0029631 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_251-7_0_6_load_37 | 16 | 0.023761 | 0.005955 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_251-7_0_6_load_7 | 18 | 0.0090222 | 0.0022612 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_251-7_0_6_load_22 | 22 | 0.0089952 | 0.0022544 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_251-7_0_6_load_58 | 24 | 0.0032288 | 0.00080921 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_251-7_0_6_load_60 | 25 | 0.0023324 | 0.00058455 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_251-7_0_6_load_35 | 27 | 0.0087819 | 0.002201 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_251-7_0_6_load_27 | 31 | 0.0039742 | 0.00099603 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_251-7_0_6_load_34 | 32 | 0.023069 | 0.0057818 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_251-7_0_6_load_23 | 33 | 0.0039282 | 0.00098449 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_251-7_0_6_load_52 | 35 | 0.003472 | 0.00087017 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_251-7_0_6_load_49 | 37 | 0.0025144 | 0.00063016 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_251-7_0_6_load_64 | 38 | 0.0019019 | 0.00047667 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_251-7_0_6_load_73 | 41 | 0.0029943 | 0.00075043 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_251-7_0_6_load_57 | 42 | 0.0036927 | 0.00092547 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_251-7_0_6_load_50 | 43 | 0.0051047 | 0.0012794 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_251-7_0_6_load_36 | 44 | 0.01071 | 0.0026841 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_251-7_0_6_load_28 | 45 | 0.0039442 | 0.0009885 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_251-7_0_6_load_24 | 46 | 0.0039231 | 0.00098323 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_251-7_0_6_load_71 | 48 | 0.0024412 | 0.00061182 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_251-7_0_6_load_63 | 50 | 0.0032599 | 0.00081701 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_251-7_0_6_load_61 | 51 | 0.0039857 | 0.00099891 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_251-7_0_6_load_25 | 52 | 0.012816 | 0.003212 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_251-7_0_6_load_29 | 53 | 0.0038798 | 0.00097238 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_251-7_0_6_load_41 | 54 | 0.0039005 | 0.00097755 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_251-7_0_6_load_42 | 55 | 0.0039267 | 0.00098413 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_251-7_0_6_load_66 | 56 | 0.0019048 | 0.00047739 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_251-7_0_6_load_59 | 57 | 0.0078701 | 0.0019724 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_251-7_0_6_load_56 | 58 | 0.0018881 | 0.0004732 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_251-7_0_6_load_53 | 59 | 0.0027053 | 0.000678 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_251-7_0_6_load_72 | 60 | 0.0035104 | 0.0008798 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_251-7_0_6_load_44 | 61 | 0.0024655 | 0.00061791 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_251-7_0_6_load_45 | 62 | 0.0040651 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_251-7_0_6_load_46 | 63 | 0.018899 | 0.0047365 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_251-7_0_6_load_54 | 65 | 0.082242 | 0.020612 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_251-7_0_6_load_55 | 66 | 0.012629 | 0.003165 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_251-7_0_6_load_62 | 67 | 0.0020412 | 0.00051157 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_251-7_0_6_load_65 | 68 | 0.0015374 | 0.0003853 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_251-7_0_6_load_67 | 69 | 0.0023895 | 0.00059886 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_251-7_0_6_load_69 | 70 | 0.00029699 | 7.4432e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_251-7_0_6_line_0 |  | 0 | 1 | 0.04752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_251-7_0_6_line_1 |  | 1 | 2 | 0.009644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_251-7_0_6_line_2 |  | 1 | 3 | 0.040763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_251-7_0_6_line_3 |  | 2 | 4 | 0.0089834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_251-7_0_6_line_4 |  | 3 | 5 | 0.023779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_251-7_0_6_line_5 |  | 3 | 6 | 0.016346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_251-7_0_6_line_6 |  | 4 | 10 | 0.41767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_251-7_0_6_line_7 |  | 4 | 11 | 0.016573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_251-7_0_6_line_8 |  | 6 | 12 | 0.011271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_251-7_0_6_line_9 |  | 6 | 13 | 0.040656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_251-7_0_6_line_10 |  | 7 | 8 | 0.014632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_251-7_0_6_line_11 |  | 7 | 9 | 0.004863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_251-7_0_6_line_12 |  | 9 | 15 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_251-7_0_6_line_13 |  | 10 | 47 | 0.35057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_251-7_0_6_line_14 |  | 10 | 48 | 0.020397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_251-7_0_6_line_15 |  | 12 | 57 | 0.033254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_251-7_0_6_line_16 |  | 12 | 58 | 0.017569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_251-7_0_6_line_17 |  | 12 | 28 | 0.028531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_251-7_0_6_line_18 |  | 14 | 15 | 0.024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_251-7_0_6_line_19 |  | 14 | 16 | 0.021274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_251-7_0_6_line_20 |  | 14 | 17 | 0.037051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_251-7_0_6_line_21 |  | 15 | 33 | 0.019057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_251-7_0_6_line_22 |  | 17 | 32 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_251-7_0_6_line_23 |  | 17 | 29 | 0.009042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_251-7_0_6_line_24 |  | 18 | 19 | 0.0090938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_251-7_0_6_line_25 |  | 19 | 20 | 0.025325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_251-7_0_6_line_26 |  | 20 | 24 | 0.014158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_251-7_0_6_line_27 |  | 20 | 25 | 0.037479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_251-7_0_6_line_28 |  | 21 | 22 | 0.026732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_251-7_0_6_line_29 |  | 21 | 23 | 0.23434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_251-7_0_6_line_30 |  | 22 | 29 | 0.017509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_251-7_0_6_line_31 |  | 23 | 41 | 0.04509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_251-7_0_6_line_32 |  | 24 | 42 | 0.025056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_251-7_0_6_line_33 |  | 25 | 43 | 0.007769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_251-7_0_6_line_34 |  | 26 | 27 | 0.025874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_251-7_0_6_line_35 |  | 26 | 28 | 0.031695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_251-7_0_6_line_36 |  | 27 | 32 | 0.044265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_251-7_0_6_line_37 |  | 28 | 44 | 0.026095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_251-7_0_6_line_38 |  | 29 | 30 | 0.017649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_251-7_0_6_line_39 |  | 30 | 31 | 0.0084468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_251-7_0_6_line_40 |  | 31 | 45 | 0.005951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_251-7_0_6_line_41 |  | 33 | 46 | 0.0059413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_251-7_0_6_line_42 |  | 34 | 35 | 0.018729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_251-7_0_6_line_43 |  | 34 | 36 | 0.040571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_251-7_0_6_line_44 |  | 34 | 37 | 0.039995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_251-7_0_6_line_45 |  | 35 | 49 | 0.031233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_251-7_0_6_line_46 |  | 36 | 38 | 0.028154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_251-7_0_6_line_47 |  | 37 | 39 | 0.016066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_251-7_0_6_line_48 |  | 39 | 40 | 0.012542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_251-7_0_6_line_49 |  | 40 | 50 | 0.022404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_251-7_0_6_line_50 |  | 40 | 51 | 0.015264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_251-7_0_6_line_51 |  | 42 | 58 | 0.035151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_251-7_0_6_line_52 |  | 45 | 53 | 0.012793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_251-7_0_6_line_53 |  | 46 | 52 | 0.0068997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_251-7_0_6_line_54 |  | 47 | 56 | 0.039166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_251-7_0_6_line_55 |  | 49 | 66 | 0.03246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_251-7_0_6_line_56 |  | 51 | 67 | 0.0045345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_251-7_0_6_line_57 |  | 53 | 54 | 0.0058733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_251-7_0_6_line_58 |  | 54 | 55 | 0.0058738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_251-7_0_6_line_59 |  | 55 | 60 | 0.0058493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_251-7_0_6_line_60 |  | 56 | 68 | 0.016666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_251-7_0_6_line_61 |  | 57 | 59 | 0.0063125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_251-7_0_6_line_62 |  | 59 | 64 | 0.020611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_251-7_0_6_line_63 |  | 61 | 62 | 0.017395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_251-7_0_6_line_64 |  | 61 | 63 | 0.04249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_251-7_0_6_line_65 |  | 62 | 64 | 0.040516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_251-7_0_6_line_66 |  | 64 | 65 | 0.050584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_251-7_0_6_line_67 |  | 65 | 66 | 0.011375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_251-7_0_6_line_68 |  | 68 | 69 | 0.0068509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_251-7_0_6_line_69 |  | 69 | 70 | 0.010783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_251-7_0_6_trafo_40 | 0.63 MVA 20/0.4 kV | 71 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2675412.0412 | 1252236.2626 | 2675452.878 | 1252211.9628
1 | 2675412.0412 | 1252236.2626 | 2675405.0098 | 1252229.6622
2 | 2675412.0412 | 1252236.2626 | 2675421.9203 | 1252246.3513 | 2675433.6567 | 1252257.5645 | 2675440.9584 | 1252264.9851
3 | 2675398.46 | 1252223.5138 | 2675405.0098 | 1252229.6622
4 | 2675440.9584 | 1252264.9851 | 2675455.7395 | 1252246.3262
5 | 2675440.9584 | 1252264.9851 | 2675453.0594 | 1252276.0139
6 | 2675166.516 | 1251968.0695 | 2675194.7673 | 1251963.2466 | 2675209.7141 | 1251961.8463 | 2675225.2186 | 1251961.1092 | 2675233.4007 | 1251961.6579 | 2675240.8869 | 1251962.9206 | 2675250.7946 | 1251965.4704 | 2675261.8397 | 1251969.3913 | 2675304.0214 | 1251989.0971 | 2675300.9616 | 1252002.9906 | 2675300.5946 | 1252011.6701 | 2675302.508 | 1252020.2674 | 2675304.9077 | 1252026.8249 | 2675314.2109 | 1252042.4767 | 2675323.6923 | 1252056.5742 | 2675343.3415 | 1252084.8002 | 2675357.2445 | 1252107.2823 | 2675367.5365 | 1252124.6815 | 2675377.0719 | 1252144.0058 | 2675394.2228 | 1252181.0844 | 2675387.1903 | 1252194.6049 | 2675378.4332 | 1252209.0151 | 2675383.1575 | 1252212.5889 | 2675398.46 | 1252223.5138
7 | 2675398.46 | 1252223.5138 | 2675412.7486 | 1252215.1181
8 | 2675453.0594 | 1252276.0139 | 2675457.8554 | 1252281.6568 | 2675454.6505 | 1252283.8176
9 | 2675453.0594 | 1252276.0139 | 2675485.6743 | 1252251.7409
10 | 2675512.5353 | 1252221.2202 | 2675525.2475 | 1252213.9101
11 | 2675529.4747 | 1252211.4845 | 2675525.2475 | 1252213.9101
12 | 2675529.4747 | 1252211.4845 | 2675539.3299 | 1252226.3876
13 | 2675079.6563 | 1252173.0739 | 2675056.0835 | 1252120.8816 | 2675001.8787 | 1252010.0255 | 2675166.516 | 1251968.0695
14 | 2675166.516 | 1251968.0695 | 2675161.2896 | 1251954.6712 | 2675158.6931 | 1251949.2452
15 | 2675454.6505 | 1252283.8176 | 2675427.0884 | 1252302.4222
16 | 2675454.6505 | 1252283.8176 | 2675466.3089 | 1252296.9614
17 | 2675474.2622 | 1252300.0681 | 2675471.044 | 1252296.1687 | 2675457.8554 | 1252281.6568 | 2675454.6505 | 1252283.8176
18 | 2675539.3299 | 1252226.3876 | 2675551.3407 | 1252243.2976 | 2675548.0209 | 1252245.5903
19 | 2675548.0209 | 1252245.5903 | 2675530.5084 | 1252257.6684
20 | 2675548.0209 | 1252245.5903 | 2675550.2146 | 1252248.7428 | 2675569.1343 | 1252276.0373
21 | 2675539.3299 | 1252226.3876 | 2675544.4243 | 1252223.4282 | 2675553.9643 | 1252221.6263 | 2675556.8441 | 1252219.7152
22 | 2675569.1343 | 1252276.0373 | 2675552.6602 | 1252286.7395
23 | 2675569.1343 | 1252276.0373 | 2675574.3379 | 1252283.4424
24 | 2675531.27 | 1252347.6515 | 2675539.7013 | 1252344.2442
25 | 2675507.63 | 1252356.7347 | 2675515.4265 | 1252353.743 | 2675531.27 | 1252347.6515
26 | 2675507.63 | 1252356.7347 | 2675508.5091 | 1252353.488 | 2675508.0451 | 1252350.2241 | 2675503.5166 | 1252344.2481
27 | 2675507.63 | 1252356.7347 | 2675500.2301 | 1252361.7663 | 2675473.6345 | 1252372.0941
28 | 2675599.7928 | 1252319.627 | 2675584.4122 | 1252297.7633
29 | 2675599.7928 | 1252319.627 | 2675602.2379 | 1252318.4573 | 2675605.3182 | 1252322.5107 | 2675618.1002 | 1252316.2247 | 2675643.1048 | 1252303.1454 | 2675666.2555 | 1252291.0431 | 2675680.2377 | 1252282.9824 | 2675684.1465 | 1252276.5387 | 2675700.1469 | 1252265.2904 | 2675711.7408 | 1252256.9102 | 2675718.7954 | 1252247.6268 | 2675721.6524 | 1252239.6241 | 2675721.9706 | 1252229.4985 | 2675720.2094 | 1252218.4902 | 2675715.6506 | 1252211.4268 | 2675703.0122 | 1252204.6826 | 2675685.8193 | 1252200.5711 | 2675677.5872 | 1252197.4637 | 2675669.5987 | 1252191.8353
30 | 2675574.3379 | 1252283.4424 | 2675584.4122 | 1252297.7633
31 | 2675669.5987 | 1252191.8353 | 2675668.741 | 1252191.6242 | 2675653.1435 | 1252186.6882 | 2675637.778 | 1252180.721 | 2675627.3864 | 1252176.1235
32 | 2675503.5166 | 1252344.2481 | 2675497.5204 | 1252336.3354 | 2675488.4207 | 1252324.2499
33 | 2675466.3924 | 1252374.9064 | 2675473.6345 | 1252372.0941
34 | 2675494.4328 | 1252324.5652 | 2675515.3643 | 1252309.3551
35 | 2675494.4328 | 1252324.5652 | 2675489.6253 | 1252318.6441 | 2675478.9447 | 1252305.7319 | 2675474.2622 | 1252300.0681
36 | 2675515.3643 | 1252309.3551 | 2675527.5164 | 1252300.5247 | 2675531.3648 | 1252300.5738 | 2675552.6602 | 1252286.7395
37 | 2675474.2622 | 1252300.0681 | 2675495.546 | 1252284.9707
38 | 2675574.3379 | 1252283.4424 | 2675577.4518 | 1252281.3139 | 2675580.8169 | 1252279.0218 | 2675582.1266 | 1252271.6109 | 2675580.8754 | 1252269.7046
39 | 2675580.8754 | 1252269.7046 | 2675587.8189 | 1252264.8946
40 | 2675587.8189 | 1252264.8946 | 2675592.7107 | 1252261.5057
41 | 2675556.8441 | 1252219.7152 | 2675561.7946 | 1252216.4301
42 | 2675365.7026 | 1252418.818 | 2675355.9816 | 1252402.809
43 | 2675330.7402 | 1252439.3663 | 2675361.3437 | 1252420.9308 | 2675365.7026 | 1252418.818
44 | 2675365.7026 | 1252418.818 | 2675401.7071 | 1252401.4041
45 | 2675339.7711 | 1252376.1125 | 2675355.9816 | 1252402.809
46 | 2675330.7402 | 1252439.3663 | 2675316.9747 | 1252414.8074
47 | 2675416.1705 | 1252394.4088 | 2675401.7071 | 1252401.4041
48 | 2675410.3044 | 1252383.3149 | 2675416.1705 | 1252394.4088
49 | 2675430.1952 | 1252372.8938 | 2675410.3044 | 1252383.3149
50 | 2675410.3044 | 1252383.3149 | 2675403.0217 | 1252369.9004
51 | 2675466.3089 | 1252296.9614 | 2675476.6661 | 1252308.6384 | 2675488.4207 | 1252324.2499
52 | 2675603.227 | 1252254.2205 | 2675592.7107 | 1252261.5057
53 | 2675567.5436 | 1252212.615 | 2675561.7946 | 1252216.4301
54 | 2675079.6563 | 1252173.0739 | 2675089.4942 | 1252205.5112 | 2675090.7901 | 1252210.619
55 | 2675339.7711 | 1252376.1125 | 2675354.3675 | 1252368.3702 | 2675356.867 | 1252360.5407 | 2675363.5233 | 1252356.6334
56 | 2675400.8582 | 1252365.9153 | 2675403.0217 | 1252369.9004
57 | 2675603.227 | 1252254.2205 | 2675608.055 | 1252250.8759
58 | 2675612.8834 | 1252247.531 | 2675608.055 | 1252250.8759
59 | 2675617.6916 | 1252244.2001 | 2675612.8834 | 1252247.531
60 | 2675094.8885 | 1252226.7733 | 2675090.7901 | 1252210.619
61 | 2675421.8563 | 1252305.9539 | 2675427.0884 | 1252302.4222
62 | 2675404.773 | 1252317.4852 | 2675421.8563 | 1252305.9539
63 | 2675372.6562 | 1252273.9114 | 2675384.7203 | 1252286.4432
64 | 2675372.6562 | 1252273.9114 | 2675372.6562 | 1252273.9114 | 2675345.4406 | 1252285.2292 | 2675336.0098 | 1252294.1987
65 | 2675404.773 | 1252317.4852 | 2675402.6282 | 1252312.8545 | 2675405.3408 | 1252307.8632 | 2675384.7203 | 1252286.4432
66 | 2675404.773 | 1252317.4852 | 2675403.2355 | 1252333.3217 | 2675373.3334 | 1252350.8747
67 | 2675363.5233 | 1252356.6334 | 2675373.3334 | 1252350.8747
68 | 2675094.8885 | 1252226.7733 | 2675096.5732 | 1252233.4138
69 | 2675099.2249 | 1252243.866 | 2675096.5732 | 1252233.4138

## bus_geodata
| x | y | coords
0 | 2675452.878 | 1252211.9628
1 | 2675412.0412 | 1252236.2626
2 | 2675405.0098 | 1252229.6622
3 | 2675440.9584 | 1252264.9851
4 | 2675398.46 | 1252223.5138
5 | 2675455.7395 | 1252246.3262
6 | 2675453.0594 | 1252276.0139
7 | 2675525.2475 | 1252213.9101
8 | 2675512.5353 | 1252221.2202
9 | 2675529.4747 | 1252211.4845
10 | 2675166.516 | 1251968.0695
11 | 2675412.7486 | 1252215.1181
12 | 2675454.6505 | 1252283.8176
13 | 2675485.6743 | 1252251.7409
14 | 2675548.0209 | 1252245.5903
15 | 2675539.3299 | 1252226.3876
16 | 2675530.5084 | 1252257.6684
17 | 2675569.1343 | 1252276.0373
18 | 2675539.7013 | 1252344.2442
19 | 2675531.27 | 1252347.6515
20 | 2675507.63 | 1252356.7347
21 | 2675599.7928 | 1252319.627
22 | 2675584.4122 | 1252297.7633
23 | 2675669.5987 | 1252191.8353
24 | 2675503.5166 | 1252344.2481
25 | 2675473.6345 | 1252372.0941
26 | 2675494.4328 | 1252324.5652
27 | 2675515.3643 | 1252309.3551
28 | 2675474.2622 | 1252300.0681
29 | 2675574.3379 | 1252283.4424
30 | 2675580.8754 | 1252269.7046
31 | 2675587.8189 | 1252264.8946
32 | 2675552.6602 | 1252286.7395
33 | 2675556.8441 | 1252219.7152
34 | 2675365.7025 | 1252418.818
35 | 2675355.9816 | 1252402.809
36 | 2675330.7402 | 1252439.3663
37 | 2675401.7071 | 1252401.4041
38 | 2675316.9747 | 1252414.8074
39 | 2675416.1705 | 1252394.4088
40 | 2675410.3044 | 1252383.3149
41 | 2675627.3864 | 1252176.1235
42 | 2675488.4207 | 1252324.2499
43 | 2675466.3924 | 1252374.9064
44 | 2675495.546 | 1252284.9707
45 | 2675592.7107 | 1252261.5057
46 | 2675561.7946 | 1252216.4301
47 | 2675079.6563 | 1252173.0739
48 | 2675158.6931 | 1251949.2452
49 | 2675339.7711 | 1252376.1125
50 | 2675430.1952 | 1252372.8938
51 | 2675403.0217 | 1252369.9004
52 | 2675567.5436 | 1252212.615
53 | 2675603.227 | 1252254.2205
54 | 2675608.055 | 1252250.8759
55 | 2675612.8834 | 1252247.531
56 | 2675090.7901 | 1252210.619
57 | 2675427.0884 | 1252302.4222
58 | 2675466.3089 | 1252296.9614
59 | 2675421.8563 | 1252305.9539
60 | 2675617.6916 | 1252244.2001
61 | 2675372.6562 | 1252273.9114
62 | 2675384.7203 | 1252286.4432
63 | 2675336.0098 | 1252294.1987
64 | 2675404.773 | 1252317.4852
65 | 2675373.3334 | 1252350.8747
66 | 2675363.5233 | 1252356.6334
67 | 2675400.8582 | 1252365.9153
68 | 2675094.8885 | 1252226.7733
69 | 2675096.5732 | 1252233.4138
70 | 2675099.2249 | 1252243.866
71 | 2675457.8554 | 1252281.6568

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99713 | -0.055121 | 0.014968 | 0.0037513
1 | 0.99778 | -0.04266 | 0 | 0
2 | 0.99765 | -0.045096 | 0.00147 | 0.00036842
3 | 0.99887 | -0.021702 | 0 | 0
4 | 0.99755 | -0.047135 | 0 | 0
5 | 0.99864 | -0.026193 | 0.010808 | 0.0027087
6 | 0.99947 | -0.010227 | 0 | 0
7 | 0.98247 | -0.3376 | 0 | 0
8 | 0.98216 | -0.3436 | 0.022698 | 0.0056886
9 | 0.98257 | -0.33561 | 0.025792 | 0.006464
10 | 0.99428 | -0.11019 | 0 | 0
11 | 0.99748 | -0.048401 | 0.0043595 | 0.0010926
12 | 1 | 0 | -0.40122 | -0.10153
13 | 0.99903 | -0.018618 | 0.011823 | 0.0029631
14 | 0.98495 | -0.28916 | 0 | 0
15 | 0.98337 | -0.32 | 0 | 0
16 | 0.98448 | -0.29825 | 0.023761 | 0.005955
17 | 0.98812 | -0.22751 | 0 | 0
18 | 0.99791 | -0.040225 | 0.0090222 | 0.0022612
19 | 0.99798 | -0.038789 | 0 | 0
20 | 0.99819 | -0.034791 | 0 | 0
21 | 0.98757 | -0.23837 | 0 | 0
22 | 0.98764 | -0.23693 | 0.0089952 | 0.0022544
23 | 0.98692 | -0.25094 | 0 | 0
24 | 0.9984 | -0.030715 | 0.0032288 | 0.00080921
25 | 0.99794 | -0.039669 | 0.0023324 | 0.00058455
26 | 0.99543 | -0.086994 | 0 | 0
27 | 0.99352 | -0.12346 | 0.0087819 | 0.002201
28 | 0.99776 | -0.04252 | 0 | 0
29 | 0.98783 | -0.23318 | 0 | 0
30 | 0.98746 | -0.24048 | 0 | 0
31 | 0.98728 | -0.24397 | 0.0039742 | 0.00099603
32 | 0.99044 | -0.1827 | 0.023069 | 0.0057818
33 | 0.983 | -0.3271 | 0.0039282 | 0.00098449
34 | 0.988 | -0.23104 | 0 | 0
35 | 0.98823 | -0.22646 | 0.003472 | 0.00087017
36 | 0.98793 | -0.23242 | 0 | 0
37 | 0.98756 | -0.23947 | 0.0025144 | 0.00063016
38 | 0.98788 | -0.23338 | 0.0019019 | 0.00047667
39 | 0.98743 | -0.24214 | 0 | 0
40 | 0.98732 | -0.24422 | 0 | 0
41 | 0.9868 | -0.25335 | 0.0029943 | 0.00075043
42 | 0.99885 | -0.022092 | 0.0036927 | 0.00092547
43 | 0.9979 | -0.040363 | 0.0051047 | 0.0012794
44 | 0.99751 | -0.047415 | 0.01071 | 0.0026841
45 | 0.98717 | -0.24601 | 0.0039442 | 0.0009885
46 | 0.98291 | -0.32889 | 0.0039231 | 0.00098323
47 | 0.99232 | -0.1482 | 0 | 0
48 | 0.99423 | -0.11107 | 0.0024412 | 0.00061182
49 | 0.98872 | -0.21688 | 0 | 0
50 | 0.98725 | -0.24553 | 0.0032599 | 0.00081701
51 | 0.98723 | -0.24587 | 0.0039857 | 0.00099891
52 | 0.98283 | -0.33049 | 0.012816 | 0.003212
53 | 0.98699 | -0.24949 | 0.0038798 | 0.00097238
54 | 0.98693 | -0.25068 | 0.0039005 | 0.00097755
55 | 0.98689 | -0.25147 | 0.0039267 | 0.00098413
56 | 0.9921 | -0.15245 | 0.0019048 | 0.00047739
57 | 0.99774 | -0.043006 | 0.0078701 | 0.0019724
58 | 0.9996 | -0.0077426 | 0.0018881 | 0.0004732
59 | 0.99734 | -0.050756 | 0.0027053 | 0.000678
60 | 0.98687 | -0.25183 | 0.0035104 | 0.0008798
61 | 0.99346 | -0.12527 | 0.0024655 | 0.00061791
62 | 0.9938 | -0.11871 | 0.0040651 | 0.0010188
63 | 0.99273 | -0.13946 | 0.018899 | 0.0047365
64 | 0.99474 | -0.10054 | 0 | 0
65 | 0.98955 | -0.20091 | 0.082242 | 0.020612
66 | 0.98924 | -0.20695 | 0.012629 | 0.003165
67 | 0.98723 | -0.24603 | 0.0020412 | 0.00051157
68 | 0.99203 | -0.1537 | 0.0015374 | 0.0003853
69 | 0.99202 | -0.15402 | 0.0023895 | 0.00059886
70 | 0.99201 | -0.15408 | 0.00029699 | 7.4432e-05
71 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014968 | -0.0037513 | 0.014977 | 0.0037564 | 8.8908e-06 | 5.0698e-06 | 0.022337 | 0.022336 | 0.022337 | 0.99713 | -0.055121 | 0.99778 | -0.04266 | 6.1365
1 | 0.014441 | 0.0036239 | -0.014439 | -0.003623 | 1.6777e-06 | 9.4775e-07 | 0.021538 | 0.021538 | 0.021538 | 0.99778 | -0.04266 | 0.99765 | -0.045096 | 5.9171
2 | -0.029418 | -0.0073803 | 0.029447 | 0.0073986 | 2.9425e-05 | 1.8299e-05 | 0.043875 | 0.043874 | 0.043875 | 0.99778 | -0.04266 | 0.99887 | -0.021702 | 12.0534
3 | 0.012969 | 0.0032545 | -0.012968 | -0.0032539 | 1.2608e-06 | 6.896e-07 | 0.019346 | 0.019346 | 0.019346 | 0.99765 | -0.045096 | 0.99755 | -0.047135 | 5.3147
4 | 0.01081 | 0.0027099 | -0.010808 | -0.0027087 | 2.3126e-06 | 1.1689e-06 | 0.016104 | 0.016104 | 0.016104 | 0.99887 | -0.021702 | 0.99864 | -0.026193 | 4.4242
5 | -0.040258 | -0.010108 | 0.04028 | 0.010122 | 2.2051e-05 | 1.3899e-05 | 0.059978 | 0.059978 | 0.059978 | 0.99887 | -0.021702 | 0.99947 | -0.010227 | 16.4776
6 | 0.0086084 | 0.0021613 | -0.0085826 | -0.0021502 | 2.5835e-05 | 1.11e-05 | 0.012842 | 0.012844 | 0.012844 | 0.99755 | -0.047135 | 0.99428 | -0.11019 | 3.5286
7 | 0.0043598 | 0.0010926 | -0.0043595 | -0.0010926 | 2.6284e-07 | -4.8121e-08 | 0.0065033 | 0.0065034 | 0.0065034 | 0.99755 | -0.047135 | 0.99748 | -0.048401 | 1.7867
8 | -0.052107 | -0.013088 | 0.052133 | 0.013104 | 2.5444e-05 | 1.6136e-05 | 0.077588 | 0.077588 | 0.077588 | 0.99947 | -0.010227 | 1 | 0 | 21.3153
9 | 0.011828 | 0.0029656 | -0.011823 | -0.0029631 | 4.7278e-06 | 2.4932e-06 | 0.01761 | 0.01761 | 0.01761 | 0.99947 | -0.010227 | 0.99903 | -0.018618 | 4.8379
10 | 0.022704 | 0.0056925 | -0.022698 | -0.0056886 | 6.4885e-06 | 3.9674e-06 | 0.034388 | 0.034388 | 0.034388 | 0.98247 | -0.3376 | 0.98216 | -0.3436 | 9.4472
11 | -0.022704 | -0.0056925 | 0.022706 | 0.0056938 | 2.1565e-06 | 1.3186e-06 | 0.034388 | 0.034388 | 0.034388 | 0.98247 | -0.3376 | 0.98257 | -0.33561 | 9.4472
12 | -0.048498 | -0.012158 | 0.048534 | 0.012181 | 3.6114e-05 | 2.2886e-05 | 0.073447 | 0.073447 | 0.073447 | 0.98257 | -0.33561 | 0.98337 | -0.32 | 20.1778
13 | 0.0061413 | 0.0015386 | -0.0061302 | -0.001536 | 1.1106e-05 | 2.5704e-06 | 0.0091907 | 0.0091923 | 0.0091923 | 0.99428 | -0.11019 | 0.99232 | -0.1482 | 2.5254
14 | 0.0024413 | 0.00061162 | -0.0024412 | -0.00061182 | 1.021e-07 | -1.9918e-07 | 0.0036535 | 0.0036536 | 0.0036536 | 0.99428 | -0.11019 | 0.99423 | -0.11107 | 1.0037
15 | 0.14936 | 0.037935 | -0.14905 | -0.037738 | 0.00030846 | 0.00019655 | 0.22242 | 0.22242 | 0.22242 | 1 | 0 | 0.99774 | -0.043006 | 30.5527
16 | 0.02531 | 0.0063569 | -0.0253 | -0.0063511 | 9.3472e-06 | 5.7518e-06 | 0.037666 | 0.037666 | 0.037666 | 1 | 0 | 0.9996 | -0.0077426 | 10.3478
17 | 0.17277 | 0.044133 | -0.17242 | -0.043907 | 0.00035438 | 0.00022605 | 0.25738 | 0.25738 | 0.25738 | 1 | 0 | 0.99776 | -0.04252 | 35.3545
18 | 0.069313 | 0.017431 | -0.069211 | -0.017366 | 0.00010192 | 6.4913e-05 | 0.10474 | 0.10474 | 0.10474 | 0.98495 | -0.28916 | 0.98337 | -0.32 | 28.7737
19 | 0.023771 | 0.0059613 | -0.023761 | -0.005955 | 1.029e-05 | 6.3147e-06 | 0.035914 | 0.035914 | 0.035914 | 0.98495 | -0.28916 | 0.98448 | -0.29825 | 9.8664
20 | -0.093084 | -0.023392 | 0.093359 | 0.023568 | 0.00027486 | 0.00017544 | 0.14065 | 0.14065 | 0.14065 | 0.98495 | -0.28916 | 0.98812 | -0.22751 | 38.6401
21 | 0.020677 | 0.0051853 | -0.02067 | -0.0051811 | 6.9962e-06 | 4.2359e-06 | 0.031289 | 0.031289 | 0.031289 | 0.98337 | -0.32 | 0.983 | -0.3271 | 8.5959
22 | -0.12852 | -0.032386 | 0.12879 | 0.032562 | 0.0002761 | 0.00017645 | 0.19359 | 0.19359 | 0.19359 | 0.98812 | -0.22751 | 0.99044 | -0.1827 | 53.1853
23 | 0.035157 | 0.0088182 | -0.035147 | -0.0088122 | 9.5048e-06 | 5.9673e-06 | 0.052945 | 0.052945 | 0.052945 | 0.98812 | -0.22751 | 0.98783 | -0.23318 | 14.5453
24 | -0.0090222 | -0.0022612 | 0.0090228 | 0.0022614 | 6.1721e-07 | 2.762e-07 | 0.013453 | 0.013453 | 0.013453 | 0.99791 | -0.040225 | 0.99798 | -0.038789 | 3.696
25 | -0.0090228 | -0.0022614 | 0.0090245 | 0.0022622 | 1.7188e-06 | 7.6907e-07 | 0.013453 | 0.013453 | 0.013453 | 0.99798 | -0.038789 | 0.99819 | -0.034791 | 3.6959
26 | -0.016463 | -0.0041267 | 0.016467 | 0.0041286 | 3.198e-06 | 1.8616e-06 | 0.024542 | 0.024542 | 0.024542 | 0.99819 | -0.034791 | 0.9984 | -0.030715 | 6.7424
27 | 0.0074389 | 0.0018645 | -0.0074372 | -0.0018639 | 1.7284e-06 | 6.1637e-07 | 0.011089 | 0.01109 | 0.01109 | 0.99819 | -0.034791 | 0.99794 | -0.039669 | 3.0466
28 | -0.0029964 | -0.00074822 | 0.0029966 | 0.00074801 | 2.0424e-07 | -2.1135e-07 | 0.0045138 | 0.0045137 | 0.0045138 | 0.98757 | -0.23837 | 0.98764 | -0.23693 | 1.2401
29 | 0.0029964 | 0.00074822 | -0.0029946 | -0.00075007 | 1.7909e-06 | -1.8503e-06 | 0.0045138 | 0.0045149 | 0.0045149 | 0.98757 | -0.23837 | 0.98692 | -0.25094 | 1.2404
30 | -0.011992 | -0.0030024 | 0.011994 | 0.0030036 | 2.1431e-06 | 1.1475e-06 | 0.018066 | 0.018066 | 0.018066 | 0.98764 | -0.23693 | 0.98783 | -0.23318 | 4.9633
31 | 0.0029946 | 0.00075007 | -0.0029943 | -0.00075043 | 3.4469e-07 | -3.555e-07 | 0.0045149 | 0.0045151 | 0.0045151 | 0.98692 | -0.25094 | 0.9868 | -0.25335 | 1.2404
32 | -0.019695 | -0.0049378 | 0.019704 | 0.0049427 | 8.0965e-06 | 4.8539e-06 | 0.029355 | 0.029354 | 0.029355 | 0.9984 | -0.030715 | 0.99885 | -0.022092 | 8.0645
33 | 0.0051048 | 0.0012794 | -0.0051047 | -0.0012794 | 1.688e-07 | 6.5318e-09 | 0.0076118 | 0.0076118 | 0.0076118 | 0.99794 | -0.039669 | 0.9979 | -0.040363 | 2.0912
34 | 0.16136 | 0.041001 | -0.16108 | -0.040821 | 0.00028273 | 0.00018027 | 0.24141 | 0.24141 | 0.24141 | 0.99543 | -0.086994 | 0.99352 | -0.12346 | 33.1601
35 | -0.16136 | -0.041001 | 0.1617 | 0.041222 | 0.00034633 | 0.00022082 | 0.24141 | 0.24141 | 0.24141 | 0.99543 | -0.086994 | 0.99776 | -0.04252 | 33.1601
36 | 0.15229 | 0.03862 | -0.15186 | -0.038344 | 0.00043241 | 0.0002756 | 0.22825 | 0.22825 | 0.22825 | 0.99352 | -0.12346 | 0.99044 | -0.1827 | 31.3535
37 | 0.010712 | 0.0026854 | -0.01071 | -0.0026841 | 2.4976e-06 | 1.2577e-06 | 0.015976 | 0.015976 | 0.015976 | 0.99776 | -0.04252 | 0.99751 | -0.047415 | 4.389
38 | 0.023153 | 0.0058086 | -0.023145 | -0.0058037 | 8.0516e-06 | 4.9272e-06 | 0.034879 | 0.034879 | 0.034879 | 0.98783 | -0.23318 | 0.98746 | -0.24048 | 9.5821
39 | 0.023145 | 0.0058037 | -0.023141 | -0.0058014 | 3.8534e-06 | 2.3581e-06 | 0.034879 | 0.034879 | 0.034879 | 0.98746 | -0.24048 | 0.98728 | -0.24397 | 9.5821
40 | 0.019167 | 0.0048053 | -0.019165 | -0.0048042 | 1.8625e-06 | 1.1159e-06 | 0.028889 | 0.028889 | 0.028889 | 0.98728 | -0.24397 | 0.98717 | -0.24601 | 7.9365
41 | 0.016742 | 0.0041966 | -0.01674 | -0.0041958 | 1.431e-06 | 8.405e-07 | 0.025343 | 0.025343 | 0.025343 | 0.983 | -0.3271 | 0.98291 | -0.32889 | 6.9623
42 | -0.013711 | -0.003437 | 0.013714 | 0.0034387 | 2.995e-06 | 1.6769e-06 | 0.02065 | 0.02065 | 0.02065 | 0.988 | -0.23104 | 0.98823 | -0.22646 | 5.6731
43 | 0.0019022 | 0.00047593 | -0.001902 | -0.00047637 | 1.2485e-07 | -4.3962e-07 | 0.0028645 | 0.0028647 | 0.0028647 | 0.988 | -0.23104 | 0.98793 | -0.23242 | 0.78701
44 | 0.011809 | 0.0029611 | -0.011804 | -0.0029585 | 4.7443e-06 | 2.5244e-06 | 0.017786 | 0.017786 | 0.017786 | 0.988 | -0.23104 | 0.98756 | -0.23947 | 4.8862
45 | -0.017186 | -0.0043088 | 0.017194 | 0.0043134 | 7.8433e-06 | 4.6194e-06 | 0.025878 | 0.025878 | 0.025878 | 0.98823 | -0.22646 | 0.98872 | -0.21688 | 7.1093
46 | 0.001902 | 0.00047637 | -0.0019019 | -0.00047667 | 8.6647e-08 | -3.0502e-07 | 0.0028647 | 0.0028649 | 0.0028649 | 0.98793 | -0.23242 | 0.98788 | -0.23338 | 0.78705
47 | 0.0092896 | 0.0023284 | -0.0092884 | -0.0023278 | 1.1804e-06 | 5.4992e-07 | 0.013997 | 0.013997 | 0.013997 | 0.98756 | -0.23947 | 0.98743 | -0.24214 | 3.8454
48 | 0.0092884 | 0.0023278 | -0.0092875 | -0.0023274 | 9.2148e-07 | 4.2934e-07 | 0.013997 | 0.013997 | 0.013997 | 0.98743 | -0.24214 | 0.98732 | -0.24422 | 3.8454
49 | 0.0032601 | 0.00081685 | -0.0032599 | -0.00081701 | 2.0282e-07 | -1.5669e-07 | 0.0049133 | 0.0049134 | 0.0049134 | 0.98732 | -0.24422 | 0.98725 | -0.24553 | 1.3498
50 | 0.0060274 | 0.0015105 | -0.0060269 | -0.0015104 | 4.7234e-07 | 1.0711e-07 | 0.009084 | 0.0090841 | 0.0090841 | 0.98732 | -0.24422 | 0.98723 | -0.24587 | 2.4956
51 | -0.023396 | -0.0058681 | 0.023412 | 0.0058779 | 1.6014e-05 | 9.7887e-06 | 0.034856 | 0.034855 | 0.034856 | 0.99885 | -0.022092 | 0.9996 | -0.0077426 | 9.5757
52 | 0.015221 | 0.0038157 | -0.015218 | -0.0038143 | 2.5255e-06 | 1.4528e-06 | 0.022944 | 0.022944 | 0.022944 | 0.98717 | -0.24601 | 0.98699 | -0.24949 | 6.3032
53 | 0.012817 | 0.0032126 | -0.012816 | -0.003212 | 9.7416e-07 | 5.3602e-07 | 0.019404 | 0.019404 | 0.019404 | 0.98291 | -0.32889 | 0.98283 | -0.33049 | 5.3307
54 | 0.0061302 | 0.001536 | -0.0061289 | -0.0015357 | 1.2411e-06 | 2.8844e-07 | 0.0091923 | 0.0091925 | 0.0091925 | 0.99232 | -0.1482 | 0.9921 | -0.15245 | 2.5254
55 | -0.017194 | -0.0043134 | 0.017202 | 0.0043182 | 8.1514e-06 | 4.8004e-06 | 0.025878 | 0.025878 | 0.025878 | 0.98872 | -0.21688 | 0.98924 | -0.20695 | 7.1093
56 | 0.0020412 | 0.00051152 | -0.0020412 | -0.00051157 | 1.6096e-08 | -4.7679e-08 | 0.0030766 | 0.0030766 | 0.0030766 | 0.98723 | -0.24587 | 0.98723 | -0.24603 | 0.84523
57 | 0.011339 | 0.0028419 | -0.011338 | -0.0028415 | 6.4361e-07 | 3.3685e-07 | 0.017094 | 0.017094 | 0.017094 | 0.98699 | -0.24949 | 0.98693 | -0.25068 | 4.6963
58 | 0.0074375 | 0.001864 | -0.0074372 | -0.0018639 | 2.7698e-07 | 1.0221e-07 | 0.011214 | 0.011214 | 0.011214 | 0.98693 | -0.25068 | 0.98689 | -0.25147 | 3.0807
59 | 0.0035105 | 0.00087977 | -0.0035104 | -0.0008798 | 6.1454e-08 | -3.5408e-08 | 0.0052931 | 0.0052931 | 0.0052931 | 0.98689 | -0.25147 | 0.98687 | -0.25183 | 1.4541
60 | 0.0042241 | 0.0010583 | -0.0042239 | -0.0010584 | 2.5086e-07 | -5.4639e-08 | 0.0063355 | 0.0063356 | 0.0063356 | 0.9921 | -0.15245 | 0.99203 | -0.1537 | 1.7405
61 | 0.14118 | 0.035766 | -0.14113 | -0.035732 | 5.2539e-05 | 3.346e-05 | 0.21069 | 0.21069 | 0.21069 | 0.99774 | -0.043006 | 0.99734 | -0.050756 | 28.9405
62 | 0.13842 | 0.035054 | -0.13809 | -0.034843 | 0.00033007 | 0.00021097 | 0.20665 | 0.20665 | 0.20665 | 0.99734 | -0.050756 | 0.99474 | -0.10054 | 56.7722
63 | -0.021377 | -0.0053621 | 0.021384 | 0.0053661 | 6.6883e-06 | 4.0552e-06 | 0.032021 | 0.03202 | 0.032021 | 0.99346 | -0.12527 | 0.9938 | -0.11871 | 8.7968
64 | 0.018912 | 0.0047442 | -0.018899 | -0.0047365 | 1.2786e-05 | 7.6335e-06 | 0.028328 | 0.028328 | 0.028328 | 0.99346 | -0.12527 | 0.99273 | -0.13946 | 7.7824
65 | -0.025449 | -0.0063849 | 0.025471 | 0.0063985 | 2.2064e-05 | 1.3595e-05 | 0.038107 | 0.038107 | 0.038107 | 0.9938 | -0.11871 | 0.99474 | -0.10054 | 10.469
66 | 0.11262 | 0.028445 | -0.11208 | -0.0281 | 0.00053886 | 0.00034421 | 0.16854 | 0.16854 | 0.16854 | 0.99474 | -0.10054 | 0.98955 | -0.20091 | 46.3033
67 | 0.029839 | 0.0074886 | -0.02983 | -0.0074833 | 8.5898e-06 | 5.3514e-06 | 0.044874 | 0.044874 | 0.044874 | 0.98955 | -0.20091 | 0.98924 | -0.20695 | 12.328
68 | 0.0026865 | 0.00067309 | -0.0026865 | -0.00067315 | 4.1716e-08 | -6.1752e-08 | 0.0040296 | 0.0040296 | 0.0040296 | 0.99203 | -0.1537 | 0.99202 | -0.15402 | 1.107
69 | 0.00029699 | 7.4294e-05 | -0.00029699 | -7.4432e-05 | 8.0241e-10 | -1.3871e-07 | 0.00044543 | 0.00044548 | 0.00044548 | 0.99202 | -0.15402 | 0.99201 | -0.15408 | 0.12239

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40122 | 0.10153

## res_load
| p_mw | q_mvar
0 | 0.014968 | 0.0037513
1 | 0.00147 | 0.00036842
2 | 0.010808 | 0.0027087
3 | 0.022698 | 0.0056886
4 | 0.025792 | 0.006464
5 | 0.0043595 | 0.0010926
6 | 0.011823 | 0.0029631
7 | 0.023761 | 0.005955
8 | 0.0090222 | 0.0022612
9 | 0.0089952 | 0.0022544
10 | 0.0032288 | 0.00080921
11 | 0.0023324 | 0.00058455
12 | 0.0087819 | 0.002201
13 | 0.0039742 | 0.00099603
14 | 0.023069 | 0.0057818
15 | 0.0039282 | 0.00098449
16 | 0.003472 | 0.00087017
17 | 0.0025144 | 0.00063016
18 | 0.0019019 | 0.00047667
19 | 0.0029943 | 0.00075043
20 | 0.0036927 | 0.00092547
21 | 0.0051047 | 0.0012794
22 | 0.01071 | 0.0026841
23 | 0.0039442 | 0.0009885
24 | 0.0039231 | 0.00098323
25 | 0.0024412 | 0.00061182
26 | 0.0032599 | 0.00081701
27 | 0.0039857 | 0.00099891
28 | 0.012816 | 0.003212
29 | 0.0038798 | 0.00097238
30 | 0.0039005 | 0.00097755
31 | 0.0039267 | 0.00098413
32 | 0.0019048 | 0.00047739
33 | 0.0078701 | 0.0019724
34 | 0.0018881 | 0.0004732
35 | 0.0027053 | 0.000678
36 | 0.0035104 | 0.0008798
37 | 0.0024655 | 0.00061791
38 | 0.0040651 | 0.0010188
39 | 0.018899 | 0.0047365
40 | 0.082242 | 0.020612
41 | 0.012629 | 0.003165
42 | 0.0020412 | 0.00051157
43 | 0.0015374 | 0.0003853
44 | 0.0023895 | 0.00059886
45 | 0.00029699 | 7.4432e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1