## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_251-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_251-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_251-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_251-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_251-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_251-8_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_251-8_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_251-8_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_251-8_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_251-8_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_251-8_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_251-8_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_251-8_0_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_251-8_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_251-8_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_251-8_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_251-8_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_251-8_0_4_node_69 | 0.4 | n |  | TRUE
18 | bus_LV_251-8_0_4_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_251-8_0_4_node_66 | 0.4 | n |  | TRUE
20 | bus_LV_251-8_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_251-8_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_251-8_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_251-8_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_251-8_0_4_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_251-8_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_251-8_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_251-8_0_4_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_251-8_0_4_node_135 | 0.4 | n |  | TRUE
29 | bus_LV_251-8_0_4_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_251-8_0_4_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_251-8_0_4_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_251-8_0_4_node_144 | 0.4 | n |  | TRUE
33 | bus_LV_251-8_0_4_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_251-8_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_251-8_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_251-8_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_251-8_0_4_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_251-8_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_251-8_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_251-8_0_4_node_145 | 0.4 | n |  | TRUE
41 | bus_LV_251-8_0_4_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_251-8_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_251-8_0_4_node_134 | 0.4 | n |  | TRUE
44 | bus_LV_251-8_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_251-8_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_251-8_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_251-8_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_251-8_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_251-8_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_251-8_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_251-8_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_251-8_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_251-8_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_251-8_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_251-8_0_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_251-8_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_251-8_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_251-8_0_4_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_251-8_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_251-8_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_251-8_0_4_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_251-8_0_4_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_251-8_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_251-8_0_4_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_251-8_0_4_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_251-8_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_251-8_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_251-8_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_251-8_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_251-8_0_4_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_251-8_0_4_node_80 | 0.4 | n |  | TRUE
72 | bus_LV_251-8_0_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_251-8_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_251-8_0_4_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_251-8_0_4_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_251-8_0_4_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_251-8_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_251-8_0_4_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_251-8_0_4_node_137 | 0.4 | n |  | TRUE
80 | bus_LV_251-8_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_251-8_0_4_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_251-8_0_4_node_138 | 0.4 | n |  | TRUE
83 | bus_LV_251-8_0_4_node_88 | 0.4 | n |  | TRUE
84 | bus_LV_251-8_0_4_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_251-8_0_4_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_251-8_0_4_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_251-8_0_4_node_136 | 0.4 | n |  | TRUE
88 | bus_LV_251-8_0_4_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_251-8_0_4_node_139 | 0.4 | n |  | TRUE
90 | bus_LV_251-8_0_4_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_251-8_0_4_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_251-8_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_251-8_0_4_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_251-8_0_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_251-8_0_4_node_118 | 0.4 | n |  | TRUE
96 | bus_LV_251-8_0_4_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_251-8_0_4_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_251-8_0_4_node_117 | 0.4 | n |  | TRUE
99 | bus_LV_251-8_0_4_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_251-8_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_251-8_0_4_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_251-8_0_4_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_251-8_0_4_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_251-8_0_4_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_251-8_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_251-8_0_4_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_251-8_0_4_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_251-8_0_4_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_251-8_0_4_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_251-8_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_251-8_0_4_node_122 | 0.4 | n |  | TRUE
112 | bus_LV_251-8_0_4_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_251-8_0_4_node_110 | 0.4 | n |  | TRUE
114 | bus_LV_251-8_0_4_node_123 | 0.4 | n |  | TRUE
115 | bus_LV_251-8_0_4_node_124 | 0.4 | n |  | TRUE
116 | bus_LV_251-8_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_251-8_0_4_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_251-8_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_251-8_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_251-8_0_4_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_251-8_0_4_node_105 | 0.4 | n |  | TRUE
122 | bus_LV_251-8_0_4_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_251-8_0_4_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_251-8_0_4_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_251-8_0_4_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_251-8_0_4_node_141 | 0.4 | n |  | TRUE
127 | bus_LV_251-8_0_4_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_251-8_0_4_node_114 | 0.4 | n |  | TRUE
129 | bus_LV_251-8_0_4_node_119 | 0.4 | n |  | TRUE
130 | bus_LV_251-8_0_4_node_127 | 0.4 | n |  | TRUE
131 | bus_LV_251-8_0_4_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_251-8_0_4_node_143 | 0.4 | n |  | TRUE
133 | bus_LV_251-8_0_4_node_121 | 0.4 | n |  | TRUE
134 | bus_LV_251-8_0_4_node_130 | 0.4 | n |  | TRUE
135 | bus_LV_251-8_0_4_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_251-8_0_4_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_251-8_0_4_node_126 | 0.4 | n |  | TRUE
138 | bus_LV_251-8_0_4_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_251-8_0_4_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_251-8_0_4_node_133 | 0.4 | n |  | TRUE
141 | bus_LV_251-8_0_4_node_140 | 0.4 | n |  | TRUE
142 | bus_MV_516_1_node_75 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_251-8_0_4_load_0 | 0 | 0.001986 | 0.00049773 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_251-8_0_4_load_1 | 1 | 0.0024491 | 0.0006138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_251-8_0_4_load_2 | 2 | 0.0012594 | 0.00031564 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_251-8_0_4_load_6 | 6 | 0.0031523 | 0.00079004 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_251-8_0_4_load_8 | 7 | 0.004951 | 0.0012408 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_251-8_0_4_load_13 | 9 | 0.00069132 | 0.00017326 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_251-8_0_4_load_14 | 10 | 0.0010685 | 0.00026779 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_251-8_0_4_load_25 | 12 | 0.0020605 | 0.00051642 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_251-8_0_4_load_23 | 15 | 0.0015313 | 0.00038377 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_251-8_0_4_load_69 | 17 | 0.0057459 | 0.00144 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_251-8_0_4_load_71 | 18 | 0.0025041 | 0.00062758 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_251-8_0_4_load_20 | 22 | 0.0065832 | 0.0016499 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_251-8_0_4_load_43 | 23 | 0.00066548 | 0.00016679 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_251-8_0_4_load_24 | 25 | 0.00020317 | 5.0919e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_251-8_0_4_load_15 | 26 | 0.00076821 | 0.00019253 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_251-8_0_4_load_30 | 27 | 0.00038153 | 9.562e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_251-8_0_4_load_135 | 28 | 0.001107 | 0.00027745 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_251-8_0_4_load_48 | 29 | 0.0024643 | 0.00061762 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_251-8_0_4_load_64 | 31 | 0.00081813 | 0.00020504 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_251-8_0_4_load_44 | 33 | 0.0010913 | 0.00027352 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_251-8_0_4_load_19 | 34 | 0.0050241 | 0.0012592 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_251-8_0_4_load_41 | 35 | 0.0049142 | 0.0012316 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_251-8_0_4_load_31 | 36 | 0.00058745 | 0.00014723 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_251-8_0_4_load_16 | 37 | 0.0010963 | 0.00027477 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_251-8_0_4_load_17 | 38 | 0.0020685 | 0.00051841 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_251-8_0_4_load_18 | 39 | 0.0062815 | 0.0015743 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_251-8_0_4_load_145 | 40 | 0.0017289 | 0.00043329 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_251-8_0_4_load_42 | 41 | 0.00098805 | 0.00024763 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_251-8_0_4_load_29 | 42 | 0.0004023 | 0.00010083 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_251-8_0_4_load_134 | 43 | 0.0014264 | 0.00035748 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_251-8_0_4_load_27 | 44 | 0.00039776 | 9.9689e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_251-8_0_4_load_28 | 45 | 0.0021188 | 0.00053101 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_251-8_0_4_load_32 | 46 | 0.0019637 | 0.00049215 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_251-8_0_4_load_33 | 47 | 0.0046549 | 0.0011666 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_251-8_0_4_load_34 | 48 | 0.00086093 | 0.00021577 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_251-8_0_4_load_35 | 49 | 0.0055964 | 0.0014026 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_251-8_0_4_load_36 | 50 | 0.0024808 | 0.00062176 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_251-8_0_4_load_37 | 51 | 0.0033369 | 0.0008363 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_251-8_0_4_load_38 | 52 | 0.0016203 | 0.00040608 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_251-8_0_4_load_45 | 53 | 0.0036649 | 0.00091852 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_251-8_0_4_load_39 | 55 | 0.0017692 | 0.0004434 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_251-8_0_4_load_40 | 56 | 0.00099357 | 0.00024901 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_251-8_0_4_load_51 | 57 | 0.0019604 | 0.00049133 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_251-8_0_4_load_49 | 58 | 0.0017209 | 0.00043131 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_251-8_0_4_load_47 | 60 | 0.0014425 | 0.00036152 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_251-8_0_4_load_59 | 62 | 0.0019488 | 0.00048843 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_251-8_0_4_load_61 | 63 | 0.023984 | 0.0060108 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_251-8_0_4_load_58 | 65 | 0.0060092 | 0.001506 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_251-8_0_4_load_53 | 66 | 0.0088243 | 0.0022116 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_251-8_0_4_load_54 | 67 | 0.0041898 | 0.0010501 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_251-8_0_4_load_55 | 68 | 0.0039362 | 0.0009865 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_251-8_0_4_load_56 | 69 | 0.0030238 | 0.00075784 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_251-8_0_4_load_80 | 71 | 0.064095 | 0.016064 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_251-8_0_4_load_67 | 72 | 0.0051068 | 0.0012799 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_251-8_0_4_load_65 | 73 | 0.0051388 | 0.0012879 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_251-8_0_4_load_75 | 74 | 0.022929 | 0.0057466 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_251-8_0_4_load_63 | 75 | 0.00099379 | 0.00024907 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_251-8_0_4_load_68 | 76 | 0.0017928 | 0.00044931 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_251-8_0_4_load_74 | 78 | 0.0023059 | 0.00057792 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_251-8_0_4_load_137 | 79 | 0.000837 | 0.00020977 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_251-8_0_4_load_76 | 80 | 0.0062105 | 0.0015565 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_251-8_0_4_load_92 | 81 | 0.0066623 | 0.0016697 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_251-8_0_4_load_138 | 82 | 0.00063104 | 0.00015815 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_251-8_0_4_load_78 | 85 | 0.00143 | 0.00035839 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_251-8_0_4_load_79 | 86 | 0.0045306 | 0.0011355 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_251-8_0_4_load_136 | 87 | 0.00078442 | 0.00019659 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_251-8_0_4_load_90 | 88 | 0.0037497 | 0.00093975 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_251-8_0_4_load_139 | 89 | 0.00072462 | 0.00018161 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_251-8_0_4_load_83 | 93 | 0.0016058 | 0.00040244 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_251-8_0_4_load_94 | 94 | 0.0012631 | 0.00031656 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_251-8_0_4_load_118 | 95 | 0.0019408 | 0.00048641 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_251-8_0_4_load_95 | 96 | 0.00097135 | 0.00024344 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_251-8_0_4_load_117 | 98 | 0.0026925 | 0.00067481 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_251-8_0_4_load_84 | 99 | 0.0024203 | 0.00060659 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_251-8_0_4_load_85 | 100 | 0.0018385 | 0.00046077 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_251-8_0_4_load_89 | 101 | 0.0018087 | 0.0004533 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_251-8_0_4_load_91 | 102 | 0.0059651 | 0.001495 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_251-8_0_4_load_93 | 103 | 0.0018347 | 0.00045983 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_251-8_0_4_load_100 | 105 | 0.012922 | 0.0032385 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_251-8_0_4_load_96 | 106 | 0.0029004 | 0.00072692 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_251-8_0_4_load_97 | 107 | 0.0029713 | 0.00074468 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_251-8_0_4_load_99 | 108 | 0.0029179 | 0.00073129 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_251-8_0_4_load_101 | 109 | 0.0028942 | 0.00072537 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_251-8_0_4_load_110 | 113 | 0.0022865 | 0.00057305 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_251-8_0_4_load_123 | 114 | 0.0011086 | 0.00027785 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_251-8_0_4_load_124 | 115 | 0.0018355 | 0.00046002 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_251-8_0_4_load_115 | 116 | 0.0022371 | 0.00056067 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_251-8_0_4_load_116 | 117 | 0.0017839 | 0.0004471 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_251-8_0_4_load_111 | 118 | 0.0024604 | 0.00061664 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_251-8_0_4_load_103 | 119 | 0.0010263 | 0.00025722 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_251-8_0_4_load_104 | 120 | 0.0010627 | 0.00026633 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_251-8_0_4_load_105 | 121 | 0.0012146 | 0.0003044 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_251-8_0_4_load_106 | 122 | 0.0014901 | 0.00037345 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_251-8_0_4_load_107 | 123 | 0.0011734 | 0.00029408 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_251-8_0_4_load_108 | 124 | 0.0015747 | 0.00039465 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_251-8_0_4_load_141 | 126 | 0.003293 | 0.00082531 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_251-8_0_4_load_112 | 127 | 0.0028491 | 0.00071406 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_251-8_0_4_load_114 | 128 | 0.0021022 | 0.00052686 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_251-8_0_4_load_119 | 129 | 0.0027764 | 0.00069583 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_251-8_0_4_load_120 | 131 | 0.0024553 | 0.00061537 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_251-8_0_4_load_143 | 132 | 0.0022371 | 0.00056067 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_251-8_0_4_load_121 | 133 | 0.0021231 | 0.00053211 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_251-8_0_4_load_130 | 134 | 0.0030465 | 0.00076353 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_251-8_0_4_load_131 | 135 | 0.0025269 | 0.00063331 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_251-8_0_4_load_125 | 136 | 0.0010713 | 0.00026849 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_251-8_0_4_load_126 | 137 | 0.0010762 | 0.00026973 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_251-8_0_4_load_129 | 138 | 0.0004516 | 0.00011318 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_251-8_0_4_load_132 | 139 | 0.00091053 | 0.0002282 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_251-8_0_4_load_133 | 140 | 0.0014973 | 0.00037526 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_251-8_0_4_load_140 | 141 | 0.0025465 | 0.00063823 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_251-8_0_4_line_0 |  | 0 | 1 | 0.0069524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_251-8_0_4_line_1 |  | 0 | 2 | 0.0048661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_251-8_0_4_line_2 |  | 1 | 3 | 0.0055168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_251-8_0_4_line_3 |  | 2 | 4 | 0.030805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_251-8_0_4_line_4 |  | 3 | 5 | 0.030158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_251-8_0_4_line_5 |  | 3 | 6 | 0.014487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_251-8_0_4_line_6 |  | 4 | 7 | 0.020379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_251-8_0_4_line_7 |  | 4 | 8 | 0.019911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_251-8_0_4_line_8 |  | 5 | 9 | 0.022472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_251-8_0_4_line_9 |  | 5 | 10 | 0.024018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_251-8_0_4_line_10 |  | 7 | 15 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_251-8_0_4_line_11 |  | 8 | 23 | 0.0075438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_251-8_0_4_line_12 |  | 8 | 24 | 0.001651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_251-8_0_4_line_13 |  | 8 | 16 | 0.01938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_251-8_0_4_line_14 |  | 9 | 25 | 0.023012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_251-8_0_4_line_15 |  | 10 | 26 | 0.025447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_251-8_0_4_line_16 |  | 11 | 12 | 0.0066323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_251-8_0_4_line_17 |  | 11 | 13 | 0.0151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_251-8_0_4_line_18 |  | 11 | 14 | 0.012986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_251-8_0_4_line_19 |  | 12 | 27 | 0.032229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_251-8_0_4_line_20 |  | 13 | 28 | 0.01615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_251-8_0_4_line_21 |  | 14 | 18 | 0.021536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_251-8_0_4_line_22 |  | 14 | 19 | 0.012318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_251-8_0_4_line_23 |  | 16 | 17 | 0.044259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_251-8_0_4_line_24 |  | 17 | 19 | 0.025835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_251-8_0_4_line_25 |  | 18 | 30 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_251-8_0_4_line_26 |  | 19 | 31 | 0.010092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_251-8_0_4_line_27 |  | 20 | 21 | 0.035935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_251-8_0_4_line_28 |  | 20 | 22 | 0.020043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_251-8_0_4_line_29 |  | 21 | 32 | 0.057516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_251-8_0_4_line_30 |  | 21 | 33 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_251-8_0_4_line_31 |  | 22 | 34 | 0.0038467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_251-8_0_4_line_32 |  | 23 | 35 | 0.013761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_251-8_0_4_line_33 |  | 24 | 29 | 0.034506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_251-8_0_4_line_34 |  | 25 | 36 | 0.013948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_251-8_0_4_line_35 |  | 26 | 37 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_251-8_0_4_line_36 |  | 27 | 42 | 0.00045458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_251-8_0_4_line_37 |  | 28 | 43 | 0.062438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_251-8_0_4_line_38 |  | 29 | 60 | 0.019876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_251-8_0_4_line_39 |  | 30 | 78 | 0.0044846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_251-8_0_4_line_40 |  | 30 | 77 | 0.007369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_251-8_0_4_line_41 |  | 31 | 75 | 0.020935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_251-8_0_4_line_42 |  | 32 | 40 | 0.035017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_251-8_0_4_line_43 |  | 33 | 41 | 0.0011476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_251-8_0_4_line_44 |  | 35 | 55 | 0.031036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_251-8_0_4_line_45 |  | 37 | 38 | 0.0060031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_251-8_0_4_line_46 |  | 38 | 39 | 0.029043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_251-8_0_4_line_47 |  | 41 | 56 | 0.0074658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_251-8_0_4_line_48 |  | 42 | 45 | 0.02711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_251-8_0_4_line_49 |  | 43 | 140 | 0.064575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_251-8_0_4_line_50 |  | 44 | 45 | 0.02846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_251-8_0_4_line_51 |  | 46 | 47 | 0.0070804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_251-8_0_4_line_52 |  | 46 | 48 | 0.0084882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_251-8_0_4_line_53 |  | 47 | 49 | 0.021867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_251-8_0_4_line_54 |  | 48 | 50 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_251-8_0_4_line_55 |  | 49 | 51 | 0.0057137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_251-8_0_4_line_56 |  | 50 | 52 | 0.00050067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_251-8_0_4_line_57 |  | 51 | 53 | 0.0086673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_251-8_0_4_line_58 |  | 53 | 54 | 0.0072364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_251-8_0_4_line_59 |  | 54 | 57 | 0.015384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_251-8_0_4_line_60 |  | 54 | 58 | 0.047548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_251-8_0_4_line_61 |  | 55 | 56 | 0.010628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_251-8_0_4_line_62 |  | 57 | 59 | 0.023243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_251-8_0_4_line_63 |  | 58 | 60 | 0.021265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_251-8_0_4_line_64 |  | 59 | 61 | 0.06044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_251-8_0_4_line_65 |  | 59 | 62 | 0.017673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_251-8_0_4_line_66 |  | 61 | 63 | 0.014279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_251-8_0_4_line_67 |  | 61 | 64 | 0.011462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_251-8_0_4_line_68 |  | 62 | 65 | 0.022767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_251-8_0_4_line_69 |  | 64 | 71 | 0.027727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_251-8_0_4_line_70 |  | 65 | 70 | 0.015402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_251-8_0_4_line_71 |  | 66 | 67 | 0.035317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_251-8_0_4_line_72 |  | 66 | 68 | 0.022529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_251-8_0_4_line_73 |  | 67 | 69 | 0.026775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_251-8_0_4_line_74 |  | 68 | 70 | 0.023613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_251-8_0_4_line_75 |  | 71 | 74 | 0.031299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_251-8_0_4_line_76 |  | 72 | 73 | 0.0056934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_251-8_0_4_line_77 |  | 73 | 75 | 0.017352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_251-8_0_4_line_78 |  | 76 | 77 | 0.013554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_251-8_0_4_line_79 |  | 78 | 79 | 0.037686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_251-8_0_4_line_80 |  | 79 | 82 | 0.022058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_251-8_0_4_line_81 |  | 80 | 81 | 0.025389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_251-8_0_4_line_82 |  | 81 | 83 | 0.055381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_251-8_0_4_line_83 |  | 82 | 89 | 0.00032517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_251-8_0_4_line_84 |  | 83 | 97 | 0.005772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_251-8_0_4_line_85 |  | 83 | 92 | 0.043332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_251-8_0_4_line_86 |  | 84 | 85 | 0.02661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_251-8_0_4_line_87 |  | 84 | 86 | 0.0050383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_251-8_0_4_line_88 |  | 85 | 87 | 0.0038502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_251-8_0_4_line_89 |  | 86 | 88 | 0.0077704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_251-8_0_4_line_90 |  | 87 | 89 | 0.021347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_251-8_0_4_line_91 |  | 88 | 90 | 0.0066589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_251-8_0_4_line_92 |  | 90 | 102 | 0.031505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_251-8_0_4_line_93 |  | 90 | 100 | 0.017857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_251-8_0_4_line_94 |  | 91 | 92 | 0.027859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_251-8_0_4_line_95 |  | 91 | 93 | 0.023533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_251-8_0_4_line_96 |  | 92 | 94 | 0.026649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_251-8_0_4_line_97 |  | 93 | 95 | 0.025155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_251-8_0_4_line_98 |  | 94 | 96 | 0.0069662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_251-8_0_4_line_99 |  | 95 | 98 | 0.018285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_251-8_0_4_line_100 |  | 97 | 101 | 0.014253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_251-8_0_4_line_101 |  | 97 | 99 | 0.018986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_251-8_0_4_line_102 |  | 98 | 124 | 0.029156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_251-8_0_4_line_103 |  | 99 | 100 | 0.0081343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_251-8_0_4_line_104 |  | 101 | 103 | 0.0098253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_251-8_0_4_line_105 |  | 102 | 104 | 0.01416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_251-8_0_4_line_106 |  | 104 | 105 | 0.03644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_251-8_0_4_line_107 |  | 104 | 106 | 0.021817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_251-8_0_4_line_108 |  | 105 | 110 | 0.0084089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_251-8_0_4_line_109 |  | 106 | 107 | 3.5504e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_251-8_0_4_line_110 |  | 107 | 108 | 0.022879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_251-8_0_4_line_111 |  | 108 | 109 | 0.00015357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_251-8_0_4_line_112 |  | 109 | 111 | 0.0099583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_251-8_0_4_line_113 |  | 110 | 112 | 0.033305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_251-8_0_4_line_114 |  | 110 | 113 | 0.020101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_251-8_0_4_line_115 |  | 111 | 114 | 0.025987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_251-8_0_4_line_116 |  | 111 | 115 | 0.024885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_251-8_0_4_line_117 |  | 112 | 116 | 0.0021363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_251-8_0_4_line_118 |  | 112 | 117 | 0.0091907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_251-8_0_4_line_119 |  | 113 | 118 | 0.0014796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_251-8_0_4_line_120 |  | 114 | 136 | 3.9891e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_251-8_0_4_line_121 |  | 115 | 137 | 0.0010256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_251-8_0_4_line_122 |  | 116 | 130 | 0.027938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_251-8_0_4_line_123 |  | 118 | 127 | 0.022208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_251-8_0_4_line_124 |  | 119 | 120 | 0.019461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_251-8_0_4_line_125 |  | 119 | 121 | 0.025337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_251-8_0_4_line_126 |  | 120 | 122 | 0.021614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_251-8_0_4_line_127 |  | 121 | 123 | 0.013086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_251-8_0_4_line_128 |  | 122 | 124 | 0.029909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_251-8_0_4_line_129 |  | 123 | 125 | 0.02316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_251-8_0_4_line_130 |  | 125 | 126 | 0.052279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_251-8_0_4_line_131 |  | 127 | 128 | 0.0023455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_251-8_0_4_line_132 |  | 128 | 129 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_251-8_0_4_line_133 |  | 129 | 131 | 0.0074016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_251-8_0_4_line_134 |  | 130 | 132 | 0.012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_251-8_0_4_line_135 |  | 131 | 133 | 0.02617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_251-8_0_4_line_136 |  | 133 | 134 | 0.00089146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_251-8_0_4_line_137 |  | 134 | 135 | 0.019489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_251-8_0_4_line_138 |  | 135 | 141 | 0.00085603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_251-8_0_4_line_139 |  | 138 | 139 | 0.019033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_251-8_0_4_line_140 |  | 139 | 140 | 0.12219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_251-8_0_4_trafo_75 | 0.63 MVA 20/0.4 kV | 142 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2674911.1192 | 1252423.3417 | 2674910.1139 | 1252416.4624
1 | 2674911.1192 | 1252423.3417 | 2674911.8229 | 1252428.1566
2 | 2674909.3162 | 1252411.0035 | 2674910.1139 | 1252416.4624
3 | 2674915.3546 | 1252458.6591 | 2674915.727 | 1252454.8722 | 2674911.8229 | 1252428.1566
4 | 2674909.3162 | 1252411.0035 | 2674907.5007 | 1252380.903
5 | 2674909.3162 | 1252411.0035 | 2674896.0852 | 1252416.9042
6 | 2674915.3546 | 1252458.6591 | 2674934.2351 | 1252466.3285
7 | 2674915.3546 | 1252458.6591 | 2674914.9901 | 1252462.4128 | 2674924.4058 | 1252466.8129 | 2674921.1236 | 1252471.5304
8 | 2674907.5007 | 1252380.903 | 2674897.8989 | 1252360.5857
9 | 2674907.5007 | 1252380.903 | 2674930.0304 | 1252372.5788
10 | 2674934.2351 | 1252466.3285 | 2674936.5731 | 1252467.2782 | 2674948.8894 | 1252474.2494
11 | 2674921.1236 | 1252471.5304 | 2674928.1085 | 1252474.3801
12 | 2674920.1782 | 1252472.8861 | 2674921.1236 | 1252471.5304
13 | 2674921.1236 | 1252471.5304 | 2674910.5846 | 1252467.6388 | 2674902.8141 | 1252465.0275
14 | 2674888.066 | 1252339.7798 | 2674897.8989 | 1252360.5857
15 | 2674953.6055 | 1252363.0438 | 2674944.0482 | 1252367.3996 | 2674930.0304 | 1252372.5788
16 | 2674838.2551 | 1252433.6111 | 2674835.5412 | 1252427.5595
17 | 2674828.9163 | 1252424.909 | 2674832.9918 | 1252433.8559 | 2674838.2551 | 1252433.6111
18 | 2674836.482 | 1252440.7384 | 2674832.9918 | 1252433.8559 | 2674838.2551 | 1252433.6111
19 | 2674835.5412 | 1252427.5595 | 2674833.7116 | 1252423.4796 | 2674821.9485 | 1252398.3378
20 | 2674828.9163 | 1252424.909 | 2674819.565 | 1252414.2054 | 2674818.7552 | 1252412.4455
21 | 2674836.482 | 1252440.7384 | 2674826.8739 | 1252442.0069 | 2674822.262 | 1252442.6602 | 2674816.108 | 1252442.916 | 2674815.0804 | 1252442.9301
22 | 2674836.482 | 1252440.7384 | 2674833.8922 | 1252452.7811
23 | 2674902.8141 | 1252465.0275 | 2674885.0764 | 1252460.4556 | 2674868.0464 | 1252457.2047 | 2674859.5132 | 1252456.0995
24 | 2674833.8922 | 1252452.7811 | 2674859.5132 | 1252456.0995
25 | 2674799.2151 | 1252443.1474 | 2674815.0804 | 1252442.9301
26 | 2674833.8922 | 1252452.7811 | 2674831.7699 | 1252462.6479
27 | 2674984.3571 | 1252494.3246 | 2675006.0962 | 1252508.8882 | 2675003.2987 | 1252512.8779 | 2675000.4933 | 1252516.8898
28 | 2674984.3571 | 1252494.3246 | 2674989.5173 | 1252487.9186 | 2674998.5546 | 1252480.4719 | 2674998.6459 | 1252480.4166
29 | 2675023.3952 | 1252554.6295 | 2675025.8765 | 1252549.3905 | 2675032.5102 | 1252537.4768 | 2675017.9564 | 1252528.8196 | 2675000.4933 | 1252516.8898
30 | 2675000.4933 | 1252516.8898 | 2674984.9794 | 1252506.5637 | 2674983.7563 | 1252505.7224
31 | 2675001.9359 | 1252478.4235 | 2674998.6459 | 1252480.4166
32 | 2674940.6884 | 1252479.9504 | 2674931.9804 | 1252475.9598 | 2674928.1085 | 1252474.3801
33 | 2674920.1782 | 1252472.8861 | 2674911.5971 | 1252505.1234 | 2674911.3114 | 1252506.2335
34 | 2674888.066 | 1252339.7798 | 2674882.1062 | 1252327.169
35 | 2674971.0067 | 1252355.1129 | 2674953.6055 | 1252363.0438
36 | 2674821.7559 | 1252397.9261 | 2674821.9485 | 1252398.3378
37 | 2674818.7552 | 1252412.4455 | 2674802.2007 | 1252376.4697 | 2674792.36 | 1252355.863
38 | 2674906.3572 | 1252525.4821 | 2674911.3114 | 1252506.2335
39 | 2674799.2151 | 1252443.1474 | 2674794.7309 | 1252443.2086
40 | 2674799.2151 | 1252443.1474 | 2674798.3454 | 1252450.464
41 | 2674827.6642 | 1252483.17 | 2674828.5683 | 1252477.532 | 2674831.7699 | 1252462.6479
42 | 2675023.3952 | 1252554.6295 | 2675020.8993 | 1252556.2547 | 2675016.3337 | 1252554.4511 | 2675009.6496 | 1252556.6459 | 2674997.9705 | 1252573.0657
43 | 2674983.7563 | 1252505.7224 | 2674982.8108 | 1252505.0721
44 | 2674967.9032 | 1252494.8184 | 2674966.8139 | 1252494.0692 | 2674954.7304 | 1252486.9889 | 2674942.6351 | 1252480.8425 | 2674940.6884 | 1252479.9504
45 | 2674971.0067 | 1252355.1129 | 2674976.4692 | 1252352.6234
46 | 2675002.8875 | 1252340.5579 | 2674999.1197 | 1252342.3002 | 2674976.4692 | 1252352.6234
47 | 2674982.8108 | 1252505.0721 | 2674976.6596 | 1252500.8412
48 | 2674821.7559 | 1252397.9261 | 2674810.2671 | 1252373.3706
49 | 2674792.36 | 1252355.863 | 2674786.1794 | 1252342.9207 | 2674763.3195 | 1252299.2781 | 2674762.8702 | 1252298.4237
50 | 2674810.2671 | 1252373.3706 | 2674798.2065 | 1252347.5927
51 | 2674926.971 | 1252602.4137 | 2674920.1737 | 1252600.4314
52 | 2674935.1197 | 1252604.7901 | 2674926.971 | 1252602.4137
53 | 2674899.2091 | 1252594.2138 | 2674908.2694 | 1252596.9597 | 2674920.1737 | 1252600.4314
54 | 2674935.1197 | 1252604.7901 | 2674945.8651 | 1252607.9238
55 | 2674899.2091 | 1252594.2138 | 2674893.7411 | 1252592.5566
56 | 2674946.3458 | 1252608.064 | 2674945.8651 | 1252607.9238
57 | 2674885.4464 | 1252590.0427 | 2674893.7411 | 1252592.5566
58 | 2674878.5211 | 1252587.9438 | 2674885.4464 | 1252590.0427
59 | 2674878.5211 | 1252587.9438 | 2674863.9052 | 1252583.1446
60 | 2674878.5211 | 1252587.9438 | 2674901.0569 | 1252546.0757
61 | 2674967.9032 | 1252494.8184 | 2674976.6596 | 1252500.8412
62 | 2674841.8227 | 1252575.8936 | 2674863.9052 | 1252583.1446
63 | 2674901.0569 | 1252546.0757 | 2674906.3572 | 1252525.4821
64 | 2674841.8227 | 1252575.8936 | 2674811.7752 | 1252569.6319 | 2674781.9144 | 1252567.698
65 | 2674841.8227 | 1252575.8936 | 2674836.9244 | 1252592.8744
66 | 2674781.9144 | 1252567.698 | 2674795.422 | 1252563.0678
67 | 2674781.9144 | 1252567.698 | 2674770.7575 | 1252564.933
68 | 2674830.6143 | 1252614.7498 | 2674836.9244 | 1252592.8744
69 | 2674770.7575 | 1252564.933 | 2674773.0007 | 1252537.2966
70 | 2674826.3455 | 1252629.5486 | 2674830.6143 | 1252614.7498
71 | 2674871.0158 | 1252640.8299 | 2674880.265 | 1252643.9958 | 2674903.889 | 1252653.7031
72 | 2674871.0158 | 1252640.8299 | 2674861.7802 | 1252637.6687 | 2674849.3977 | 1252634.556
73 | 2674928.6545 | 1252663.8795 | 2674903.889 | 1252653.7031
74 | 2674826.3455 | 1252629.5486 | 2674834.4875 | 1252630.8079 | 2674849.3977 | 1252634.556
75 | 2674771.7958 | 1252510.7953 | 2674771.1512 | 1252521.2059 | 2674776.5569 | 1252527.601 | 2674775.9156 | 1252537.1555 | 2674773.0007 | 1252537.2966 | 2674773.0007 | 1252537.2966
76 | 2674824.0155 | 1252505.9246 | 2674824.9169 | 1252500.3031
77 | 2674827.6642 | 1252483.17 | 2674824.9169 | 1252500.3031
78 | 2674798.3454 | 1252450.464 | 2674811.8826 | 1252451.1317
79 | 2674794.7309 | 1252443.2086 | 2674772.5548 | 1252443.5112 | 2674769.2355 | 1252443.4026 | 2674757.056 | 1252442.9964
80 | 2674757.056 | 1252442.9964 | 2674735.0105 | 1252442.2611
81 | 2674745.9008 | 1252473.2745 | 2674739.8012 | 1252473.4088 | 2674731.286 | 1252473.5905 | 2674726.5265 | 1252481.7586 | 2674725.2098 | 1252481.7241
82 | 2674671.3695 | 1252482.7196 | 2674672.4636 | 1252480.3428 | 2674725.2098 | 1252481.7241
83 | 2674735.0105 | 1252442.2611 | 2674734.6855 | 1252442.2502
84 | 2674671.3695 | 1252482.7196 | 2674665.5837 | 1252482.5132
85 | 2674667.565 | 1252525.881 | 2674671.3695 | 1252482.7196
86 | 2674682.9003 | 1252441.4903 | 2674685.8024 | 1252441.7716 | 2674709.4963 | 1252441.7613
87 | 2674682.9003 | 1252441.4903 | 2674677.8847 | 1252441.0127
88 | 2674709.4963 | 1252441.7613 | 2674713.3465 | 1252441.7597
89 | 2674677.8847 | 1252441.0127 | 2674670.1494 | 1252440.2761
90 | 2674734.6855 | 1252442.2502 | 2674719.8919 | 1252441.7568 | 2674713.3465 | 1252441.7597
91 | 2674663.5205 | 1252439.6448 | 2674670.1494 | 1252440.2761
92 | 2674663.5205 | 1252439.6448 | 2674659.822 | 1252439.0867 | 2674638.0281 | 1252435.365 | 2674632.5034 | 1252434.156
93 | 2674663.5205 | 1252439.6448 | 2674663.4312 | 1252457.5012
94 | 2674667.7345 | 1252553.7369 | 2674667.565 | 1252525.881
95 | 2674667.7345 | 1252553.7369 | 2674644.2036 | 1252554.0255
96 | 2674667.565 | 1252525.881 | 2674641.5117 | 1252520.2784
97 | 2674619.2915 | 1252551.2737 | 2674635.9954 | 1252554.1262 | 2674644.2036 | 1252554.0255
98 | 2674641.5117 | 1252520.2784 | 2674634.7012 | 1252518.8138
99 | 2674619.2915 | 1252551.2737 | 2674601.2675 | 1252548.1958
100 | 2674665.5837 | 1252482.5132 | 2674665.5927 | 1252486.583 | 2674655.4095 | 1252486.647
101 | 2674665.5837 | 1252482.5132 | 2674665.5538 | 1252463.5268
102 | 2674572.6489 | 1252542.6515 | 2674589.0348 | 1252546.1069 | 2674601.2675 | 1252548.1958
103 | 2674665.5538 | 1252463.5268 | 2674665.5443 | 1252457.5056 | 2674663.4312 | 1252457.5012
104 | 2674645.5844 | 1252486.7088 | 2674655.4095 | 1252486.647
105 | 2674618.6708 | 1252431.1292 | 2674632.5034 | 1252434.156
106 | 2674618.6708 | 1252431.1292 | 2674583.1919 | 1252422.8133
107 | 2674618.6708 | 1252431.1292 | 2674615.1002 | 1252452.6525
108 | 2674575.0049 | 1252420.8943 | 2674583.1919 | 1252422.8133
109 | 2674615.0944 | 1252452.6875 | 2674615.1002 | 1252452.6525
110 | 2674611.35 | 1252475.258 | 2674615.0944 | 1252452.6875
111 | 2674611.3249 | 1252475.4095 | 2674611.35 | 1252475.258
112 | 2674609.6951 | 1252485.2335 | 2674611.3249 | 1252475.4095
113 | 2674575.0049 | 1252420.8943 | 2674542.3469 | 1252413.8894
114 | 2674575.0049 | 1252420.8943 | 2674570.1814 | 1252440.4075
115 | 2674609.6951 | 1252485.2335 | 2674617.8861 | 1252486.8156 | 2674615.0269 | 1252504.2267
116 | 2674609.6951 | 1252485.2335 | 2674601.5212 | 1252484.0854 | 2674598.5892 | 1252500.4555
117 | 2674542.3469 | 1252413.8894 | 2674540.2631 | 1252413.4185
118 | 2674542.3469 | 1252413.8894 | 2674538.1821 | 1252405.6965
119 | 2674570.1814 | 1252440.4075 | 2674569.8264 | 1252441.8438
120 | 2674615.0269 | 1252504.2267 | 2674615.0204 | 1252504.2661
121 | 2674598.5892 | 1252500.4555 | 2674598.4084 | 1252501.465
122 | 2674513.0124 | 1252407.2601 | 2674540.2631 | 1252413.4185
123 | 2674569.8264 | 1252441.8438 | 2674564.497 | 1252463.4031
124 | 2674506.0088 | 1252518.8314 | 2674506.0088 | 1252518.8314 | 2674523.7492 | 1252526.8309
125 | 2674506.0088 | 1252518.8314 | 2674487.305 | 1252516.0498 | 2674480.8807 | 1252515.8534
126 | 2674543.8935 | 1252534.5778 | 2674533.1515 | 1252531.0705 | 2674523.7492 | 1252526.8309
127 | 2674480.8807 | 1252515.8534 | 2674467.8007 | 1252515.4537
128 | 2674543.8935 | 1252534.5778 | 2674561.276 | 1252540.2533 | 2674572.6489 | 1252542.6515
129 | 2674444.6517 | 1252514.7462 | 2674467.8007 | 1252515.4537
130 | 2674444.6517 | 1252514.7462 | 2674449.9378 | 1252480.2652 | 2674452.605 | 1252466.2106 | 2674453.9842 | 1252463.4452
131 | 2674563.9342 | 1252465.6801 | 2674564.497 | 1252463.4031
132 | 2674563.9342 | 1252465.6801 | 2674561.4388 | 1252475.7748 | 2674561.4388 | 1252475.7748
133 | 2674554.2079 | 1252474.1943 | 2674561.4388 | 1252475.7748
134 | 2674513.0124 | 1252407.2601 | 2674509.1859 | 1252412.6715 | 2674504.462 | 1252415.3843
135 | 2674554.2079 | 1252474.1943 | 2674528.6413 | 1252468.6058
136 | 2674527.7704 | 1252468.4155 | 2674528.6413 | 1252468.6058
137 | 2674508.731 | 1252464.2538 | 2674527.7704 | 1252468.4155
138 | 2674507.8947 | 1252464.071 | 2674508.731 | 1252464.2538
139 | 2674702.5867 | 1252192.1397 | 2674692.7878 | 1252175.8227
140 | 2674762.8702 | 1252298.4237 | 2674702.5867 | 1252192.1397

## bus_geodata
| x | y | coords
0 | 2674911.1192 | 1252423.3417
1 | 2674910.1139 | 1252416.4624
2 | 2674911.8229 | 1252428.1566
3 | 2674909.3162 | 1252411.0035
4 | 2674915.3546 | 1252458.6591
5 | 2674907.5007 | 1252380.903
6 | 2674896.0852 | 1252416.9042
7 | 2674934.2351 | 1252466.3285
8 | 2674921.1236 | 1252471.5304
9 | 2674897.8989 | 1252360.5857
10 | 2674930.0304 | 1252372.5788
11 | 2674838.2551 | 1252433.6111
12 | 2674835.5412 | 1252427.5595
13 | 2674828.9163 | 1252424.909
14 | 2674836.482 | 1252440.7384
15 | 2674948.8894 | 1252474.2494
16 | 2674902.8141 | 1252465.0275
17 | 2674859.5132 | 1252456.0995
18 | 2674815.0804 | 1252442.9301
19 | 2674833.8922 | 1252452.7811
20 | 2674984.3571 | 1252494.3246
21 | 2675000.4933 | 1252516.8898
22 | 2674998.6459 | 1252480.4166
23 | 2674928.1085 | 1252474.3801
24 | 2674920.1782 | 1252472.8861
25 | 2674888.066 | 1252339.7798
26 | 2674953.6055 | 1252363.0438
27 | 2674821.9485 | 1252398.3378
28 | 2674818.7552 | 1252412.4455
29 | 2674911.3114 | 1252506.2335
30 | 2674799.2151 | 1252443.1474
31 | 2674831.7699 | 1252462.6479
32 | 2675023.3952 | 1252554.6296
33 | 2674983.7563 | 1252505.7224
34 | 2675001.9359 | 1252478.4235
35 | 2674940.6884 | 1252479.9504
36 | 2674882.1062 | 1252327.169
37 | 2674971.0067 | 1252355.1129
38 | 2674976.4692 | 1252352.6234
39 | 2675002.8875 | 1252340.5579
40 | 2674997.9705 | 1252573.0657
41 | 2674982.8108 | 1252505.0721
42 | 2674821.7559 | 1252397.9261
43 | 2674792.36 | 1252355.863
44 | 2674798.2065 | 1252347.5926
45 | 2674810.2671 | 1252373.3706
46 | 2674926.971 | 1252602.4137
47 | 2674920.1737 | 1252600.4314
48 | 2674935.1197 | 1252604.7901
49 | 2674899.2091 | 1252594.2138
50 | 2674945.8651 | 1252607.9238
51 | 2674893.7411 | 1252592.5566
52 | 2674946.3458 | 1252608.064
53 | 2674885.4464 | 1252590.0427
54 | 2674878.5211 | 1252587.9438
55 | 2674967.9032 | 1252494.8184
56 | 2674976.6596 | 1252500.8412
57 | 2674863.9052 | 1252583.1446
58 | 2674901.0569 | 1252546.0757
59 | 2674841.8227 | 1252575.8936
60 | 2674906.3572 | 1252525.4821
61 | 2674781.9144 | 1252567.698
62 | 2674836.9244 | 1252592.8744
63 | 2674795.422 | 1252563.0678
64 | 2674770.7575 | 1252564.933
65 | 2674830.6143 | 1252614.7498
66 | 2674871.0158 | 1252640.8299
67 | 2674903.889 | 1252653.7031
68 | 2674849.3977 | 1252634.556
69 | 2674928.6545 | 1252663.8795
70 | 2674826.3455 | 1252629.5486
71 | 2674773.0007 | 1252537.2966
72 | 2674824.0155 | 1252505.9246
73 | 2674824.9169 | 1252500.3031
74 | 2674771.7958 | 1252510.7953
75 | 2674827.6642 | 1252483.17
76 | 2674811.8826 | 1252451.1317
77 | 2674798.3454 | 1252450.464
78 | 2674794.7309 | 1252443.2086
79 | 2674757.056 | 1252442.9964
80 | 2674745.9008 | 1252473.2745
81 | 2674725.2098 | 1252481.7241
82 | 2674735.0105 | 1252442.2611
83 | 2674671.3695 | 1252482.7196
84 | 2674682.9003 | 1252441.4903
85 | 2674709.4963 | 1252441.7613
86 | 2674677.8847 | 1252441.0127
87 | 2674713.3465 | 1252441.7597
88 | 2674670.1494 | 1252440.2761
89 | 2674734.6855 | 1252442.2502
90 | 2674663.5205 | 1252439.6448
91 | 2674667.7345 | 1252553.7369
92 | 2674667.565 | 1252525.881
93 | 2674644.2036 | 1252554.0255
94 | 2674641.5117 | 1252520.2784
95 | 2674619.2915 | 1252551.2737
96 | 2674634.7012 | 1252518.8138
97 | 2674665.5837 | 1252482.5132
98 | 2674601.2675 | 1252548.1958
99 | 2674665.5538 | 1252463.5268
100 | 2674663.4312 | 1252457.5012
101 | 2674655.4095 | 1252486.647
102 | 2674632.5034 | 1252434.156
103 | 2674645.5844 | 1252486.7088
104 | 2674618.6708 | 1252431.1292
105 | 2674583.1919 | 1252422.8133
106 | 2674615.1002 | 1252452.6525
107 | 2674615.0944 | 1252452.6875
108 | 2674611.35 | 1252475.258
109 | 2674611.3249 | 1252475.4095
110 | 2674575.0049 | 1252420.8943
111 | 2674609.6951 | 1252485.2335
112 | 2674542.3469 | 1252413.8894
113 | 2674570.1814 | 1252440.4075
114 | 2674615.0269 | 1252504.2267
115 | 2674598.5892 | 1252500.4555
116 | 2674540.2631 | 1252413.4185
117 | 2674538.1821 | 1252405.6965
118 | 2674569.8264 | 1252441.8438
119 | 2674506.0088 | 1252518.8314
120 | 2674523.7492 | 1252526.8309
121 | 2674480.8807 | 1252515.8534
122 | 2674543.8935 | 1252534.5778
123 | 2674467.8007 | 1252515.4537
124 | 2674572.6489 | 1252542.6515
125 | 2674444.6517 | 1252514.7462
126 | 2674453.9842 | 1252463.4452
127 | 2674564.497 | 1252463.4031
128 | 2674563.9342 | 1252465.6801
129 | 2674561.4388 | 1252475.7748
130 | 2674513.0124 | 1252407.2601
131 | 2674554.2079 | 1252474.1943
132 | 2674504.462 | 1252415.3843
133 | 2674528.6413 | 1252468.6058
134 | 2674527.7704 | 1252468.4155
135 | 2674508.731 | 1252464.2538
136 | 2674615.0204 | 1252504.2661
137 | 2674598.4084 | 1252501.465
138 | 2674692.7878 | 1252175.8227
139 | 2674702.5867 | 1252192.1397
140 | 2674762.8702 | 1252298.4237
141 | 2674507.8947 | 1252464.071
142 | 2674770.7575 | 1252564.933

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98161 | -0.35224 | 0.001986 | 0.00049773
1 | 0.9815 | -0.35456 | 0.0024491 | 0.0006138
2 | 0.98171 | -0.35045 | 0.0012594 | 0.00031564
3 | 0.98141 | -0.35614 | 0 | 0
4 | 0.98232 | -0.33842 | 0 | 0
5 | 0.98106 | -0.36312 | 0 | 0
6 | 0.98137 | -0.35697 | 0.0031523 | 0.00079004
7 | 0.9822 | -0.3408 | 0.004951 | 0.0012408
8 | 0.98284 | -0.32831 | 0 | 0
9 | 0.98103 | -0.36372 | 0.00069132 | 0.00017326
10 | 0.98081 | -0.36803 | 0.0010685 | 0.00026779
11 | 0.97912 | -0.40068 | 0 | 0
12 | 0.97909 | -0.40132 | 0.0020605 | 0.00051642
13 | 0.97905 | -0.40216 | 0 | 0
14 | 0.97925 | -0.39814 | 0 | 0
15 | 0.98218 | -0.34126 | 0.0015313 | 0.00038377
16 | 0.98214 | -0.34188 | 0 | 0
17 | 0.98054 | -0.37295 | 0.0057459 | 0.00144
18 | 0.97862 | -0.41053 | 0.0025041 | 0.00062758
19 | 0.97964 | -0.39045 | 0 | 0
20 | 0.98094 | -0.36543 | 0 | 0
21 | 0.98133 | -0.35788 | 0 | 0
22 | 0.98073 | -0.36965 | 0.0065832 | 0.0016499
23 | 0.98267 | -0.33155 | 0.00066548 | 0.00016679
24 | 0.98292 | -0.32677 | 0 | 0
25 | 0.98101 | -0.36405 | 0.00020317 | 5.0919e-05
26 | 0.98057 | -0.37274 | 0.00076821 | 0.00019253
27 | 0.97899 | -0.40326 | 0.00038153 | 9.562e-05
28 | 0.97897 | -0.40375 | 0.001107 | 0.00027745
29 | 0.98458 | -0.29461 | 0.0024643 | 0.00061762
30 | 0.97816 | -0.41948 | 0 | 0
31 | 0.97953 | -0.39266 | 0.00081813 | 0.00020504
32 | 0.98123 | -0.35968 | 0 | 0
33 | 0.98157 | -0.35302 | 0.0010913 | 0.00027352
34 | 0.98071 | -0.37 | 0.0050241 | 0.0012592
35 | 0.98238 | -0.33729 | 0.0049142 | 0.0012316
36 | 0.981 | -0.3642 | 0.00058745 | 0.00014723
37 | 0.9804 | -0.37601 | 0.0010963 | 0.00027477
38 | 0.98035 | -0.37692 | 0.0020685 | 0.00051841
39 | 0.98019 | -0.38023 | 0.0062815 | 0.0015743
40 | 0.98118 | -0.36078 | 0.0017289 | 0.00043329
41 | 0.98159 | -0.35272 | 0.00098805 | 0.00024763
42 | 0.97899 | -0.40328 | 0.0004023 | 0.00010083
43 | 0.97872 | -0.40862 | 0.0014264 | 0.00035748
44 | 0.97892 | -0.40473 | 0.00039776 | 9.9689e-05
45 | 0.97893 | -0.40452 | 0.0021188 | 0.00053101
46 | 0.98824 | -0.2241 | 0.0019637 | 0.00049215
47 | 0.98829 | -0.22322 | 0.0046549 | 0.0011666
48 | 0.9882 | -0.22485 | 0.00086093 | 0.00021577
49 | 0.98852 | -0.2187 | 0.0055964 | 0.0014026
50 | 0.98816 | -0.22567 | 0.0024808 | 0.00062176
51 | 0.98861 | -0.21695 | 0.0033369 | 0.0008363
52 | 0.98816 | -0.22568 | 0.0016203 | 0.00040608
53 | 0.98877 | -0.21378 | 0.0036649 | 0.00091852
54 | 0.98893 | -0.21066 | 0 | 0
55 | 0.98186 | -0.34749 | 0.0017692 | 0.0004434
56 | 0.9817 | -0.35064 | 0.00099357 | 0.00024901
57 | 0.98978 | -0.19445 | 0.0019604 | 0.00049133
58 | 0.98658 | -0.25582 | 0.0017209 | 0.00043131
59 | 0.99106 | -0.16979 | 0 | 0
60 | 0.98554 | -0.27592 | 0.0014425 | 0.00036152
61 | 0.9948 | -0.098545 | 0 | 0
62 | 0.99061 | -0.17856 | 0.0019488 | 0.00048843
63 | 0.99449 | -0.10458 | 0.023984 | 0.0060108
64 | 0.99557 | -0.083884 | 0 | 0
65 | 0.99007 | -0.18907 | 0.0060092 | 0.001506
66 | 0.98902 | -0.20938 | 0.0088243 | 0.0022116
67 | 0.98879 | -0.21392 | 0.0041898 | 0.0010501
68 | 0.98936 | -0.20294 | 0.0039362 | 0.0009865
69 | 0.98872 | -0.21536 | 0.0030238 | 0.00075784
70 | 0.98979 | -0.19455 | 0 | 0
71 | 0.99744 | -0.048514 | 0.064095 | 0.016064
72 | 0.97912 | -0.4007 | 0.0051068 | 0.0012799
73 | 0.97915 | -0.40017 | 0.0051388 | 0.0012879
74 | 1 | 0 | -0.36182 | -0.092352
75 | 0.97931 | -0.39694 | 0.00099379 | 0.00024907
76 | 0.97812 | -0.42017 | 0.0017928 | 0.00044931
77 | 0.97815 | -0.41973 | 0 | 0
78 | 0.97803 | -0.42198 | 0.0023059 | 0.00057792
79 | 0.97698 | -0.44259 | 0.000837 | 0.00020977
80 | 0.9732 | -0.51701 | 0.0062105 | 0.0015565
81 | 0.97334 | -0.5141 | 0.0066623 | 0.0016697
82 | 0.97637 | -0.45459 | 0.00063104 | 0.00015815
83 | 0.97401 | -0.501 | 0 | 0
84 | 0.97495 | -0.4824 | 0 | 0
85 | 0.97567 | -0.46832 | 0.00143 | 0.00035839
86 | 0.97482 | -0.48507 | 0.0045306 | 0.0011355
87 | 0.97577 | -0.46626 | 0.00078442 | 0.00019659
88 | 0.97462 | -0.48903 | 0.0037497 | 0.00093975
89 | 0.97636 | -0.45477 | 0.00072462 | 0.00018161
90 | 0.97445 | -0.4923 | 0 | 0
91 | 0.9737 | -0.50703 | 0 | 0
92 | 0.97381 | -0.50484 | 0 | 0
93 | 0.97333 | -0.51442 | 0.0016058 | 0.00040244
94 | 0.97376 | -0.50594 | 0.0012631 | 0.00031656
95 | 0.97296 | -0.52159 | 0.0019408 | 0.00048641
96 | 0.97375 | -0.50606 | 0.00097135 | 0.00024344
97 | 0.97405 | -0.50014 | 0 | 0
98 | 0.97273 | -0.52615 | 0.0026925 | 0.00067481
99 | 0.97421 | -0.49702 | 0.0024203 | 0.00060659
100 | 0.97428 | -0.49559 | 0.0018385 | 0.00046077
101 | 0.974 | -0.5011 | 0.0018087 | 0.0004533
102 | 0.97396 | -0.50201 | 0.0059651 | 0.001495
103 | 0.97399 | -0.50143 | 0.0018347 | 0.00045983
104 | 0.97375 | -0.50599 | 0 | 0
105 | 0.97338 | -0.51342 | 0.012922 | 0.0032385
106 | 0.97341 | -0.51272 | 0.0029004 | 0.00072692
107 | 0.97341 | -0.51273 | 0.0029713 | 0.00074468
108 | 0.97318 | -0.51732 | 0.0029179 | 0.00073129
109 | 0.97318 | -0.51734 | 0.0028942 | 0.00072537
110 | 0.97313 | -0.51828 | 0 | 0
111 | 0.97313 | -0.51827 | 0 | 0
112 | 0.97294 | -0.52212 | 0 | 0
113 | 0.97266 | -0.5276 | 0.0022865 | 0.00057305
114 | 0.97308 | -0.51932 | 0.0011086 | 0.00027785
115 | 0.97307 | -0.51961 | 0.0018355 | 0.00046002
116 | 0.97293 | -0.5223 | 0.0022371 | 0.00056067
117 | 0.97292 | -0.52242 | 0.0017839 | 0.0004471
118 | 0.97263 | -0.52822 | 0.0024604 | 0.00061664
119 | 0.9719 | -0.54259 | 0.0010263 | 0.00025722
120 | 0.97202 | -0.54018 | 0.0010627 | 0.00026633
121 | 0.97177 | -0.54525 | 0.0012146 | 0.0003044
122 | 0.97218 | -0.53708 | 0.0014901 | 0.00037345
123 | 0.97171 | -0.54632 | 0.0011734 | 0.00029408
124 | 0.97244 | -0.53197 | 0.0015747 | 0.00039465
125 | 0.97164 | -0.54773 | 0 | 0
126 | 0.97148 | -0.55091 | 0.003293 | 0.00082531
127 | 0.9722 | -0.53659 | 0.0028491 | 0.00071406
128 | 0.97217 | -0.53735 | 0.0021022 | 0.00052686
129 | 0.97202 | -0.54032 | 0.0027764 | 0.00069583
130 | 0.97287 | -0.52345 | 0 | 0
131 | 0.97193 | -0.54205 | 0.0024553 | 0.00061537
132 | 0.97285 | -0.52395 | 0.0022371 | 0.00056067
133 | 0.97168 | -0.547 | 0.0021231 | 0.00053211
134 | 0.97167 | -0.54713 | 0.0030465 | 0.00076353
135 | 0.97158 | -0.54896 | 0.0025269 | 0.00063331
136 | 0.97308 | -0.51932 | 0.0010713 | 0.00026849
137 | 0.97306 | -0.51963 | 0.0010762 | 0.00026973
138 | 0.97838 | -0.41518 | 0.0004516 | 0.00011318
139 | 0.97839 | -0.41503 | 0.00091053 | 0.0002282
140 | 0.97855 | -0.41199 | 0.0014973 | 0.00037526
141 | 0.97158 | -0.549 | 0.0025465 | 0.00063823
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.018382 | 0.0046101 | -0.01838 | -0.0046089 | 2.0245e-06 | 1.2078e-06 | 0.027866 | 0.027866 | 0.027866 | 0.98161 | -0.35224 | 0.9815 | -0.35456 | 7.6555
1 | -0.020368 | -0.0051079 | 0.020369 | 0.0051089 | 1.7397e-06 | 1.0519e-06 | 0.030876 | 0.030876 | 0.030876 | 0.98161 | -0.35224 | 0.98171 | -0.35045 | 8.4825
2 | 0.015931 | 0.0039951 | -0.015929 | -0.0039944 | 1.2069e-06 | 7.0268e-07 | 0.024153 | 0.024153 | 0.024153 | 0.9815 | -0.35456 | 0.98141 | -0.35614 | 6.6354
3 | -0.021629 | -0.0054246 | 0.021641 | 0.0054321 | 1.2417e-05 | 7.5569e-06 | 0.032785 | 0.032785 | 0.032785 | 0.98171 | -0.35045 | 0.98232 | -0.33842 | 9.0069
4 | 0.012777 | 0.0032045 | -0.012773 | -0.0032021 | 4.2447e-06 | 2.3356e-06 | 0.019373 | 0.019373 | 0.019373 | 0.98141 | -0.35614 | 0.98106 | -0.36312 | 5.3224
5 | 0.0031524 | 0.00078994 | -0.0031523 | -0.00079004 | 1.2411e-07 | -1.0362e-07 | 0.0047796 | 0.0047797 | 0.0047797 | 0.98141 | -0.35614 | 0.98137 | -0.35697 | 1.3131
6 | 0.006483 | 0.0016246 | -0.0064823 | -0.0016244 | 7.3701e-07 | 2.1373e-07 | 0.0098204 | 0.0098205 | 0.0098205 | 0.98232 | -0.33842 | 0.9822 | -0.3408 | 2.6979
7 | -0.028124 | -0.0070567 | 0.028138 | 0.0070652 | 1.3554e-05 | 8.4223e-06 | 0.042606 | 0.042605 | 0.042606 | 0.98232 | -0.33842 | 0.98284 | -0.32831 | 11.7048
8 | 0.001482 | 0.0003707 | -0.001482 | -0.00037095 | 4.2571e-08 | -2.565e-07 | 0.0022476 | 0.0022477 | 0.0022477 | 0.98106 | -0.36312 | 0.98103 | -0.36372 | 0.61749
9 | 0.011291 | 0.0028315 | -0.011288 | -0.0028301 | 2.6417e-06 | 1.3875e-06 | 0.017126 | 0.017126 | 0.017126 | 0.98106 | -0.36312 | 0.98081 | -0.36803 | 4.7049
10 | 0.0015313 | 0.00038358 | -0.0015313 | -0.00038377 | 3.3655e-08 | -1.8951e-07 | 0.0023198 | 0.0023199 | 0.0023199 | 0.9822 | -0.3408 | 0.98218 | -0.34126 | 0.63734
11 | 0.023791 | 0.0059723 | -0.023787 | -0.0059701 | 3.671e-06 | 2.2539e-06 | 0.036023 | 0.036023 | 0.036023 | 0.98284 | -0.32831 | 0.98267 | -0.33155 | 9.8965
12 | -0.20817 | -0.052628 | 0.20818 | 0.052638 | 1.539e-05 | 9.7661e-06 | 0.31533 | 0.31533 | 0.31533 | 0.98284 | -0.32831 | 0.98292 | -0.32677 | 21.6572
13 | 0.15624 | 0.039591 | -0.15614 | -0.039527 | 0.00010179 | 6.4167e-05 | 0.2367 | 0.2367 | 0.2367 | 0.98284 | -0.32831 | 0.98214 | -0.34188 | 16.2569
14 | 0.00079063 | 0.00019769 | -0.00079062 | -0.00019797 | 1.2408e-08 | -2.8261e-07 | 0.0011991 | 0.0011992 | 0.0011992 | 0.98103 | -0.36372 | 0.98101 | -0.36405 | 0.32944
15 | 0.01022 | 0.0025623 | -0.010217 | -0.0025611 | 2.2941e-06 | 1.1471e-06 | 0.015505 | 0.015505 | 0.015505 | 0.98081 | -0.36803 | 0.98057 | -0.37274 | 4.2596
16 | 0.0053615 | 0.0013428 | -0.0053613 | -0.0013427 | 1.6511e-07 | 2.2258e-08 | 0.0081478 | 0.0081478 | 0.0081478 | 0.97912 | -0.40068 | 0.97909 | -0.40132 | 2.2384
17 | 0.0053953 | 0.0013494 | -0.0053949 | -0.0013493 | 3.8061e-07 | 5.3687e-08 | 0.0081984 | 0.0081985 | 0.0081985 | 0.97912 | -0.40068 | 0.97905 | -0.40216 | 2.2523
18 | -0.010757 | -0.0026921 | 0.010758 | 0.0026928 | 1.3012e-06 | 6.694e-07 | 0.016346 | 0.016346 | 0.016346 | 0.97912 | -0.40068 | 0.97925 | -0.39814 | 4.4907
19 | 0.0033008 | 0.00082633 | -0.0033005 | -0.00082654 | 3.0412e-07 | -2.1064e-07 | 0.0050162 | 0.0050164 | 0.0050164 | 0.97909 | -0.40132 | 0.97899 | -0.40326 | 1.3781
20 | 0.0053949 | 0.0013493 | -0.0053945 | -0.0013493 | 4.0709e-07 | 5.7457e-08 | 0.0081985 | 0.0081986 | 0.0081986 | 0.97905 | -0.40216 | 0.97897 | -0.40375 | 2.2524
21 | 0.12716 | 0.032111 | -0.12709 | -0.032064 | 7.5452e-05 | 4.7206e-05 | 0.19331 | 0.19331 | 0.19331 | 0.97925 | -0.39814 | 0.97862 | -0.41053 | 13.2771
22 | -0.13792 | -0.034804 | 0.13797 | 0.034836 | 5.0762e-05 | 3.1868e-05 | 0.20966 | 0.20966 | 0.20966 | 0.97925 | -0.39814 | 0.97964 | -0.39045 | 14.3997
23 | 0.15614 | 0.039527 | -0.1559 | -0.03938 | 0.00023248 | 0.00014655 | 0.2367 | 0.2367 | 0.2367 | 0.98214 | -0.34188 | 0.98054 | -0.37295 | 16.257
24 | 0.15016 | 0.03794 | -0.15003 | -0.037861 | 0.00012589 | 7.9266e-05 | 0.22798 | 0.22798 | 0.22798 | 0.98054 | -0.37295 | 0.97964 | -0.39045 | 15.6582
25 | 0.12458 | 0.031437 | -0.12453 | -0.031403 | 5.3421e-05 | 3.3392e-05 | 0.18951 | 0.18951 | 0.18951 | 0.97862 | -0.41053 | 0.97816 | -0.41948 | 13.0156
26 | 0.012063 | 0.0030246 | -0.012062 | -0.0030239 | 1.2707e-06 | 6.8617e-07 | 0.018323 | 0.018323 | 0.018323 | 0.97964 | -0.39045 | 0.97953 | -0.39266 | 5.0338
27 | -0.01161 | -0.0029103 | 0.011614 | 0.0029125 | 4.1795e-06 | 2.2211e-06 | 0.017611 | 0.017611 | 0.017611 | 0.98094 | -0.36543 | 0.98133 | -0.35788 | 4.8383
28 | 0.01161 | 0.0029103 | -0.011607 | -0.0029091 | 2.3312e-06 | 1.239e-06 | 0.017611 | 0.017611 | 0.017611 | 0.98094 | -0.36543 | 0.98073 | -0.36965 | 4.8383
29 | 0.0017291 | 0.00043228 | -0.001729 | -0.00043291 | 1.4824e-07 | -6.3171e-07 | 0.0026215 | 0.0026218 | 0.0026218 | 0.98133 | -0.35788 | 0.98123 | -0.35968 | 0.72027
30 | -0.013343 | -0.0033448 | 0.013346 | 0.0033465 | 3.0887e-06 | 1.7225e-06 | 0.020233 | 0.020233 | 0.020233 | 0.98133 | -0.35788 | 0.98157 | -0.35302 | 5.5584
31 | 0.0050242 | 0.0012592 | -0.0050241 | -0.0012592 | 8.3824e-08 | 5.1086e-09 | 0.0076229 | 0.007623 | 0.007623 | 0.98073 | -0.36965 | 0.98071 | -0.37 | 2.0942
32 | 0.023122 | 0.0058033 | -0.023116 | -0.0057994 | 6.3269e-06 | 3.8749e-06 | 0.035015 | 0.035015 | 0.035015 | 0.98267 | -0.33155 | 0.98238 | -0.33729 | 9.6196
33 | -0.20818 | -0.052638 | 0.2085 | 0.052842 | 0.00032166 | 0.00020411 | 0.31533 | 0.31533 | 0.31533 | 0.98292 | -0.32677 | 0.98458 | -0.29461 | 21.6572
34 | 0.00058745 | 0.00014705 | -0.00058745 | -0.00014723 | 4.1527e-09 | -1.7345e-07 | 0.00089099 | 0.00089106 | 0.00089106 | 0.98101 | -0.36405 | 0.981 | -0.3642 | 0.2448
35 | 0.0094492 | 0.0023686 | -0.0094477 | -0.0023679 | 1.4745e-06 | 7.0251e-07 | 0.014339 | 0.014339 | 0.014339 | 0.98057 | -0.37274 | 0.9804 | -0.37601 | 3.9394
36 | 0.002919 | 0.00073092 | -0.002919 | -0.00073093 | 3.3551e-09 | -3.5682e-09 | 0.0044365 | 0.0044365 | 0.0044365 | 0.97899 | -0.40326 | 0.97899 | -0.40328 | 1.2188
37 | 0.0042875 | 0.0010718 | -0.0042865 | -0.001072 | 9.9414e-07 | -1.4859e-07 | 0.0065159 | 0.0065162 | 0.0065162 | 0.97897 | -0.40375 | 0.97872 | -0.40862 | 1.7902
38 | -0.21097 | -0.05346 | 0.21116 | 0.05358 | 0.00018968 | 0.00012038 | 0.31905 | 0.31905 | 0.31905 | 0.98458 | -0.29461 | 0.98554 | -0.27592 | 21.913
39 | 0.12274 | 0.030954 | -0.12272 | -0.030945 | 1.4667e-05 | 9.162e-06 | 0.18678 | 0.18678 | 0.18678 | 0.97816 | -0.41948 | 0.97803 | -0.42198 | 12.8283
40 | 0.0017928 | 0.00044909 | -0.0017928 | -0.00044917 | 2.0554e-08 | -7.9343e-08 | 0.0027273 | 0.0027273 | 0.0027273 | 0.97816 | -0.41948 | 0.97815 | -0.41973 | 0.74925
41 | 0.011243 | 0.0028189 | -0.011241 | -0.0028177 | 2.2903e-06 | 1.2023e-06 | 0.01708 | 0.01708 | 0.01708 | 0.97953 | -0.39266 | 0.97931 | -0.39694 | 4.6924
42 | 0.001729 | 0.00043291 | -0.0017289 | -0.00043329 | 9.0266e-08 | -3.8452e-07 | 0.0026218 | 0.0026219 | 0.0026219 | 0.98123 | -0.35968 | 0.98118 | -0.36078 | 0.72031
43 | -0.014437 | -0.00362 | 0.014438 | 0.0036202 | 2.0615e-07 | 1.1743e-07 | 0.021887 | 0.021887 | 0.021887 | 0.98157 | -0.35302 | 0.98159 | -0.35272 | 6.0129
44 | 0.018201 | 0.0045678 | -0.018192 | -0.0045625 | 8.8477e-06 | 5.2698e-06 | 0.027572 | 0.027572 | 0.027572 | 0.98238 | -0.33729 | 0.98186 | -0.34749 | 7.5747
45 | 0.0083513 | 0.0020931 | -0.008351 | -0.002093 | 3.6168e-07 | 1.5578e-07 | 0.012675 | 0.012675 | 0.012675 | 0.9804 | -0.37601 | 0.98035 | -0.37692 | 3.4823
46 | 0.0062825 | 0.0015746 | -0.0062815 | -0.0015743 | 9.9036e-07 | 2.6769e-07 | 0.0095358 | 0.0095359 | 0.0095359 | 0.98035 | -0.37692 | 0.98019 | -0.38023 | 2.6198
47 | -0.015426 | -0.0038678 | 0.015427 | 0.0038687 | 1.531e-06 | 8.8545e-07 | 0.023385 | 0.023385 | 0.023385 | 0.98159 | -0.35272 | 0.9817 | -0.35064 | 6.4244
48 | 0.0025167 | 0.0006301 | -0.0025165 | -0.00063035 | 1.4875e-07 | -2.4566e-07 | 0.003825 | 0.0038251 | 0.0038251 | 0.97899 | -0.40328 | 0.97893 | -0.40452 | 1.0509
49 | 0.0028601 | 0.00071448 | -0.0028596 | -0.00071499 | 4.5774e-07 | -5.1841e-07 | 0.0043476 | 0.0043479 | 0.0043479 | 0.97872 | -0.40862 | 0.97855 | -0.41199 | 1.1945
50 | -0.00039776 | -9.9689e-05 | 0.00039777 | 9.9334e-05 | 3.9008e-09 | -3.553e-07 | 0.00060463 | 0.0006045 | 0.00060463 | 0.97892 | -0.40473 | 0.97893 | -0.40452 | 0.16611
51 | -0.0069261 | -0.0017357 | 0.0069264 | 0.0017358 | 2.8877e-07 | 9.409e-08 | 0.010429 | 0.010429 | 0.010429 | 0.98824 | -0.2241 | 0.98829 | -0.22322 | 2.865
52 | 0.0049624 | 0.0012436 | -0.0049622 | -0.0012436 | 1.7771e-07 | 4.9839e-09 | 0.0074719 | 0.007472 | 0.007472 | 0.98824 | -0.2241 | 0.9882 | -0.22485 | 2.0527
53 | -0.011581 | -0.0029024 | 0.011584 | 0.0029037 | 2.4934e-06 | 1.3155e-06 | 0.017437 | 0.017437 | 0.017437 | 0.98829 | -0.22322 | 0.98852 | -0.2187 | 4.7905
54 | 0.0041013 | 0.0010278 | -0.0041011 | -0.0010278 | 1.6008e-07 | -4.0942e-08 | 0.0061756 | 0.0061757 | 0.0061757 | 0.9882 | -0.22485 | 0.98816 | -0.22567 | 1.6966
55 | -0.01718 | -0.0043063 | 0.017182 | 0.0043072 | 1.433e-06 | 8.4387e-07 | 0.025861 | 0.025861 | 0.025861 | 0.98852 | -0.2187 | 0.98861 | -0.21695 | 7.1048
56 | 0.0016203 | 0.00040607 | -0.0016203 | -0.00040608 | 1.1178e-09 | -5.6985e-09 | 0.0024399 | 0.0024399 | 0.0024399 | 0.98816 | -0.22567 | 0.98816 | -0.22568 | 0.6703
57 | -0.020518 | -0.0051435 | 0.020522 | 0.0051453 | 3.1001e-06 | 1.8729e-06 | 0.030884 | 0.030884 | 0.030884 | 0.98861 | -0.21695 | 0.98877 | -0.21378 | 8.4846
58 | -0.024186 | -0.0060639 | 0.02419 | 0.0060661 | 3.5953e-06 | 2.2082e-06 | 0.036399 | 0.036399 | 0.036399 | 0.98877 | -0.21378 | 0.98893 | -0.21066 | 9.9998
59 | -0.23919 | -0.060866 | 0.23937 | 0.060985 | 0.00018714 | 0.00011898 | 0.36022 | 0.36022 | 0.36022 | 0.98893 | -0.21066 | 0.98978 | -0.19445 | 24.7407
60 | 0.215 | 0.0548 | -0.21453 | -0.054504 | 0.00046744 | 0.00029673 | 0.32382 | 0.32383 | 0.32383 | 0.98893 | -0.21066 | 0.98658 | -0.25582 | 22.2408
61 | 0.016423 | 0.0041191 | -0.016421 | -0.0041177 | 2.4691e-06 | 1.4459e-06 | 0.024891 | 0.024891 | 0.024891 | 0.98186 | -0.34749 | 0.9817 | -0.35064 | 6.8381
62 | -0.24133 | -0.061477 | 0.24162 | 0.061659 | 0.00028739 | 0.00018274 | 0.36317 | 0.36317 | 0.36317 | 0.98978 | -0.19445 | 0.99106 | -0.16979 | 24.9431
63 | 0.21281 | 0.054072 | -0.2126 | -0.053942 | 0.00020571 | 0.00013057 | 0.32123 | 0.32123 | 0.32123 | 0.98658 | -0.25582 | 0.98554 | -0.27592 | 22.0625
64 | -0.2696 | -0.068686 | 0.27053 | 0.069279 | 0.00093023 | 0.00059222 | 0.40518 | 0.40518 | 0.40518 | 0.99106 | -0.16979 | 0.9948 | -0.098545 | 27.8283
65 | 0.027977 | 0.0070269 | -0.027965 | -0.0070196 | 1.1697e-05 | 7.2583e-06 | 0.042011 | 0.042011 | 0.042011 | 0.99106 | -0.16979 | 0.99061 | -0.17856 | 11.5414
66 | 0.02399 | 0.0060151 | -0.023984 | -0.0060108 | 6.8956e-06 | 4.2279e-06 | 0.035886 | 0.035886 | 0.035886 | 0.9948 | -0.098545 | 0.99449 | -0.10458 | 9.8587
67 | -0.29452 | -0.075294 | 0.29473 | 0.075427 | 0.00020904 | 0.00013319 | 0.44106 | 0.44106 | 0.44106 | 0.9948 | -0.098545 | 0.99557 | -0.083884 | 30.2929
68 | 0.026016 | 0.0065312 | -0.026003 | -0.0065232 | 1.3041e-05 | 8.0536e-06 | 0.039083 | 0.039083 | 0.039083 | 0.99061 | -0.17856 | 0.99007 | -0.18907 | 10.7372
69 | -0.29473 | -0.075427 | 0.29523 | 0.075749 | 0.00050569 | 0.00032219 | 0.44106 | 0.44106 | 0.44106 | 0.99557 | -0.083884 | 0.99744 | -0.048514 | 30.2929
70 | 0.019994 | 0.0050171 | -0.019989 | -0.005014 | 5.2162e-06 | 3.1404e-06 | 0.030052 | 0.030052 | 0.030052 | 0.99007 | -0.18907 | 0.98979 | -0.19455 | 8.256
71 | 0.0072154 | 0.0018082 | -0.0072138 | -0.0018077 | 1.5607e-06 | 5.4577e-07 | 0.010856 | 0.010856 | 0.010856 | 0.98902 | -0.20938 | 0.98879 | -0.21392 | 2.9824
72 | -0.01604 | -0.0040198 | 0.016045 | 0.0040227 | 4.92e-06 | 2.8596e-06 | 0.024132 | 0.024132 | 0.024132 | 0.98902 | -0.20938 | 0.98936 | -0.20294 | 6.6297
73 | 0.003024 | 0.00075763 | -0.0030238 | -0.00075784 | 2.0793e-07 | -2.1033e-07 | 0.0045507 | 0.0045508 | 0.0045508 | 0.98879 | -0.21392 | 0.98872 | -0.21536 | 1.2502
74 | -0.019981 | -0.0050092 | 0.019989 | 0.005014 | 7.997e-06 | 4.8147e-06 | 0.030052 | 0.030052 | 0.030052 | 0.98936 | -0.20294 | 0.98979 | -0.19455 | 8.2561
75 | -0.35933 | -0.091813 | 0.36017 | 0.092352 | 0.00084514 | 0.00053925 | 0.53668 | 0.53668 | 0.53668 | 0.99744 | -0.048514 | 1 | 0 | 36.86
76 | -0.0051068 | -0.0012799 | 0.005107 | 0.0012799 | 1.286e-07 | 1.0696e-08 | 0.0077611 | 0.007761 | 0.0077611 | 0.97912 | -0.4007 | 0.97915 | -0.40017 | 2.1322
77 | -0.010246 | -0.0025678 | 0.010247 | 0.0025686 | 1.5775e-06 | 7.9134e-07 | 0.015571 | 0.01557 | 0.015571 | 0.97915 | -0.40017 | 0.97931 | -0.39694 | 4.2776
78 | -0.0017928 | -0.00044931 | 0.0017928 | 0.00044917 | 3.7806e-08 | -1.4593e-07 | 0.0027273 | 0.0027273 | 0.0027273 | 0.97812 | -0.42017 | 0.97815 | -0.41973 | 0.74927
79 | 0.12041 | 0.030367 | -0.1203 | -0.030293 | 0.00011867 | 7.4059e-05 | 0.18327 | 0.18327 | 0.18327 | 0.97803 | -0.42198 | 0.97698 | -0.44259 | 12.5874
80 | 0.11946 | 0.030083 | -0.11939 | -0.030041 | 6.8496e-05 | 4.2733e-05 | 0.182 | 0.182 | 0.182 | 0.97698 | -0.44259 | 0.97637 | -0.45459 | 12.4998
81 | -0.0062105 | -0.0015565 | 0.0062113 | 0.0015567 | 8.5849e-07 | 2.3392e-07 | 0.0094958 | 0.0094957 | 0.0094958 | 0.9732 | -0.51701 | 0.97334 | -0.5141 | 2.6087
82 | -0.012874 | -0.0032265 | 0.012882 | 0.0032309 | 8.044e-06 | 4.4593e-06 | 0.019681 | 0.019681 | 0.019681 | 0.97334 | -0.5141 | 0.97401 | -0.501 | 5.4068
83 | 0.11876 | 0.029882 | -0.11876 | -0.029882 | 9.9912e-07 | 6.2317e-07 | 0.18104 | 0.18104 | 0.18104 | 0.97637 | -0.45459 | 0.97636 | -0.45477 | 12.4338
84 | -0.032218 | -0.0080808 | 0.03222 | 0.0080814 | 1.3111e-06 | 5.5173e-07 | 0.049223 | 0.049223 | 0.049223 | 0.97401 | -0.501 | 0.97405 | -0.50014 | 3.3807
85 | 0.019337 | 0.0048499 | -0.019333 | -0.0048498 | 3.5456e-06 | 1.1234e-07 | 0.029543 | 0.029543 | 0.029543 | 0.97401 | -0.501 | 0.97381 | -0.50484 | 2.0291
86 | -0.11567 | -0.029049 | 0.11574 | 0.029098 | 7.7762e-05 | 4.844e-05 | 0.17656 | 0.17655 | 0.17656 | 0.97495 | -0.4824 | 0.97567 | -0.46832 | 12.1261
87 | 0.11567 | 0.029049 | -0.11565 | -0.02904 | 1.4724e-05 | 9.1719e-06 | 0.17656 | 0.17656 | 0.17656 | 0.97495 | -0.4824 | 0.97482 | -0.48507 | 12.1261
88 | -0.11717 | -0.029456 | 0.11718 | 0.029463 | 1.1531e-05 | 7.1876e-06 | 0.17874 | 0.17874 | 0.17874 | 0.97567 | -0.46832 | 0.97577 | -0.46626 | 12.2758
89 | 0.11112 | 0.027905 | -0.1111 | -0.027892 | 2.0964e-05 | 1.3029e-05 | 0.16964 | 0.16964 | 0.16964 | 0.97482 | -0.48507 | 0.97462 | -0.48903 | 11.6511
90 | -0.11797 | -0.02966 | 0.11803 | 0.0297 | 6.4793e-05 | 4.04e-05 | 0.17993 | 0.17993 | 0.17993 | 0.97577 | -0.46626 | 0.97636 | -0.45477 | 12.358
91 | 0.10735 | 0.026952 | -0.10733 | -0.026941 | 1.6773e-05 | 1.0403e-05 | 0.16392 | 0.16392 | 0.16392 | 0.97462 | -0.48903 | 0.97445 | -0.4923 | 11.2579
92 | 0.067196 | 0.016873 | -0.067165 | -0.016854 | 3.1106e-05 | 1.8338e-05 | 0.10262 | 0.10262 | 0.10262 | 0.97445 | -0.4923 | 0.97396 | -0.50201 | 7.0483
93 | 0.040136 | 0.010069 | -0.04013 | -0.010065 | 6.2892e-06 | 3.1355e-06 | 0.061293 | 0.061293 | 0.061293 | 0.97445 | -0.4923 | 0.97428 | -0.49559 | 4.2097
94 | -0.017097 | -0.0042904 | 0.017099 | 0.0042902 | 1.7832e-06 | -2.4501e-07 | 0.02613 | 0.026129 | 0.02613 | 0.9737 | -0.50703 | 0.97381 | -0.50484 | 1.7946
95 | 0.017097 | 0.0042904 | -0.017091 | -0.0042868 | 6.0252e-06 | 3.5635e-06 | 0.02613 | 0.02613 | 0.02613 | 0.9737 | -0.50703 | 0.97333 | -0.51442 | 7.1785
96 | 0.0022345 | 0.00055966 | -0.0022344 | -0.00055992 | 1.165e-07 | -2.5696e-07 | 0.0034143 | 0.0034144 | 0.0034144 | 0.97381 | -0.50484 | 0.97376 | -0.50594 | 0.93803
97 | 0.015485 | 0.0038844 | -0.01548 | -0.0038813 | 5.2872e-06 | 3.0713e-06 | 0.023675 | 0.023675 | 0.023675 | 0.97333 | -0.51442 | 0.97296 | -0.52159 | 6.5041
98 | 0.00097135 | 0.00024336 | -0.00097135 | -0.00024344 | 5.7555e-09 | -8.2974e-08 | 0.0014843 | 0.0014843 | 0.0014843 | 0.97376 | -0.50594 | 0.97375 | -0.50606 | 0.40779
99 | 0.013539 | 0.0033949 | -0.013536 | -0.0033933 | 2.94e-06 | 1.6546e-06 | 0.020707 | 0.020707 | 0.020707 | 0.97296 | -0.52159 | 0.97273 | -0.52615 | 5.6887
100 | 0.0036436 | 0.00091295 | -0.0036434 | -0.00091302 | 1.656e-07 | -7.1423e-08 | 0.0055661 | 0.0055662 | 0.0055662 | 0.97405 | -0.50014 | 0.974 | -0.5011 | 1.5292
101 | -0.035863 | -0.0089943 | 0.035869 | 0.0089968 | 5.3432e-06 | 2.4742e-06 | 0.054789 | 0.054789 | 0.054789 | 0.97405 | -0.50014 | 0.97421 | -0.49702 | 3.763
102 | 0.010844 | 0.0027184 | -0.010841 | -0.0027169 | 3.0085e-06 | 1.5636e-06 | 0.016588 | 0.016588 | 0.016588 | 0.97273 | -0.52615 | 0.97244 | -0.53197 | 4.5572
103 | -0.038289 | -0.0096034 | 0.038292 | 0.0096047 | 2.6085e-06 | 1.2643e-06 | 0.058486 | 0.058485 | 0.058486 | 0.97421 | -0.49702 | 0.97428 | -0.49559 | 4.0169
104 | 0.0018348 | 0.00045972 | -0.0018347 | -0.00045983 | 2.8948e-08 | -1.0376e-07 | 0.002803 | 0.002803 | 0.002803 | 0.974 | -0.5011 | 0.97399 | -0.50143 | 0.77006
105 | 0.0612 | 0.015359 | -0.061188 | -0.015353 | 1.1607e-05 | 6.7241e-06 | 0.093509 | 0.093509 | 0.093509 | 0.97396 | -0.50201 | 0.97375 | -0.50599 | 6.4223
106 | 0.044404 | 0.011144 | -0.044389 | -0.011136 | 1.5733e-05 | 8.2563e-06 | 0.067861 | 0.067862 | 0.067862 | 0.97375 | -0.50599 | 0.97338 | -0.51342 | 4.6608
107 | 0.016784 | 0.0042083 | -0.016778 | -0.0042052 | 5.3822e-06 | 3.1733e-06 | 0.025648 | 0.025649 | 0.025649 | 0.97375 | -0.50599 | 0.97341 | -0.51272 | 7.0463
108 | 0.031467 | 0.0078976 | -0.031459 | -0.007893 | 7.2979e-06 | 4.5662e-06 | 0.048108 | 0.048108 | 0.048108 | 0.97338 | -0.51342 | 0.97313 | -0.51828 | 13.2164
109 | 0.013878 | 0.0034782 | -0.013878 | -0.0034782 | 5.9918e-09 | 3.3941e-09 | 0.021215 | 0.021215 | 0.021215 | 0.97341 | -0.51272 | 0.97341 | -0.51273 | 5.8282
110 | 0.010907 | 0.0027336 | -0.010904 | -0.0027323 | 2.385e-06 | 1.242e-06 | 0.016673 | 0.016673 | 0.016673 | 0.97341 | -0.51273 | 0.97318 | -0.51732 | 4.5804
111 | 0.0079864 | 0.002001 | -0.0079864 | -0.002001 | 8.588e-09 | 3.5886e-09 | 0.012211 | 0.012211 | 0.012211 | 0.97318 | -0.51732 | 0.97318 | -0.51734 | 3.3547
112 | 0.0050922 | 0.0012757 | -0.005092 | -0.0012756 | 2.2638e-07 | 2.1156e-08 | 0.0077859 | 0.0077859 | 0.0077859 | 0.97318 | -0.51734 | 0.97313 | -0.51827 | 2.139
113 | 0.0062595 | 0.0015683 | -0.0062583 | -0.0015679 | 1.1441e-06 | 3.1856e-07 | 0.0095712 | 0.0095714 | 0.0095714 | 0.97313 | -0.51828 | 0.97294 | -0.52212 | 2.6295
114 | 0.0252 | 0.0063248 | -0.025189 | -0.0063178 | 1.1194e-05 | 6.9145e-06 | 0.038537 | 0.038537 | 0.038537 | 0.97313 | -0.51828 | 0.97266 | -0.5276 | 10.587
115 | 0.00218 | 0.00054609 | -0.0021799 | -0.00054634 | 1.0829e-07 | -2.5353e-07 | 0.0033334 | 0.0033335 | 0.0033335 | 0.97313 | -0.51827 | 0.97308 | -0.51932 | 0.9158
116 | 0.0029119 | 0.00072954 | -0.0029117 | -0.00072973 | 1.8501e-07 | -1.9074e-07 | 0.0044525 | 0.0044526 | 0.0044526 | 0.97313 | -0.51827 | 0.97307 | -0.51961 | 1.2232
117 | 0.0044744 | 0.0011209 | -0.0044743 | -0.0011209 | 3.7514e-08 | -2.5215e-09 | 0.006843 | 0.006843 | 0.006843 | 0.97294 | -0.52212 | 0.97293 | -0.5223 | 1.8799
118 | 0.001784 | 0.000447 | -0.0017839 | -0.0004471 | 2.5656e-08 | -9.7716e-08 | 0.0027284 | 0.0027284 | 0.0027284 | 0.97294 | -0.52212 | 0.97292 | -0.52242 | 0.74956
119 | 0.022902 | 0.0057448 | -0.022902 | -0.0057444 | 6.8117e-07 | 4.1759e-07 | 0.035039 | 0.035039 | 0.035039 | 0.97266 | -0.5276 | 0.97263 | -0.52822 | 9.626
120 | 0.0010713 | 0.00026849 | -0.0010713 | -0.00026849 | 3.9195e-11 | -4.6992e-10 | 0.0016382 | 0.0016382 | 0.0016382 | 0.97308 | -0.51932 | 0.97308 | -0.51932 | 0.45006
121 | 0.0010762 | 0.00026972 | -0.0010762 | -0.00026973 | 1.0419e-09 | -1.2073e-08 | 0.0016458 | 0.0016458 | 0.0016458 | 0.97307 | -0.51961 | 0.97306 | -0.51963 | 0.45214
122 | 0.0022373 | 0.00056028 | -0.0022371 | -0.00056055 | 1.2266e-07 | -2.6843e-07 | 0.0034216 | 0.0034217 | 0.0034217 | 0.97293 | -0.5223 | 0.97287 | -0.52345 | 0.94002
123 | 0.020441 | 0.0051277 | -0.020433 | -0.0051228 | 8.1456e-06 | 4.9377e-06 | 0.031274 | 0.031275 | 0.031275 | 0.97263 | -0.52822 | 0.9722 | -0.53659 | 8.5919
124 | -0.006709 | -0.0016807 | 0.0067098 | 0.0016809 | 7.6992e-07 | 2.5155e-07 | 0.010271 | 0.010271 | 0.010271 | 0.9719 | -0.54259 | 0.97202 | -0.54018 | 2.8218
125 | 0.0056827 | 0.0014234 | -0.0056819 | -0.0014233 | 7.1917e-07 | 1.4633e-07 | 0.0087001 | 0.0087002 | 0.0087002 | 0.9719 | -0.54259 | 0.97177 | -0.54525 | 2.3902
126 | -0.0077724 | -0.0019472 | 0.0077736 | 0.0019477 | 1.1474e-06 | 4.6638e-07 | 0.011898 | 0.011898 | 0.011898 | 0.97202 | -0.54018 | 0.97218 | -0.53708 | 3.2687
127 | 0.0044674 | 0.0011189 | -0.0044671 | -0.0011189 | 2.2962e-07 | -1.516e-08 | 0.0068404 | 0.0068404 | 0.0068404 | 0.97177 | -0.54525 | 0.97171 | -0.54632 | 1.8792
128 | -0.0092636 | -0.0023212 | 0.0092659 | 0.0023222 | 2.2547e-06 | 1.0721e-06 | 0.014179 | 0.014179 | 0.014179 | 0.97218 | -0.53708 | 0.97244 | -0.53197 | 3.8952
129 | 0.0032937 | 0.00082483 | -0.0032935 | -0.00082498 | 2.2093e-07 | -1.4548e-07 | 0.0050436 | 0.0050437 | 0.0050437 | 0.97171 | -0.54632 | 0.97164 | -0.54773 | 1.3856
130 | 0.0032935 | 0.00082498 | -0.003293 | -0.00082531 | 4.9874e-07 | -3.2822e-07 | 0.0050437 | 0.0050439 | 0.0050439 | 0.97164 | -0.54773 | 0.97148 | -0.55091 | 1.3857
131 | 0.017584 | 0.0044087 | -0.017583 | -0.0044084 | 6.3712e-07 | 3.7867e-07 | 0.026914 | 0.026914 | 0.026914 | 0.9722 | -0.53659 | 0.97217 | -0.53735 | 7.3939
132 | 0.015481 | 0.0038815 | -0.015479 | -0.0038802 | 2.1896e-06 | 1.2724e-06 | 0.023696 | 0.023696 | 0.023696 | 0.97217 | -0.53735 | 0.97202 | -0.54032 | 6.5099
133 | 0.012702 | 0.0031844 | -0.012701 | -0.0031838 | 1.0496e-06 | 5.8e-07 | 0.019446 | 0.019446 | 0.019446 | 0.97202 | -0.54032 | 0.97193 | -0.54205 | 5.3423
134 | 0.0022371 | 0.00056055 | -0.0022371 | -0.00056067 | 5.3016e-08 | -1.16e-07 | 0.0034217 | 0.0034217 | 0.0034217 | 0.97287 | -0.52345 | 0.97285 | -0.52395 | 0.94004
135 | 0.010246 | 0.0025685 | -0.010244 | -0.0025672 | 2.415e-06 | 1.2213e-06 | 0.015687 | 0.015687 | 0.015687 | 0.97193 | -0.54205 | 0.97168 | -0.547 | 4.3096
136 | 0.0081205 | 0.0020351 | -0.0081205 | -0.0020351 | 5.1697e-08 | 2.2044e-08 | 0.012436 | 0.012436 | 0.012436 | 0.97168 | -0.547 | 0.97167 | -0.54713 | 3.4164
137 | 0.0050739 | 0.0012716 | -0.0050735 | -0.0012715 | 4.4125e-07 | 4.1024e-08 | 0.0077702 | 0.0077703 | 0.0077703 | 0.97167 | -0.54713 | 0.97158 | -0.54896 | 2.1347
138 | 0.0025466 | 0.00063822 | -0.0025465 | -0.00063823 | 4.883e-09 | -7.476e-09 | 0.0039002 | 0.0039002 | 0.0039002 | 0.97158 | -0.54896 | 0.97158 | -0.549 | 1.0715
139 | -0.0004516 | -0.00011318 | 0.0004516 | 0.00011294 | 3.3666e-09 | -2.3687e-07 | 0.00068683 | 0.00068675 | 0.00068683 | 0.97838 | -0.41518 | 0.97839 | -0.41503 | 0.18869
140 | -0.0013621 | -0.00034114 | 0.0013623 | 0.00033974 | 1.9658e-07 | -1.4089e-06 | 0.0020716 | 0.002071 | 0.0020716 | 0.97839 | -0.41503 | 0.97855 | -0.41199 | 0.56911

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38475 | 0.098099

## res_load
| p_mw | q_mvar
0 | 0.001986 | 0.00049773
1 | 0.0024491 | 0.0006138
2 | 0.0012594 | 0.00031564
3 | 0.0031523 | 0.00079004
4 | 0.004951 | 0.0012408
5 | 0.00069132 | 0.00017326
6 | 0.0010685 | 0.00026779
7 | 0.0020605 | 0.00051642
8 | 0.0015313 | 0.00038377
9 | 0.0057459 | 0.00144
10 | 0.0025041 | 0.00062758
11 | 0.0065832 | 0.0016499
12 | 0.00066548 | 0.00016679
13 | 0.00020317 | 5.0919e-05
14 | 0.00076821 | 0.00019253
15 | 0.00038153 | 9.562e-05
16 | 0.001107 | 0.00027745
17 | 0.0024643 | 0.00061762
18 | 0.00081813 | 0.00020504
19 | 0.0010913 | 0.00027352
20 | 0.0050241 | 0.0012592
21 | 0.0049142 | 0.0012316
22 | 0.00058745 | 0.00014723
23 | 0.0010963 | 0.00027477
24 | 0.0020685 | 0.00051841
25 | 0.0062815 | 0.0015743
26 | 0.0017289 | 0.00043329
27 | 0.00098805 | 0.00024763
28 | 0.0004023 | 0.00010083
29 | 0.0014264 | 0.00035748
30 | 0.00039776 | 9.9689e-05
31 | 0.0021188 | 0.00053101
32 | 0.0019637 | 0.00049215
33 | 0.0046549 | 0.0011666
34 | 0.00086093 | 0.00021577
35 | 0.0055964 | 0.0014026
36 | 0.0024808 | 0.00062176
37 | 0.0033369 | 0.0008363
38 | 0.0016203 | 0.00040608
39 | 0.0036649 | 0.00091852
40 | 0.0017692 | 0.0004434
41 | 0.00099357 | 0.00024901
42 | 0.0019604 | 0.00049133
43 | 0.0017209 | 0.00043131
44 | 0.0014425 | 0.00036152
45 | 0.0019488 | 0.00048843
46 | 0.023984 | 0.0060108
47 | 0.0060092 | 0.001506
48 | 0.0088243 | 0.0022116
49 | 0.0041898 | 0.0010501
50 | 0.0039362 | 0.0009865
51 | 0.0030238 | 0.00075784
52 | 0.064095 | 0.016064
53 | 0.0051068 | 0.0012799
54 | 0.0051388 | 0.0012879
55 | 0.022929 | 0.0057466
56 | 0.00099379 | 0.00024907
57 | 0.0017928 | 0.00044931
58 | 0.0023059 | 0.00057792
59 | 0.000837 | 0.00020977
60 | 0.0062105 | 0.0015565
61 | 0.0066623 | 0.0016697
62 | 0.00063104 | 0.00015815
63 | 0.00143 | 0.00035839
64 | 0.0045306 | 0.0011355
65 | 0.00078442 | 0.00019659
66 | 0.0037497 | 0.00093975
67 | 0.00072462 | 0.00018161
68 | 0.0016058 | 0.00040244
69 | 0.0012631 | 0.00031656
70 | 0.0019408 | 0.00048641
71 | 0.00097135 | 0.00024344
72 | 0.0026925 | 0.00067481
73 | 0.0024203 | 0.00060659
74 | 0.0018385 | 0.00046077
75 | 0.0018087 | 0.0004533
76 | 0.0059651 | 0.001495
77 | 0.0018347 | 0.00045983
78 | 0.012922 | 0.0032385
79 | 0.0029004 | 0.00072692
80 | 0.0029713 | 0.00074468
81 | 0.0029179 | 0.00073129
82 | 0.0028942 | 0.00072537
83 | 0.0022865 | 0.00057305
84 | 0.0011086 | 0.00027785
85 | 0.0018355 | 0.00046002
86 | 0.0022371 | 0.00056067
87 | 0.0017839 | 0.0004471
88 | 0.0024604 | 0.00061664
89 | 0.0010263 | 0.00025722
90 | 0.0010627 | 0.00026633
91 | 0.0012146 | 0.0003044
92 | 0.0014901 | 0.00037345
93 | 0.0011734 | 0.00029408
94 | 0.0015747 | 0.00039465
95 | 0.003293 | 0.00082531
96 | 0.0028491 | 0.00071406
97 | 0.0021022 | 0.00052686
98 | 0.0027764 | 0.00069583
99 | 0.0024553 | 0.00061537
100 | 0.0022371 | 0.00056067
101 | 0.0021231 | 0.00053211
102 | 0.0030465 | 0.00076353
103 | 0.0025269 | 0.00063331
104 | 0.0010713 | 0.00026849
105 | 0.0010762 | 0.00026973
106 | 0.0004516 | 0.00011318
107 | 0.00091053 | 0.0002282
108 | 0.0014973 | 0.00037526
109 | 0.0025465 | 0.00063823

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1