## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2513-16_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2513-16_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2513-16_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2513-16_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2513-16_0_5_node_83 | 0.4 | n |  | TRUE
5 | bus_LV_2513-16_0_5_node_81 | 0.4 | n |  | TRUE
6 | bus_LV_2513-16_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2513-16_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2513-16_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2513-16_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2513-16_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2513-16_0_5_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_2513-16_0_5_node_82 | 0.4 | n |  | TRUE
13 | bus_LV_2513-16_0_5_node_111 | 0.4 | n |  | TRUE
14 | bus_LV_2513-16_0_5_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2513-16_0_5_node_80 | 0.4 | n |  | TRUE
16 | bus_LV_2513-16_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2513-16_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2513-16_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2513-16_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2513-16_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2513-16_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2513-16_0_5_node_118 | 0.4 | n |  | TRUE
23 | bus_LV_2513-16_0_5_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2513-16_0_5_node_86 | 0.4 | n |  | TRUE
25 | bus_LV_2513-16_0_5_node_85 | 0.4 | n |  | TRUE
26 | bus_LV_2513-16_0_5_node_99 | 0.4 | n |  | TRUE
27 | bus_LV_2513-16_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2513-16_0_5_node_105 | 0.4 | n |  | TRUE
29 | bus_LV_2513-16_0_5_node_107 | 0.4 | n |  | TRUE
30 | bus_LV_2513-16_0_5_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2513-16_0_5_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2513-16_0_5_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2513-16_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2513-16_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2513-16_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2513-16_0_5_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_2513-16_0_5_node_123 | 0.4 | n |  | TRUE
38 | bus_LV_2513-16_0_5_node_56 | 0.4 | n |  | TRUE
39 | bus_LV_2513-16_0_5_node_114 | 0.4 | n |  | TRUE
40 | bus_LV_2513-16_0_5_node_122 | 0.4 | n |  | TRUE
41 | bus_LV_2513-16_0_5_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2513-16_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2513-16_0_5_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2513-16_0_5_node_113 | 0.4 | n |  | TRUE
45 | bus_LV_2513-16_0_5_node_103 | 0.4 | n |  | TRUE
46 | bus_LV_2513-16_0_5_node_102 | 0.4 | n |  | TRUE
47 | bus_LV_2513-16_0_5_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_2513-16_0_5_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2513-16_0_5_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_2513-16_0_5_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2513-16_0_5_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_2513-16_0_5_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_2513-16_0_5_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_2513-16_0_5_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_2513-16_0_5_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2513-16_0_5_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_2513-16_0_5_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2513-16_0_5_node_77 | 0.4 | n |  | TRUE
59 | bus_LV_2513-16_0_5_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2513-16_0_5_node_116 | 0.4 | n |  | TRUE
61 | bus_LV_2513-16_0_5_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_2513-16_0_5_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2513-16_0_5_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_2513-16_0_5_node_40 | 0.4 | n |  | TRUE
65 | bus_LV_2513-16_0_5_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_2513-16_0_5_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_2513-16_0_5_node_87 | 0.4 | n |  | TRUE
68 | bus_LV_2513-16_0_5_node_78 | 0.4 | n |  | TRUE
69 | bus_LV_2513-16_0_5_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_2513-16_0_5_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_2513-16_0_5_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_2513-16_0_5_node_46 | 0.4 | n |  | TRUE
73 | bus_LV_2513-16_0_5_node_47 | 0.4 | n |  | TRUE
74 | bus_LV_2513-16_0_5_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_2513-16_0_5_node_124 | 0.4 | n |  | TRUE
76 | bus_LV_2513-16_0_5_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_2513-16_0_5_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_2513-16_0_5_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_2513-16_0_5_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_2513-16_0_5_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_2513-16_0_5_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_2513-16_0_5_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_2513-16_0_5_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_2513-16_0_5_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_2513-16_0_5_node_89 | 0.4 | n |  | TRUE
86 | bus_LV_2513-16_0_5_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_2513-16_0_5_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_2513-16_0_5_node_63 | 0.4 | n |  | TRUE
89 | bus_LV_2513-16_0_5_node_64 | 0.4 | n |  | TRUE
90 | bus_LV_2513-16_0_5_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_2513-16_0_5_node_112 | 0.4 | n |  | TRUE
92 | bus_LV_2513-16_0_5_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_2513-16_0_5_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_2513-16_0_5_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_2513-16_0_5_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_2513-16_0_5_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_2513-16_0_5_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_2513-16_0_5_node_75 | 0.4 | n |  | TRUE
99 | bus_LV_2513-16_0_5_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_2513-16_0_5_node_129 | 0.4 | n |  | TRUE
101 | bus_LV_2513-16_0_5_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_2513-16_0_5_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2513-16_0_5_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_2513-16_0_5_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_2513-16_0_5_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_2513-16_0_5_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_2513-16_0_5_node_74 | 0.4 | n |  | TRUE
108 | bus_LV_2513-16_0_5_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_2513-16_0_5_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_2513-16_0_5_node_79 | 0.4 | n |  | TRUE
111 | bus_LV_2513-16_0_5_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_2513-16_0_5_node_119 | 0.4 | n |  | TRUE
113 | bus_LV_2513-16_0_5_node_120 | 0.4 | n |  | TRUE
114 | bus_LV_2513-16_0_5_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_2513-16_0_5_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_2513-16_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2513-16_0_5_node_91 | 0.4 | n |  | TRUE
118 | bus_LV_2513-16_0_5_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_2513-16_0_5_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2513-16_0_5_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_2513-16_0_5_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_2513-16_0_5_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_2513-16_0_5_node_126 | 0.4 | n |  | TRUE
124 | bus_LV_2513-16_0_5_node_127 | 0.4 | n |  | TRUE
125 | bus_LV_2513-16_0_5_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_2513-16_0_5_node_131 | 0.4 | n |  | TRUE
127 | bus_MV_393_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2513-16_0_5_load_0 | 0 | 0.00075078 | 0.00018816 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2513-16_0_5_load_1 | 1 | 0.00079369 | 0.00019892 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2513-16_0_5_load_4 | 3 | 0.0065451 | 0.0016404 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2513-16_0_5_load_5 | 6 | 0.0022991 | 0.0005762 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2513-16_0_5_load_6 | 7 | 0.0023837 | 0.00059741 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2513-16_0_5_load_7 | 8 | 0.0015459 | 0.00038745 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2513-16_0_5_load_8 | 9 | 0.0016356 | 0.00040993 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2513-16_0_5_load_9 | 10 | 0.0016758 | 0.00042 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2513-16_0_5_load_82 | 12 | 0.0020268 | 0.00050796 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2513-16_0_5_load_111 | 13 | 0.0016066 | 0.00040264 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2513-16_0_5_load_25 | 14 | 0.0013487 | 0.00033802 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2513-16_0_5_load_80 | 15 | 0.0049622 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2513-16_0_5_load_10 | 16 | 0.0030082 | 0.00075392 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2513-16_0_5_load_11 | 17 | 0.00057662 | 0.00014452 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2513-16_0_5_load_13 | 19 | 0.00060466 | 0.00015154 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2513-16_0_5_load_14 | 20 | 0.0007066 | 0.00017709 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2513-16_0_5_load_118 | 22 | 0.0021741 | 0.00054487 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2513-16_0_5_load_21 | 23 | 0.0032839 | 0.00082301 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2513-16_0_5_load_85 | 25 | 0.0018218 | 0.00045659 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2513-16_0_5_load_99 | 26 | 0.00055781 | 0.0001398 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2513-16_0_5_load_22 | 27 | 0.0019684 | 0.00049334 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2513-16_0_5_load_105 | 28 | 0.0020472 | 0.00051308 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2513-16_0_5_load_107 | 29 | 0.0019165 | 0.00048032 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2513-16_0_5_load_32 | 30 | 0.0017514 | 0.00043894 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2513-16_0_5_load_16 | 31 | 0.0016392 | 0.00041081 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2513-16_0_5_load_17 | 32 | 0.0018474 | 0.00046301 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2513-16_0_5_load_18 | 33 | 0.010319 | 0.0025862 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2513-16_0_5_load_19 | 34 | 0.0017734 | 0.00044446 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2513-16_0_5_load_20 | 35 | 0.020506 | 0.0051392 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2513-16_0_5_load_58 | 36 | 0.0021645 | 0.00054247 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2513-16_0_5_load_123 | 37 | 0.013915 | 0.0034874 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2513-16_0_5_load_114 | 39 | 0.017126 | 0.0042923 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2513-16_0_5_load_122 | 40 | 0.0017845 | 0.00044724 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2513-16_0_5_load_23 | 41 | 0.0018344 | 0.00045974 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2513-16_0_5_load_24 | 42 | 0.0025289 | 0.00063381 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2513-16_0_5_load_26 | 43 | 0.0029404 | 0.00073694 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2513-16_0_5_load_113 | 44 | 0.0042247 | 0.0010588 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2513-16_0_5_load_102 | 46 | 0.0032221 | 0.00080753 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2513-16_0_5_load_28 | 47 | 0.0019464 | 0.00048782 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2513-16_0_5_load_29 | 48 | 0.00051759 | 0.00012972 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2513-16_0_5_load_30 | 49 | 0.00049088 | 0.00012303 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2513-16_0_5_load_31 | 50 | 0.0018246 | 0.00045729 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2513-16_0_5_load_51 | 51 | 0.00040359 | 0.00010115 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2513-16_0_5_load_49 | 52 | 0.00027745 | 6.9535e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2513-16_0_5_load_33 | 53 | 0.0012741 | 0.00031932 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2513-16_0_5_load_34 | 54 | 0.0026673 | 0.00066848 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2513-16_0_5_load_35 | 55 | 0.0012761 | 0.00031983 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2513-16_0_5_load_36 | 56 | 0.0012439 | 0.00031176 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2513-16_0_5_load_37 | 57 | 0.00073693 | 0.00018469 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2513-16_0_5_load_77 | 58 | 0.001198 | 0.00030025 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2513-16_0_5_load_57 | 61 | 0.0014692 | 0.00036822 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2513-16_0_5_load_38 | 62 | 0.0016348 | 0.00040972 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2513-16_0_5_load_39 | 63 | 0.0015547 | 0.00038964 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2513-16_0_5_load_40 | 64 | 0.00099122 | 0.00024842 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2513-16_0_5_load_41 | 65 | 0.0015356 | 0.00038487 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2513-16_0_5_load_87 | 67 | 0.0022178 | 0.00055584 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2513-16_0_5_load_78 | 68 | 0.0015792 | 0.00039579 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2513-16_0_5_load_43 | 69 | 0.0038087 | 0.00095456 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2513-16_0_5_load_44 | 70 | 0.0035209 | 0.00088243 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2513-16_0_5_load_45 | 71 | 0.00060293 | 0.00015111 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2513-16_0_5_load_46 | 72 | 0.0023539 | 0.00058993 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2513-16_0_5_load_76 | 74 | 0.0033805 | 0.00084722 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2513-16_0_5_load_124 | 75 | 0.0004836 | 0.0001212 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2513-16_0_5_load_73 | 76 | 0.0032739 | 0.00082052 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2513-16_0_5_load_48 | 77 | 0.00055472 | 0.00013902 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2513-16_0_5_load_50 | 78 | 0.00058179 | 0.00014581 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2513-16_0_5_load_52 | 79 | 0.00047034 | 0.00011788 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2513-16_0_5_load_115 | 80 | 0.0018137 | 0.00045456 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2513-16_0_5_load_55 | 81 | 0.0039653 | 0.00099379 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2513-16_0_5_load_54 | 82 | 0.00098203 | 0.00024612 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2513-16_0_5_load_59 | 83 | 0.0014949 | 0.00037466 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2513-16_0_5_load_88 | 84 | 0.0017796 | 0.000446 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2513-16_0_5_load_60 | 86 | 0.025453 | 0.006379 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2513-16_0_5_load_63 | 88 | 0.0063334 | 0.0015873 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2513-16_0_5_load_100 | 90 | 0.0031448 | 0.00078816 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2513-16_0_5_load_112 | 91 | 0.00066139 | 0.00016576 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2513-16_0_5_load_101 | 92 | 0.002992 | 0.00074988 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2513-16_0_5_load_65 | 93 | 0.0031759 | 0.00079597 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2513-16_0_5_load_67 | 95 | 0.0068073 | 0.0017061 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2513-16_0_5_load_69 | 97 | 0.00060202 | 0.00015088 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2513-16_0_5_load_75 | 98 | 0.023735 | 0.0059486 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2513-16_0_5_load_129 | 100 | 0.00046105 | 0.00011555 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2513-16_0_5_load_94 | 103 | 0.0078702 | 0.0019725 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2513-16_0_5_load_90 | 104 | 0.017525 | 0.0043922 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2513-16_0_5_load_70 | 105 | 0.0061795 | 0.0015487 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2513-16_0_5_load_71 | 106 | 0.002466 | 0.00061804 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2513-16_0_5_load_74 | 107 | 0.020665 | 0.0051791 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2513-16_0_5_load_109 | 109 | 0.0091422 | 0.0022912 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2513-16_0_5_load_79 | 110 | 0.0066435 | 0.001665 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2513-16_0_5_load_119 | 112 | 0.0078385 | 0.0019645 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2513-16_0_5_load_120 | 113 | 0.0016978 | 0.00042551 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2513-16_0_5_load_104 | 114 | 0.0013355 | 0.0003347 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2513-16_0_5_load_97 | 115 | 0.0013244 | 0.00033192 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2513-16_0_5_load_96 | 116 | 0.001233 | 0.00030901 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2513-16_0_5_load_91 | 117 | 0.015239 | 0.0038192 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2513-16_0_5_load_93 | 118 | 0.0012515 | 0.00031366 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2513-16_0_5_load_108 | 119 | 0.024792 | 0.0062135 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2513-16_0_5_load_98 | 120 | 0.0013898 | 0.00034832 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2513-16_0_5_load_106 | 121 | 0.0023043 | 0.00057752 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2513-16_0_5_load_127 | 124 | 0.019195 | 0.0048108 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2513-16_0_5_load_131 | 126 | 0.024629 | 0.0061725 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2513-16_0_5_line_0 |  | 0 | 1 | 0.021523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2513-16_0_5_line_1 |  | 0 | 2 | 0.0034842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2513-16_0_5_line_2 |  | 2 | 3 | 0.019561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2513-16_0_5_line_3 |  | 3 | 4 | 0.0096503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2513-16_0_5_line_4 |  | 4 | 5 | 0.030511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2513-16_0_5_line_5 |  | 5 | 111 | 0.048705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2513-16_0_5_line_6 |  | 5 | 110 | 0.012742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2513-16_0_5_line_7 |  | 6 | 7 | 0.025266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2513-16_0_5_line_8 |  | 6 | 8 | 0.021245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2513-16_0_5_line_9 |  | 7 | 9 | 0.013327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2513-16_0_5_line_10 |  | 8 | 10 | 3.2305e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2513-16_0_5_line_11 |  | 9 | 11 | 0.0041874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2513-16_0_5_line_12 |  | 10 | 12 | 0.026326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2513-16_0_5_line_13 |  | 11 | 13 | 0.035055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2513-16_0_5_line_14 |  | 11 | 14 | 0.016901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2513-16_0_5_line_15 |  | 12 | 15 | 0.024527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2513-16_0_5_line_16 |  | 13 | 46 | 0.012018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2513-16_0_5_line_17 |  | 14 | 41 | 0.0040462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2513-16_0_5_line_18 |  | 15 | 110 | 0.032877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2513-16_0_5_line_19 |  | 16 | 17 | 0.02174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2513-16_0_5_line_20 |  | 16 | 18 | 0.025303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2513-16_0_5_line_21 |  | 17 | 19 | 0.019884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2513-16_0_5_line_22 |  | 18 | 20 | 0.099731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2513-16_0_5_line_23 |  | 18 | 21 | 0.039317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2513-16_0_5_line_24 |  | 19 | 22 | 0.019307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2513-16_0_5_line_25 |  | 20 | 23 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2513-16_0_5_line_26 |  | 21 | 24 | 0.033565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2513-16_0_5_line_27 |  | 21 | 25 | 0.012591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2513-16_0_5_line_28 |  | 22 | 26 | 0.01272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2513-16_0_5_line_29 |  | 23 | 27 | 0.0088335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2513-16_0_5_line_30 |  | 24 | 28 | 0.017317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2513-16_0_5_line_31 |  | 24 | 29 | 0.0085669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2513-16_0_5_line_32 |  | 25 | 30 | 0.012597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2513-16_0_5_line_33 |  | 26 | 120 | 0.015151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2513-16_0_5_line_34 |  | 27 | 40 | 0.019291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2513-16_0_5_line_35 |  | 28 | 114 | 0.01304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2513-16_0_5_line_36 |  | 29 | 66 | 0.015244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2513-16_0_5_line_37 |  | 30 | 49 | 0.010357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2513-16_0_5_line_38 |  | 31 | 32 | 0.023351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2513-16_0_5_line_39 |  | 31 | 33 | 0.0012617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2513-16_0_5_line_40 |  | 32 | 34 | 0.0081311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2513-16_0_5_line_41 |  | 33 | 35 | 0.023999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2513-16_0_5_line_42 |  | 34 | 36 | 0.030808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2513-16_0_5_line_43 |  | 35 | 37 | 0.0037823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2513-16_0_5_line_44 |  | 36 | 38 | 0.0031113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2513-16_0_5_line_45 |  | 37 | 39 | 0.029859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2513-16_0_5_line_46 |  | 38 | 83 | 0.022989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2513-16_0_5_line_47 |  | 38 | 82 | 0.020687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2513-16_0_5_line_48 |  | 39 | 108 | 0.013521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2513-16_0_5_line_49 |  | 41 | 42 | 0.020015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2513-16_0_5_line_50 |  | 42 | 43 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2513-16_0_5_line_51 |  | 43 | 44 | 0.015385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2513-16_0_5_line_52 |  | 44 | 45 | 0.018145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2513-16_0_5_line_53 |  | 45 | 91 | 0.029772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2513-16_0_5_line_54 |  | 46 | 92 | 0.027274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2513-16_0_5_line_55 |  | 47 | 48 | 0.0095023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2513-16_0_5_line_56 |  | 47 | 49 | 0.0094903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2513-16_0_5_line_57 |  | 48 | 50 | 0.011898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2513-16_0_5_line_58 |  | 50 | 51 | 0.0072779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2513-16_0_5_line_59 |  | 51 | 52 | 0.011724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2513-16_0_5_line_60 |  | 52 | 77 | 0.00056271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2513-16_0_5_line_61 |  | 53 | 54 | 0.024047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2513-16_0_5_line_62 |  | 53 | 55 | 0.028069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2513-16_0_5_line_63 |  | 54 | 56 | 0.016007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2513-16_0_5_line_64 |  | 55 | 57 | 0.018157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2513-16_0_5_line_65 |  | 56 | 58 | 0.01866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2513-16_0_5_line_66 |  | 57 | 59 | 0.041412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2513-16_0_5_line_67 |  | 59 | 60 | 0.038785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2513-16_0_5_line_68 |  | 59 | 61 | 0.0098832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2513-16_0_5_line_69 |  | 60 | 80 | 0.0030014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2513-16_0_5_line_70 |  | 61 | 81 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2513-16_0_5_line_71 |  | 62 | 63 | 0.020816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2513-16_0_5_line_72 |  | 62 | 64 | 0.018951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2513-16_0_5_line_73 |  | 63 | 65 | 0.019764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2513-16_0_5_line_74 |  | 64 | 66 | 0.032538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2513-16_0_5_line_75 |  | 65 | 67 | 0.020428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2513-16_0_5_line_76 |  | 66 | 68 | 0.013474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2513-16_0_5_line_77 |  | 69 | 70 | 0.0187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2513-16_0_5_line_78 |  | 69 | 71 | 0.020577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2513-16_0_5_line_79 |  | 70 | 72 | 0.0026405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2513-16_0_5_line_80 |  | 71 | 73 | 0.033345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2513-16_0_5_line_81 |  | 72 | 74 | 0.017345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2513-16_0_5_line_82 |  | 73 | 75 | 0.036002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2513-16_0_5_line_83 |  | 74 | 76 | 0.002816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2513-16_0_5_line_84 |  | 76 | 106 | 0.015372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2513-16_0_5_line_85 |  | 77 | 78 | 0.012548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2513-16_0_5_line_86 |  | 78 | 79 | 0.0085273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2513-16_0_5_line_87 |  | 81 | 82 | 0.034552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2513-16_0_5_line_88 |  | 83 | 84 | 0.011489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2513-16_0_5_line_89 |  | 84 | 85 | 0.016563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2513-16_0_5_line_90 |  | 85 | 115 | 0.0059065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2513-16_0_5_line_91 |  | 85 | 91 | 0.040185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2513-16_0_5_line_92 |  | 86 | 87 | 0.032924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2513-16_0_5_line_93 |  | 87 | 88 | 0.019053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2513-16_0_5_line_94 |  | 87 | 89 | 0.076315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2513-16_0_5_line_95 |  | 89 | 90 | 0.017238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2513-16_0_5_line_96 |  | 90 | 92 | 0.021055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2513-16_0_5_line_97 |  | 93 | 94 | 0.020138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2513-16_0_5_line_98 |  | 93 | 95 | 0.013318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2513-16_0_5_line_99 |  | 94 | 96 | 0.03085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2513-16_0_5_line_100 |  | 94 | 97 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2513-16_0_5_line_101 |  | 96 | 98 | 0.013718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2513-16_0_5_line_102 |  | 97 | 99 | 0.018781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2513-16_0_5_line_103 |  | 98 | 101 | 0.017731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2513-16_0_5_line_104 |  | 99 | 100 | 0.032443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2513-16_0_5_line_105 |  | 101 | 107 | 0.011277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2513-16_0_5_line_106 |  | 101 | 105 | 0.015429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2513-16_0_5_line_107 |  | 102 | 103 | 0.010393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2513-16_0_5_line_108 |  | 102 | 104 | 0.020222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2513-16_0_5_line_109 |  | 103 | 119 | 0.038665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2513-16_0_5_line_110 |  | 104 | 117 | 0.019823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2513-16_0_5_line_111 |  | 105 | 106 | 0.021684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2513-16_0_5_line_112 |  | 107 | 108 | 0.012854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2513-16_0_5_line_113 |  | 108 | 109 | 0.024788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2513-16_0_5_line_114 |  | 109 | 119 | 0.0038285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2513-16_0_5_line_115 |  | 111 | 112 | 0.031347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2513-16_0_5_line_116 |  | 112 | 113 | 0.044279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2513-16_0_5_line_117 |  | 113 | 122 | 0.063055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2513-16_0_5_line_118 |  | 114 | 121 | 0.0046405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2513-16_0_5_line_119 |  | 115 | 116 | 0.025501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2513-16_0_5_line_120 |  | 116 | 120 | 0.025019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2513-16_0_5_line_121 |  | 117 | 118 | 0.021192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2513-16_0_5_line_122 |  | 122 | 123 | 0.016129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2513-16_0_5_line_123 |  | 122 | 124 | 0.0094303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2513-16_0_5_line_124 |  | 123 | 125 | 0.024427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2513-16_0_5_line_125 |  | 125 | 126 | 0.013034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2513-16_0_5_trafo_6 | 0.63 MVA 20/0.4 kV | 127 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2608835.3373 | 1226243.0861 | 2608850.9291 | 1226257.9232
1 | 2608832.8132 | 1226240.6843 | 2608835.3373 | 1226243.0861
2 | 2608832.8132 | 1226240.6843 | 2608819.7424 | 1226228.2466 | 2608818.6715 | 1226227.1706
3 | 2608811.8641 | 1226220.3304 | 2608818.6715 | 1226227.1706
4 | 2608790.3104 | 1226198.6749 | 2608811.8641 | 1226220.3304
5 | 2608790.3104 | 1226198.6749 | 2608790.8808 | 1226192.1386 | 2608791.4548 | 1226183.2008 | 2608795.7172 | 1226150.2878
6 | 2608790.3104 | 1226198.6749 | 2608784.3374 | 1226199.0553 | 2608777.6007 | 1226198.5393
7 | 2608680.7135 | 1226161.5692 | 2608659.2034 | 1226148.3155
8 | 2608680.7135 | 1226161.5692 | 2608686.4861 | 1226165.1261 | 2608699.0535 | 1226172.2872
9 | 2608647.8571 | 1226141.3243 | 2608659.2034 | 1226148.3155
10 | 2608699.0816 | 1226172.3032 | 2608699.0535 | 1226172.2872
11 | 2608644.2921 | 1226139.1276 | 2608647.8571 | 1226141.3243
12 | 2608699.0816 | 1226172.3032 | 2608719.6027 | 1226183.9964 | 2608722.1826 | 1226184.8175
13 | 2608644.2921 | 1226139.1276 | 2608662.1243 | 1226108.9468
14 | 2608644.2921 | 1226139.1276 | 2608630.4678 | 1226129.4054
15 | 2608745.5541 | 1226192.2559 | 2608722.1826 | 1226184.8175
16 | 2608654.097 | 1226100.0022 | 2608662.1243 | 1226108.9468
17 | 2608630.4678 | 1226129.4054 | 2608627.1581 | 1226127.0778
18 | 2608777.6007 | 1226198.5393 | 2608761.3978 | 1226197.2984 | 2608745.5541 | 1226192.2559
19 | 2608440.021 | 1226015.2099 | 2608450.4376 | 1226034.2917
20 | 2608427.8971 | 1225993.0005 | 2608440.021 | 1226015.2099
21 | 2608450.4376 | 1226034.2917 | 2608459.965 | 1226051.7446
22 | 2608427.8971 | 1225993.0005 | 2608499.4051 | 1225923.481
23 | 2608402.9029 | 1226023.4055 | 2608427.8971 | 1225993.0005
24 | 2608469.216 | 1226068.6911 | 2608459.965 | 1226051.7446
25 | 2608499.4051 | 1225923.481 | 2608512.0983 | 1225911.1408
26 | 2608402.9029 | 1226023.4055 | 2608384.9378 | 1226051.7859
27 | 2608402.9029 | 1226023.4055 | 2608391.8517 | 1226017.3723
28 | 2608476.0153 | 1226079.3819 | 2608473.0976 | 1226075.8017 | 2608469.216 | 1226068.6911
29 | 2608512.0983 | 1225911.1408 | 2608518.432 | 1225904.9832
30 | 2608384.9378 | 1226051.7859 | 2608401.0516 | 1226058.1292
31 | 2608384.9378 | 1226051.7859 | 2608380.3545 | 1226059.0236
32 | 2608391.8517 | 1226017.3723 | 2608380.7952 | 1226011.3362
33 | 2608476.0153 | 1226079.3819 | 2608485.5864 | 1226091.1266
34 | 2608518.432 | 1225904.9832 | 2608532.2641 | 1225891.5358
35 | 2608413.1857 | 1226062.9059 | 2608401.0516 | 1226058.1292
36 | 2608372.1991 | 1226071.9022 | 2608380.3545 | 1226059.0236
37 | 2608371.7045 | 1226006.3733 | 2608380.7952 | 1226011.3362
38 | 2608617.7232 | 1226200.9117 | 2608604.3991 | 1226194.2026 | 2608597.7548 | 1226189.01
39 | 2608617.7232 | 1226200.9117 | 2608618.8501 | 1226201.4791
40 | 2608591.3482 | 1226184.003 | 2608597.7548 | 1226189.01
41 | 2608640.2846 | 1226212.2721 | 2608618.8501 | 1226201.4791
42 | 2608591.3482 | 1226184.003 | 2608567.0738 | 1226165.0321
43 | 2608640.2846 | 1226212.2721 | 2608643.6628 | 1226213.9732
44 | 2608564.6224 | 1226163.1163 | 2608567.0738 | 1226165.0321
45 | 2608670.3317 | 1226227.4018 | 2608643.6628 | 1226213.9732
46 | 2608564.6224 | 1226163.1163 | 2608546.5054 | 1226148.9645
47 | 2608564.6224 | 1226163.1163 | 2608551.9929 | 1226179.501
48 | 2608682.408 | 1226233.4826 | 2608670.3317 | 1226227.4018
49 | 2608627.1581 | 1226127.0778 | 2608610.7863 | 1226115.564
50 | 2608600.7478 | 1226107.9494 | 2608603.0267 | 1226110.1068 | 2608610.7863 | 1226115.564
51 | 2608589.5753 | 1226097.3725 | 2608600.7478 | 1226107.9494
52 | 2608576.3988 | 1226084.8983 | 2608589.5753 | 1226097.3725
53 | 2608576.3988 | 1226084.8983 | 2608554.2685 | 1226104.8145
54 | 2608635.8804 | 1226079.7039 | 2608654.097 | 1226100.0022
55 | 2608363.3747 | 1226001.8257 | 2608355.0344 | 1225997.2725
56 | 2608371.7045 | 1226006.3733 | 2608363.3747 | 1226001.8257
57 | 2608344.5913 | 1225991.5712 | 2608355.0344 | 1225997.2725
58 | 2608338.2033 | 1225988.0838 | 2608344.5913 | 1225991.5712
59 | 2608327.9126 | 1225982.4658 | 2608338.2033 | 1225988.0838
60 | 2608327.4187 | 1225982.1961 | 2608327.9126 | 1225982.4658
61 | 2608456.397 | 1226161.8401 | 2608439.9628 | 1226144.2855
62 | 2608475.5801 | 1226182.3309 | 2608456.397 | 1226161.8401
63 | 2608429.0232 | 1226132.6001 | 2608439.9628 | 1226144.2855
64 | 2608475.5801 | 1226182.3309 | 2608487.9891 | 1226195.5859
65 | 2608416.2706 | 1226118.9781 | 2608429.0232 | 1226132.6001
66 | 2608516.2914 | 1226225.8176 | 2608487.9891 | 1226195.5859
67 | 2608516.2914 | 1226225.8176 | 2608543.6508 | 1226253.3838
68 | 2608516.2914 | 1226225.8176 | 2608522.325 | 1226217.99
69 | 2608543.6508 | 1226253.3838 | 2608546.1857 | 1226254.9909
70 | 2608530.899 | 1226206.8667 | 2608522.325 | 1226217.99
71 | 2608309.0709 | 1226036.6477 | 2608327.2449 | 1226046.7971
72 | 2608343.7906 | 1226056.0372 | 2608327.2449 | 1226046.7971
73 | 2608309.0709 | 1226036.6477 | 2608291.8154 | 1226027.0112
74 | 2608372.1991 | 1226071.9022 | 2608343.7906 | 1226056.0372
75 | 2608273.9799 | 1226017.0508 | 2608291.8154 | 1226027.0112
76 | 2608372.1991 | 1226071.9022 | 2608381.4074 | 1226081.7383
77 | 2608771.2051 | 1226278.1928 | 2608772.6016 | 1226278.8961 | 2608786.6133 | 1226288.7617
78 | 2608803.4383 | 1226300.6082 | 2608786.6133 | 1226288.7617
79 | 2608771.2051 | 1226278.1928 | 2608768.8468 | 1226277.0052
80 | 2608830.7033 | 1226319.8054 | 2608803.4383 | 1226300.6082
81 | 2608753.3552 | 1226269.2041 | 2608768.8468 | 1226277.0052
82 | 2608830.7033 | 1226319.8054 | 2608859.2283 | 1226297.8399
83 | 2608753.3552 | 1226269.2041 | 2608750.8401 | 1226267.9376
84 | 2608737.1104 | 1226261.0237 | 2608750.8401 | 1226267.9376
85 | 2608327.4187 | 1225982.1961 | 2608316.4048 | 1225976.1832
86 | 2608308.9202 | 1225972.0971 | 2608316.4048 | 1225976.1832
87 | 2608551.9929 | 1226179.501 | 2608530.899 | 1226206.8667
88 | 2608546.5054 | 1226148.9645 | 2608537.4515 | 1226141.8922
89 | 2608524.3985 | 1226131.6961 | 2608537.4515 | 1226141.8922
90 | 2608524.3985 | 1226131.6961 | 2608519.8131 | 1226127.9732
91 | 2608524.3985 | 1226131.6961 | 2608554.2685 | 1226104.8145
92 | 2608665.7013 | 1226009.6048 | 2608688.1816 | 1225985.5495
93 | 2608665.7013 | 1226009.6048 | 2608682.9333 | 1226017.7343
94 | 2608610.3041 | 1226051.2049 | 2608644.5747 | 1226016.734 | 2608656.8713 | 1226004.3667 | 2608665.7013 | 1226009.6048
95 | 2608610.3041 | 1226051.2049 | 2608621.8173 | 1226064.0337
96 | 2608621.8173 | 1226064.0337 | 2608635.8804 | 1226079.7039
97 | 2608697.1091 | 1226287.3688 | 2608698.5881 | 1226286.615 | 2608703.3742 | 1226284.1094 | 2608707.1609 | 1226280.8463 | 2608708.9301 | 1226278.592 | 2608709.9407 | 1226276.7701 | 2608711.4149 | 1226274.0118
98 | 2608715.2668 | 1226262.5473 | 2608716.508 | 1226263.7832 | 2608716.5062 | 1226264.9727 | 2608715.7538 | 1226266.4169 | 2608712.6539 | 1226271.6933 | 2608711.4149 | 1226274.0118
99 | 2608684.6378 | 1226269.0067 | 2608687.6059 | 1226270.9899 | 2608693.9295 | 1226269.2202 | 2608697.4143 | 1226270.3371 | 2608697.8865 | 1226273.951 | 2608697.1091 | 1226287.3688
100 | 2608697.1091 | 1226287.3688 | 2608694.4477 | 1226298.6383 | 2608689.8326 | 1226306.4649
101 | 2608684.6378 | 1226269.0067 | 2608692.1213 | 1226257.5093
102 | 2608680.2931 | 1226322.643 | 2608689.8326 | 1226306.4649
103 | 2608703.9625 | 1226244.3313 | 2608692.7276 | 1226256.5777 | 2608692.1213 | 1226257.5093
104 | 2608680.2931 | 1226322.643 | 2608704.5741 | 1226334.5852 | 2608709.5956 | 1226336.5281
105 | 2608703.9625 | 1226244.3313 | 2608693.8895 | 1226239.2614
106 | 2608703.9625 | 1226244.3313 | 2608717.7431 | 1226251.2709
107 | 2608637.5238 | 1226296.8661 | 2608643.4582 | 1226288.3342
108 | 2608637.5238 | 1226296.8661 | 2608620.1173 | 1226286.5741
109 | 2608665.5363 | 1226256.5923 | 2608643.4582 | 1226288.3342
110 | 2608620.1173 | 1226286.5741 | 2608613.3974 | 1226282.6008 | 2608602.151 | 1226278.3695
111 | 2608717.7431 | 1226251.2709 | 2608737.1104 | 1226261.0237
112 | 2608682.408 | 1226233.4826 | 2608693.8895 | 1226239.2614
113 | 2608682.408 | 1226233.4826 | 2608670.402 | 1226249.5969 | 2608667.7224 | 1226253.4493
114 | 2608665.5363 | 1226256.5923 | 2608667.7224 | 1226253.4493
115 | 2608795.7172 | 1226150.2878 | 2608767.832 | 1226135.9672
116 | 2608767.832 | 1226135.9672 | 2608728.4431 | 1226115.7389
117 | 2608709.2312 | 1226071.393 | 2608700.8719 | 1226081.3645 | 2608697.5719 | 1226088.6084 | 2608712.0894 | 1226107.3404 | 2608728.4431 | 1226115.7389
118 | 2608417.5036 | 1226064.6057 | 2608413.1857 | 1226062.9059
119 | 2608501.3919 | 1226110.5214 | 2608507.4026 | 1226117.8972 | 2608519.8131 | 1226127.9732
120 | 2608501.3919 | 1226110.5214 | 2608485.5864 | 1226091.1266
121 | 2608582.316 | 1226270.907 | 2608602.151 | 1226278.3695
122 | 2608709.2312 | 1226071.393 | 2608725.4059 | 1226071.1608
123 | 2608709.2312 | 1226071.393 | 2608711.3895 | 1226062.2129
124 | 2608732.27 | 1226078.3194 | 2608736.2573 | 1226072.6886 | 2608736.6898 | 1226067.1527 | 2608725.4059 | 1226071.1608
125 | 2608724.342 | 1226088.6806 | 2608732.27 | 1226078.3194

## bus_geodata
| x | y | coords
0 | 2608835.3373 | 1226243.0861
1 | 2608850.9291 | 1226257.9232
2 | 2608832.8132 | 1226240.6843
3 | 2608818.6715 | 1226227.1706
4 | 2608811.8641 | 1226220.3304
5 | 2608790.3104 | 1226198.6749
6 | 2608680.7135 | 1226161.5692
7 | 2608659.2034 | 1226148.3155
8 | 2608699.0535 | 1226172.2872
9 | 2608647.8571 | 1226141.3243
10 | 2608699.0816 | 1226172.3032
11 | 2608644.2921 | 1226139.1276
12 | 2608722.1826 | 1226184.8175
13 | 2608662.1243 | 1226108.9468
14 | 2608630.4678 | 1226129.4054
15 | 2608745.5541 | 1226192.2559
16 | 2608440.021 | 1226015.2099
17 | 2608450.4376 | 1226034.2917
18 | 2608427.8971 | 1225993.0005
19 | 2608459.965 | 1226051.7446
20 | 2608499.4051 | 1225923.481
21 | 2608402.9029 | 1226023.4055
22 | 2608469.216 | 1226068.6911
23 | 2608512.0983 | 1225911.1408
24 | 2608384.9378 | 1226051.7859
25 | 2608391.8517 | 1226017.3723
26 | 2608476.0153 | 1226079.3819
27 | 2608518.432 | 1225904.9832
28 | 2608401.0516 | 1226058.1292
29 | 2608380.3545 | 1226059.0236
30 | 2608380.7952 | 1226011.3362
31 | 2608617.7232 | 1226200.9117
32 | 2608597.7548 | 1226189.01
33 | 2608618.8501 | 1226201.4791
34 | 2608591.3482 | 1226184.003
35 | 2608640.2846 | 1226212.2721
36 | 2608567.0738 | 1226165.0321
37 | 2608643.6628 | 1226213.9732
38 | 2608564.6224 | 1226163.1163
39 | 2608670.3317 | 1226227.4018
40 | 2608532.2641 | 1225891.5358
41 | 2608627.1581 | 1226127.0778
42 | 2608610.7863 | 1226115.564
43 | 2608600.7478 | 1226107.9494
44 | 2608589.5753 | 1226097.3725
45 | 2608576.3988 | 1226084.8983
46 | 2608654.097 | 1226100.0022
47 | 2608363.3747 | 1226001.8257
48 | 2608355.0344 | 1225997.2725
49 | 2608371.7045 | 1226006.3733
50 | 2608344.5913 | 1225991.5712
51 | 2608338.2033 | 1225988.0838
52 | 2608327.9126 | 1225982.4658
53 | 2608456.397 | 1226161.8401
54 | 2608439.9628 | 1226144.2855
55 | 2608475.5801 | 1226182.3309
56 | 2608429.0232 | 1226132.6001
57 | 2608487.9891 | 1226195.5859
58 | 2608416.2706 | 1226118.9781
59 | 2608516.2914 | 1226225.8176
60 | 2608543.6508 | 1226253.3838
61 | 2608522.325 | 1226217.99
62 | 2608327.2449 | 1226046.7971
63 | 2608309.0709 | 1226036.6477
64 | 2608343.7906 | 1226056.0372
65 | 2608291.8154 | 1226027.0112
66 | 2608372.1991 | 1226071.9022
67 | 2608273.9799 | 1226017.0508
68 | 2608381.4074 | 1226081.7383
69 | 2608786.6133 | 1226288.7617
70 | 2608771.2051 | 1226278.1928
71 | 2608803.4383 | 1226300.6082
72 | 2608768.8468 | 1226277.0052
73 | 2608830.7033 | 1226319.8054
74 | 2608753.3552 | 1226269.2041
75 | 2608859.2283 | 1226297.84
76 | 2608750.8401 | 1226267.9376
77 | 2608327.4187 | 1225982.1961
78 | 2608316.4048 | 1225976.1832
79 | 2608308.9202 | 1225972.0971
80 | 2608546.1857 | 1226254.9909
81 | 2608530.899 | 1226206.8667
82 | 2608551.9929 | 1226179.501
83 | 2608546.5054 | 1226148.9645
84 | 2608537.4515 | 1226141.8922
85 | 2608524.3985 | 1226131.6961
86 | 2608688.1816 | 1225985.5495
87 | 2608665.7013 | 1226009.6048
88 | 2608682.9333 | 1226017.7343
89 | 2608610.3041 | 1226051.2049
90 | 2608621.8173 | 1226064.0337
91 | 2608554.2685 | 1226104.8145
92 | 2608635.8804 | 1226079.7039
93 | 2608711.4149 | 1226274.0118
94 | 2608697.1091 | 1226287.3688
95 | 2608715.2668 | 1226262.5473
96 | 2608684.6378 | 1226269.0067
97 | 2608689.8326 | 1226306.4649
98 | 2608692.1213 | 1226257.5093
99 | 2608680.2931 | 1226322.643
100 | 2608709.5956 | 1226336.5281
101 | 2608703.9625 | 1226244.3313
102 | 2608637.5238 | 1226296.8661
103 | 2608643.4582 | 1226288.3342
104 | 2608620.1173 | 1226286.5741
105 | 2608717.7431 | 1226251.2709
106 | 2608737.1104 | 1226261.0237
107 | 2608693.8895 | 1226239.2614
108 | 2608682.408 | 1226233.4826
109 | 2608667.7224 | 1226253.4493
110 | 2608777.6007 | 1226198.5393
111 | 2608795.7172 | 1226150.2878
112 | 2608767.832 | 1226135.9672
113 | 2608728.4431 | 1226115.7389
114 | 2608413.1857 | 1226062.9059
115 | 2608519.8131 | 1226127.9732
116 | 2608501.3919 | 1226110.5214
117 | 2608602.151 | 1226278.3695
118 | 2608582.316 | 1226270.907
119 | 2608665.5363 | 1226256.5923
120 | 2608485.5864 | 1226091.1266
121 | 2608417.5036 | 1226064.6057
122 | 2608709.2312 | 1226071.393
123 | 2608725.4059 | 1226071.1608
124 | 2608711.3895 | 1226062.2129
125 | 2608732.27 | 1226078.3194
126 | 2608724.342 | 1226088.6806
127 | 2608644.2921 | 1226139.1276

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99 | -0.19111 | 0.00075078 | 0.00018816
1 | 0.98998 | -0.19141 | 0.00079369 | 0.00019892
2 | 0.99 | -0.19101 | 0 | 0
3 | 0.99003 | -0.19048 | 0.0065451 | 0.0016404
4 | 0.9901 | -0.18909 | 0 | 0
5 | 0.99033 | -0.1847 | 0 | 0
6 | 0.99812 | -0.035568 | 0.0022991 | 0.0005762
7 | 1 | 0 | -0.44055 | -0.11287
8 | 0.99659 | -0.064722 | 0.0015459 | 0.00038745
9 | 0.99892 | -0.020401 | 0.0016356 | 0.00040993
10 | 0.99659 | -0.064766 | 0.0016758 | 0.00042
11 | 0.99858 | -0.02679 | 0 | 0
12 | 0.99477 | -0.099524 | 0.0020268 | 0.00050796
13 | 0.99721 | -0.053026 | 0.0016066 | 0.00040264
14 | 0.99738 | -0.049455 | 0.0013487 | 0.00033802
15 | 0.99312 | -0.13114 | 0.0049622 | 0.0012436
16 | 0.98212 | -0.34234 | 0.0030082 | 0.00075392
17 | 0.9829 | -0.32721 | 0.00057662 | 0.00014452
18 | 0.98129 | -0.35859 | 0 | 0
19 | 0.98361 | -0.3132 | 0.00060466 | 0.00015154
20 | 0.98058 | -0.37258 | 0.0007066 | 0.00017709
21 | 0.98028 | -0.37837 | 0 | 0
22 | 0.98432 | -0.29939 | 0.0021741 | 0.00054487
23 | 0.98046 | -0.37484 | 0.0032839 | 0.00082301
24 | 0.97975 | -0.3888 | 0 | 0
25 | 0.98016 | -0.3808 | 0.0018218 | 0.00045659
26 | 0.98482 | -0.28982 | 0.00055781 | 0.0001398
27 | 0.98043 | -0.37544 | 0.0019684 | 0.00049334
28 | 0.97966 | -0.39059 | 0.0020472 | 0.00051308
29 | 0.97966 | -0.39058 | 0.0019165 | 0.00048032
30 | 0.98005 | -0.38282 | 0.0017514 | 0.00043894
31 | 0.98145 | -0.35486 | 0.0016392 | 0.00041081
32 | 0.98265 | -0.33156 | 0.0018474 | 0.00046301
33 | 0.98139 | -0.35611 | 0.010319 | 0.0025862
34 | 0.98307 | -0.32339 | 0.0017734 | 0.00044446
35 | 0.98023 | -0.37882 | 0.020506 | 0.0051392
36 | 0.98468 | -0.29226 | 0.0021645 | 0.00054247
37 | 0.98006 | -0.38205 | 0.013915 | 0.0034874
38 | 0.98484 | -0.28909 | 0 | 0
39 | 0.97885 | -0.40571 | 0.017126 | 0.0042923
40 | 0.9804 | -0.37607 | 0.0017845 | 0.00044724
41 | 0.99709 | -0.054865 | 0.0018344 | 0.00045974
42 | 0.99568 | -0.081513 | 0.0025289 | 0.00063381
43 | 0.9948 | -0.098219 | 0.0029404 | 0.00073694
44 | 0.99374 | -0.11842 | 0.0042247 | 0.0010588
45 | 0.9925 | -0.14196 | 0 | 0
46 | 0.99676 | -0.061698 | 0.0032221 | 0.00080753
47 | 0.97993 | -0.38528 | 0.0019464 | 0.00048782
48 | 0.97989 | -0.38608 | 0.00051759 | 0.00012972
49 | 0.97998 | -0.38415 | 0.00049088 | 0.00012303
50 | 0.97984 | -0.38697 | 0.0018246 | 0.00045729
51 | 0.97983 | -0.38727 | 0.00040359 | 0.00010115
52 | 0.97981 | -0.38767 | 0.00027745 | 6.9535e-05
53 | 0.98317 | -0.32178 | 0.0012741 | 0.00031932
54 | 0.98305 | -0.324 | 0.0026673 | 0.00066848
55 | 0.98333 | -0.31855 | 0.0012761 | 0.00031983
56 | 0.98302 | -0.3247 | 0.0012439 | 0.00031176
57 | 0.98346 | -0.31604 | 0.00073693 | 0.00018469
58 | 0.983 | -0.32511 | 0.001198 | 0.00030025
59 | 0.98378 | -0.30978 | 0 | 0
60 | 0.98372 | -0.31104 | 0 | 0
61 | 0.98388 | -0.30796 | 0.0014692 | 0.00036822
62 | 0.97916 | -0.4003 | 0.0016348 | 0.00040972
63 | 0.97906 | -0.40231 | 0.0015547 | 0.00038964
64 | 0.97928 | -0.39791 | 0.00099122 | 0.00024842
65 | 0.97899 | -0.40366 | 0.0015356 | 0.00038487
66 | 0.97952 | -0.39322 | 0 | 0
67 | 0.97895 | -0.40448 | 0.0022178 | 0.00055584
68 | 0.9795 | -0.3936 | 0.0015792 | 0.00039579
69 | 0.97491 | -0.48316 | 0.0038087 | 0.00095456
70 | 0.97499 | -0.48148 | 0.0035209 | 0.00088243
71 | 0.97489 | -0.48357 | 0.00060293 | 0.00015111
72 | 0.97501 | -0.48107 | 0.0023539 | 0.00058993
73 | 0.97487 | -0.48387 | 0 | 0
74 | 0.97519 | -0.47765 | 0.0033805 | 0.00084722
75 | 0.97486 | -0.48419 | 0.0004836 | 0.0001212
76 | 0.97522 | -0.47692 | 0.0032739 | 0.00082052
77 | 0.9798 | -0.38769 | 0.00055472 | 0.00013902
78 | 0.97979 | -0.38793 | 0.00058179 | 0.00014581
79 | 0.97979 | -0.388 | 0.00047034 | 0.00011788
80 | 0.98371 | -0.31114 | 0.0018137 | 0.00045456
81 | 0.98403 | -0.305 | 0.0039653 | 0.00099379
82 | 0.98452 | -0.29527 | 0.00098203 | 0.00024612
83 | 0.98614 | -0.26399 | 0.0014949 | 0.00037466
84 | 0.98679 | -0.2514 | 0.0017796 | 0.000446
85 | 0.98774 | -0.23314 | 0 | 0
86 | 0.99166 | -0.16013 | 0.025453 | 0.006379
87 | 0.99242 | -0.14529 | 0 | 0
88 | 0.99231 | -0.14742 | 0.0063334 | 0.0015873
89 | 0.99464 | -0.10245 | 0 | 0
90 | 0.99514 | -0.092801 | 0.0031448 | 0.00078816
91 | 0.99047 | -0.18071 | 0.00066139 | 0.00016576
92 | 0.99581 | -0.079863 | 0.002992 | 0.00074988
93 | 0.97503 | -0.48074 | 0.0031759 | 0.00079597
94 | 0.97522 | -0.47706 | 0 | 0
95 | 0.97495 | -0.4824 | 0.0068073 | 0.0017061
96 | 0.97553 | -0.47081 | 0 | 0
97 | 0.9752 | -0.47746 | 0.00060202 | 0.00015088
98 | 0.97568 | -0.46803 | 0.023735 | 0.0059486
99 | 0.97519 | -0.47762 | 0 | 0
100 | 0.97518 | -0.47789 | 0.00046105 | 0.00011555
101 | 0.97625 | -0.45675 | 0 | 0
102 | 0.97404 | -0.50026 | 0 | 0
103 | 0.97437 | -0.49376 | 0.0078702 | 0.0019725
104 | 0.9734 | -0.5129 | 0.017525 | 0.0043922
105 | 0.97587 | -0.46411 | 0.0061795 | 0.0015487
106 | 0.97547 | -0.47201 | 0.002466 | 0.00061804
107 | 0.97689 | -0.4442 | 0.020665 | 0.0051791
108 | 0.97786 | -0.42508 | 0 | 0
109 | 0.97611 | -0.4594 | 0.0091422 | 0.0022912
110 | 0.99105 | -0.17079 | 0.0066435 | 0.001665
111 | 0.98793 | -0.23101 | 0 | 0
112 | 0.98638 | -0.26093 | 0.0078385 | 0.0019645
113 | 0.98452 | -0.29711 | 0.0016978 | 0.00042551
114 | 0.97961 | -0.39145 | 0.0013355 | 0.0003347
115 | 0.98749 | -0.23804 | 0.0013244 | 0.00033192
116 | 0.98642 | -0.2586 | 0.001233 | 0.00030901
117 | 0.97309 | -0.51892 | 0.015239 | 0.0038192
118 | 0.97307 | -0.5194 | 0.0012515 | 0.00031366
119 | 0.97587 | -0.46408 | 0.024792 | 0.0062135
120 | 0.98541 | -0.27827 | 0.0013898 | 0.00034832
121 | 0.9796 | -0.39165 | 0.0023043 | 0.00057752
122 | 0.98197 | -0.34693 | 0 | 0
123 | 0.9816 | -0.35411 | 0 | 0
124 | 0.9818 | -0.3502 | 0.019195 | 0.0048108
125 | 0.98104 | -0.365 | 0 | 0
126 | 0.98075 | -0.37082 | 0.024629 | 0.0061725
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0007937 | 0.00019865 | -0.00079369 | -0.00019892 | 1.1486e-08 | -2.6939e-07 | 0.0011929 | 0.001193 | 0.001193 | 0.99 | -0.19111 | 0.98998 | -0.19141 | 0.32774
1 | -0.0015445 | -0.00038681 | 0.0015445 | 0.00038677 | 7.0407e-09 | -4.0295e-08 | 0.0023213 | 0.0023213 | 0.0023213 | 0.99 | -0.19111 | 0.99 | -0.19101 | 0.63773
2 | -0.0015445 | -0.00038677 | 0.0015445 | 0.00038654 | 3.9525e-08 | -2.2623e-07 | 0.0023213 | 0.0023212 | 0.0023213 | 0.99 | -0.19101 | 0.99003 | -0.19048 | 0.63773
3 | -0.0080897 | -0.0020269 | 0.0080902 | 0.0020271 | 5.3498e-07 | 2.1828e-07 | 0.012159 | 0.012159 | 0.012159 | 0.99003 | -0.19048 | 0.9901 | -0.18909 | 3.3403
4 | -0.0080902 | -0.0020271 | 0.0080919 | 0.0020278 | 1.6914e-06 | 6.9e-07 | 0.012159 | 0.012158 | 0.012159 | 0.9901 | -0.18909 | 0.99033 | -0.1847 | 3.3403
5 | 0.053771 | 0.013633 | -0.053652 | -0.013557 | 0.00011939 | 7.5784e-05 | 0.08085 | 0.08085 | 0.08085 | 0.99033 | -0.1847 | 0.98793 | -0.23101 | 22.2115
6 | -0.061863 | -0.015661 | 0.061904 | 0.015687 | 4.1333e-05 | 2.6289e-05 | 0.093008 | 0.093008 | 0.093008 | 0.99033 | -0.1847 | 0.99105 | -0.17079 | 25.5516
7 | -0.081539 | -0.020794 | 0.08168 | 0.020884 | 0.0001403 | 8.9459e-05 | 0.12169 | 0.12169 | 0.12169 | 0.99812 | -0.035568 | 1 | 0 | 33.4304
8 | 0.07924 | 0.020218 | -0.079129 | -0.020147 | 0.00011142 | 7.1031e-05 | 0.11826 | 0.11826 | 0.11826 | 0.99812 | -0.035568 | 0.99659 | -0.064722 | 32.4889
9 | 0.35722 | 0.091982 | -0.35687 | -0.091756 | 0.00035419 | 0.00022598 | 0.53243 | 0.53243 | 0.53243 | 1 | 0 | 0.99892 | -0.020401 | 36.5679
10 | 0.077583 | 0.01976 | -0.077583 | -0.01976 | 1.6287e-07 | 1.0382e-07 | 0.11595 | 0.11595 | 0.11595 | 0.99659 | -0.064722 | 0.99659 | -0.064766 | 31.8547
11 | 0.35523 | 0.091346 | -0.35512 | -0.091276 | 0.00011027 | 7.0354e-05 | 0.52999 | 0.52999 | 0.52999 | 0.99892 | -0.020401 | 0.99858 | -0.02679 | 36.4005
12 | 0.075907 | 0.01934 | -0.07578 | -0.019259 | 0.00012706 | 8.0979e-05 | 0.11345 | 0.11345 | 0.11345 | 0.99659 | -0.064766 | 0.99477 | -0.099524 | 31.1674
13 | 0.042976 | 0.010855 | -0.042922 | -0.010821 | 5.3962e-05 | 3.4078e-05 | 0.06407 | 0.06407 | 0.06407 | 0.99858 | -0.02679 | 0.99721 | -0.053026 | 17.6016
14 | 0.31215 | 0.080421 | -0.3118 | -0.080201 | 0.00034396 | 0.00021925 | 0.46592 | 0.46592 | 0.46592 | 0.99858 | -0.02679 | 0.99738 | -0.049455 | 32.0002
15 | 0.073753 | 0.018751 | -0.073641 | -0.018679 | 0.00011214 | 7.1449e-05 | 0.11042 | 0.11042 | 0.11042 | 0.99477 | -0.099524 | 0.99312 | -0.13114 | 30.3345
16 | 0.041315 | 0.010418 | -0.041298 | -0.010407 | 1.7142e-05 | 1.0814e-05 | 0.061672 | 0.061673 | 0.061673 | 0.99721 | -0.053026 | 0.99676 | -0.061698 | 16.943
17 | 0.31046 | 0.079863 | -0.31037 | -0.079811 | 8.1637e-05 | 5.2037e-05 | 0.46391 | 0.46391 | 0.46391 | 0.99738 | -0.049455 | 0.99709 | -0.054865 | 31.862
18 | 0.068679 | 0.017435 | -0.068548 | -0.017352 | 0.00013075 | 8.3258e-05 | 0.10298 | 0.10298 | 0.10298 | 0.99312 | -0.13114 | 0.99105 | -0.17079 | 28.292
19 | -0.038587 | -0.0096944 | 0.038615 | 0.009712 | 2.7873e-05 | 1.7563e-05 | 0.058472 | 0.058472 | 0.058472 | 0.98212 | -0.34234 | 0.9829 | -0.32721 | 16.0637
20 | 0.035579 | 0.0089405 | -0.035551 | -0.0089232 | 2.7581e-05 | 1.7332e-05 | 0.053914 | 0.053914 | 0.053914 | 0.98212 | -0.34234 | 0.98129 | -0.35859 | 14.8116
21 | -0.039192 | -0.0098565 | 0.039218 | 0.0098731 | 2.626e-05 | 1.6554e-05 | 0.059345 | 0.059345 | 0.059345 | 0.9829 | -0.32721 | 0.98361 | -0.3132 | 16.3035
22 | 0.0077495 | 0.0019427 | -0.0077443 | -0.0019407 | 5.1649e-06 | 2.0465e-06 | 0.011751 | 0.011752 | 0.011752 | 0.98129 | -0.35859 | 0.98058 | -0.37258 | 3.2285
23 | 0.027802 | 0.0069804 | -0.027776 | -0.0069642 | 2.621e-05 | 1.6279e-05 | 0.042163 | 0.042163 | 0.042163 | 0.98129 | -0.35859 | 0.98028 | -0.37837 | 11.5833
24 | -0.039822 | -0.010025 | 0.039849 | 0.010041 | 2.629e-05 | 1.6581e-05 | 0.060259 | 0.060259 | 0.060259 | 0.98361 | -0.3132 | 0.98432 | -0.29939 | 16.5548
25 | 0.0070377 | 0.0017636 | -0.007037 | -0.0017633 | 7.5717e-07 | 2.613e-07 | 0.01068 | 0.01068 | 0.01068 | 0.98058 | -0.37258 | 0.98046 | -0.37484 | 2.934
26 | 0.017132 | 0.0042966 | -0.017123 | -0.0042916 | 8.5128e-06 | 5.0253e-06 | 0.026006 | 0.026006 | 0.026006 | 0.98028 | -0.37837 | 0.97975 | -0.3888 | 7.1446
27 | 0.010644 | 0.0026676 | -0.010643 | -0.0026669 | 1.2325e-06 | 6.3012e-07 | 0.016157 | 0.016157 | 0.016157 | 0.98028 | -0.37837 | 0.98016 | -0.3808 | 4.4387
28 | -0.042023 | -0.010586 | 0.042042 | 0.010598 | 1.9261e-05 | 1.2165e-05 | 0.063546 | 0.063546 | 0.063546 | 0.98432 | -0.29939 | 0.98482 | -0.28982 | 17.4577
29 | 0.0037531 | 0.00094032 | -0.003753 | -0.00094037 | 1.0747e-07 | -4.262e-08 | 0.0056959 | 0.0056959 | 0.0056959 | 0.98046 | -0.37484 | 0.98043 | -0.37544 | 1.5648
30 | 0.0056877 | 0.0014253 | -0.0056872 | -0.0014252 | 4.8458e-07 | 9.2072e-08 | 0.0086383 | 0.0086383 | 0.0086383 | 0.97975 | -0.3888 | 0.97966 | -0.39059 | 2.3732
31 | 0.011435 | 0.0028663 | -0.011435 | -0.0028658 | 9.6907e-07 | 5.1233e-07 | 0.017368 | 0.017368 | 0.017368 | 0.97975 | -0.3888 | 0.97966 | -0.39058 | 4.7715
32 | 0.0088209 | 0.0022103 | -0.00882 | -0.00221 | 8.471e-07 | 3.8339e-07 | 0.013391 | 0.013391 | 0.013391 | 0.98016 | -0.3808 | 0.98005 | -0.38282 | 3.6789
33 | -0.0426 | -0.010738 | 0.042623 | 0.010753 | 2.3555e-05 | 1.4882e-05 | 0.064389 | 0.064389 | 0.064389 | 0.98482 | -0.28982 | 0.98541 | -0.27827 | 17.6892
34 | 0.0017846 | 0.00044703 | -0.0017845 | -0.00044724 | 5.3067e-08 | -2.0931e-07 | 0.0027084 | 0.0027085 | 0.0027085 | 0.98043 | -0.37544 | 0.9804 | -0.37607 | 0.74408
35 | 0.00364 | 0.00091211 | -0.0036398 | -0.00091218 | 1.4948e-07 | -6.8516e-08 | 0.0055288 | 0.0055288 | 0.0055288 | 0.97966 | -0.39059 | 0.97961 | -0.39145 | 1.5189
36 | 0.009518 | 0.0023855 | -0.0095168 | -0.0023849 | 1.1948e-06 | 5.7274e-07 | 0.014457 | 0.014457 | 0.014457 | 0.97966 | -0.39058 | 0.97952 | -0.39322 | 3.9717
37 | 0.0070686 | 0.001771 | -0.0070682 | -0.0017709 | 4.4735e-07 | 1.558e-07 | 0.010732 | 0.010732 | 0.010732 | 0.98005 | -0.38282 | 0.97998 | -0.38415 | 2.9484
38 | -0.22185 | -0.055985 | 0.2221 | 0.056142 | 0.00024787 | 0.00015745 | 0.33649 | 0.33649 | 0.33649 | 0.98145 | -0.35486 | 0.98265 | -0.33156 | 23.1108
39 | 0.22021 | 0.055574 | -0.2202 | -0.055565 | 1.3196e-05 | 8.3814e-06 | 0.33401 | 0.33401 | 0.33401 | 0.98145 | -0.35486 | 0.98139 | -0.35611 | 22.9402
40 | -0.22395 | -0.056605 | 0.22403 | 0.056661 | 8.7753e-05 | 5.575e-05 | 0.33929 | 0.33929 | 0.33929 | 0.98265 | -0.33156 | 0.98307 | -0.32339 | 23.3029
41 | 0.20988 | 0.052979 | -0.20965 | -0.052834 | 0.00022803 | 0.00014473 | 0.31836 | 0.31836 | 0.31836 | 0.98139 | -0.35611 | 0.98023 | -0.37882 | 21.8656
42 | -0.22581 | -0.057105 | 0.22615 | 0.05732 | 0.00033777 | 0.00021461 | 0.34198 | 0.34197 | 0.34198 | 0.98307 | -0.32339 | 0.98468 | -0.29226 | 23.4873
43 | 0.18915 | 0.047695 | -0.18912 | -0.047677 | 2.9255e-05 | 1.8533e-05 | 0.28723 | 0.28723 | 0.28723 | 0.98023 | -0.37882 | 0.98006 | -0.38205 | 19.7277
44 | -0.22831 | -0.057862 | 0.22834 | 0.057884 | 3.4767e-05 | 2.2092e-05 | 0.34525 | 0.34525 | 0.34525 | 0.98468 | -0.29226 | 0.98484 | -0.28909 | 23.7119
45 | 0.1752 | 0.044189 | -0.175 | -0.044064 | 0.00019823 | 0.00012536 | 0.26611 | 0.26611 | 0.26611 | 0.98006 | -0.38205 | 0.97885 | -0.40571 | 18.2767
46 | -0.24499 | -0.062061 | 0.24529 | 0.062249 | 0.00029569 | 0.00018807 | 0.3704 | 0.3704 | 0.3704 | 0.98484 | -0.28909 | 0.98614 | -0.26399 | 25.4394
47 | 0.016646 | 0.0041763 | -0.016642 | -0.0041735 | 4.9081e-06 | 2.878e-06 | 0.025153 | 0.025153 | 0.025153 | 0.98484 | -0.28909 | 0.98452 | -0.29527 | 6.9102
48 | 0.15788 | 0.039772 | -0.15773 | -0.039679 | 0.00014611 | 9.3173e-05 | 0.24007 | 0.24007 | 0.24007 | 0.97885 | -0.40571 | 0.97786 | -0.42508 | 32.9771
49 | 0.30854 | 0.079352 | -0.30814 | -0.079097 | 0.00039908 | 0.00025437 | 0.46117 | 0.46117 | 0.46117 | 0.99709 | -0.054865 | 0.99568 | -0.081513 | 31.674
50 | 0.30561 | 0.078463 | -0.30536 | -0.078306 | 0.00024761 | 0.00015782 | 0.45739 | 0.45739 | 0.45739 | 0.99568 | -0.081513 | 0.9948 | -0.098219 | 31.4145
51 | 0.30242 | 0.077569 | -0.30213 | -0.07738 | 0.00029597 | 0.00018863 | 0.453 | 0.453 | 0.453 | 0.9948 | -0.098219 | 0.99374 | -0.11842 | 31.1124
52 | 0.2979 | 0.076321 | -0.29756 | -0.076105 | 0.00033939 | 0.00021627 | 0.44667 | 0.44667 | 0.44667 | 0.99374 | -0.11842 | 0.9925 | -0.14196 | 30.678
53 | 0.29756 | 0.076105 | -0.29701 | -0.07575 | 0.00055688 | 0.00035487 | 0.44667 | 0.44667 | 0.44667 | 0.9925 | -0.14196 | 0.99047 | -0.18071 | 30.678
54 | 0.038076 | 0.0095999 | -0.038043 | -0.0095791 | 3.307e-05 | 2.0809e-05 | 0.056862 | 0.056863 | 0.056863 | 0.99676 | -0.061698 | 0.99581 | -0.079863 | 15.6216
55 | 0.0046305 | 0.0011599 | -0.0046304 | -0.0011599 | 1.7617e-07 | -6.957e-09 | 0.0070312 | 0.0070313 | 0.0070313 | 0.97993 | -0.38528 | 0.97989 | -0.38608 | 1.9317
56 | -0.0065769 | -0.0016477 | 0.0065773 | 0.0016478 | 3.5495e-07 | 1.076e-07 | 0.0099869 | 0.0099868 | 0.0099869 | 0.97993 | -0.38528 | 0.97998 | -0.38415 | 2.7436
57 | 0.0041128 | 0.0010302 | -0.0041126 | -0.0010302 | 1.7403e-07 | -3.8494e-08 | 0.0062453 | 0.0062453 | 0.0062453 | 0.97989 | -0.38608 | 0.97984 | -0.38697 | 1.7157
58 | 0.002288 | 0.00057294 | -0.0022879 | -0.00057301 | 3.2946e-08 | -7.0583e-08 | 0.0034744 | 0.0034744 | 0.0034744 | 0.97984 | -0.38697 | 0.97983 | -0.38727 | 0.95452
59 | 0.0018843 | 0.00047186 | -0.0018843 | -0.00047199 | 3.6002e-08 | -1.2463e-07 | 0.0028615 | 0.0028616 | 0.0028616 | 0.97983 | -0.38727 | 0.97981 | -0.38767 | 0.78615
60 | 0.0016069 | 0.00040245 | -0.0016069 | -0.00040246 | 1.2567e-09 | -6.283e-09 | 0.0024402 | 0.0024402 | 0.0024402 | 0.97981 | -0.38767 | 0.9798 | -0.38769 | 0.67039
61 | 0.0051098 | 0.0012802 | -0.0051093 | -0.0012801 | 5.3932e-07 | 4.0257e-08 | 0.0077335 | 0.0077336 | 0.0077336 | 0.98317 | -0.32178 | 0.98305 | -0.324 | 2.1246
62 | -0.0063839 | -0.0015995 | 0.0063849 | 0.0015997 | 9.8259e-07 | 2.7284e-07 | 0.0096618 | 0.0096617 | 0.0096618 | 0.98317 | -0.32178 | 0.98333 | -0.31855 | 2.6544
63 | 0.0024421 | 0.00061164 | -0.002442 | -0.00061179 | 8.2013e-08 | -1.5045e-07 | 0.0036963 | 0.0036964 | 0.0036964 | 0.98305 | -0.324 | 0.98302 | -0.3247 | 1.0155
64 | -0.007661 | -0.0019196 | 0.007662 | 0.0019199 | 9.1506e-07 | 3.5528e-07 | 0.011593 | 0.011593 | 0.011593 | 0.98333 | -0.31855 | 0.98346 | -0.31604 | 3.1848
65 | 0.001198 | 0.00030003 | -0.001198 | -0.00030025 | 2.3012e-08 | -2.2183e-07 | 0.0018134 | 0.0018135 | 0.0018135 | 0.98302 | -0.3247 | 0.983 | -0.32511 | 0.49822
66 | -0.0083989 | -0.0021046 | 0.0084014 | 0.0021057 | 2.5078e-06 | 1.0793e-06 | 0.012708 | 0.012708 | 0.012708 | 0.98346 | -0.31604 | 0.98378 | -0.30978 | 3.4911
67 | 0.0018138 | 0.00045411 | -0.0018137 | -0.00045453 | 1.0947e-07 | -4.2237e-07 | 0.0027433 | 0.0027435 | 0.0027435 | 0.98378 | -0.30978 | 0.98372 | -0.31104 | 0.75371
68 | -0.010215 | -0.0025598 | 0.010216 | 0.0025602 | 8.8477e-07 | 4.4075e-07 | 0.015451 | 0.015451 | 0.015451 | 0.98378 | -0.30978 | 0.98388 | -0.30796 | 4.2447
69 | 0.0018137 | 0.00045453 | -0.0018137 | -0.00045456 | 8.4719e-09 | -3.2683e-08 | 0.0027435 | 0.0027435 | 0.0027435 | 0.98372 | -0.31104 | 0.98371 | -0.31114 | 0.75372
70 | -0.011685 | -0.0029285 | 0.011687 | 0.0029293 | 1.6449e-06 | 8.7435e-07 | 0.017673 | 0.017673 | 0.017673 | 0.98388 | -0.30796 | 0.98403 | -0.305 | 4.8552
71 | 0.005309 | 0.0013301 | -0.0053085 | -0.0013301 | 5.081e-07 | 6.3384e-08 | 0.0080679 | 0.0080679 | 0.0080679 | 0.97916 | -0.4003 | 0.97906 | -0.40231 | 2.2165
72 | -0.0069438 | -0.0017398 | 0.0069446 | 0.0017401 | 7.9131e-07 | 2.6804e-07 | 0.010552 | 0.010552 | 0.010552 | 0.97916 | -0.4003 | 0.97928 | -0.39791 | 2.899
73 | 0.0037538 | 0.00094041 | -0.0037536 | -0.00094051 | 2.4123e-07 | -9.4139e-08 | 0.005705 | 0.0057051 | 0.0057051 | 0.97906 | -0.40231 | 0.97899 | -0.40366 | 1.5673
74 | -0.0079358 | -0.0019885 | 0.0079376 | 0.0019893 | 1.7742e-06 | 7.2598e-07 | 0.012058 | 0.012058 | 0.012058 | 0.97928 | -0.39791 | 0.97952 | -0.39322 | 3.3127
75 | 0.0022179 | 0.00055564 | -0.0022178 | -0.00055584 | 8.7056e-08 | -2.0113e-07 | 0.003371 | 0.0033711 | 0.0033711 | 0.97899 | -0.40366 | 0.97895 | -0.40448 | 0.92613
76 | 0.0015792 | 0.00039564 | -0.0015792 | -0.00039579 | 2.908e-08 | -1.5099e-07 | 0.002399 | 0.0023991 | 0.0023991 | 0.97952 | -0.39322 | 0.9795 | -0.3936 | 0.65909
77 | -0.0048953 | -0.0012258 | 0.0048957 | 0.0012258 | 3.9144e-07 | 1.733e-08 | 0.0074714 | 0.0074713 | 0.0074714 | 0.97491 | -0.48316 | 0.97499 | -0.48148 | 2.0526
78 | 0.0010866 | 0.00027121 | -0.0010865 | -0.00027145 | 2.1215e-08 | -2.43e-07 | 0.001658 | 0.0016581 | 0.0016581 | 0.97491 | -0.48316 | 0.97489 | -0.48357 | 0.45553
79 | -0.0084166 | -0.0021082 | 0.0084168 | 0.0021083 | 1.6337e-07 | 7.1627e-08 | 0.012845 | 0.012845 | 0.012845 | 0.97499 | -0.48148 | 0.97501 | -0.48107 | 3.5288
80 | 0.00048362 | 0.00012035 | -0.00048361 | -0.00012076 | 6.8093e-09 | -4.1141e-07 | 0.00073786 | 0.00073801 | 0.00073801 | 0.97489 | -0.48357 | 0.97487 | -0.48387 | 0.20275
81 | -0.010771 | -0.0026982 | 0.010772 | 0.0026991 | 1.7574e-06 | 9.0834e-07 | 0.016437 | 0.016437 | 0.016437 | 0.97501 | -0.48107 | 0.97519 | -0.47765 | 4.5157
82 | 0.00048361 | 0.00012076 | -0.0004836 | -0.0001212 | 7.3549e-09 | -4.4417e-07 | 0.00073801 | 0.00073817 | 0.00073817 | 0.97487 | -0.48387 | 0.97486 | -0.48419 | 0.20279
83 | -0.014153 | -0.0035464 | 0.014153 | 0.0035466 | 4.9247e-07 | 2.8005e-07 | 0.021595 | 0.021595 | 0.021595 | 0.97519 | -0.47765 | 0.97522 | -0.47692 | 5.9328
84 | -0.017427 | -0.0043672 | 0.017431 | 0.0043696 | 4.0759e-06 | 2.4167e-06 | 0.026591 | 0.026591 | 0.026591 | 0.97522 | -0.47692 | 0.97547 | -0.47201 | 7.3051
85 | 0.0010521 | 0.00026343 | -0.0010521 | -0.00026358 | 1.2014e-08 | -1.5035e-07 | 0.0015978 | 0.0015978 | 0.0015978 | 0.9798 | -0.38769 | 0.97979 | -0.38793 | 0.43897
86 | 0.00047034 | 0.00011777 | -0.00047034 | -0.00011788 | 1.6315e-09 | -1.0635e-07 | 0.00071427 | 0.00071431 | 0.00071431 | 0.97979 | -0.38793 | 0.97979 | -0.388 | 0.19624
87 | -0.015652 | -0.0039231 | 0.015659 | 0.0039273 | 7.2587e-06 | 4.2064e-06 | 0.023669 | 0.023669 | 0.023669 | 0.98403 | -0.305 | 0.98452 | -0.29527 | 6.5025
88 | -0.24678 | -0.062624 | 0.24693 | 0.062719 | 0.00014957 | 9.5141e-05 | 0.37265 | 0.37265 | 0.37265 | 0.98614 | -0.26399 | 0.98679 | -0.2514 | 25.5943
89 | -0.24871 | -0.063165 | 0.24893 | 0.063304 | 0.00021875 | 0.00013916 | 0.37534 | 0.37534 | 0.37534 | 0.98679 | -0.2514 | 0.98774 | -0.23314 | 25.7786
90 | 0.046668 | 0.011804 | -0.046657 | -0.011797 | 1.096e-05 | 6.9386e-06 | 0.070343 | 0.070343 | 0.070343 | 0.98774 | -0.23314 | 0.98749 | -0.23804 | 19.3249
91 | -0.2956 | -0.075107 | 0.29635 | 0.075584 | 0.00074831 | 0.00047685 | 0.44568 | 0.44568 | 0.44568 | 0.98774 | -0.23314 | 0.99047 | -0.18071 | 30.6098
92 | -0.025453 | -0.006379 | 0.025471 | 0.0063901 | 1.801e-05 | 1.1101e-05 | 0.038193 | 0.038193 | 0.038193 | 0.99166 | -0.16013 | 0.99242 | -0.14529 | 10.4925
93 | 0.0063341 | 0.0015875 | -0.0063334 | -0.0015873 | 6.4446e-07 | 1.6629e-07 | 0.0094972 | 0.0094973 | 0.0094973 | 0.99242 | -0.14529 | 0.99231 | -0.14742 | 2.6091
94 | -0.031805 | -0.0079776 | 0.03187 | 0.0080183 | 6.5086e-05 | 4.0667e-05 | 0.04769 | 0.047689 | 0.04769 | 0.99242 | -0.14529 | 0.99464 | -0.10245 | 13.1016
95 | -0.03187 | -0.0080183 | 0.031885 | 0.0080275 | 1.4701e-05 | 9.1849e-06 | 0.047689 | 0.047689 | 0.047689 | 0.99464 | -0.10245 | 0.99514 | -0.092801 | 13.1015
96 | -0.035029 | -0.0088156 | 0.035051 | 0.0088292 | 2.1673e-05 | 1.3597e-05 | 0.052392 | 0.052392 | 0.052392 | 0.99514 | -0.092801 | 0.99581 | -0.079863 | 14.3933
97 | -0.0099838 | -0.0025022 | 0.0099856 | 0.0025031 | 1.7531e-06 | 8.7078e-07 | 0.015237 | 0.015236 | 0.015237 | 0.97503 | -0.48074 | 0.97522 | -0.47706 | 4.1859
98 | 0.0068079 | 0.0017063 | -0.0068073 | -0.0017061 | 5.3911e-07 | 1.7894e-07 | 0.01039 | 0.01039 | 0.01039 | 0.97503 | -0.48074 | 0.97495 | -0.4824 | 2.8543
99 | -0.011049 | -0.0027687 | 0.011052 | 0.0027704 | 3.2878e-06 | 1.7192e-06 | 0.016858 | 0.016858 | 0.016858 | 0.97522 | -0.47706 | 0.97553 | -0.47081 | 4.6314
100 | 0.0010631 | 0.00026555 | -0.0010631 | -0.0002658 | 2.0384e-08 | -2.4479e-07 | 0.0016218 | 0.0016219 | 0.0016219 | 0.97522 | -0.47706 | 0.9752 | -0.47746 | 0.44557
101 | -0.011052 | -0.0027704 | 0.011053 | 0.0027711 | 1.462e-06 | 7.6438e-07 | 0.016858 | 0.016858 | 0.016858 | 0.97553 | -0.47081 | 0.97568 | -0.46803 | 4.6314
102 | 0.00046106 | 0.00011492 | -0.00046105 | -0.00011515 | 3.4839e-09 | -2.3209e-07 | 0.00070328 | 0.00070336 | 0.00070336 | 0.9752 | -0.47746 | 0.97519 | -0.47762 | 0.19323
103 | -0.034789 | -0.0087198 | 0.034807 | 0.0087315 | 1.8717e-05 | 1.1758e-05 | 0.053057 | 0.053057 | 0.053057 | 0.97568 | -0.46803 | 0.97625 | -0.45675 | 14.5761
104 | 0.00046105 | 0.00011515 | -0.00046105 | -0.00011555 | 6.0201e-09 | -4.0091e-07 | 0.00070336 | 0.00070351 | 0.00070351 | 0.97519 | -0.47762 | 0.97518 | -0.47789 | 0.19327
105 | -0.060901 | -0.015278 | 0.060937 | 0.015301 | 3.6443e-05 | 2.3183e-05 | 0.092832 | 0.092832 | 0.092832 | 0.97625 | -0.45675 | 0.97689 | -0.4442 | 25.5033
106 | 0.026094 | 0.0065465 | -0.026084 | -0.0065409 | 9.1536e-06 | 5.6655e-06 | 0.039775 | 0.039775 | 0.039775 | 0.97625 | -0.45675 | 0.97587 | -0.46411 | 10.9272
107 | -0.03404 | -0.0085404 | 0.034051 | 0.008547 | 1.0541e-05 | 6.6167e-06 | 0.052006 | 0.052006 | 0.052006 | 0.97404 | -0.50026 | 0.97437 | -0.49376 | 14.2874
108 | 0.03404 | 0.0085404 | -0.03402 | -0.0085275 | 2.051e-05 | 1.2875e-05 | 0.052006 | 0.052006 | 0.052006 | 0.97404 | -0.50026 | 0.9734 | -0.5129 | 14.2874
109 | -0.041921 | -0.010519 | 0.041981 | 0.010557 | 5.9436e-05 | 3.7557e-05 | 0.064025 | 0.064025 | 0.064025 | 0.97437 | -0.49376 | 0.97587 | -0.46408 | 17.5894
110 | 0.016495 | 0.0041354 | -0.01649 | -0.0041326 | 4.7267e-06 | 2.7787e-06 | 0.025216 | 0.025216 | 0.025216 | 0.9734 | -0.5129 | 0.97309 | -0.51892 | 6.9276
111 | 0.019905 | 0.0049921 | -0.019897 | -0.0049876 | 7.4913e-06 | 4.5237e-06 | 0.030352 | 0.030352 | 0.030352 | 0.97587 | -0.46411 | 0.97547 | -0.47201 | 8.3386
112 | -0.081602 | -0.02048 | 0.081677 | 0.020528 | 7.4485e-05 | 4.7509e-05 | 0.12431 | 0.12431 | 0.12431 | 0.97689 | -0.4442 | 0.97786 | -0.42508 | 34.1508
113 | 0.076054 | 0.019151 | -0.07593 | -0.019071 | 0.00012457 | 7.9416e-05 | 0.11576 | 0.11576 | 0.11576 | 0.97786 | -0.42508 | 0.97611 | -0.4594 | 31.8035
114 | 0.066788 | 0.01678 | -0.066773 | -0.016771 | 1.4887e-05 | 9.4796e-06 | 0.10183 | 0.10183 | 0.10183 | 0.97611 | -0.4594 | 0.97587 | -0.46408 | 27.9748
115 | 0.053652 | 0.013557 | -0.053575 | -0.013509 | 7.6841e-05 | 4.8777e-05 | 0.08085 | 0.08085 | 0.08085 | 0.98793 | -0.23101 | 0.98638 | -0.26093 | 22.2115
116 | 0.045736 | 0.011544 | -0.045657 | -0.011494 | 7.9113e-05 | 5.0068e-05 | 0.069025 | 0.069025 | 0.069025 | 0.98638 | -0.26093 | 0.98452 | -0.29711 | 18.963
117 | 0.04396 | 0.011068 | -0.043855 | -0.011002 | 0.00010444 | 6.6042e-05 | 0.066459 | 0.06646 | 0.06646 | 0.98452 | -0.29711 | 0.98197 | -0.34693 | 18.2581
118 | 0.0023043 | 0.00057747 | -0.0023043 | -0.00057752 | 2.132e-08 | -4.4777e-08 | 0.0035002 | 0.0035003 | 0.0035003 | 0.97961 | -0.39145 | 0.9796 | -0.39165 | 0.96161
119 | 0.045332 | 0.011465 | -0.045288 | -0.011436 | 4.467e-05 | 2.8263e-05 | 0.068347 | 0.068347 | 0.068347 | 0.98749 | -0.23804 | 0.98642 | -0.2586 | 18.7767
120 | 0.044055 | 0.011127 | -0.044013 | -0.011101 | 4.1475e-05 | 2.6225e-05 | 0.066487 | 0.066487 | 0.066487 | 0.98642 | -0.2586 | 0.98541 | -0.27827 | 18.2657
121 | 0.0012515 | 0.00031341 | -0.0012515 | -0.00031366 | 2.9106e-08 | -2.4463e-07 | 0.0019137 | 0.0019138 | 0.0019138 | 0.97309 | -0.51892 | 0.97307 | -0.5194 | 0.52577
122 | 0.024657 | 0.0061898 | -0.024648 | -0.0061846 | 8.4454e-06 | 5.2011e-06 | 0.037367 | 0.037367 | 0.037367 | 0.98197 | -0.34693 | 0.9816 | -0.35411 | 10.2657
123 | 0.019198 | 0.0048126 | -0.019195 | -0.0048108 | 2.9931e-06 | 1.7963e-06 | 0.029092 | 0.029092 | 0.029092 | 0.98197 | -0.34693 | 0.9818 | -0.3502 | 7.9924
124 | 0.024648 | 0.0061846 | -0.024636 | -0.0061767 | 1.2791e-05 | 7.8773e-06 | 0.037367 | 0.037367 | 0.037367 | 0.9816 | -0.35411 | 0.98104 | -0.365 | 10.2658
125 | 0.024636 | 0.0061767 | -0.024629 | -0.0061725 | 6.8249e-06 | 4.2034e-06 | 0.037367 | 0.037367 | 0.037367 | 0.98104 | -0.365 | 0.98075 | -0.37082 | 10.2658

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44294 | 0.11346

## res_load
| p_mw | q_mvar
0 | 0.00075078 | 0.00018816
1 | 0.00079369 | 0.00019892
2 | 0.0065451 | 0.0016404
3 | 0.0022991 | 0.0005762
4 | 0.0023837 | 0.00059741
5 | 0.0015459 | 0.00038745
6 | 0.0016356 | 0.00040993
7 | 0.0016758 | 0.00042
8 | 0.0020268 | 0.00050796
9 | 0.0016066 | 0.00040264
10 | 0.0013487 | 0.00033802
11 | 0.0049622 | 0.0012436
12 | 0.0030082 | 0.00075392
13 | 0.00057662 | 0.00014452
14 | 0.00060466 | 0.00015154
15 | 0.0007066 | 0.00017709
16 | 0.0021741 | 0.00054487
17 | 0.0032839 | 0.00082301
18 | 0.0018218 | 0.00045659
19 | 0.00055781 | 0.0001398
20 | 0.0019684 | 0.00049334
21 | 0.0020472 | 0.00051308
22 | 0.0019165 | 0.00048032
23 | 0.0017514 | 0.00043894
24 | 0.0016392 | 0.00041081
25 | 0.0018474 | 0.00046301
26 | 0.010319 | 0.0025862
27 | 0.0017734 | 0.00044446
28 | 0.020506 | 0.0051392
29 | 0.0021645 | 0.00054247
30 | 0.013915 | 0.0034874
31 | 0.017126 | 0.0042923
32 | 0.0017845 | 0.00044724
33 | 0.0018344 | 0.00045974
34 | 0.0025289 | 0.00063381
35 | 0.0029404 | 0.00073694
36 | 0.0042247 | 0.0010588
37 | 0.0032221 | 0.00080753
38 | 0.0019464 | 0.00048782
39 | 0.00051759 | 0.00012972
40 | 0.00049088 | 0.00012303
41 | 0.0018246 | 0.00045729
42 | 0.00040359 | 0.00010115
43 | 0.00027745 | 6.9535e-05
44 | 0.0012741 | 0.00031932
45 | 0.0026673 | 0.00066848
46 | 0.0012761 | 0.00031983
47 | 0.0012439 | 0.00031176
48 | 0.00073693 | 0.00018469
49 | 0.001198 | 0.00030025
50 | 0.0014692 | 0.00036822
51 | 0.0016348 | 0.00040972
52 | 0.0015547 | 0.00038964
53 | 0.00099122 | 0.00024842
54 | 0.0015356 | 0.00038487
55 | 0.0022178 | 0.00055584
56 | 0.0015792 | 0.00039579
57 | 0.0038087 | 0.00095456
58 | 0.0035209 | 0.00088243
59 | 0.00060293 | 0.00015111
60 | 0.0023539 | 0.00058993
61 | 0.0033805 | 0.00084722
62 | 0.0004836 | 0.0001212
63 | 0.0032739 | 0.00082052
64 | 0.00055472 | 0.00013902
65 | 0.00058179 | 0.00014581
66 | 0.00047034 | 0.00011788
67 | 0.0018137 | 0.00045456
68 | 0.0039653 | 0.00099379
69 | 0.00098203 | 0.00024612
70 | 0.0014949 | 0.00037466
71 | 0.0017796 | 0.000446
72 | 0.025453 | 0.006379
73 | 0.0063334 | 0.0015873
74 | 0.0031448 | 0.00078816
75 | 0.00066139 | 0.00016576
76 | 0.002992 | 0.00074988
77 | 0.0031759 | 0.00079597
78 | 0.0068073 | 0.0017061
79 | 0.00060202 | 0.00015088
80 | 0.023735 | 0.0059486
81 | 0.00046105 | 0.00011555
82 | 0.0078702 | 0.0019725
83 | 0.017525 | 0.0043922
84 | 0.0061795 | 0.0015487
85 | 0.002466 | 0.00061804
86 | 0.020665 | 0.0051791
87 | 0.0091422 | 0.0022912
88 | 0.0066435 | 0.001665
89 | 0.0078385 | 0.0019645
90 | 0.0016978 | 0.00042551
91 | 0.0013355 | 0.0003347
92 | 0.0013244 | 0.00033192
93 | 0.001233 | 0.00030901
94 | 0.015239 | 0.0038192
95 | 0.0012515 | 0.00031366
96 | 0.024792 | 0.0062135
97 | 0.0013898 | 0.00034832
98 | 0.0023043 | 0.00057752
99 | 0.019195 | 0.0048108
100 | 0.024629 | 0.0061725

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1