## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2513-17_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2513-17_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2513-17_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2513-17_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2513-17_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2513-17_0_5_node_66 | 0.4 | n |  | TRUE
6 | bus_LV_2513-17_0_5_node_68 | 0.4 | n |  | TRUE
7 | bus_LV_2513-17_0_5_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_2513-17_0_5_node_64 | 0.4 | n |  | TRUE
9 | bus_LV_2513-17_0_5_node_49 | 0.4 | n |  | TRUE
10 | bus_LV_2513-17_0_5_node_98 | 0.4 | n |  | TRUE
11 | bus_LV_2513-17_0_5_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_2513-17_0_5_node_99 | 0.4 | n |  | TRUE
13 | bus_LV_2513-17_0_5_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_2513-17_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2513-17_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2513-17_0_5_node_59 | 0.4 | n |  | TRUE
17 | bus_LV_2513-17_0_5_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_2513-17_0_5_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_2513-17_0_5_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2513-17_0_5_node_48 | 0.4 | n |  | TRUE
21 | bus_LV_2513-17_0_5_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_2513-17_0_5_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_2513-17_0_5_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_2513-17_0_5_node_103 | 0.4 | n |  | TRUE
25 | bus_LV_2513-17_0_5_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_2513-17_0_5_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_2513-17_0_5_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2513-17_0_5_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2513-17_0_5_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_2513-17_0_5_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_2513-17_0_5_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_2513-17_0_5_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_2513-17_0_5_node_74 | 0.4 | n |  | TRUE
34 | bus_LV_2513-17_0_5_node_83 | 0.4 | n |  | TRUE
35 | bus_LV_2513-17_0_5_node_120 | 0.4 | n |  | TRUE
36 | bus_LV_2513-17_0_5_node_80 | 0.4 | n |  | TRUE
37 | bus_LV_2513-17_0_5_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_2513-17_0_5_node_82 | 0.4 | n |  | TRUE
39 | bus_LV_2513-17_0_5_node_119 | 0.4 | n |  | TRUE
40 | bus_LV_2513-17_0_5_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_2513-17_0_5_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_2513-17_0_5_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2513-17_0_5_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_2513-17_0_5_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_2513-17_0_5_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_2513-17_0_5_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_2513-17_0_5_node_62 | 0.4 | n |  | TRUE
48 | bus_LV_2513-17_0_5_node_73 | 0.4 | n |  | TRUE
49 | bus_LV_2513-17_0_5_node_21 | 0.4 | n |  | TRUE
50 | bus_LV_2513-17_0_5_node_22 | 0.4 | n |  | TRUE
51 | bus_LV_2513-17_0_5_node_23 | 0.4 | n |  | TRUE
52 | bus_LV_2513-17_0_5_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_2513-17_0_5_node_25 | 0.4 | n |  | TRUE
54 | bus_LV_2513-17_0_5_node_116 | 0.4 | n |  | TRUE
55 | bus_LV_2513-17_0_5_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_2513-17_0_5_node_112 | 0.4 | n |  | TRUE
57 | bus_LV_2513-17_0_5_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_2513-17_0_5_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_2513-17_0_5_node_109 | 0.4 | n |  | TRUE
60 | bus_LV_2513-17_0_5_node_107 | 0.4 | n |  | TRUE
61 | bus_LV_2513-17_0_5_node_63 | 0.4 | n |  | TRUE
62 | bus_LV_2513-17_0_5_node_26 | 0.4 | n |  | TRUE
63 | bus_LV_2513-17_0_5_node_27 | 0.4 | n |  | TRUE
64 | bus_LV_2513-17_0_5_node_28 | 0.4 | n |  | TRUE
65 | bus_LV_2513-17_0_5_node_29 | 0.4 | n |  | TRUE
66 | bus_LV_2513-17_0_5_node_30 | 0.4 | n |  | TRUE
67 | bus_LV_2513-17_0_5_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_2513-17_0_5_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_2513-17_0_5_node_106 | 0.4 | n |  | TRUE
70 | bus_LV_2513-17_0_5_node_96 | 0.4 | n |  | TRUE
71 | bus_LV_2513-17_0_5_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_2513-17_0_5_node_38 | 0.4 | n |  | TRUE
73 | bus_LV_2513-17_0_5_node_31 | 0.4 | n |  | TRUE
74 | bus_LV_2513-17_0_5_node_32 | 0.4 | n |  | TRUE
75 | bus_LV_2513-17_0_5_node_33 | 0.4 | n |  | TRUE
76 | bus_LV_2513-17_0_5_node_35 | 0.4 | n |  | TRUE
77 | bus_LV_2513-17_0_5_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_2513-17_0_5_node_124 | 0.4 | n |  | TRUE
79 | bus_LV_2513-17_0_5_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_2513-17_0_5_node_93 | 0.4 | n |  | TRUE
81 | bus_LV_2513-17_0_5_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_2513-17_0_5_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_2513-17_0_5_node_115 | 0.4 | n |  | TRUE
84 | bus_LV_2513-17_0_5_node_36 | 0.4 | n |  | TRUE
85 | bus_LV_2513-17_0_5_node_37 | 0.4 | n |  | TRUE
86 | bus_LV_2513-17_0_5_node_39 | 0.4 | n |  | TRUE
87 | bus_LV_2513-17_0_5_node_40 | 0.4 | n |  | TRUE
88 | bus_LV_2513-17_0_5_node_41 | 0.4 | n |  | TRUE
89 | bus_LV_2513-17_0_5_node_88 | 0.4 | n |  | TRUE
90 | bus_LV_2513-17_0_5_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_2513-17_0_5_node_43 | 0.4 | n |  | TRUE
92 | bus_LV_2513-17_0_5_node_45 | 0.4 | n |  | TRUE
93 | bus_LV_2513-17_0_5_node_56 | 0.4 | n |  | TRUE
94 | bus_LV_2513-17_0_5_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2513-17_0_5_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_2513-17_0_5_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_2513-17_0_5_node_58 | 0.4 | n |  | TRUE
98 | bus_LV_2513-17_0_5_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_2513-17_0_5_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2513-17_0_5_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_2513-17_0_5_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_2513-17_0_5_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_2513-17_0_5_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_2513-17_0_5_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_2513-17_0_5_node_111 | 0.4 | n |  | TRUE
106 | bus_LV_2513-17_0_5_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_2513-17_0_5_node_78 | 0.4 | n |  | TRUE
108 | bus_LV_2513-17_0_5_node_108 | 0.4 | n |  | TRUE
109 | bus_LV_2513-17_0_5_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_2513-17_0_5_node_85 | 0.4 | n |  | TRUE
111 | bus_LV_2513-17_0_5_node_86 | 0.4 | n |  | TRUE
112 | bus_LV_2513-17_0_5_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_2513-17_0_5_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_2513-17_0_5_node_90 | 0.4 | n |  | TRUE
115 | bus_LV_2513-17_0_5_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_2513-17_0_5_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_2513-17_0_5_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_2513-17_0_5_node_92 | 0.4 | n |  | TRUE
119 | bus_LV_2513-17_0_5_node_121 | 0.4 | n |  | TRUE
120 | bus_MV_393_0_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2513-17_0_5_load_0 | 0 | 0.00031202 | 7.8201e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2513-17_0_5_load_1 | 1 | 0.000342 | 8.5712e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2513-17_0_5_load_2 | 2 | 0.0038497 | 0.00096482 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2513-17_0_5_load_3 | 3 | 0.00080783 | 0.00020246 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2513-17_0_5_load_4 | 4 | 0.002757 | 0.00069098 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2513-17_0_5_load_68 | 6 | 0.0028992 | 0.00072662 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2513-17_0_5_load_64 | 8 | 0.0029902 | 0.00074941 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2513-17_0_5_load_49 | 9 | 0.0010394 | 0.00026049 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2513-17_0_5_load_98 | 10 | 0.0013929 | 0.00034909 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2513-17_0_5_load_99 | 12 | 0.00011967 | 2.9991e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2513-17_0_5_load_5 | 13 | 0.00067343 | 0.00016878 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2513-17_0_5_load_6 | 14 | 0.00034892 | 8.7448e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2513-17_0_5_load_59 | 16 | 0.0040512 | 0.0010153 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2513-17_0_5_load_52 | 17 | 0.0032077 | 0.00080392 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2513-17_0_5_load_57 | 18 | 0.0004362 | 0.00010932 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2513-17_0_5_load_46 | 19 | 0.00053565 | 0.00013425 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2513-17_0_5_load_50 | 21 | 0.0018258 | 0.00045758 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2513-17_0_5_load_51 | 22 | 0.0085554 | 0.0021442 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2513-17_0_5_load_102 | 23 | 0.0034494 | 0.0008645 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2513-17_0_5_load_103 | 24 | 0.0029908 | 0.00074957 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2513-17_0_5_load_10 | 25 | 0.0033766 | 0.00084625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2513-17_0_5_load_11 | 26 | 0.014444 | 0.0036199 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2513-17_0_5_load_15 | 30 | 0.0020422 | 0.00051182 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2513-17_0_5_load_53 | 32 | 0.0031758 | 0.00079592 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2513-17_0_5_load_74 | 33 | 0.0082573 | 0.0020695 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2513-17_0_5_load_83 | 34 | 0.0048321 | 0.001211 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2513-17_0_5_load_120 | 35 | 0.0019387 | 0.00048588 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2513-17_0_5_load_80 | 36 | 0.0037683 | 0.00094443 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2513-17_0_5_load_72 | 37 | 0.0023044 | 0.00057752 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2513-17_0_5_load_82 | 38 | 0.0018272 | 0.00045794 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2513-17_0_5_load_119 | 39 | 0.0012864 | 0.00032239 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2513-17_0_5_load_16 | 40 | 0.0028749 | 0.00072053 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2513-17_0_5_load_17 | 41 | 0.0026824 | 0.00067227 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2513-17_0_5_load_18 | 42 | 0.0031487 | 0.00078914 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2513-17_0_5_load_19 | 43 | 0.0042692 | 0.00107 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2513-17_0_5_load_61 | 45 | 0.00257 | 0.0006441 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2513-17_0_5_load_75 | 46 | 0.0029082 | 0.00072886 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2513-17_0_5_load_62 | 47 | 0.0041623 | 0.0010432 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2513-17_0_5_load_73 | 48 | 0.0059882 | 0.0015008 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2513-17_0_5_load_21 | 49 | 0.0029522 | 0.0007399 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2513-17_0_5_load_22 | 50 | 0.0055849 | 0.0013997 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2513-17_0_5_load_23 | 51 | 0.0019873 | 0.00049806 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2513-17_0_5_load_116 | 54 | 0.0026244 | 0.00065773 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2513-17_0_5_load_44 | 55 | 0.0027229 | 0.00068242 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2513-17_0_5_load_112 | 56 | 0.0013216 | 0.00033121 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2513-17_0_5_load_117 | 57 | 0.0032851 | 0.00082331 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2513-17_0_5_load_42 | 58 | 0.0021897 | 0.00054878 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2513-17_0_5_load_109 | 59 | 0.00096439 | 0.0002417 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2513-17_0_5_load_107 | 60 | 0.00077135 | 0.00019332 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2513-17_0_5_load_63 | 61 | 0.0028466 | 0.00071342 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2513-17_0_5_load_26 | 62 | 0.0037581 | 0.00094187 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2513-17_0_5_load_30 | 66 | 0.0051282 | 0.0012853 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2513-17_0_5_load_69 | 68 | 0.003069 | 0.00076916 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2513-17_0_5_load_96 | 70 | 0.0027429 | 0.00068743 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2513-17_0_5_load_70 | 71 | 0.004286 | 0.0010742 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2513-17_0_5_load_31 | 73 | 0.00071933 | 0.00018028 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2513-17_0_5_load_32 | 74 | 0.001433 | 0.00035916 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2513-17_0_5_load_33 | 75 | 0.0015199 | 0.00038093 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2513-17_0_5_load_94 | 77 | 0.0018151 | 0.0004549 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2513-17_0_5_load_124 | 78 | 0.0031885 | 0.00079912 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2513-17_0_5_load_113 | 81 | 0.003376 | 0.00084612 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2513-17_0_5_load_115 | 83 | 0.0020109 | 0.00050399 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2513-17_0_5_load_36 | 84 | 0.0023421 | 0.00058699 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2513-17_0_5_load_37 | 85 | 0.0022368 | 0.0005606 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2513-17_0_5_load_39 | 86 | 0.024822 | 0.0062209 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2513-17_0_5_load_88 | 89 | 0.015301 | 0.0038347 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2513-17_0_5_load_87 | 90 | 0.0027123 | 0.00067976 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2513-17_0_5_load_43 | 91 | 0.0014797 | 0.00037084 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2513-17_0_5_load_56 | 93 | 0.0019542 | 0.00048977 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2513-17_0_5_load_76 | 94 | 0.0021852 | 0.00054765 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2513-17_0_5_load_77 | 95 | 0.0017269 | 0.00043281 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2513-17_0_5_load_79 | 96 | 0.0017378 | 0.00043553 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2513-17_0_5_load_58 | 97 | 0.00060688 | 0.0001521 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2513-17_0_5_load_60 | 98 | 0.0015518 | 0.00038892 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2513-17_0_5_load_81 | 99 | 0.00064003 | 0.00016041 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2513-17_0_5_load_100 | 100 | 0.0022947 | 0.0005751 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2513-17_0_5_load_65 | 101 | 0.0071838 | 0.0018004 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2513-17_0_5_load_67 | 102 | 0.0060173 | 0.0015081 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2513-17_0_5_load_110 | 103 | 0.0028377 | 0.0007112 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2513-17_0_5_load_104 | 104 | 0.0032862 | 0.0008236 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2513-17_0_5_load_111 | 105 | 0.0019661 | 0.00049276 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2513-17_0_5_load_97 | 106 | 0.0030923 | 0.000775 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2513-17_0_5_load_78 | 107 | 0.0046868 | 0.0011746 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2513-17_0_5_load_108 | 108 | 0.0020591 | 0.00051605 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2513-17_0_5_load_85 | 110 | 0.0018326 | 0.0004593 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2513-17_0_5_load_86 | 111 | 0.0013403 | 0.00033592 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2513-17_0_5_load_118 | 112 | 0.011447 | 0.0028689 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2513-17_0_5_load_90 | 114 | 0.0039737 | 0.00099591 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2513-17_0_5_load_91 | 115 | 0.024496 | 0.0061392 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2513-17_0_5_load_122 | 117 | 0.014578 | 0.0036535 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2513-17_0_5_load_92 | 118 | 0.024756 | 0.0062045 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2513-17_0_5_load_121 | 119 | 0.0022014 | 0.00055174 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 113 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2513-17_0_5_line_0 |  | 0 | 1 | 0.027996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2513-17_0_5_line_1 |  | 0 | 2 | 0.0017862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2513-17_0_5_line_2 |  | 1 | 3 | 0.0012053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2513-17_0_5_line_3 |  | 2 | 4 | 0.012089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2513-17_0_5_line_4 |  | 3 | 9 | 0.033478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2513-17_0_5_line_5 |  | 4 | 10 | 0.0039515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2513-17_0_5_line_6 |  | 5 | 6 | 0.061463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2513-17_0_5_line_7 |  | 5 | 7 | 0.04517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2513-17_0_5_line_8 |  | 5 | 8 | 0.013063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2513-17_0_5_line_9 |  | 6 | 76 | 0.030999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2513-17_0_5_line_10 |  | 7 | 16 | 0.0082682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2513-17_0_5_line_11 |  | 7 | 17 | 0.053619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2513-17_0_5_line_12 |  | 7 | 15 | 0.066978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2513-17_0_5_line_13 |  | 8 | 101 | 0.031189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2513-17_0_5_line_14 |  | 9 | 11 | 0.018236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2513-17_0_5_line_15 |  | 10 | 12 | 0.0057692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2513-17_0_5_line_16 |  | 11 | 21 | 0.018354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2513-17_0_5_line_17 |  | 11 | 22 | 0.039914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2513-17_0_5_line_18 |  | 11 | 19 | 0.018403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2513-17_0_5_line_19 |  | 12 | 104 | 0.018705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2513-17_0_5_line_20 |  | 13 | 14 | 0.026103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2513-17_0_5_line_21 |  | 13 | 15 | 0.0084085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2513-17_0_5_line_22 |  | 16 | 18 | 0.033041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2513-17_0_5_line_23 |  | 17 | 20 | 0.008617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2513-17_0_5_line_24 |  | 18 | 97 | 0.0037276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2513-17_0_5_line_25 |  | 19 | 20 | 0.020607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2513-17_0_5_line_26 |  | 21 | 23 | 0.014578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2513-17_0_5_line_27 |  | 23 | 24 | 0.019517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2513-17_0_5_line_28 |  | 25 | 26 | 0.01557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2513-17_0_5_line_29 |  | 25 | 27 | 0.0082074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2513-17_0_5_line_30 |  | 26 | 28 | 0.019587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2513-17_0_5_line_31 |  | 27 | 29 | 0.029473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2513-17_0_5_line_32 |  | 27 | 30 | 0.025507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2513-17_0_5_line_33 |  | 28 | 31 | 0.04861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2513-17_0_5_line_34 |  | 28 | 32 | 0.03717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2513-17_0_5_line_35 |  | 29 | 33 | 0.024373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2513-17_0_5_line_36 |  | 29 | 34 | 0.05862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2513-17_0_5_line_37 |  | 30 | 35 | 0.036288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2513-17_0_5_line_38 |  | 31 | 36 | 0.046756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2513-17_0_5_line_39 |  | 33 | 37 | 0.036313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2513-17_0_5_line_40 |  | 34 | 38 | 0.0082772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2513-17_0_5_line_41 |  | 35 | 39 | 0.0045789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2513-17_0_5_line_42 |  | 36 | 96 | 0.036681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2513-17_0_5_line_43 |  | 37 | 48 | 0.04102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2513-17_0_5_line_44 |  | 38 | 109 | 0.022125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2513-17_0_5_line_45 |  | 39 | 119 | 0.019019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2513-17_0_5_line_46 |  | 40 | 41 | 0.018143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2513-17_0_5_line_47 |  | 40 | 42 | 0.019764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2513-17_0_5_line_48 |  | 41 | 43 | 0.0054125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2513-17_0_5_line_49 |  | 42 | 44 | 0.019385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2513-17_0_5_line_50 |  | 43 | 45 | 0.022023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2513-17_0_5_line_51 |  | 44 | 46 | 0.022231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2513-17_0_5_line_52 |  | 45 | 47 | 0.00090489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2513-17_0_5_line_53 |  | 46 | 48 | 0.011277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2513-17_0_5_line_54 |  | 47 | 61 | 0.021209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2513-17_0_5_line_55 |  | 49 | 50 | 0.010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_2513-17_0_5_line_56 |  | 49 | 51 | 0.033135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2513-17_0_5_line_57 |  | 50 | 52 | 0.026866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2513-17_0_5_line_58 |  | 51 | 53 | 0.023839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2513-17_0_5_line_59 |  | 52 | 54 | 0.0028148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2513-17_0_5_line_60 |  | 52 | 55 | 0.015923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2513-17_0_5_line_61 |  | 53 | 56 | 0.013938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2513-17_0_5_line_62 |  | 54 | 57 | 0.023204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2513-17_0_5_line_63 |  | 55 | 58 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2513-17_0_5_line_64 |  | 56 | 61 | 0.0055936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2513-17_0_5_line_65 |  | 57 | 116 | 0.022486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2513-17_0_5_line_66 |  | 58 | 91 | 0.02611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2513-17_0_5_line_67 |  | 59 | 60 | 0.0088334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2513-17_0_5_line_68 |  | 60 | 108 | 0.0073374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2513-17_0_5_line_69 |  | 62 | 63 | 0.032735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2513-17_0_5_line_70 |  | 62 | 64 | 0.0032836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2513-17_0_5_line_71 |  | 63 | 65 | 0.011218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2513-17_0_5_line_72 |  | 64 | 66 | 0.025682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2513-17_0_5_line_73 |  | 65 | 67 | 0.027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2513-17_0_5_line_74 |  | 65 | 68 | 0.020851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2513-17_0_5_line_75 |  | 66 | 69 | 0.020154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2513-17_0_5_line_76 |  | 67 | 70 | 0.022142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2513-17_0_5_line_77 |  | 68 | 71 | 0.0010009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2513-17_0_5_line_78 |  | 69 | 72 | 0.029037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2513-17_0_5_line_79 |  | 70 | 106 | 0.0033565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2513-17_0_5_line_80 |  | 72 | 85 | 0.012747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2513-17_0_5_line_81 |  | 73 | 74 | 0.021574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2513-17_0_5_line_82 |  | 73 | 75 | 0.022649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2513-17_0_5_line_83 |  | 75 | 76 | 0.03308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2513-17_0_5_line_84 |  | 76 | 77 | 0.01106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2513-17_0_5_line_85 |  | 77 | 80 | 0.035205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2513-17_0_5_line_86 |  | 78 | 79 | 0.038614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2513-17_0_5_line_87 |  | 79 | 83 | 0.013325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2513-17_0_5_line_88 |  | 79 | 81 | 0.0019661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2513-17_0_5_line_89 |  | 80 | 116 | 0.008996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2513-17_0_5_line_90 |  | 80 | 118 | 0.037715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2513-17_0_5_line_91 |  | 81 | 82 | 0.057341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2513-17_0_5_line_92 |  | 82 | 104 | 0.04379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2513-17_0_5_line_93 |  | 84 | 85 | 0.019071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2513-17_0_5_line_94 |  | 86 | 87 | 0.060163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2513-17_0_5_line_95 |  | 87 | 88 | 0.067024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2513-17_0_5_line_96 |  | 88 | 89 | 0.055522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2513-17_0_5_line_97 |  | 89 | 90 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2513-17_0_5_line_98 |  | 90 | 113 | 0.042705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2513-17_0_5_line_99 |  | 91 | 92 | 0.0045468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2513-17_0_5_line_100 |  | 92 | 93 | 0.019506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2513-17_0_5_line_101 |  | 92 | 94 | 0.017908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2513-17_0_5_line_102 |  | 94 | 95 | 0.021281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2513-17_0_5_line_103 |  | 95 | 107 | 0.026708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2513-17_0_5_line_104 |  | 97 | 98 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2513-17_0_5_line_105 |  | 98 | 99 | 0.0071598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2513-17_0_5_line_106 |  | 99 | 100 | 0.015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2513-17_0_5_line_107 |  | 101 | 102 | 0.036941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2513-17_0_5_line_108 |  | 102 | 103 | 0.031185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2513-17_0_5_line_109 |  | 103 | 105 | 0.020929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2513-17_0_5_line_110 |  | 106 | 111 | 0.026136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2513-17_0_5_line_111 |  | 107 | 108 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2513-17_0_5_line_112 |  | 109 | 110 | 0.011212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2513-17_0_5_line_113 |  | 109 | 111 | 0.037314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2513-17_0_5_line_114 |  | 110 | 112 | 0.02837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2513-17_0_5_line_115 |  | 113 | 114 | 0.0056691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2513-17_0_5_line_116 |  | 113 | 115 | 0.024882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2513-17_0_5_line_117 |  | 114 | 116 | 0.053713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_2513-17_0_5_line_118 |  | 115 | 117 | 0.068233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2513-17_0_5_trafo_89 | 0.63 MVA 20/0.4 kV | 120 | 113 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2609776.5292 | 1226008.0998 | 2609759.5311 | 1225985.855
1 | 2609776.5292 | 1226008.0998 | 2609777.6137 | 1226009.519
2 | 2609758.7992 | 1225984.8973 | 2609759.5311 | 1225985.855
3 | 2609784.954 | 1226019.1249 | 2609777.6137 | 1226009.519
4 | 2609758.7992 | 1225984.8973 | 2609738.4723 | 1225958.2963
5 | 2609784.954 | 1226019.1249 | 2609787.3532 | 1226022.2647
6 | 2609629.1036 | 1225965.805 | 2609612.6842 | 1226025.0342
7 | 2609642.3538 | 1225922.6454 | 2609633.0123 | 1225953.0704 | 2609630.5263 | 1225962.4386 | 2609629.1036 | 1225965.805
8 | 2609629.1036 | 1225965.805 | 2609616.6958 | 1225961.7211
9 | 2609604.4031 | 1226054.9065 | 2609612.6842 | 1226025.0342
10 | 2609642.3538 | 1225922.6454 | 2609640.8017 | 1225921.5978 | 2609637.4782 | 1225916.1335
11 | 2609642.3538 | 1225922.6454 | 2609695.8486 | 1225918.9962
12 | 2609660.3835 | 1225858.1366 | 2609642.3538 | 1225922.6454
13 | 2609616.6958 | 1225961.7211 | 2609605.3089 | 1225957.9733 | 2609590.6021 | 1225950.1007 | 2609588.5797 | 1225948.598
14 | 2609727.3999 | 1225943.8064 | 2609738.4723 | 1225958.2963
15 | 2609790.8561 | 1226026.8487 | 2609787.3532 | 1226022.2647
16 | 2609727.3999 | 1225943.8064 | 2609712.7118 | 1225954.8114
17 | 2609727.3999 | 1225943.8064 | 2609730.0012 | 1225933.5602 | 2609744.8677 | 1225922.4222 | 2609754.3033 | 1225927.6073
18 | 2609727.3999 | 1225943.8064 | 2609714.7107 | 1225930.478
19 | 2609790.8561 | 1226026.8487 | 2609802.2129 | 1226041.711
20 | 2609655.0881 | 1225851.6116 | 2609639.1909 | 1225830.9075
21 | 2609660.3835 | 1225858.1366 | 2609658.3029 | 1225855.7985 | 2609655.0881 | 1225851.6116
22 | 2609620.3082 | 1225887.9037 | 2609637.4782 | 1225916.1335
23 | 2609702.6939 | 1225913.7376 | 2609695.8486 | 1225918.9962
24 | 2609620.3082 | 1225887.9037 | 2609618.3712 | 1225884.719
25 | 2609702.6939 | 1225913.7376 | 2609714.7107 | 1225930.478
26 | 2609701.0453 | 1225963.5524 | 2609712.7118 | 1225954.8114
27 | 2609701.0453 | 1225963.5524 | 2609685.4261 | 1225975.255
28 | 2609402.5522 | 1226095.6342 | 2609410.3223 | 1226109.1267
29 | 2609398.4563 | 1226088.5219 | 2609402.5522 | 1226095.6342
30 | 2609420.0969 | 1226126.1001 | 2609410.3223 | 1226109.1267
31 | 2609398.4563 | 1226088.5219 | 2609392.8024 | 1226078.6961 | 2609387.3497 | 1226061.3885
32 | 2609398.4563 | 1226088.5219 | 2609376.0811 | 1226100.7681
33 | 2609420.0969 | 1226126.1001 | 2609377.6986 | 1226150.0922
34 | 2609420.0969 | 1226126.1001 | 2609435.2017 | 1226140.9993 | 2609448.1182 | 1226150.3622
35 | 2609387.3497 | 1226061.3885 | 2609387.4412 | 1226037.016
36 | 2609387.3497 | 1226061.3885 | 2609378.3871 | 1226058.9508 | 2609372.7906 | 1226055.9626 | 2609370.3739 | 1226050.3777 | 2609369.0857 | 1226035.6671 | 2609367.3025 | 1226027.3038 | 2609364.2591 | 1226020.206 | 2609360.8022 | 1226015.4727
37 | 2609376.0811 | 1226100.7681 | 2609367.2634 | 1226105.5942 | 2609364.9364 | 1226105.7017 | 2609363.1419 | 1226104.5315 | 2609351.7831 | 1226085.9666
38 | 2609377.6986 | 1226150.0922 | 2609346.0667 | 1226128.1632 | 2609340.2087 | 1226122.331
39 | 2609387.5776 | 1226000.7036 | 2609387.4412 | 1226037.016
40 | 2609355.9204 | 1226008.7883 | 2609360.8022 | 1226015.4727
41 | 2609347.9544 | 1226084.1737 | 2609347.9544 | 1226084.1737 | 2609351.0156 | 1226084.7121 | 2609351.7831 | 1226085.9666
42 | 2609340.2087 | 1226122.331 | 2609314.2138 | 1226096.4508
43 | 2609387.5776 | 1226000.7036 | 2609387.6488 | 1225981.7534 | 2609387.7316 | 1225959.684
44 | 2609345.2521 | 1225989.6473 | 2609348.6031 | 1225998.769 | 2609355.9204 | 1226008.7883
45 | 2609347.9544 | 1226084.1737 | 2609344.3651 | 1226082.0668 | 2609336.2518 | 1226069.6213
46 | 2609420.0568 | 1225943.6046 | 2609428.6217 | 1225959.5986
47 | 2609420.0568 | 1225943.6046 | 2609417.0653 | 1225938.0183 | 2609413.4424 | 1225933.132 | 2609408.7089 | 1225930.7676 | 2609406.7497 | 1225930.1524
48 | 2609431.1769 | 1225964.37 | 2609428.6217 | 1225959.5986
49 | 2609387.8572 | 1225926.1766 | 2609398.1407 | 1225927.4491 | 2609406.7497 | 1225930.1524
50 | 2609441.5735 | 1225983.7846 | 2609431.1769 | 1225964.37
51 | 2609387.8572 | 1225926.1766 | 2609387.7738 | 1225948.4074
52 | 2609441.5735 | 1225983.7846 | 2609442.0007 | 1225984.5823
53 | 2609387.7316 | 1225959.684 | 2609387.7738 | 1225948.4074
54 | 2609452.0131 | 1226003.2795 | 2609442.0007 | 1225984.5823
55 | 2609508.6073 | 1226052.4673 | 2609517.8782 | 1226057.8222
56 | 2609508.6073 | 1226052.4673 | 2609505.2035 | 1226050.5013 | 2609480.8914 | 1226034.3202
57 | 2609541.1422 | 1226071.2595 | 2609517.8782 | 1226057.8222
58 | 2609461.8974 | 1226020.1038 | 2609465.8548 | 1226024.3125 | 2609480.8914 | 1226034.3202
59 | 2609541.1422 | 1226071.2595 | 2609541.9807 | 1226068.5725
60 | 2609541.1422 | 1226071.2595 | 2609537.0957 | 1226086.6602
61 | 2609461.8974 | 1226020.1038 | 2609457.0356 | 1226012.6584 | 2609454.6537 | 1226008.2105
62 | 2609541.9807 | 1226068.5725 | 2609548.8929 | 1226046.4218
63 | 2609537.0957 | 1226086.6602 | 2609533.1133 | 1226101.8173
64 | 2609452.0131 | 1226003.2795 | 2609454.6537 | 1226008.2105
65 | 2609557.4043 | 1226025.8031 | 2609553.362 | 1226032.1004 | 2609548.8929 | 1226046.4218
66 | 2609524.9558 | 1226126.455 | 2609528.1254 | 1226120.8012 | 2609533.1133 | 1226101.8173
67 | 2609447.2212 | 1226079.2931 | 2609447.2212 | 1226079.2931 | 2609441.3871 | 1226072.6606
68 | 2609447.2212 | 1226079.2931 | 2609453.131 | 1226083.6419
69 | 2609224.479 | 1226000.6555 | 2609216.2843 | 1226006.4797 | 2609212.7513 | 1226011.9997 | 2609210.1487 | 1226013.8968 | 2609204.204 | 1226015.4664 | 2609198.7092 | 1226019.4011
70 | 2609196.0395 | 1226021.3128 | 2609198.7092 | 1226019.4011
71 | 2609224.479 | 1226000.6555 | 2609233.5997 | 1225994.0879
72 | 2609196.0395 | 1226021.3128 | 2609175.3007 | 1226036.4617
73 | 2609257.1572 | 1225979.0377 | 2609233.5997 | 1225994.0879
74 | 2609233.5997 | 1225994.0879 | 2609247.6361 | 1226009.5067
75 | 2609159.0258 | 1226048.3498 | 2609175.3007 | 1226036.4617
76 | 2609257.1572 | 1225979.0377 | 2609264.3968 | 1225978.2039 | 2609279.1046 | 1225980.2855
77 | 2609247.6361 | 1226009.5067 | 2609248.3099 | 1226010.2468
78 | 2609159.0258 | 1226048.3498 | 2609134.6338 | 1226064.2108
79 | 2609279.1046 | 1225980.2855 | 2609282.4279 | 1225980.7558
80 | 2609134.6338 | 1226064.2108 | 2609141.4094 | 1226075.0078
81 | 2609582.425 | 1226129.0182 | 2609588.5587 | 1226108.3348
82 | 2609594.9981 | 1226086.6209 | 2609588.5587 | 1226108.3348
83 | 2609604.4031 | 1226054.9065 | 2609594.9981 | 1226086.6209
84 | 2609604.4031 | 1226054.9065 | 2609594.9994 | 1226049.0842
85 | 2609565.0671 | 1226030.5515 | 2609594.9994 | 1226049.0842
86 | 2609781.901 | 1226112.8055 | 2609749.4276 | 1226133.6981
87 | 2609781.901 | 1226112.8055 | 2609790.1243 | 1226123.2901
88 | 2609781.901 | 1226112.8055 | 2609783.4558 | 1226111.6021
89 | 2609557.4043 | 1226025.8031 | 2609565.0671 | 1226030.5515
90 | 2609565.0671 | 1226030.5515 | 2609582.6123 | 1226002.8299 | 2609584.0875 | 1225998.1491
91 | 2609828.8008 | 1226076.5054 | 2609783.4558 | 1226111.6021
92 | 2609828.8008 | 1226076.5054 | 2609802.2129 | 1226041.711
93 | 2609141.4094 | 1226075.0078 | 2609151.5467 | 1226091.1617
94 | 2609498.4958 | 1225888.0175 | 2609528.8142 | 1225878.4378 | 2609540.8843 | 1225900.1253 | 2609541.7385 | 1225903.5678
95 | 2609433.4902 | 1225904.3133 | 2609436.8644 | 1225903.507 | 2609473.8288 | 1225894.6824 | 2609498.4958 | 1225888.0175
96 | 2609433.4902 | 1225904.3133 | 2609455.4042 | 1225937.0003 | 2609466.3895 | 1225948.8645
97 | 2609478.3746 | 1225961.8085 | 2609466.3895 | 1225948.8645
98 | 2609509.2011 | 1225991.1506 | 2609496.7026 | 1225981.6029 | 2609478.3746 | 1225961.8085
99 | 2609521.1698 | 1226128.9727 | 2609524.9558 | 1226126.455
100 | 2609521.1698 | 1226128.9727 | 2609519.6484 | 1226137.1973 | 2609512.5709 | 1226145.8023
101 | 2609521.1698 | 1226128.9727 | 2609516.1144 | 1226128.9647 | 2609508.073 | 1226124.0712 | 2609505.3025 | 1226122.0326
102 | 2609505.3025 | 1226122.0326 | 2609488.1622 | 1226109.4198
103 | 2609488.1622 | 1226109.4198 | 2609466.6509 | 1226093.5906
104 | 2609618.3712 | 1225884.719 | 2609603.6391 | 1225860.4973
105 | 2609599.9185 | 1225854.3801 | 2609603.6391 | 1225860.4973
106 | 2609599.9185 | 1225854.3801 | 2609591.6957 | 1225840.8607
107 | 2609561.8983 | 1225923.468 | 2609572.6978 | 1225936.7975 | 2609588.5797 | 1225948.598
108 | 2609561.8983 | 1225923.468 | 2609555.2008 | 1225915.2014 | 2609545.3531 | 1225897.1689
109 | 2609535.3218 | 1225878.8002 | 2609545.3531 | 1225897.1689
110 | 2609282.4279 | 1225980.7558 | 2609308.3061 | 1225984.4184
111 | 2609453.131 | 1226083.6419 | 2609466.6509 | 1226093.5906
112 | 2609345.2521 | 1225989.6473 | 2609344.3526 | 1225978.4712
113 | 2609345.2521 | 1225989.6473 | 2609308.3061 | 1225984.4184
114 | 2609338.2611 | 1225950.8115 | 2609342.1155 | 1225964.5054 | 2609344.3375 | 1225978.2836 | 2609344.3526 | 1225978.4712
115 | 2609509.2011 | 1225991.1506 | 2609513.7055 | 1225994.5929
116 | 2609509.2011 | 1225991.1506 | 2609516.5533 | 1225981.5566 | 2609528.9663 | 1225978.4529
117 | 2609557.4043 | 1226025.8031 | 2609527.2486 | 1226004.9429 | 2609513.7055 | 1225994.5929
118 | 2609577.461 | 1225949.0123 | 2609580.1494 | 1225959.9119 | 2609555.8168 | 1225966.1878 | 2609553.5787 | 1225972.299 | 2609528.9663 | 1225978.4529

## bus_geodata
| x | y | coords
0 | 2609776.5292 | 1226008.0998
1 | 2609759.5311 | 1225985.855
2 | 2609777.6137 | 1226009.519
3 | 2609758.7992 | 1225984.8973
4 | 2609784.954 | 1226019.1249
5 | 2609629.1036 | 1225965.805
6 | 2609612.6842 | 1226025.0342
7 | 2609642.3538 | 1225922.6454
8 | 2609616.6958 | 1225961.7211
9 | 2609738.4723 | 1225958.2963
10 | 2609787.3532 | 1226022.2647
11 | 2609727.3999 | 1225943.8064
12 | 2609790.8561 | 1226026.8487
13 | 2609655.0881 | 1225851.6116
14 | 2609639.1909 | 1225830.9075
15 | 2609660.3835 | 1225858.1366
16 | 2609637.4782 | 1225916.1335
17 | 2609695.8486 | 1225918.9962
18 | 2609620.3082 | 1225887.9037
19 | 2609714.7107 | 1225930.478
20 | 2609702.6939 | 1225913.7376
21 | 2609712.7118 | 1225954.8114
22 | 2609754.3033 | 1225927.6073
23 | 2609701.0453 | 1225963.5524
24 | 2609685.4261 | 1225975.255
25 | 2609402.5522 | 1226095.6342
26 | 2609410.3222 | 1226109.1267
27 | 2609398.4563 | 1226088.5219
28 | 2609420.0969 | 1226126.1001
29 | 2609387.3497 | 1226061.3885
30 | 2609376.0811 | 1226100.7681
31 | 2609377.6986 | 1226150.0922
32 | 2609448.1182 | 1226150.3622
33 | 2609387.4412 | 1226037.016
34 | 2609360.8022 | 1226015.4727
35 | 2609351.7831 | 1226085.9666
36 | 2609340.2087 | 1226122.331
37 | 2609387.5776 | 1226000.7036
38 | 2609355.9204 | 1226008.7883
39 | 2609347.9544 | 1226084.1737
40 | 2609420.0568 | 1225943.6046
41 | 2609428.6217 | 1225959.5986
42 | 2609406.7497 | 1225930.1524
43 | 2609431.1769 | 1225964.37
44 | 2609387.8572 | 1225926.1766
45 | 2609441.5735 | 1225983.7846
46 | 2609387.7738 | 1225948.4074
47 | 2609442.0007 | 1225984.5823
48 | 2609387.7316 | 1225959.684
49 | 2609508.6073 | 1226052.4673
50 | 2609517.8782 | 1226057.8222
51 | 2609480.8914 | 1226034.3202
52 | 2609541.1422 | 1226071.2595
53 | 2609461.8974 | 1226020.1038
54 | 2609541.9807 | 1226068.5725
55 | 2609537.0957 | 1226086.6602
56 | 2609454.6537 | 1226008.2105
57 | 2609548.8929 | 1226046.4218
58 | 2609533.1133 | 1226101.8173
59 | 2609441.3871 | 1226072.6606
60 | 2609447.2212 | 1226079.2931
61 | 2609452.0131 | 1226003.2795
62 | 2609198.7092 | 1226019.4011
63 | 2609224.479 | 1226000.6555
64 | 2609196.0395 | 1226021.3128
65 | 2609233.5997 | 1225994.0879
66 | 2609175.3007 | 1226036.4617
67 | 2609257.1572 | 1225979.0377
68 | 2609247.6361 | 1226009.5067
69 | 2609159.0258 | 1226048.3498
70 | 2609279.1046 | 1225980.2855
71 | 2609248.3099 | 1226010.2468
72 | 2609134.6338 | 1226064.2108
73 | 2609588.5587 | 1226108.3348
74 | 2609582.425 | 1226129.0182
75 | 2609594.9981 | 1226086.6209
76 | 2609604.4031 | 1226054.9065
77 | 2609594.9994 | 1226049.0842
78 | 2609749.4276 | 1226133.6981
79 | 2609781.901 | 1226112.8055
80 | 2609565.0671 | 1226030.5515
81 | 2609783.4558 | 1226111.6021
82 | 2609828.8008 | 1226076.5054
83 | 2609790.1243 | 1226123.2901
84 | 2609151.5467 | 1226091.1617
85 | 2609141.4094 | 1226075.0078
86 | 2609541.7385 | 1225903.5678
87 | 2609498.4958 | 1225888.0175
88 | 2609433.4902 | 1225904.3133
89 | 2609466.3895 | 1225948.8645
90 | 2609478.3746 | 1225961.8085
91 | 2609524.9558 | 1226126.455
92 | 2609521.1698 | 1226128.9727
93 | 2609512.5709 | 1226145.8023
94 | 2609505.3025 | 1226122.0326
95 | 2609488.1622 | 1226109.4198
96 | 2609314.2138 | 1226096.4508
97 | 2609618.3712 | 1225884.719
98 | 2609603.6391 | 1225860.4973
99 | 2609599.9185 | 1225854.3801
100 | 2609591.6957 | 1225840.8607
101 | 2609588.5797 | 1225948.598
102 | 2609561.8983 | 1225923.468
103 | 2609545.3531 | 1225897.1689
104 | 2609802.2129 | 1226041.711
105 | 2609535.3218 | 1225878.8002
106 | 2609282.4279 | 1225980.7558
107 | 2609466.6509 | 1226093.5906
108 | 2609453.131 | 1226083.6419
109 | 2609345.2521 | 1225989.6473
110 | 2609344.3526 | 1225978.4712
111 | 2609308.3061 | 1225984.4184
112 | 2609338.2611 | 1225950.8115
113 | 2609509.2011 | 1225991.1506
114 | 2609513.7055 | 1225994.5929
115 | 2609528.9663 | 1225978.4529
116 | 2609557.4043 | 1226025.8031
117 | 2609577.461 | 1225949.0123
118 | 2609584.0875 | 1225998.1491
119 | 2609336.2518 | 1226069.6213
120 | 2609557.4043 | 1226025.8031

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9764 | -0.45497 | 0.00031202 | 7.8201e-05
1 | 0.97693 | -0.44459 | 0.000342 | 8.5712e-05
2 | 0.97637 | -0.45562 | 0.0038497 | 0.00096482
3 | 0.97695 | -0.44413 | 0.00080783 | 0.00020246
4 | 0.97618 | -0.45919 | 0.002757 | 0.00069098
5 | 0.98414 | -0.30365 | 0 | 0
6 | 0.98839 | -0.22141 | 0.0028992 | 0.00072662
7 | 0.98189 | -0.34737 | 0 | 0
8 | 0.98389 | -0.30858 | 0.0029902 | 0.00074941
9 | 0.97762 | -0.43103 | 0.0010394 | 0.00026049
10 | 0.97614 | -0.46016 | 0.0013929 | 0.00034909
11 | 0.978 | -0.42355 | 0 | 0
12 | 0.97607 | -0.46142 | 0.00011967 | 2.9991e-05
13 | 0.98182 | -0.34877 | 0.00067343 | 0.00016878
14 | 0.98181 | -0.34894 | 0.00034892 | 8.7448e-05
15 | 0.98183 | -0.34861 | 0 | 0
16 | 0.98182 | -0.34881 | 0.0040512 | 0.0010153
17 | 0.97975 | -0.38921 | 0.0032077 | 0.00080392
18 | 0.98165 | -0.35211 | 0.0004362 | 0.00010932
19 | 0.97867 | -0.41038 | 0.00053565 | 0.00013425
20 | 0.97943 | -0.39544 | 0 | 0
21 | 0.97786 | -0.42632 | 0.0018258 | 0.00045758
22 | 0.97768 | -0.42978 | 0.0085554 | 0.0021442
23 | 0.97777 | -0.42803 | 0.0034494 | 0.0008645
24 | 0.97772 | -0.42909 | 0.0029908 | 0.00074957
25 | 0.9792 | -0.39993 | 0.0033766 | 0.00084625
26 | 0.97886 | -0.40648 | 0.014444 | 0.0036199
27 | 0.9794 | -0.39598 | 0 | 0
28 | 0.97871 | -0.40958 | 0 | 0
29 | 0.98033 | -0.3778 | 0 | 0
30 | 0.97922 | -0.39944 | 0.0020422 | 0.00051182
31 | 0.97846 | -0.41445 | 0 | 0
32 | 0.9786 | -0.41172 | 0.0031758 | 0.00079592
33 | 0.98125 | -0.35971 | 0.0082573 | 0.0020695
34 | 0.97771 | -0.42891 | 0.0048321 | 0.001211
35 | 0.97904 | -0.40302 | 0.0019387 | 0.00048588
36 | 0.97822 | -0.41914 | 0.0037683 | 0.00094443
37 | 0.98227 | -0.33996 | 0.0023044 | 0.00057752
38 | 0.97738 | -0.43542 | 0.0018272 | 0.00045794
39 | 0.97903 | -0.40331 | 0.0012864 | 0.00032239
40 | 0.98573 | -0.27281 | 0.0028749 | 0.00072053
41 | 0.98633 | -0.26117 | 0.0026824 | 0.00067227
42 | 0.98509 | -0.28518 | 0.0031487 | 0.00078914
43 | 0.98651 | -0.25761 | 0.0042692 | 0.00107
44 | 0.98448 | -0.29695 | 0 | 0
45 | 0.98729 | -0.24258 | 0.00257 | 0.0006441
46 | 0.98378 | -0.31048 | 0.0029082 | 0.00072886
47 | 0.98733 | -0.24195 | 0.0041623 | 0.0010432
48 | 0.98344 | -0.31715 | 0.0059882 | 0.0015008
49 | 0.9911 | -0.16944 | 0.0029522 | 0.0007399
50 | 0.99153 | -0.1612 | 0.0055849 | 0.0013997
51 | 0.98979 | -0.19442 | 0.0019873 | 0.00049806
52 | 0.99265 | -0.13966 | 0 | 0
53 | 0.98887 | -0.21215 | 0 | 0
54 | 0.99279 | -0.13706 | 0.0026244 | 0.00065773
55 | 0.99235 | -0.14551 | 0.0027229 | 0.00068242
56 | 0.98833 | -0.22253 | 0.0013216 | 0.00033121
57 | 0.99393 | -0.11531 | 0.0032851 | 0.00082331
58 | 0.99209 | -0.15051 | 0.0021897 | 0.00054878
59 | 0.99097 | -0.1723 | 0.00096439 | 0.0002417
60 | 0.99098 | -0.17215 | 0.00077135 | 0.00019332
61 | 0.98812 | -0.22665 | 0.0028466 | 0.00071342
62 | 0.97331 | -0.51545 | 0.0037581 | 0.00094187
63 | 0.97373 | -0.50735 | 0 | 0
64 | 0.97328 | -0.51604 | 0 | 0
65 | 0.97387 | -0.50457 | 0 | 0
66 | 0.97305 | -0.52063 | 0.0051282 | 0.0012853
67 | 0.97441 | -0.4939 | 0 | 0
68 | 0.97372 | -0.50739 | 0.003069 | 0.00076916
69 | 0.97297 | -0.52233 | 0 | 0
70 | 0.97484 | -0.48544 | 0.0027429 | 0.00068743
71 | 0.97372 | -0.50747 | 0.004286 | 0.0010742
72 | 0.97284 | -0.52478 | 0 | 0
73 | 0.99046 | -0.18163 | 0.00071933 | 0.00018028
74 | 0.99043 | -0.18218 | 0.001433 | 0.00035916
75 | 0.99051 | -0.18076 | 0.0015199 | 0.00038093
76 | 0.99062 | -0.1786 | 0 | 0
77 | 0.99145 | -0.16265 | 0.0018151 | 0.0004549
78 | 0.97493 | -0.48382 | 0.0031885 | 0.00079912
79 | 0.97505 | -0.48157 | 0 | 0
80 | 0.99416 | -0.11094 | 0 | 0
81 | 0.97506 | -0.48138 | 0.003376 | 0.00084612
82 | 0.97552 | -0.47236 | 0 | 0
83 | 0.97502 | -0.48206 | 0.0020109 | 0.00050399
84 | 0.97275 | -0.52668 | 0.0023421 | 0.00058699
85 | 0.97279 | -0.52585 | 0.0022368 | 0.0005606
86 | 0.99355 | -0.12408 | 0.024822 | 0.0062209
87 | 0.99491 | -0.097748 | 0 | 0
88 | 0.99643 | -0.068496 | 0 | 0
89 | 0.99769 | -0.044329 | 0.015301 | 0.0038347
90 | 0.99833 | -0.031941 | 0.0027123 | 0.00067976
91 | 0.99171 | -0.15783 | 0.0014797 | 0.00037084
92 | 0.99165 | -0.15898 | 0 | 0
93 | 0.99162 | -0.15966 | 0.0019542 | 0.00048977
94 | 0.99145 | -0.16292 | 0.0021852 | 0.00054765
95 | 0.99125 | -0.16677 | 0.0017269 | 0.00043281
96 | 0.97816 | -0.4203 | 0.0017378 | 0.00043553
97 | 0.98163 | -0.35246 | 0.00060688 | 0.0001521
98 | 0.98152 | -0.35476 | 0.0015518 | 0.00038892
99 | 0.9815 | -0.35514 | 0.00064003 | 0.00016041
100 | 0.98146 | -0.35579 | 0.0022947 | 0.0005751
101 | 0.98337 | -0.3187 | 0.0071838 | 0.0018004
102 | 0.983 | -0.32591 | 0.0060173 | 0.0015081
103 | 0.98286 | -0.32861 | 0.0028377 | 0.0007112
104 | 0.97587 | -0.46549 | 0.0032862 | 0.0008236
105 | 0.98283 | -0.32936 | 0.0019661 | 0.00049276
106 | 0.97491 | -0.48398 | 0.0030923 | 0.000775
107 | 0.99105 | -0.17079 | 0.0046868 | 0.0011746
108 | 0.99099 | -0.17192 | 0.0020591 | 0.00051605
109 | 0.97653 | -0.4521 | 0 | 0
110 | 0.97639 | -0.45482 | 0.0018326 | 0.0004593
111 | 0.97556 | -0.47121 | 0.0013403 | 0.00033592
112 | 0.97609 | -0.46076 | 0.011447 | 0.0028689
113 | 1 | 0 | -0.36233 | -0.092139
114 | 0.99952 | -0.0090383 | 0.0039737 | 0.00099591
115 | 0.99912 | -0.016962 | 0.024496 | 0.0061392
116 | 0.99505 | -0.093851 | 0 | 0
117 | 0.99821 | -0.034346 | 0.014578 | 0.0036535
118 | 0.9933 | -0.12742 | 0.024756 | 0.0062045
119 | 0.97899 | -0.40407 | 0.0022014 | 0.00055174
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020307 | -0.0050924 | 0.020317 | 0.0050985 | 1.0055e-05 | 6.0852e-06 | 0.030949 | 0.030948 | 0.030949 | 0.9764 | -0.45497 | 0.97693 | -0.44459 | 8.5023
1 | 0.019995 | 0.0050142 | -0.019994 | -0.0050138 | 6.2199e-07 | 3.7574e-07 | 0.030473 | 0.030473 | 0.030473 | 0.9764 | -0.45497 | 0.97637 | -0.45562 | 8.3717
2 | -0.020659 | -0.0051842 | 0.020659 | 0.0051844 | 4.4761e-07 | 2.7138e-07 | 0.031469 | 0.031469 | 0.031469 | 0.97693 | -0.44459 | 0.97695 | -0.44413 | 8.6454
3 | 0.016145 | 0.004049 | -0.016142 | -0.0040474 | 2.7448e-06 | 1.6055e-06 | 0.024606 | 0.024606 | 0.024606 | 0.97637 | -0.45562 | 0.97618 | -0.45919 | 6.7599
4 | -0.021467 | -0.0053869 | 0.021481 | 0.0053951 | 1.3424e-05 | 8.1719e-06 | 0.0327 | 0.0327 | 0.0327 | 0.97695 | -0.44413 | 0.97762 | -0.43103 | 8.9834
5 | 0.013385 | 0.0033564 | -0.013384 | -0.003356 | 6.1688e-07 | 3.4541e-07 | 0.020403 | 0.020403 | 0.020403 | 0.97618 | -0.45919 | 0.97614 | -0.46016 | 5.6053
6 | -0.07498 | -0.018912 | 0.075277 | 0.019101 | 0.00029646 | 0.00018895 | 0.11341 | 0.11341 | 0.11341 | 0.98414 | -0.30365 | 0.98839 | -0.22141 | 31.1573
7 | 0.053967 | 0.01364 | -0.053854 | -0.013568 | 0.0001129 | 7.168e-05 | 0.081639 | 0.081639 | 0.081639 | 0.98414 | -0.30365 | 0.98189 | -0.34737 | 22.4283
8 | 0.021013 | 0.0052717 | -0.021008 | -0.0052687 | 4.9454e-06 | 2.9991e-06 | 0.031774 | 0.031774 | 0.031774 | 0.98414 | -0.30365 | 0.98389 | -0.30858 | 8.7291
9 | -0.078176 | -0.019827 | 0.078337 | 0.01993 | 0.00016125 | 0.0001028 | 0.11778 | 0.11778 | 0.11778 | 0.98839 | -0.22141 | 0.99062 | -0.1786 | 32.3563
10 | 0.009583 | 0.0024014 | -0.0095823 | -0.0024011 | 6.5392e-07 | 3.1394e-07 | 0.014522 | 0.014522 | 0.014522 | 0.98189 | -0.34737 | 0.98182 | -0.34881 | 3.9897
11 | 0.043249 | 0.010912 | -0.043162 | -0.010857 | 8.6443e-05 | 5.4647e-05 | 0.065567 | 0.065568 | 0.065568 | 0.98189 | -0.34737 | 0.97975 | -0.38921 | 18.0131
12 | 0.0010224 | 0.00025499 | -0.0010224 | -0.0002558 | 6.0277e-08 | -8.0854e-07 | 0.001549 | 0.0015493 | 0.0015493 | 0.98189 | -0.34737 | 0.98183 | -0.34861 | 0.42563
13 | 0.018018 | 0.0045193 | -0.018009 | -0.0045142 | 8.6858e-06 | 5.1631e-06 | 0.027252 | 0.027252 | 0.027252 | 0.98389 | -0.30858 | 0.98337 | -0.3187 | 7.4867
14 | -0.02252 | -0.0056556 | 0.022528 | 0.0056605 | 8.0368e-06 | 4.9148e-06 | 0.034282 | 0.034282 | 0.034282 | 0.97762 | -0.43103 | 0.978 | -0.42355 | 9.418
15 | 0.011991 | 0.0030069 | -0.011991 | -0.0030066 | 7.2295e-07 | 3.9057e-07 | 0.01828 | 0.01828 | 0.01828 | 0.97614 | -0.46016 | 0.97607 | -0.46142 | 5.022
16 | 0.0082677 | 0.0020721 | -0.0082667 | -0.0020717 | 1.0891e-06 | 4.6675e-07 | 0.012579 | 0.012579 | 0.012579 | 0.978 | -0.42355 | 0.97786 | -0.42632 | 3.4559
17 | 0.0085579 | 0.0021453 | -0.0085554 | -0.0021442 | 2.5377e-06 | 1.1235e-06 | 0.013021 | 0.013021 | 0.013021 | 0.978 | -0.42355 | 0.97768 | -0.42978 | 3.5772
18 | -0.039354 | -0.0098779 | 0.039379 | 0.0098935 | 2.4746e-05 | 1.5606e-05 | 0.059882 | 0.059882 | 0.059882 | 0.978 | -0.42355 | 0.97867 | -0.41038 | 16.451
19 | 0.011871 | 0.0029766 | -0.011869 | -0.0029753 | 2.2974e-06 | 1.2366e-06 | 0.018098 | 0.018098 | 0.018098 | 0.97607 | -0.46142 | 0.97587 | -0.46549 | 4.9719
20 | 0.00034893 | 8.712e-05 | -0.00034892 | -8.7448e-05 | 2.7368e-09 | -3.2837e-07 | 0.0005287 | 0.00052882 | 0.00052882 | 0.98182 | -0.34877 | 0.98181 | -0.34894 | 0.14528
21 | -0.0010224 | -0.0002559 | 0.0010224 | 0.0002558 | 7.5689e-09 | -1.015e-07 | 0.0015493 | 0.0015493 | 0.0015493 | 0.98182 | -0.34877 | 0.98183 | -0.34861 | 0.42564
22 | 0.0055312 | 0.0013857 | -0.0055303 | -0.0013856 | 8.7068e-07 | 1.3945e-07 | 0.0083827 | 0.0083828 | 0.0083828 | 0.98182 | -0.34881 | 0.98165 | -0.35211 | 2.303
23 | 0.039955 | 0.010053 | -0.039943 | -0.010046 | 1.1904e-05 | 7.5103e-06 | 0.060696 | 0.060696 | 0.060696 | 0.97975 | -0.38921 | 0.97943 | -0.39544 | 16.6747
24 | 0.0050941 | 0.0012763 | -0.005094 | -0.0012763 | 8.3344e-08 | 6.216e-09 | 0.0077216 | 0.0077216 | 0.0077216 | 0.98165 | -0.35211 | 0.98163 | -0.35246 | 2.1213
25 | -0.039914 | -0.010028 | 0.039943 | 0.010046 | 2.8469e-05 | 1.7961e-05 | 0.060696 | 0.060696 | 0.060696 | 0.97867 | -0.41038 | 0.97943 | -0.39544 | 16.6748
26 | 0.0064409 | 0.0016141 | -0.0064404 | -0.0016139 | 5.2514e-07 | 1.5323e-07 | 0.0098011 | 0.0098012 | 0.0098012 | 0.97786 | -0.42632 | 0.97777 | -0.42803 | 2.6926
27 | 0.002991 | 0.00074942 | -0.0029908 | -0.00074957 | 1.5164e-07 | -1.4773e-07 | 0.0045517 | 0.0045518 | 0.0045518 | 0.97777 | -0.42803 | 0.97772 | -0.42909 | 1.2505
28 | 0.023137 | 0.0058006 | -0.02313 | -0.0057961 | 7.2181e-06 | 4.4238e-06 | 0.03516 | 0.03516 | 0.03516 | 0.9792 | -0.39993 | 0.97886 | -0.40648 | 9.6594
29 | -0.026514 | -0.0066468 | 0.026519 | 0.0066499 | 4.9964e-06 | 3.0945e-06 | 0.040291 | 0.040291 | 0.040291 | 0.9792 | -0.39993 | 0.9794 | -0.39598 | 11.0691
30 | 0.0086861 | 0.0021762 | -0.0086848 | -0.0021756 | 1.2805e-06 | 5.7337e-07 | 0.013204 | 0.013204 | 0.013204 | 0.97886 | -0.40648 | 0.97871 | -0.40958 | 3.6274
31 | -0.03399 | -0.0085221 | 0.034019 | 0.0085406 | 2.9476e-05 | 1.8493e-05 | 0.051642 | 0.051642 | 0.051642 | 0.9794 | -0.39598 | 0.98033 | -0.3778 | 14.1874
32 | 0.007471 | 0.0018722 | -0.0074697 | -0.0018717 | 1.2324e-06 | 4.6778e-07 | 0.011351 | 0.011351 | 0.011351 | 0.9794 | -0.39598 | 0.97922 | -0.39944 | 3.1183
33 | 0.0055087 | 0.00138 | -0.0055074 | -0.0013798 | 1.2786e-06 | 2.0763e-07 | 0.0083751 | 0.0083753 | 0.0083753 | 0.97871 | -0.40958 | 0.97846 | -0.41445 | 2.3009
34 | 0.0031761 | 0.00079567 | -0.0031758 | -0.00079592 | 3.2502e-07 | -2.5903e-07 | 0.0048288 | 0.004829 | 0.004829 | 0.97871 | -0.40958 | 0.9786 | -0.41172 | 1.3266
35 | -0.082197 | -0.020705 | 0.082268 | 0.020749 | 7.1178e-05 | 4.4939e-05 | 0.1248 | 0.1248 | 0.1248 | 0.98033 | -0.3778 | 0.98125 | -0.35971 | 17.1431
36 | 0.048178 | 0.012164 | -0.04806 | -0.012089 | 0.00011766 | 7.4565e-05 | 0.07316 | 0.07316 | 0.07316 | 0.98033 | -0.3778 | 0.97771 | -0.42891 | 20.099
37 | 0.0054276 | 0.0013599 | -0.0054266 | -0.0013598 | 9.2566e-07 | 1.3601e-07 | 0.0082475 | 0.0082477 | 0.0082477 | 0.97922 | -0.39944 | 0.97904 | -0.40302 | 2.2658
38 | 0.0055074 | 0.0013798 | -0.0055062 | -0.0013796 | 1.2299e-06 | 2.0004e-07 | 0.0083753 | 0.0083756 | 0.0083756 | 0.97846 | -0.41445 | 0.97822 | -0.41914 | 2.301
39 | -0.090525 | -0.022819 | 0.090611 | 0.022872 | 8.5596e-05 | 5.3404e-05 | 0.13732 | 0.13732 | 0.13732 | 0.98125 | -0.35971 | 0.98227 | -0.33996 | 12.5754
40 | 0.043228 | 0.010878 | -0.043215 | -0.01087 | 1.3442e-05 | 8.4988e-06 | 0.065806 | 0.065806 | 0.065806 | 0.97771 | -0.42891 | 0.97738 | -0.43542 | 18.0786
41 | 0.0034879 | 0.00087391 | -0.0034879 | -0.00087394 | 4.8254e-08 | -2.6697e-08 | 0.0053011 | 0.0053012 | 0.0053012 | 0.97904 | -0.40302 | 0.97903 | -0.40331 | 1.4564
42 | 0.0017379 | 0.00043513 | -0.0017378 | -0.00043553 | 9.6124e-08 | -3.9895e-07 | 0.0026434 | 0.0026436 | 0.0026436 | 0.97822 | -0.41914 | 0.97816 | -0.4203 | 0.72626
43 | -0.092915 | -0.02345 | 0.093017 | 0.023513 | 0.00010167 | 6.3509e-05 | 0.14081 | 0.14081 | 0.14081 | 0.98227 | -0.33996 | 0.98344 | -0.31715 | 12.895
44 | 0.041387 | 0.010412 | -0.041354 | -0.010391 | 3.2955e-05 | 2.0814e-05 | 0.063024 | 0.063024 | 0.063024 | 0.97738 | -0.43542 | 0.97653 | -0.4521 | 17.3144
45 | 0.0022015 | 0.00055155 | -0.0022014 | -0.00055174 | 7.985e-08 | -1.8804e-07 | 0.003346 | 0.0033461 | 0.0033461 | 0.97903 | -0.40331 | 0.97899 | -0.40407 | 0.91926
46 | -0.10815 | -0.027389 | 0.10822 | 0.027427 | 6.0527e-05 | 3.8043e-05 | 0.16337 | 0.16337 | 0.16337 | 0.98573 | -0.27281 | 0.98633 | -0.26117 | 14.9604
47 | 0.10528 | 0.026669 | -0.10522 | -0.02663 | 6.248e-05 | 3.9232e-05 | 0.15903 | 0.15903 | 0.15903 | 0.98573 | -0.27281 | 0.98509 | -0.28518 | 14.563
48 | -0.1109 | -0.0281 | 0.11092 | 0.028112 | 1.8962e-05 | 1.1929e-05 | 0.16741 | 0.16741 | 0.16741 | 0.98633 | -0.26117 | 0.98651 | -0.25761 | 15.3309
49 | 0.10207 | 0.02584 | -0.10201 | -0.025804 | 5.7671e-05 | 3.6169e-05 | 0.15427 | 0.15427 | 0.15427 | 0.98509 | -0.28518 | 0.98448 | -0.29695 | 14.1275
50 | -0.11519 | -0.029182 | 0.11527 | 0.029234 | 8.3206e-05 | 5.2407e-05 | 0.17385 | 0.17385 | 0.17385 | 0.98651 | -0.25761 | 0.98729 | -0.24258 | 15.9206
51 | 0.10201 | 0.025804 | -0.10194 | -0.025763 | 6.6137e-05 | 4.148e-05 | 0.15427 | 0.15427 | 0.15427 | 0.98448 | -0.29695 | 0.98378 | -0.31048 | 14.1275
52 | -0.11784 | -0.029878 | 0.11784 | 0.02988 | 3.5728e-06 | 2.2519e-06 | 0.17773 | 0.17773 | 0.17773 | 0.98729 | -0.24258 | 0.98733 | -0.24195 | 16.2753
53 | 0.099037 | 0.025034 | -0.099005 | -0.025014 | 3.1662e-05 | 1.9834e-05 | 0.14987 | 0.14987 | 0.14987 | 0.98378 | -0.31048 | 0.98344 | -0.31715 | 13.7247
54 | -0.122 | -0.030923 | 0.12209 | 0.03098 | 8.9757e-05 | 5.663e-05 | 0.184 | 0.184 | 0.184 | 0.98733 | -0.24195 | 0.98812 | -0.22665 | 16.8498
55 | -0.13155 | -0.033484 | 0.13161 | 0.033517 | 5.2304e-05 | 3.3061e-05 | 0.19769 | 0.19769 | 0.19769 | 0.9911 | -0.16944 | 0.99153 | -0.1612 | 18.1039
56 | 0.1286 | 0.032744 | -0.12845 | -0.032646 | 0.0001547 | 9.773e-05 | 0.19326 | 0.19326 | 0.19326 | 0.9911 | -0.16944 | 0.98979 | -0.19442 | 17.698
57 | -0.13719 | -0.034917 | 0.13733 | 0.035007 | 0.00014261 | 9.0232e-05 | 0.20608 | 0.20608 | 0.20608 | 0.99153 | -0.1612 | 0.99265 | -0.13966 | 18.8714
58 | 0.12646 | 0.032148 | -0.12635 | -0.03208 | 0.00010789 | 6.813e-05 | 0.19027 | 0.19028 | 0.19028 | 0.98979 | -0.19442 | 0.98887 | -0.21215 | 17.4245
59 | -0.1581 | -0.040217 | 0.15811 | 0.04023 | 1.9797e-05 | 1.2561e-05 | 0.2372 | 0.2372 | 0.2372 | 0.99265 | -0.13966 | 0.99279 | -0.13706 | 21.7217
60 | 0.020763 | 0.00521 | -0.020757 | -0.0052065 | 5.7852e-06 | 3.4967e-06 | 0.031126 | 0.031126 | 0.031126 | 0.99265 | -0.13966 | 0.99235 | -0.14551 | 8.5511
61 | 0.12635 | 0.03208 | -0.12629 | -0.03204 | 6.3076e-05 | 3.9832e-05 | 0.19028 | 0.19028 | 0.19028 | 0.98887 | -0.21215 | 0.98833 | -0.22253 | 17.4245
62 | -0.16074 | -0.040887 | 0.16091 | 0.040994 | 0.00016865 | 0.00010704 | 0.24113 | 0.24113 | 0.24113 | 0.99279 | -0.13706 | 0.99393 | -0.11531 | 22.0819
63 | 0.018034 | 0.0045241 | -0.01803 | -0.0045216 | 4.2979e-06 | 2.5483e-06 | 0.027043 | 0.027043 | 0.027043 | 0.99235 | -0.14551 | 0.99209 | -0.15051 | 7.4295
64 | 0.12497 | 0.031709 | -0.12494 | -0.031694 | 2.4787e-05 | 1.5649e-05 | 0.18829 | 0.18829 | 0.18829 | 0.98833 | -0.22253 | 0.98812 | -0.22665 | 17.2423
65 | -0.16419 | -0.041818 | 0.16436 | 0.041926 | 0.00017016 | 0.00010803 | 0.24605 | 0.24605 | 0.24605 | 0.99393 | -0.11531 | 0.99505 | -0.093851 | 22.5323
66 | 0.01584 | 0.0039728 | -0.015834 | -0.0039696 | 5.5271e-06 | 3.2003e-06 | 0.023759 | 0.023759 | 0.023759 | 0.99209 | -0.15051 | 0.99171 | -0.15783 | 6.5273
67 | -0.00096439 | -0.0002417 | 0.00096439 | 0.00024159 | 6.9462e-09 | -1.0936e-07 | 0.0014481 | 0.0014481 | 0.0014481 | 0.99097 | -0.1723 | 0.99098 | -0.17215 | 0.39783
68 | -0.0017357 | -0.00043491 | 0.0017358 | 0.00043483 | 1.869e-08 | -8.2571e-08 | 0.0026063 | 0.0026063 | 0.0026063 | 0.99098 | -0.17215 | 0.99099 | -0.17192 | 0.71602
69 | -0.013469 | -0.0033757 | 0.013474 | 0.0033786 | 5.2049e-06 | 2.9241e-06 | 0.020591 | 0.020591 | 0.020591 | 0.97331 | -0.51545 | 0.97373 | -0.50735 | 5.657
70 | 0.0097108 | 0.0024338 | -0.0097105 | -0.0024337 | 2.7139e-07 | 1.3288e-07 | 0.014846 | 0.014846 | 0.014846 | 0.97331 | -0.51545 | 0.97328 | -0.51604 | 4.0786
71 | -0.013474 | -0.0033786 | 0.013476 | 0.0033796 | 1.7837e-06 | 1.002e-06 | 0.020591 | 0.020591 | 0.020591 | 0.97373 | -0.50735 | 0.97387 | -0.50457 | 5.657
72 | 0.0097105 | 0.0024337 | -0.0097084 | -0.0024326 | 2.1227e-06 | 1.0394e-06 | 0.014846 | 0.014846 | 0.014846 | 0.97328 | -0.51604 | 0.97305 | -0.52063 | 4.0786
73 | -0.020832 | -0.0052233 | 0.020842 | 0.0052297 | 1.06e-05 | 6.4366e-06 | 0.031831 | 0.031831 | 0.031831 | 0.97387 | -0.50457 | 0.97441 | -0.4939 | 8.7447
74 | 0.007356 | 0.0018437 | -0.007355 | -0.0018433 | 9.8778e-07 | 3.7278e-07 | 0.01124 | 0.01124 | 0.01124 | 0.97387 | -0.50457 | 0.97372 | -0.50739 | 3.0878
75 | 0.0045802 | 0.0011474 | -0.0045798 | -0.0011474 | 3.7076e-07 | -1.3047e-08 | 0.0070039 | 0.007004 | 0.007004 | 0.97305 | -0.52063 | 0.97297 | -0.52233 | 1.9242
76 | -0.020842 | -0.0052297 | 0.020851 | 0.0052348 | 8.4127e-06 | 5.1082e-06 | 0.031831 | 0.031831 | 0.031831 | 0.97441 | -0.4939 | 0.97484 | -0.48544 | 8.7447
77 | 0.004286 | 0.0010742 | -0.004286 | -0.0010742 | 1.6102e-08 | -2.1452e-09 | 0.0065497 | 0.0065497 | 0.0065497 | 0.97372 | -0.50739 | 0.97372 | -0.50747 | 1.7994
78 | 0.0045798 | 0.0011474 | -0.0045793 | -0.0011474 | 5.3418e-07 | -1.8708e-08 | 0.007004 | 0.0070041 | 0.0070041 | 0.97297 | -0.52233 | 0.97284 | -0.52478 | 1.9242
79 | -0.023594 | -0.0059223 | 0.023595 | 0.0059233 | 1.6328e-06 | 1.0032e-06 | 0.036017 | 0.036017 | 0.036017 | 0.97484 | -0.48544 | 0.97491 | -0.48398 | 9.8949
80 | 0.0045793 | 0.0011474 | -0.004579 | -0.0011474 | 2.345e-07 | -8.1798e-09 | 0.0070041 | 0.0070042 | 0.0070042 | 0.97284 | -0.52478 | 0.97279 | -0.52585 | 1.9242
81 | 0.0014331 | 0.0003589 | -0.001433 | -0.00035916 | 3.7499e-08 | -2.5365e-07 | 0.0021529 | 0.002153 | 0.002153 | 0.99046 | -0.18163 | 0.99043 | -0.18218 | 0.59148
82 | -0.0021524 | -0.00053918 | 0.0021525 | 0.00053895 | 8.8803e-08 | -2.3467e-07 | 0.0032336 | 0.0032335 | 0.0032336 | 0.99046 | -0.18163 | 0.99051 | -0.18076 | 0.88835
83 | -0.0036724 | -0.00091987 | 0.0036728 | 0.00091969 | 3.7753e-07 | -1.8421e-07 | 0.0055168 | 0.0055167 | 0.0055168 | 0.99051 | -0.18076 | 0.99062 | -0.1786 | 1.5156
84 | -0.08201 | -0.02085 | 0.082073 | 0.02089 | 6.3048e-05 | 4.0208e-05 | 0.12329 | 0.12329 | 0.12329 | 0.99062 | -0.1786 | 0.99145 | -0.16265 | 33.8718
85 | -0.083888 | -0.021345 | 0.084098 | 0.021478 | 0.00020965 | 0.00013372 | 0.12602 | 0.12602 | 0.12602 | 0.99145 | -0.16265 | 0.99416 | -0.11094 | 34.6202
86 | -0.0031885 | -0.00079912 | 0.0031889 | 0.00079886 | 3.4293e-07 | -2.6209e-07 | 0.0048666 | 0.0048664 | 0.0048666 | 0.97493 | -0.48382 | 0.97505 | -0.48157 | 1.337
87 | 0.002011 | 0.00050385 | -0.0020109 | -0.00050399 | 4.7061e-08 | -1.3607e-07 | 0.0030689 | 0.003069 | 0.003069 | 0.97505 | -0.48157 | 0.97502 | -0.48206 | 0.84312
88 | -0.0051999 | -0.0013027 | 0.0051999 | 0.0013027 | 4.6426e-08 | 5.1896e-09 | 0.0079353 | 0.0079353 | 0.0079353 | 0.97505 | -0.48157 | 0.97506 | -0.48138 | 2.18
89 | -0.10887 | -0.027695 | 0.10896 | 0.027752 | 8.9744e-05 | 5.7319e-05 | 0.1631 | 0.1631 | 0.1631 | 0.99416 | -0.11094 | 0.99505 | -0.093851 | 44.8086
90 | 0.024776 | 0.0062165 | -0.024756 | -0.0062045 | 1.9452e-05 | 1.1961e-05 | 0.037086 | 0.037086 | 0.037086 | 0.99416 | -0.11094 | 0.9933 | -0.12742 | 10.1885
91 | -0.0085759 | -0.0021488 | 0.0085796 | 0.0021505 | 3.6829e-06 | 1.6415e-06 | 0.013087 | 0.013087 | 0.013087 | 0.97506 | -0.48138 | 0.97552 | -0.47236 | 3.5954
92 | -0.0085796 | -0.0021505 | 0.0085824 | 0.0021517 | 2.8125e-06 | 1.2531e-06 | 0.013087 | 0.013087 | 0.013087 | 0.97552 | -0.47236 | 0.97587 | -0.46549 | 3.5954
93 | -0.0023421 | -0.00058699 | 0.0023422 | 0.00058681 | 9.1797e-08 | -1.7801e-07 | 0.0035827 | 0.0035827 | 0.0035827 | 0.97275 | -0.52668 | 0.97279 | -0.52585 | 0.98427
94 | -0.024822 | -0.0062209 | 0.024853 | 0.0062401 | 3.1178e-05 | 1.9174e-05 | 0.037175 | 0.037175 | 0.037175 | 0.99355 | -0.12408 | 0.99491 | -0.097748 | 10.2129
95 | -0.024853 | -0.0062401 | 0.024888 | 0.0062614 | 3.4733e-05 | 2.1358e-05 | 0.037175 | 0.037174 | 0.037175 | 0.99491 | -0.097748 | 0.99643 | -0.068496 | 10.2128
96 | -0.024888 | -0.0062614 | 0.024916 | 0.0062791 | 2.8773e-05 | 1.769e-05 | 0.037174 | 0.037174 | 0.037174 | 0.99643 | -0.068496 | 0.99769 | -0.044329 | 10.2127
97 | -0.040217 | -0.010114 | 0.040241 | 0.010129 | 2.381e-05 | 1.5008e-05 | 0.059994 | 0.059994 | 0.059994 | 0.99769 | -0.044329 | 0.99833 | -0.031941 | 16.482
98 | -0.042953 | -0.010809 | 0.043019 | 0.01085 | 6.567e-05 | 4.1469e-05 | 0.064037 | 0.064037 | 0.064037 | 0.99833 | -0.031941 | 1 | 0 | 17.5926
99 | 0.014355 | 0.0035988 | -0.014354 | -0.0035983 | 7.9102e-07 | 4.4759e-07 | 0.021539 | 0.021539 | 0.021539 | 0.99171 | -0.15783 | 0.99165 | -0.15898 | 5.9173
100 | 0.0019543 | 0.00048956 | -0.0019542 | -0.00048977 | 6.29e-08 | -2.1138e-07 | 0.0029324 | 0.0029325 | 0.0029325 | 0.99165 | -0.15898 | 0.99162 | -0.15966 | 0.80562
101 | 0.0124 | 0.0031088 | -0.012397 | -0.0031075 | 2.325e-06 | 1.257e-06 | 0.018607 | 0.018607 | 0.018607 | 0.99165 | -0.15898 | 0.99145 | -0.16292 | 5.1118
102 | 0.010212 | 0.0025598 | -0.01021 | -0.0025589 | 1.8748e-06 | 9.2547e-07 | 0.015327 | 0.015327 | 0.015327 | 0.99145 | -0.16292 | 0.99125 | -0.16677 | 4.2108
103 | 0.0084835 | 0.0021261 | -0.0084818 | -0.0021254 | 1.6243e-06 | 6.9533e-07 | 0.012735 | 0.012735 | 0.012735 | 0.99125 | -0.16677 | 0.99105 | -0.17079 | 3.4986
104 | 0.0044871 | 0.0011242 | -0.0044866 | -0.0011242 | 4.9184e-07 | -4.3574e-08 | 0.0068017 | 0.0068018 | 0.0068018 | 0.98163 | -0.35246 | 0.98152 | -0.35476 | 1.8686
105 | 0.0029348 | 0.00073529 | -0.0029348 | -0.00073535 | 5.3149e-08 | -5.6474e-08 | 0.0044492 | 0.0044492 | 0.0044492 | 0.98152 | -0.35476 | 0.9815 | -0.35514 | 1.2223
106 | 0.0022947 | 0.00057494 | -0.0022947 | -0.0005751 | 7.1818e-08 | -1.5401e-07 | 0.0034789 | 0.003479 | 0.003479 | 0.9815 | -0.35514 | 0.98146 | -0.35579 | 0.95576
107 | 0.010826 | 0.0027137 | -0.010822 | -0.0027118 | 3.7175e-06 | 1.9107e-06 | 0.016381 | 0.016381 | 0.016381 | 0.98337 | -0.3187 | 0.983 | -0.32591 | 4.5004
108 | 0.0048046 | 0.0012037 | -0.0048039 | -0.0012037 | 6.1857e-07 | 6.0115e-10 | 0.0072728 | 0.0072729 | 0.0072729 | 0.983 | -0.32591 | 0.98286 | -0.32861 | 1.998
109 | 0.0019662 | 0.00049254 | -0.0019661 | -0.00049276 | 6.9545e-08 | -2.2073e-07 | 0.0029767 | 0.0029768 | 0.0029768 | 0.98286 | -0.32861 | 0.98283 | -0.32936 | 0.81779
110 | -0.026688 | -0.0066983 | 0.026704 | 0.0067084 | 1.6265e-05 | 1.0083e-05 | 0.040737 | 0.040737 | 0.040737 | 0.97491 | -0.48398 | 0.97556 | -0.47121 | 11.1915
111 | 0.0037951 | 0.00095079 | -0.0037948 | -0.00095088 | 2.0437e-07 | -8.548e-08 | 0.005698 | 0.0056981 | 0.0056981 | 0.99105 | -0.17079 | 0.99099 | -0.17192 | 1.5654
112 | 0.013284 | 0.0033308 | -0.013283 | -0.0033299 | 1.723e-06 | 9.6245e-07 | 0.020243 | 0.020243 | 0.020243 | 0.97653 | -0.4521 | 0.97639 | -0.45482 | 5.5613
113 | 0.02807 | 0.0070602 | -0.028044 | -0.0070443 | 2.561e-05 | 1.5924e-05 | 0.042781 | 0.042781 | 0.042781 | 0.97653 | -0.4521 | 0.97556 | -0.47121 | 11.7532
114 | 0.01145 | 0.0028706 | -0.011447 | -0.0028689 | 3.2397e-06 | 1.7187e-06 | 0.01745 | 0.01745 | 0.01745 | 0.97639 | -0.45482 | 0.97609 | -0.46076 | 4.7941
115 | 0.27855 | 0.071469 | -0.27842 | -0.071391 | 0.00012209 | 7.7913e-05 | 0.41507 | 0.41507 | 0.41507 | 1 | 0 | 0.99952 | -0.0090383 | 38.0101
116 | 0.039117 | 0.0098194 | -0.039085 | -0.0097995 | 3.1619e-05 | 1.991e-05 | 0.058212 | 0.058212 | 0.058212 | 1 | 0 | 0.99912 | -0.016962 | 15.9924
117 | 0.27445 | 0.070395 | -0.27333 | -0.069678 | 0.001124 | 0.00071725 | 0.40915 | 0.40916 | 0.40916 | 0.99952 | -0.0090383 | 0.99505 | -0.093851 | 37.4684
118 | 0.01459 | 0.0036603 | -0.014578 | -0.0036535 | 1.2082e-05 | 6.84e-06 | 0.02173 | 0.02173 | 0.02173 | 0.99912 | -0.016962 | 0.99821 | -0.034346 | 5.9699

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36233 | 0.092139

## res_load
| p_mw | q_mvar
0 | 0.00031202 | 7.8201e-05
1 | 0.000342 | 8.5712e-05
2 | 0.0038497 | 0.00096482
3 | 0.00080783 | 0.00020246
4 | 0.002757 | 0.00069098
5 | 0.0028992 | 0.00072662
6 | 0.0029902 | 0.00074941
7 | 0.0010394 | 0.00026049
8 | 0.0013929 | 0.00034909
9 | 0.00011967 | 2.9991e-05
10 | 0.00067343 | 0.00016878
11 | 0.00034892 | 8.7448e-05
12 | 0.0040512 | 0.0010153
13 | 0.0032077 | 0.00080392
14 | 0.0004362 | 0.00010932
15 | 0.00053565 | 0.00013425
16 | 0.0018258 | 0.00045758
17 | 0.0085554 | 0.0021442
18 | 0.0034494 | 0.0008645
19 | 0.0029908 | 0.00074957
20 | 0.0033766 | 0.00084625
21 | 0.014444 | 0.0036199
22 | 0.0020422 | 0.00051182
23 | 0.0031758 | 0.00079592
24 | 0.0082573 | 0.0020695
25 | 0.0048321 | 0.001211
26 | 0.0019387 | 0.00048588
27 | 0.0037683 | 0.00094443
28 | 0.0023044 | 0.00057752
29 | 0.0018272 | 0.00045794
30 | 0.0012864 | 0.00032239
31 | 0.0028749 | 0.00072053
32 | 0.0026824 | 0.00067227
33 | 0.0031487 | 0.00078914
34 | 0.0042692 | 0.00107
35 | 0.00257 | 0.0006441
36 | 0.0029082 | 0.00072886
37 | 0.0041623 | 0.0010432
38 | 0.0059882 | 0.0015008
39 | 0.0029522 | 0.0007399
40 | 0.0055849 | 0.0013997
41 | 0.0019873 | 0.00049806
42 | 0.0026244 | 0.00065773
43 | 0.0027229 | 0.00068242
44 | 0.0013216 | 0.00033121
45 | 0.0032851 | 0.00082331
46 | 0.0021897 | 0.00054878
47 | 0.00096439 | 0.0002417
48 | 0.00077135 | 0.00019332
49 | 0.0028466 | 0.00071342
50 | 0.0037581 | 0.00094187
51 | 0.0051282 | 0.0012853
52 | 0.003069 | 0.00076916
53 | 0.0027429 | 0.00068743
54 | 0.004286 | 0.0010742
55 | 0.00071933 | 0.00018028
56 | 0.001433 | 0.00035916
57 | 0.0015199 | 0.00038093
58 | 0.0018151 | 0.0004549
59 | 0.0031885 | 0.00079912
60 | 0.003376 | 0.00084612
61 | 0.0020109 | 0.00050399
62 | 0.0023421 | 0.00058699
63 | 0.0022368 | 0.0005606
64 | 0.024822 | 0.0062209
65 | 0.015301 | 0.0038347
66 | 0.0027123 | 0.00067976
67 | 0.0014797 | 0.00037084
68 | 0.0019542 | 0.00048977
69 | 0.0021852 | 0.00054765
70 | 0.0017269 | 0.00043281
71 | 0.0017378 | 0.00043553
72 | 0.00060688 | 0.0001521
73 | 0.0015518 | 0.00038892
74 | 0.00064003 | 0.00016041
75 | 0.0022947 | 0.0005751
76 | 0.0071838 | 0.0018004
77 | 0.0060173 | 0.0015081
78 | 0.0028377 | 0.0007112
79 | 0.0032862 | 0.0008236
80 | 0.0019661 | 0.00049276
81 | 0.0030923 | 0.000775
82 | 0.0046868 | 0.0011746
83 | 0.0020591 | 0.00051605
84 | 0.0018326 | 0.0004593
85 | 0.0013403 | 0.00033592
86 | 0.011447 | 0.0028689
87 | 0.0039737 | 0.00099591
88 | 0.024496 | 0.0061392
89 | 0.014578 | 0.0036535
90 | 0.024756 | 0.0062045
91 | 0.0022014 | 0.00055174

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1