## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2513-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2513-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2513-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2513-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2513-3_0_3_node_113 | 0.4 | n |  | TRUE
5 | bus_LV_2513-3_0_3_node_80 | 0.4 | n |  | TRUE
6 | bus_LV_2513-3_0_3_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_2513-3_0_3_node_81 | 0.4 | n |  | TRUE
8 | bus_LV_2513-3_0_3_node_139 | 0.4 | n |  | TRUE
9 | bus_LV_2513-3_0_3_node_138 | 0.4 | n |  | TRUE
10 | bus_LV_2513-3_0_3_node_119 | 0.4 | n |  | TRUE
11 | bus_LV_2513-3_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2513-3_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2513-3_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2513-3_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2513-3_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2513-3_0_3_node_72 | 0.4 | n |  | TRUE
17 | bus_LV_2513-3_0_3_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_2513-3_0_3_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_2513-3_0_3_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_2513-3_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2513-3_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2513-3_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2513-3_0_3_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2513-3_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2513-3_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2513-3_0_3_node_118 | 0.4 | n |  | TRUE
27 | bus_LV_2513-3_0_3_node_130 | 0.4 | n |  | TRUE
28 | bus_LV_2513-3_0_3_node_127 | 0.4 | n |  | TRUE
29 | bus_LV_2513-3_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2513-3_0_3_node_79 | 0.4 | n |  | TRUE
31 | bus_LV_2513-3_0_3_node_145 | 0.4 | n |  | TRUE
32 | bus_LV_2513-3_0_3_node_92 | 0.4 | n |  | TRUE
33 | bus_LV_2513-3_0_3_node_93 | 0.4 | n |  | TRUE
34 | bus_LV_2513-3_0_3_node_134 | 0.4 | n |  | TRUE
35 | bus_LV_2513-3_0_3_node_109 | 0.4 | n |  | TRUE
36 | bus_LV_2513-3_0_3_node_128 | 0.4 | n |  | TRUE
37 | bus_LV_2513-3_0_3_node_77 | 0.4 | n |  | TRUE
38 | bus_LV_2513-3_0_3_node_147 | 0.4 | n |  | TRUE
39 | bus_LV_2513-3_0_3_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_2513-3_0_3_node_18 | 0.4 | n |  | TRUE
41 | bus_LV_2513-3_0_3_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2513-3_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_2513-3_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2513-3_0_3_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_2513-3_0_3_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_2513-3_0_3_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_2513-3_0_3_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_2513-3_0_3_node_91 | 0.4 | n |  | TRUE
49 | bus_LV_2513-3_0_3_node_94 | 0.4 | n |  | TRUE
50 | bus_LV_2513-3_0_3_node_143 | 0.4 | n |  | TRUE
51 | bus_LV_2513-3_0_3_node_135 | 0.4 | n |  | TRUE
52 | bus_LV_2513-3_0_3_node_136 | 0.4 | n |  | TRUE
53 | bus_LV_2513-3_0_3_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_2513-3_0_3_node_140 | 0.4 | n |  | TRUE
55 | bus_LV_2513-3_0_3_node_95 | 0.4 | n |  | TRUE
56 | bus_LV_2513-3_0_3_node_25 | 0.4 | n |  | TRUE
57 | bus_LV_2513-3_0_3_node_26 | 0.4 | n |  | TRUE
58 | bus_LV_2513-3_0_3_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_2513-3_0_3_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_2513-3_0_3_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_2513-3_0_3_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_2513-3_0_3_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_2513-3_0_3_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_2513-3_0_3_node_131 | 0.4 | n |  | TRUE
65 | bus_LV_2513-3_0_3_node_108 | 0.4 | n |  | TRUE
66 | bus_LV_2513-3_0_3_node_120 | 0.4 | n |  | TRUE
67 | bus_LV_2513-3_0_3_node_73 | 0.4 | n |  | TRUE
68 | bus_LV_2513-3_0_3_node_75 | 0.4 | n |  | TRUE
69 | bus_LV_2513-3_0_3_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_2513-3_0_3_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_2513-3_0_3_node_105 | 0.4 | n |  | TRUE
72 | bus_LV_2513-3_0_3_node_102 | 0.4 | n |  | TRUE
73 | bus_LV_2513-3_0_3_node_125 | 0.4 | n |  | TRUE
74 | bus_LV_2513-3_0_3_node_110 | 0.4 | n |  | TRUE
75 | bus_LV_2513-3_0_3_node_32 | 0.4 | n |  | TRUE
76 | bus_LV_2513-3_0_3_node_33 | 0.4 | n |  | TRUE
77 | bus_LV_2513-3_0_3_node_34 | 0.4 | n |  | TRUE
78 | bus_LV_2513-3_0_3_node_35 | 0.4 | n |  | TRUE
79 | bus_LV_2513-3_0_3_node_36 | 0.4 | n |  | TRUE
80 | bus_LV_2513-3_0_3_node_37 | 0.4 | n |  | TRUE
81 | bus_LV_2513-3_0_3_node_100 | 0.4 | n |  | TRUE
82 | bus_LV_2513-3_0_3_node_115 | 0.4 | n |  | TRUE
83 | bus_LV_2513-3_0_3_node_38 | 0.4 | n |  | TRUE
84 | bus_LV_2513-3_0_3_node_116 | 0.4 | n |  | TRUE
85 | bus_LV_2513-3_0_3_node_40 | 0.4 | n |  | TRUE
86 | bus_LV_2513-3_0_3_node_42 | 0.4 | n |  | TRUE
87 | bus_LV_2513-3_0_3_node_44 | 0.4 | n |  | TRUE
88 | bus_LV_2513-3_0_3_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_2513-3_0_3_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_2513-3_0_3_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2513-3_0_3_node_46 | 0.4 | n |  | TRUE
92 | bus_LV_2513-3_0_3_node_48 | 0.4 | n |  | TRUE
93 | bus_LV_2513-3_0_3_node_50 | 0.4 | n |  | TRUE
94 | bus_LV_2513-3_0_3_node_51 | 0.4 | n |  | TRUE
95 | bus_LV_2513-3_0_3_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_2513-3_0_3_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_2513-3_0_3_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_2513-3_0_3_node_52 | 0.4 | n |  | TRUE
99 | bus_LV_2513-3_0_3_node_53 | 0.4 | n |  | TRUE
100 | bus_LV_2513-3_0_3_node_54 | 0.4 | n |  | TRUE
101 | bus_LV_2513-3_0_3_node_55 | 0.4 | n |  | TRUE
102 | bus_LV_2513-3_0_3_node_56 | 0.4 | n |  | TRUE
103 | bus_LV_2513-3_0_3_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_2513-3_0_3_node_132 | 0.4 | n |  | TRUE
105 | bus_LV_2513-3_0_3_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2513-3_0_3_node_57 | 0.4 | n |  | TRUE
107 | bus_LV_2513-3_0_3_node_58 | 0.4 | n |  | TRUE
108 | bus_LV_2513-3_0_3_node_59 | 0.4 | n |  | TRUE
109 | bus_LV_2513-3_0_3_node_60 | 0.4 | n |  | TRUE
110 | bus_LV_2513-3_0_3_node_61 | 0.4 | n |  | TRUE
111 | bus_LV_2513-3_0_3_node_69 | 0.4 | n |  | TRUE
112 | bus_LV_2513-3_0_3_node_144 | 0.4 | n |  | TRUE
113 | bus_LV_2513-3_0_3_node_121 | 0.4 | n |  | TRUE
114 | bus_LV_2513-3_0_3_node_62 | 0.4 | n |  | TRUE
115 | bus_LV_2513-3_0_3_node_63 | 0.4 | n |  | TRUE
116 | bus_LV_2513-3_0_3_node_64 | 0.4 | n |  | TRUE
117 | bus_LV_2513-3_0_3_node_66 | 0.4 | n |  | TRUE
118 | bus_LV_2513-3_0_3_node_67 | 0.4 | n |  | TRUE
119 | bus_LV_2513-3_0_3_node_89 | 0.4 | n |  | TRUE
120 | bus_LV_2513-3_0_3_node_87 | 0.4 | n |  | TRUE
121 | bus_LV_2513-3_0_3_node_78 | 0.4 | n |  | TRUE
122 | bus_LV_2513-3_0_3_node_82 | 0.4 | n |  | TRUE
123 | bus_LV_2513-3_0_3_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_2513-3_0_3_node_84 | 0.4 | n |  | TRUE
125 | bus_LV_2513-3_0_3_node_85 | 0.4 | n |  | TRUE
126 | bus_LV_2513-3_0_3_node_106 | 0.4 | n |  | TRUE
127 | bus_LV_2513-3_0_3_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_2513-3_0_3_node_86 | 0.4 | n |  | TRUE
129 | bus_LV_2513-3_0_3_node_88 | 0.4 | n |  | TRUE
130 | bus_LV_2513-3_0_3_node_90 | 0.4 | n |  | TRUE
131 | bus_LV_2513-3_0_3_node_117 | 0.4 | n |  | TRUE
132 | bus_LV_2513-3_0_3_node_137 | 0.4 | n |  | TRUE
133 | bus_LV_2513-3_0_3_node_107 | 0.4 | n |  | TRUE
134 | bus_LV_2513-3_0_3_node_142 | 0.4 | n |  | TRUE
135 | bus_LV_2513-3_0_3_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_2513-3_0_3_node_141 | 0.4 | n |  | TRUE
137 | bus_LV_2513-3_0_3_node_122 | 0.4 | n |  | TRUE
138 | bus_LV_2513-3_0_3_node_123 | 0.4 | n |  | TRUE
139 | bus_LV_2513-3_0_3_node_124 | 0.4 | n |  | TRUE
140 | bus_LV_2513-3_0_3_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_2513-3_0_3_node_146 | 0.4 | n |  | TRUE
142 | bus_LV_2513-3_0_3_node_129 | 0.4 | n |  | TRUE
143 | bus_MV_393_0_node_188 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2513-3_0_3_load_0 | 0 | 0.0097047 | 0.0024322 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2513-3_0_3_load_2 | 2 | 0.0022477 | 0.00056334 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2513-3_0_3_load_3 | 3 | 0.016298 | 0.0040847 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2513-3_0_3_load_113 | 4 | 0.00046546 | 0.00011665 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2513-3_0_3_load_80 | 5 | 0.016712 | 0.0041884 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2513-3_0_3_load_81 | 7 | 0.0019063 | 0.00047776 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2513-3_0_3_load_138 | 9 | 0.00071206 | 0.00017846 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2513-3_0_3_load_119 | 10 | 0.0067099 | 0.0016817 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2513-3_0_3_load_5 | 11 | 0.0026657 | 0.00066808 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2513-3_0_3_load_6 | 12 | 0.00070382 | 0.00017639 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2513-3_0_3_load_7 | 13 | 0.0012162 | 0.0003048 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2513-3_0_3_load_8 | 14 | 0.0013976 | 0.00035027 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2513-3_0_3_load_9 | 15 | 0.0040501 | 0.001015 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2513-3_0_3_load_72 | 16 | 0.0005097 | 0.00012774 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2513-3_0_3_load_49 | 17 | 0.003911 | 0.0009802 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2513-3_0_3_load_71 | 18 | 0.00082843 | 0.00020762 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2513-3_0_3_load_47 | 19 | 0.00093964 | 0.00023549 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2513-3_0_3_load_10 | 20 | 0.0060008 | 0.0015039 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2513-3_0_3_load_11 | 21 | 0.0054322 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2513-3_0_3_load_13 | 23 | 0.00096231 | 0.00024118 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2513-3_0_3_load_118 | 26 | 0.0015628 | 0.00039168 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2513-3_0_3_load_127 | 28 | 0.0012804 | 0.00032089 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2513-3_0_3_load_79 | 30 | 0.0017645 | 0.00044223 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2513-3_0_3_load_145 | 31 | 0.017423 | 0.0043666 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2513-3_0_3_load_92 | 32 | 0.0072587 | 0.0018192 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2513-3_0_3_load_109 | 35 | 0.0027282 | 0.00068374 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2513-3_0_3_load_128 | 36 | 0.0010814 | 0.00027101 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2513-3_0_3_load_77 | 37 | 0.0024618 | 0.00061698 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2513-3_0_3_load_147 | 38 | 0.017523 | 0.0043918 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2513-3_0_3_load_17 | 39 | 0.0014634 | 0.00036676 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2513-3_0_3_load_41 | 43 | 0.0078184 | 0.0019595 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2513-3_0_3_load_21 | 44 | 0.00144 | 0.00036089 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2513-3_0_3_load_22 | 45 | 0.00021618 | 5.4181e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2513-3_0_3_load_23 | 46 | 0.0014507 | 0.00036359 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2513-3_0_3_load_24 | 47 | 3.1597e-05 | 7.9191e-06 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2513-3_0_3_load_91 | 48 | 0.0096761 | 0.0024251 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2513-3_0_3_load_94 | 49 | 0.0068151 | 0.001708 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2513-3_0_3_load_143 | 50 | 0.00018358 | 4.6011e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2513-3_0_3_load_135 | 51 | 0.0033857 | 0.00084854 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2513-3_0_3_load_136 | 52 | 0.00095135 | 0.00023843 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2513-3_0_3_load_140 | 54 | 0.010147 | 0.0025431 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2513-3_0_3_load_95 | 55 | 0.0042526 | 0.0010658 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2513-3_0_3_load_25 | 56 | 0.0019436 | 0.00048711 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2513-3_0_3_load_28 | 59 | 0.00045957 | 0.00011518 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2513-3_0_3_load_30 | 61 | 0.001154 | 0.00028923 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2513-3_0_3_load_31 | 62 | 0.0014149 | 0.00035461 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2513-3_0_3_load_74 | 63 | 0.0020892 | 0.00052361 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2513-3_0_3_load_131 | 64 | 0.0025034 | 0.0006274 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2513-3_0_3_load_108 | 65 | 0.0010038 | 0.00025158 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2513-3_0_3_load_120 | 66 | 0.0038295 | 0.00095977 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2513-3_0_3_load_73 | 67 | 0.0014744 | 0.00036951 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2513-3_0_3_load_76 | 69 | 0.012601 | 0.0031581 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2513-3_0_3_load_105 | 71 | 0.0057404 | 0.0014387 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2513-3_0_3_load_102 | 72 | 0.0075793 | 0.0018996 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2513-3_0_3_load_125 | 73 | 0.0028314 | 0.00070962 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2513-3_0_3_load_110 | 74 | 0.0017005 | 0.0004262 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2513-3_0_3_load_32 | 75 | 0.00077008 | 0.000193 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2513-3_0_3_load_33 | 76 | 0.00049054 | 0.00012294 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2513-3_0_3_load_34 | 77 | 0.0015415 | 0.00038635 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2513-3_0_3_load_37 | 80 | 0.00018207 | 4.563e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2513-3_0_3_load_100 | 81 | 0.0013769 | 0.00034509 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2513-3_0_3_load_115 | 82 | 7.5325e-05 | 1.8878e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2513-3_0_3_load_38 | 83 | 0.0035463 | 0.00088878 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2513-3_0_3_load_116 | 84 | 0.0030471 | 0.00076367 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2513-3_0_3_load_40 | 85 | 0.00061942 | 0.00015524 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2513-3_0_3_load_44 | 87 | 0.0005572 | 0.00013965 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2513-3_0_3_load_45 | 88 | 0.0006882 | 0.00017248 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2513-3_0_3_load_68 | 90 | 0.00015504 | 3.8857e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2513-3_0_3_load_46 | 91 | 0.006121 | 0.0015341 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2513-3_0_3_load_51 | 94 | 0.0020209 | 0.00050649 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2513-3_0_3_load_99 | 95 | 0.0038163 | 0.00095646 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2513-3_0_3_load_96 | 96 | 0.001459 | 0.00036566 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2513-3_0_3_load_97 | 97 | 0.001839 | 0.00046089 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2513-3_0_3_load_52 | 98 | 0.0024205 | 0.00060662 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2513-3_0_3_load_53 | 99 | 0.0014061 | 0.00035241 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2513-3_0_3_load_54 | 100 | 0.00105 | 0.00026315 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2513-3_0_3_load_55 | 101 | 0.0015331 | 0.00038424 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2513-3_0_3_load_56 | 102 | 0.00032387 | 8.1171e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2513-3_0_3_load_101 | 103 | 0.001122 | 0.0002812 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2513-3_0_3_load_132 | 104 | 0.013511 | 0.0033862 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2513-3_0_3_load_65 | 105 | 0.00063567 | 0.00015931 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2513-3_0_3_load_57 | 106 | 0.00078648 | 0.00019711 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2513-3_0_3_load_58 | 107 | 0.0023832 | 0.00059728 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2513-3_0_3_load_59 | 108 | 0.00055016 | 0.00013788 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2513-3_0_3_load_60 | 109 | 0.00040549 | 0.00010162 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2513-3_0_3_load_61 | 110 | 0.005978 | 0.0014982 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2513-3_0_3_load_69 | 111 | 0.00041266 | 0.00010342 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2513-3_0_3_load_144 | 112 | 0.00091168 | 0.00022849 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2513-3_0_3_load_121 | 113 | 0.00087469 | 0.00021922 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2513-3_0_3_load_62 | 114 | 0.0012393 | 0.0003106 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2513-3_0_3_load_63 | 115 | 0.0016383 | 0.0004106 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2513-3_0_3_load_66 | 117 | 0.00033234 | 8.3291e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2513-3_0_3_load_67 | 118 | 0.0026741 | 0.00067019 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2513-3_0_3_load_89 | 119 | 0.007817 | 0.0019591 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2513-3_0_3_load_87 | 120 | 0.0034053 | 0.00085345 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2513-3_0_3_load_78 | 121 | 0.0046183 | 0.0011574 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2513-3_0_3_load_82 | 122 | 0.002729 | 0.00068396 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2513-3_0_3_load_83 | 123 | 0.0027823 | 0.00069731 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2513-3_0_3_load_84 | 124 | 0.001064 | 0.00026667 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2513-3_0_3_load_106 | 126 | 0.0033205 | 0.00083221 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2513-3_0_3_load_86 | 128 | 0.00052399 | 0.00013132 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2513-3_0_3_load_88 | 129 | 0.0033185 | 0.0008317 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2513-3_0_3_load_90 | 130 | 0.0027949 | 0.00070046 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2513-3_0_3_load_137 | 132 | 0.0032681 | 0.00081905 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2513-3_0_3_load_133 | 135 | 0.0036231 | 0.00090803 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2513-3_0_3_load_141 | 136 | 0.0045417 | 0.0011383 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2513-3_0_3_load_122 | 137 | 0.0026296 | 0.00065904 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2513-3_0_3_load_146 | 141 | 0.047985 | 0.012026 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2513-3_0_3_load_129 | 142 | 0.0022728 | 0.00056963 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2513-3_0_3_line_0 |  | 0 | 1 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2513-3_0_3_line_1 |  | 0 | 2 | 0.027933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2513-3_0_3_line_2 |  | 1 | 3 | 0.015714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2513-3_0_3_line_3 |  | 2 | 4 | 0.043473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2513-3_0_3_line_4 |  | 3 | 5 | 0.0323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2513-3_0_3_line_5 |  | 4 | 6 | 0.017637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2513-3_0_3_line_6 |  | 5 | 7 | 0.004952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2513-3_0_3_line_7 |  | 6 | 40 | 0.011273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2513-3_0_3_line_8 |  | 7 | 33 | 0.045945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2513-3_0_3_line_9 |  | 8 | 9 | 0.040542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2513-3_0_3_line_10 |  | 8 | 10 | 0.042809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2513-3_0_3_line_11 |  | 10 | 26 | 0.014061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2513-3_0_3_line_12 |  | 11 | 12 | 0.0063889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2513-3_0_3_line_13 |  | 11 | 13 | 0.0019085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2513-3_0_3_line_14 |  | 12 | 14 | 0.0048046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2513-3_0_3_line_15 |  | 13 | 15 | 0.002733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2513-3_0_3_line_16 |  | 14 | 16 | 0.0052788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2513-3_0_3_line_17 |  | 15 | 17 | 0.0114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2513-3_0_3_line_18 |  | 16 | 18 | 0.0052397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2513-3_0_3_line_19 |  | 17 | 19 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2513-3_0_3_line_20 |  | 18 | 117 | 0.032487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2513-3_0_3_line_21 |  | 19 | 91 | 0.012255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2513-3_0_3_line_22 |  | 20 | 21 | 0.00023946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2513-3_0_3_line_23 |  | 20 | 22 | 0.016654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2513-3_0_3_line_24 |  | 21 | 23 | 0.042244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2513-3_0_3_line_25 |  | 22 | 24 | 0.03397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2513-3_0_3_line_26 |  | 22 | 25 | 0.040623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2513-3_0_3_line_27 |  | 23 | 26 | 0.048274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2513-3_0_3_line_28 |  | 24 | 27 | 0.010689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2513-3_0_3_line_29 |  | 24 | 28 | 0.042121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2513-3_0_3_line_30 |  | 25 | 29 | 0.047754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2513-3_0_3_line_31 |  | 25 | 30 | 0.0096677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2513-3_0_3_line_32 |  | 26 | 33 | 0.014134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2513-3_0_3_line_33 |  | 27 | 34 | 0.049596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2513-3_0_3_line_34 |  | 27 | 35 | 0.0050207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2513-3_0_3_line_35 |  | 28 | 36 | 4.0153e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2513-3_0_3_line_36 |  | 29 | 31 | 0.005247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2513-3_0_3_line_37 |  | 30 | 37 | 0.018092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2513-3_0_3_line_38 |  | 32 | 33 | 0.012085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2513-3_0_3_line_39 |  | 34 | 38 | 0.006018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2513-3_0_3_line_40 |  | 35 | 65 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2513-3_0_3_line_41 |  | 36 | 142 | 0.012534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2513-3_0_3_line_42 |  | 37 | 121 | 0.012571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2513-3_0_3_line_43 |  | 39 | 40 | 0.0054698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2513-3_0_3_line_44 |  | 40 | 41 | 0.005082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2513-3_0_3_line_45 |  | 41 | 42 | 0.012368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2513-3_0_3_line_46 |  | 42 | 43 | 0.044017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2513-3_0_3_line_47 |  | 43 | 85 | 0.035354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2513-3_0_3_line_48 |  | 44 | 45 | 0.030252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2513-3_0_3_line_49 |  | 44 | 46 | 0.046516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2513-3_0_3_line_50 |  | 46 | 47 | 0.027043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2513-3_0_3_line_51 |  | 47 | 49 | 0.22837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2513-3_0_3_line_52 |  | 48 | 49 | 0.084456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2513-3_0_3_line_53 |  | 48 | 50 | 0.093428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2513-3_0_3_line_54 |  | 49 | 55 | 0.049717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2513-3_0_3_line_55 |  | 50 | 54 | 0.077219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2513-3_0_3_line_56 |  | 51 | 52 | 0.027082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2513-3_0_3_line_57 |  | 51 | 53 | 0.029109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2513-3_0_3_line_58 |  | 52 | 132 | 0.0016587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2513-3_0_3_line_59 |  | 53 | 125 | 0.068198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2513-3_0_3_line_60 |  | 54 | 136 | 0.042692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2513-3_0_3_line_61 |  | 56 | 57 | 0.020345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2513-3_0_3_line_62 |  | 56 | 58 | 0.056163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2513-3_0_3_line_63 |  | 57 | 59 | 0.017285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2513-3_0_3_line_64 |  | 57 | 60 | 0.021933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2513-3_0_3_line_65 |  | 58 | 61 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2513-3_0_3_line_66 |  | 58 | 62 | 0.016055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2513-3_0_3_line_67 |  | 59 | 63 | 0.037426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2513-3_0_3_line_68 |  | 60 | 64 | 0.017291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2513-3_0_3_line_69 |  | 61 | 65 | 0.015076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2513-3_0_3_line_70 |  | 62 | 66 | 0.008569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2513-3_0_3_line_71 |  | 63 | 67 | 0.015425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2513-3_0_3_line_72 |  | 64 | 73 | 0.029675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2513-3_0_3_line_73 |  | 66 | 74 | 0.014769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2513-3_0_3_line_74 |  | 67 | 68 | 0.025825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2513-3_0_3_line_75 |  | 68 | 69 | 0.039106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2513-3_0_3_line_76 |  | 69 | 104 | 0.040033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2513-3_0_3_line_77 |  | 70 | 71 | 0.034892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2513-3_0_3_line_78 |  | 70 | 72 | 0.031435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2513-3_0_3_line_79 |  | 71 | 134 | 0.051129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2513-3_0_3_line_80 |  | 72 | 127 | 0.047109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2513-3_0_3_line_81 |  | 73 | 138 | 0.036311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2513-3_0_3_line_82 |  | 74 | 125 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2513-3_0_3_line_83 |  | 75 | 76 | 0.078082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2513-3_0_3_line_84 |  | 75 | 77 | 0.020126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2513-3_0_3_line_85 |  | 76 | 78 | 0.037531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2513-3_0_3_line_86 |  | 77 | 79 | 0.036986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2513-3_0_3_line_87 |  | 78 | 80 | 0.032549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2513-3_0_3_line_88 |  | 79 | 81 | 0.0059425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2513-3_0_3_line_89 |  | 79 | 82 | 0.05386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2513-3_0_3_line_90 |  | 80 | 83 | 0.024874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2513-3_0_3_line_91 |  | 82 | 84 | 0.022025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2513-3_0_3_line_92 |  | 84 | 131 | 0.058355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2513-3_0_3_line_93 |  | 85 | 86 | 0.019549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2513-3_0_3_line_94 |  | 86 | 87 | 0.013874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2513-3_0_3_line_95 |  | 86 | 88 | 0.013798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2513-3_0_3_line_96 |  | 88 | 89 | 0.030131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2513-3_0_3_line_97 |  | 89 | 90 | 0.068863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2513-3_0_3_line_98 |  | 90 | 111 | 0.016971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2513-3_0_3_line_99 |  | 91 | 92 | 0.013181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2513-3_0_3_line_100 |  | 92 | 93 | 0.019296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2513-3_0_3_line_101 |  | 92 | 94 | 0.044837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2513-3_0_3_line_102 |  | 93 | 95 | 0.045034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2513-3_0_3_line_103 |  | 93 | 96 | 0.025391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2513-3_0_3_line_104 |  | 96 | 97 | 0.01348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2513-3_0_3_line_105 |  | 98 | 99 | 0.023801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2513-3_0_3_line_106 |  | 98 | 100 | 0.032189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_2513-3_0_3_line_107 |  | 99 | 101 | 0.027694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_2513-3_0_3_line_108 |  | 100 | 102 | 0.0094439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_2513-3_0_3_line_109 |  | 101 | 103 | 0.02066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_2513-3_0_3_line_110 |  | 102 | 104 | 0.033084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2513-3_0_3_line_111 |  | 103 | 105 | 0.0027271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_2513-3_0_3_line_112 |  | 105 | 115 | 0.018474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_2513-3_0_3_line_113 |  | 106 | 107 | 0.0083811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2513-3_0_3_line_114 |  | 106 | 108 | 0.013244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2513-3_0_3_line_115 |  | 107 | 109 | 0.00088968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2513-3_0_3_line_116 |  | 108 | 110 | 0.033528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2513-3_0_3_line_117 |  | 109 | 113 | 0.021073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2513-3_0_3_line_118 |  | 111 | 112 | 0.036713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2513-3_0_3_line_119 |  | 112 | 113 | 0.025487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2513-3_0_3_line_120 |  | 114 | 115 | 0.00347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_2513-3_0_3_line_121 |  | 114 | 116 | 0.03698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
122 | LV_2513-3_0_3_line_122 |  | 116 | 117 | 0.047394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_2513-3_0_3_line_123 |  | 116 | 118 | 0.0053513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2513-3_0_3_line_124 |  | 118 | 119 | 0.032165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2513-3_0_3_line_125 |  | 119 | 120 | 0.0091954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2513-3_0_3_line_126 |  | 120 | 128 | 0.019472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2513-3_0_3_line_127 |  | 122 | 123 | 6.7341e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2513-3_0_3_line_128 |  | 122 | 124 | 0.014271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2513-3_0_3_line_129 |  | 123 | 125 | 0.023516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2513-3_0_3_line_130 |  | 125 | 126 | 0.026585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_2513-3_0_3_line_131 |  | 126 | 127 | 0.026103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2513-3_0_3_line_132 |  | 127 | 133 | 0.008637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2513-3_0_3_line_133 |  | 128 | 129 | 0.022426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2513-3_0_3_line_134 |  | 129 | 130 | 0.041994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2513-3_0_3_line_135 |  | 130 | 131 | 0.022536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2513-3_0_3_line_136 |  | 133 | 135 | 0.025077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2513-3_0_3_line_137 |  | 134 | 136 | 0.040662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2513-3_0_3_line_138 |  | 137 | 138 | 0.023967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_2513-3_0_3_line_139 |  | 137 | 139 | 0.085767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_2513-3_0_3_line_140 |  | 139 | 140 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_2513-3_0_3_line_141 |  | 140 | 141 | 0.057085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2513-3_0_3_trafo_147 | 0.63 MVA 20/0.4 kV | 143 | 38 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2609571.1069 | 1225471.5444 | 2609585.464 | 1225482.7298
1 | 2609607.4991 | 1225499.8971 | 2609585.464 | 1225482.7298
2 | 2609571.1069 | 1225471.5444 | 2609575.051 | 1225465.2804 | 2609579.4731 | 1225458.2425
3 | 2609640.5487 | 1225528.1387 | 2609607.4991 | 1225499.8971
4 | 2609579.4731 | 1225458.2425 | 2609581.199 | 1225455.4956 | 2609593.6001 | 1225436.6044 | 2609597.0646 | 1225431.1545
5 | 2609658.0391 | 1225525.9158 | 2609650.2373 | 1225527.1262 | 2609640.5487 | 1225528.1387
6 | 2609599.7212 | 1225426.9754 | 2609597.0646 | 1225431.1545
7 | 2609659.9465 | 1225537.0254 | 2609658.0391 | 1225525.9158
8 | 2609625.4301 | 1225388.9275 | 2609614.202 | 1225404.1962 | 2609599.7212 | 1225426.9754
9 | 2609652.7998 | 1225446.9055 | 2609653.5502 | 1225451.6539 | 2609655.2493 | 1225455.6034 | 2609656.8024 | 1225465.5562 | 2609656.7501 | 1225469.7475 | 2609654.5036 | 1225476.2032 | 2609654.7682 | 1225481.34 | 2609655.5689 | 1225486.4687
10 | 2609652.7998 | 1225446.9055 | 2609642.3681 | 1225405.3866
11 | 2609642.3681 | 1225405.3866 | 2609645.021 | 1225400.8327 | 2609637.5088 | 1225396.2676
12 | 2609897.5836 | 1225603.6342 | 2609903.9685 | 1225603.8619
13 | 2609897.5836 | 1225603.6342 | 2609895.6763 | 1225603.5662
14 | 2609908.7701 | 1225604.0331 | 2609903.9685 | 1225603.8619
15 | 2609892.945 | 1225603.4688 | 2609895.6763 | 1225603.5662
16 | 2609908.7701 | 1225604.0331 | 2609914.0456 | 1225604.2213
17 | 2609881.5519 | 1225603.0614 | 2609892.5593 | 1225603.455 | 2609892.945 | 1225603.4688
18 | 2609919.2819 | 1225604.408 | 2609914.0456 | 1225604.2213
19 | 2609863.2168 | 1225602.4059 | 2609881.5519 | 1225603.0614
20 | 2609951.7484 | 1225605.5658 | 2609919.2819 | 1225604.408
21 | 2609863.2168 | 1225602.4059 | 2609850.97 | 1225601.968
22 | 2609717.9835 | 1225425.136 | 2609718.1661 | 1225425.2908
23 | 2609730.8703 | 1225436.0588 | 2609718.1661 | 1225425.2908
24 | 2609685.7578 | 1225397.8219 | 2609717.9835 | 1225425.136
25 | 2609730.8703 | 1225436.0588 | 2609742.0732 | 1225422.469 | 2609752.8118 | 1225410.0792
26 | 2609708.1977 | 1225468.9968 | 2609708.5985 | 1225464.9062 | 2609711.0997 | 1225460.3965 | 2609715.3455 | 1225455.1336 | 2609729.8754 | 1225437.269 | 2609730.8703 | 1225436.0588
27 | 2609685.7578 | 1225397.8219 | 2609637.5088 | 1225396.2676
28 | 2609752.8118 | 1225410.0792 | 2609759.7609 | 1225401.9413
29 | 2609752.8118 | 1225410.0792 | 2609721.2335 | 1225382.2041
30 | 2609708.1977 | 1225468.9968 | 2609708.5985 | 1225464.9062 | 2609711.0997 | 1225460.3965 | 2609715.3455 | 1225455.1336 | 2609733.9897 | 1225470.9843 | 2609739.6598 | 1225475.5073
31 | 2609708.1977 | 1225468.9968 | 2609700.0482 | 1225474.1978 | 2609700.0482 | 1225474.1978
32 | 2609625.4301 | 1225388.9275 | 2609637.5088 | 1225396.2676
33 | 2609759.7609 | 1225401.9413 | 2609777.5788 | 1225417.8464 | 2609783.5427 | 1225423.5261 | 2609772.0902 | 1225436.7263
34 | 2609759.7609 | 1225401.9413 | 2609763.0197 | 1225398.1219
35 | 2609721.2335 | 1225382.2041 | 2609721.2034 | 1225382.1775
36 | 2609743.7705 | 1225478.7825 | 2609739.6598 | 1225475.5073
37 | 2609702.6516 | 1225491.8888 | 2609701.5987 | 1225490.3542 | 2609700.0482 | 1225474.1978
38 | 2609625.4301 | 1225388.9275 | 2609632.5848 | 1225379.1879
39 | 2609776.7534 | 1225440.5472 | 2609772.0902 | 1225436.7263
40 | 2609773.5739 | 1225385.7521 | 2609763.0197 | 1225398.1219
41 | 2609721.2034 | 1225382.1775 | 2609711.8068 | 1225373.8829
42 | 2609702.6516 | 1225491.8888 | 2609709.7639 | 1225502.2547
43 | 2609659.9465 | 1225537.0254 | 2609660.6062 | 1225536.9264 | 2609665.3512 | 1225536.1838
44 | 2609659.9465 | 1225537.0254 | 2609654.9121 | 1225537.8177
45 | 2609645.7993 | 1225543.5064 | 2609655.1658 | 1225540.2974 | 2609654.9121 | 1225537.8177
46 | 2609645.7993 | 1225543.5064 | 2609654.4017 | 1225548.8011 | 2609660.8028 | 1225556.0045 | 2609665.0198 | 1225579.9151
47 | 2609665.0198 | 1225579.9151 | 2609671.1603 | 1225614.7314
48 | 2609409.2577 | 1225037.161 | 2609401.9474 | 1225007.806
49 | 2609409.2577 | 1225037.161 | 2609415.8402 | 1225063.593 | 2609420.3543 | 1225082.3337
50 | 2609426.687 | 1225108.6245 | 2609420.3543 | 1225082.3337
51 | 2609529.344 | 1225312.6182 | 2609426.687 | 1225108.6245
52 | 2609529.344 | 1225312.6182 | 2609597.2698 | 1225262.4297
53 | 2609660.9546 | 1225194.0706 | 2609597.2698 | 1225262.4297
54 | 2609530.2401 | 1225362.3264 | 2609529.9014 | 1225342.9034 | 2609529.4021 | 1225313.6967 | 2609529.344 | 1225312.6182
55 | 2609737.6217 | 1225184.8571 | 2609660.9546 | 1225194.0706
56 | 2609676.4378 | 1225313.3536 | 2609686.4028 | 1225292.2025 | 2609688.3142 | 1225289.0331
57 | 2609710.2 | 1225271.9958 | 2609707.7973 | 1225271.8029 | 2609703.3982 | 1225273.2967 | 2609696.9018 | 1225278 | 2609690.8036 | 1225284.9053 | 2609688.3142 | 1225289.0331
58 | 2609675.7309 | 1225314.8541 | 2609676.4378 | 1225313.3536
59 | 2609710.2 | 1225271.9958 | 2609712.8969 | 1225273.0008 | 2609714.4038 | 1225274.0038 | 2609724.5776 | 1225282.7921 | 2609741.1019 | 1225297.3053 | 2609760.5049 | 1225317.5932
60 | 2609737.6217 | 1225184.8571 | 2609744.7043 | 1225170.5036 | 2609754.0997 | 1225154.5984 | 2609758.4017 | 1225147.6013
61 | 2609848.9096 | 1225297.3593 | 2609835.5715 | 1225312.7222
62 | 2609799.2994 | 1225355.601 | 2609832.8999 | 1225315.7994 | 2609835.5715 | 1225312.7222
63 | 2609848.9096 | 1225297.3593 | 2609856.101 | 1225303.3969 | 2609857.5185 | 1225311.1642
64 | 2609866.2 | 1225283.8021 | 2609848.9096 | 1225297.3593
65 | 2609799.2994 | 1225355.601 | 2609783.3595 | 1225374.2831
66 | 2609799.2994 | 1225355.601 | 2609787.755 | 1225344.4433
67 | 2609857.5185 | 1225311.1642 | 2609859.7521 | 1225323.4035 | 2609860.4513 | 1225340.7037 | 2609863.2978 | 1225347.8259
68 | 2609866.2 | 1225283.8021 | 2609876.5021 | 1225274.3802 | 2609879.2514 | 1225272.5006
69 | 2609773.5739 | 1225385.7521 | 2609783.3595 | 1225374.2831
70 | 2609781.6493 | 1225338.4309 | 2609787.5004 | 1225344.1972 | 2609787.755 | 1225344.4433
71 | 2609875.6694 | 1225348.7742 | 2609866.2543 | 1225352.0532 | 2609864.6486 | 1225351.2056 | 2609863.2978 | 1225347.8259
72 | 2609879.2514 | 1225272.5006 | 2609885.1003 | 1225268.502 | 2609903.2971 | 1225257.0031 | 2609904.2143 | 1225256.4633
73 | 2609781.6493 | 1225338.4309 | 2609771.1302 | 1225328.0644
74 | 2609893.0022 | 1225335.4432 | 2609889.2016 | 1225337.2046 | 2609889.797 | 1225343.8539 | 2609875.6694 | 1225348.7742
75 | 2609893.0022 | 1225335.4432 | 2609894.5353 | 1225338.9144 | 2609898.8028 | 1225348.2047 | 2609907.8922 | 1225371.5879
76 | 2609922.3172 | 1225408.9314 | 2609914.6991 | 1225389.0994 | 2609907.8922 | 1225371.5879
77 | 2609827 | 1225248.0056 | 2609803.1489 | 1225222.5384
78 | 2609827 | 1225248.0056 | 2609830.3933 | 1225258.8619 | 2609830.4569 | 1225261.7193 | 2609827.2064 | 1225265.4161 | 2609824.166 | 1225265.8225 | 2609818.152 | 1225272.8009
79 | 2609803.1489 | 1225222.5384 | 2609789.7736 | 1225173.1897
80 | 2609784.2067 | 1225276.9858 | 2609787.6629 | 1225277.2583 | 2609802.8397 | 1225290.5687 | 2609818.152 | 1225272.8009
81 | 2609935.5074 | 1225238.0454 | 2609904.2143 | 1225256.4633
82 | 2609760.5049 | 1225317.5932 | 2609771.1302 | 1225328.0644
83 | 2610196.2822 | 1225547.1419 | 2610172.4886 | 1225567.0692 | 2610180.378 | 1225590.1628 | 2610169.5654 | 1225610.0561
84 | 2610180.2612 | 1225627.1053 | 2610169.5654 | 1225610.0561 | 2610169.5654 | 1225610.0561
85 | 2610225.0553 | 1225523.044 | 2610196.2822 | 1225547.1419
86 | 2610199.9165 | 1225658.4361 | 2610180.2612 | 1225627.1053
87 | 2610225.0553 | 1225523.044 | 2610242.9417 | 1225550.2377
88 | 2610199.9165 | 1225658.4361 | 2610204.9771 | 1225655.321
89 | 2610199.9165 | 1225658.4361 | 2610154.0499 | 1225686.6701
90 | 2610256.6108 | 1225571.0196 | 2610242.9417 | 1225550.2377
91 | 2610154.0499 | 1225686.6701 | 2610135.294 | 1225698.2156
92 | 2610085.5993 | 1225728.806 | 2610135.294 | 1225698.2156
93 | 2609674.5558 | 1225633.9836 | 2609671.1603 | 1225614.7314
94 | 2609674.5558 | 1225633.9836 | 2609688.2488 | 1225631.7488
95 | 2609674.5558 | 1225633.9836 | 2609676.9515 | 1225647.5715
96 | 2609662.1534 | 1225672.5862 | 2609667.9341 | 1225664.9021 | 2609675.8404 | 1225655.2203 | 2609677.5302 | 1225650.8538 | 2609676.9515 | 1225647.5715
97 | 2609662.1534 | 1225672.5862 | 2609666.7671 | 1225678.8084 | 2609692.0705 | 1225724.5094 | 2609693.2766 | 1225733.3054
98 | 2609693.2766 | 1225733.3054 | 2609693.2766 | 1225733.3054 | 2609690.7856 | 1225750.0928
99 | 2609837.7973 | 1225601.497 | 2609850.97 | 1225601.968
100 | 2609837.7973 | 1225601.497 | 2609827.5035 | 1225596.9997 | 2609820.9015 | 1225592.2972
101 | 2609793.2643 | 1225601.9465 | 2609800.2038 | 1225599.601 | 2609837.7973 | 1225601.497
102 | 2609820.9015 | 1225592.2972 | 2609807.381 | 1225581.7244 | 2609794.7639 | 1225565.6499 | 2609790.5667 | 1225559.512
103 | 2609820.9015 | 1225592.2972 | 2609814.1061 | 1225580.7015 | 2609807.0793 | 1225571.035
104 | 2609807.0793 | 1225571.035 | 2609799.1533 | 1225560.1315
105 | 2609949.1426 | 1225478.6671 | 2609957.7095 | 1225500.8725
106 | 2609949.1426 | 1225478.6671 | 2609940.3988 | 1225456.0034 | 2609937.5669 | 1225448.6312
107 | 2609957.7095 | 1225500.8725 | 2609967.404 | 1225526.0004 | 2609967.685 | 1225526.7073
108 | 2609937.5669 | 1225448.6312 | 2609934.1805 | 1225439.8153
109 | 2609974.8793 | 1225546.0706 | 2609970.7027 | 1225534.2996 | 2609967.685 | 1225526.7073
110 | 2609922.3172 | 1225408.9314 | 2609934.1805 | 1225439.8153
111 | 2609974.8793 | 1225546.0706 | 2609975.7912 | 1225548.6406
112 | 2609981.9689 | 1225566.0513 | 2609975.7912 | 1225548.6406
113 | 2609730.7993 | 1225830.9197 | 2609725.0813 | 1225824.7921
114 | 2609739.8353 | 1225840.6029 | 2609730.7993 | 1225830.9197
115 | 2609724.4743 | 1225824.1417 | 2609725.0813 | 1225824.7921
116 | 2609739.8353 | 1225840.6029 | 2609743.1986 | 1225844.207 | 2609762.4259 | 1225865.3774
117 | 2609724.4743 | 1225824.1417 | 2609720.7034 | 1225820.1007 | 2609711.4656 | 1225807.5967
118 | 2609690.7856 | 1225750.0928 | 2609697.8601 | 1225786.1174
119 | 2609711.4656 | 1225807.5967 | 2609704.1251 | 1225797.6607 | 2609697.8601 | 1225786.1174
120 | 2609983.2779 | 1225569.264 | 2609982.2006 | 1225566.7044 | 2609981.9689 | 1225566.0513
121 | 2609998.8012 | 1225602.7977 | 2609990.9511 | 1225587.5201 | 2609988.3011 | 1225581.2008 | 2609987.7726 | 1225579.9437 | 2609983.2779 | 1225569.264
122 | 2609998.8012 | 1225602.7977 | 2609977.8971 | 1225606.4983 | 2609951.7484 | 1225605.5658
123 | 2609998.8012 | 1225602.7977 | 2610001.3309 | 1225607.5133
124 | 2610018.5584 | 1225634.6155 | 2610006.9017 | 1225617.8979 | 2610001.3309 | 1225607.5133
125 | 2610023.8207 | 1225642.1563 | 2610022.8041 | 1225640.7045 | 2610018.5584 | 1225634.6155
126 | 2610034.9893 | 1225658.1071 | 2610023.8207 | 1225642.1563
127 | 2609744.6934 | 1225335.0912 | 2609744.7385 | 1225335.0413
128 | 2609735.1257 | 1225345.6794 | 2609744.6934 | 1225335.0912
129 | 2609760.5049 | 1225317.5932 | 2609744.7385 | 1225335.0413
130 | 2609760.5049 | 1225317.5932 | 2609777.5262 | 1225297.1721
131 | 2609784.2067 | 1225276.9858 | 2609784.565 | 1225280.3551 | 2609788.6376 | 1225283.8415 | 2609777.5262 | 1225297.1721
132 | 2609777.6057 | 1225271.394 | 2609784.2067 | 1225276.9858
133 | 2610034.9893 | 1225658.1071 | 2610047.8522 | 1225676.4776
134 | 2610047.8522 | 1225676.4776 | 2610068.8022 | 1225706.3979 | 2610072.0813 | 1225710.774
135 | 2610085.5993 | 1225728.806 | 2610080.7969 | 1225722.4053 | 2610072.0813 | 1225710.774
136 | 2609777.6057 | 1225271.394 | 2609794.2837 | 1225252.6664
137 | 2609789.7736 | 1225173.1897 | 2609784.8025 | 1225167.5005 | 2609770.1994 | 1225155.4029 | 2609758.4017 | 1225147.6013 | 2609758.4017 | 1225147.6013
138 | 2609935.5074 | 1225238.0454 | 2609944.8782 | 1225250.8907 | 2609948.328 | 1225255.0655 | 2609950.4733 | 1225256.6237
139 | 2610026.4277 | 1225260.2766 | 2610021.69 | 1225260.2686 | 2609985.2551 | 1225275.9948 | 2609980.6975 | 1225277.0767 | 2609976.8791 | 1225275.8029 | 2609950.4733 | 1225256.6237
140 | 2610026.4277 | 1225260.2766 | 2610031.3356 | 1225262.8307 | 2610035.8412 | 1225270.1759
141 | 2610026.3478 | 1225312.5515 | 2610012.2514 | 1225301.6548 | 2610035.8412 | 1225270.1759

## bus_geodata
| x | y | coords
0 | 2609585.464 | 1225482.7298
1 | 2609571.1069 | 1225471.5444
2 | 2609607.4991 | 1225499.8971
3 | 2609579.4731 | 1225458.2425
4 | 2609640.5487 | 1225528.1387
5 | 2609597.0646 | 1225431.1545
6 | 2609658.0391 | 1225525.9158
7 | 2609599.7212 | 1225426.9754
8 | 2609652.7998 | 1225446.9055
9 | 2609655.5689 | 1225486.4687
10 | 2609642.3681 | 1225405.3866
11 | 2609897.5837 | 1225603.6342
12 | 2609903.9685 | 1225603.8619
13 | 2609895.6763 | 1225603.5662
14 | 2609908.7701 | 1225604.0331
15 | 2609892.945 | 1225603.4688
16 | 2609914.0456 | 1225604.2213
17 | 2609881.5519 | 1225603.0614
18 | 2609919.2819 | 1225604.408
19 | 2609863.2168 | 1225602.4059
20 | 2609718.1661 | 1225425.2908
21 | 2609717.9835 | 1225425.136
22 | 2609730.8703 | 1225436.0588
23 | 2609685.7578 | 1225397.8219
24 | 2609752.8118 | 1225410.0792
25 | 2609708.1977 | 1225468.9968
26 | 2609637.5088 | 1225396.2676
27 | 2609759.7609 | 1225401.9413
28 | 2609721.2335 | 1225382.2041
29 | 2609739.6598 | 1225475.5073
30 | 2609700.0482 | 1225474.1978
31 | 2609743.7705 | 1225478.7826
32 | 2609632.5848 | 1225379.1879
33 | 2609625.4301 | 1225388.9275
34 | 2609772.0902 | 1225436.7263
35 | 2609763.0197 | 1225398.1219
36 | 2609721.2034 | 1225382.1775
37 | 2609702.6516 | 1225491.8888
38 | 2609776.7534 | 1225440.5472
39 | 2609665.3512 | 1225536.1838
40 | 2609659.9465 | 1225537.0254
41 | 2609654.9121 | 1225537.8177
42 | 2609645.7993 | 1225543.5064
43 | 2609665.0198 | 1225579.9151
44 | 2609409.2577 | 1225037.161
45 | 2609401.9474 | 1225007.806
46 | 2609420.3543 | 1225082.3337
47 | 2609426.687 | 1225108.6245
48 | 2609597.2698 | 1225262.4297
49 | 2609529.344 | 1225312.6182
50 | 2609660.9546 | 1225194.0706
51 | 2609688.3142 | 1225289.0331
52 | 2609676.4378 | 1225313.3536
53 | 2609710.2 | 1225271.9958
54 | 2609737.6217 | 1225184.8571
55 | 2609530.2401 | 1225362.3264
56 | 2609835.5715 | 1225312.7222
57 | 2609848.9096 | 1225297.3593
58 | 2609799.2994 | 1225355.601
59 | 2609857.5185 | 1225311.1642
60 | 2609866.2 | 1225283.8021
61 | 2609783.3595 | 1225374.2831
62 | 2609787.755 | 1225344.4433
63 | 2609863.2978 | 1225347.8259
64 | 2609879.2514 | 1225272.5006
65 | 2609773.5739 | 1225385.7521
66 | 2609781.6493 | 1225338.4309
67 | 2609875.6694 | 1225348.7742
68 | 2609893.0022 | 1225335.4432
69 | 2609907.8922 | 1225371.5879
70 | 2609827 | 1225248.0056
71 | 2609803.1489 | 1225222.5384
72 | 2609818.152 | 1225272.8009
73 | 2609904.2143 | 1225256.4633
74 | 2609771.1302 | 1225328.0644
75 | 2610169.5654 | 1225610.0561
76 | 2610196.2822 | 1225547.1419
77 | 2610180.2612 | 1225627.1053
78 | 2610225.0553 | 1225523.044
79 | 2610199.9165 | 1225658.4361
80 | 2610242.9417 | 1225550.2377
81 | 2610204.9771 | 1225655.321
82 | 2610154.0499 | 1225686.6701
83 | 2610256.6108 | 1225571.0196
84 | 2610135.294 | 1225698.2156
85 | 2609671.1603 | 1225614.7314
86 | 2609674.5558 | 1225633.9836
87 | 2609688.2488 | 1225631.7488
88 | 2609676.9515 | 1225647.5715
89 | 2609662.1534 | 1225672.5862
90 | 2609693.2766 | 1225733.3054
91 | 2609850.97 | 1225601.968
92 | 2609837.7973 | 1225601.497
93 | 2609820.9015 | 1225592.2972
94 | 2609793.2643 | 1225601.9465
95 | 2609790.5667 | 1225559.512
96 | 2609807.0793 | 1225571.035
97 | 2609799.1533 | 1225560.1315
98 | 2609949.1426 | 1225478.6671
99 | 2609957.7095 | 1225500.8725
100 | 2609937.5669 | 1225448.6312
101 | 2609967.685 | 1225526.7073
102 | 2609934.1805 | 1225439.8153
103 | 2609974.8793 | 1225546.0706
104 | 2609922.3172 | 1225408.9314
105 | 2609975.7912 | 1225548.6406
106 | 2609730.7993 | 1225830.9197
107 | 2609725.0813 | 1225824.7921
108 | 2609739.8353 | 1225840.6029
109 | 2609724.4743 | 1225824.1417
110 | 2609762.4259 | 1225865.3774
111 | 2609690.7856 | 1225750.0928
112 | 2609697.8601 | 1225786.1174
113 | 2609711.4656 | 1225807.5967
114 | 2609983.2779 | 1225569.264
115 | 2609981.9689 | 1225566.0513
116 | 2609998.8012 | 1225602.7977
117 | 2609951.7484 | 1225605.5658
118 | 2610001.3309 | 1225607.5133
119 | 2610018.5584 | 1225634.6155
120 | 2610023.8207 | 1225642.1563
121 | 2609709.7639 | 1225502.2547
122 | 2609744.6934 | 1225335.0912
123 | 2609744.7385 | 1225335.0413
124 | 2609735.1257 | 1225345.6794
125 | 2609760.5049 | 1225317.5932
126 | 2609777.5262 | 1225297.1721
127 | 2609784.2067 | 1225276.9858
128 | 2610034.9893 | 1225658.1071
129 | 2610047.8522 | 1225676.4776
130 | 2610072.0813 | 1225710.774
131 | 2610085.5993 | 1225728.806
132 | 2609675.7309 | 1225314.8541
133 | 2609777.6057 | 1225271.394
134 | 2609789.7736 | 1225173.1897
135 | 2609794.2837 | 1225252.6664
136 | 2609758.4017 | 1225147.6014
137 | 2609950.4733 | 1225256.6237
138 | 2609935.5074 | 1225238.0454
139 | 2610026.4277 | 1225260.2766
140 | 2610035.8412 | 1225270.1759
141 | 2610026.3478 | 1225312.5515
142 | 2609711.8068 | 1225373.8829
143 | 2609772.0902 | 1225436.7263

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97854 | -0.4125 | 0.0097047 | 0.0024322
1 | 0.97915 | -0.40057 | 0 | 0
2 | 0.97785 | -0.4259 | 0.0022477 | 0.00056334
3 | 0.97967 | -0.39028 | 0.016298 | 0.0040847
4 | 0.97688 | -0.445 | 0.00046546 | 0.00011665
5 | 0.98124 | -0.35963 | 0.016712 | 0.0041884
6 | 0.97649 | -0.45261 | 0 | 0
7 | 0.98156 | -0.35344 | 0.0019063 | 0.00047776
8 | 0.98549 | -0.27721 | 0 | 0
9 | 0.98546 | -0.27773 | 0.00071206 | 0.00017846
10 | 0.98551 | -0.27666 | 0.0067099 | 0.0016817
11 | 0.97253 | -0.52984 | 0.0026657 | 0.00066808
12 | 0.97269 | -0.52654 | 0.00070382 | 0.00017639
13 | 0.97248 | -0.53073 | 0.0012162 | 0.0003048
14 | 0.97282 | -0.524 | 0.0013976 | 0.00035027
15 | 0.97242 | -0.53195 | 0.0040501 | 0.001015
16 | 0.97297 | -0.52107 | 0.0005097 | 0.00012774
17 | 0.97221 | -0.53618 | 0.003911 | 0.0009802
18 | 0.97312 | -0.51811 | 0.00082843 | 0.00020762
19 | 0.97193 | -0.54166 | 0.00093964 | 0.00023549
20 | 0.99124 | -0.16633 | 0.0060008 | 0.0015039
21 | 0.99124 | -0.16646 | 0.0054322 | 0.0013614
22 | 0.99175 | -0.15652 | 0 | 0
23 | 0.98951 | -0.19955 | 0.00096231 | 0.00024118
24 | 0.99307 | -0.1313 | 0 | 0
25 | 0.99078 | -0.17546 | 0 | 0
26 | 0.98561 | -0.27479 | 0.0015628 | 0.00039168
27 | 0.9935 | -0.12308 | 0 | 0
28 | 0.99289 | -0.13475 | 0.0012804 | 0.00032089
29 | 0.99001 | -0.19024 | 0 | 0
30 | 0.9907 | -0.17697 | 0.0017645 | 0.00044223
31 | 0.98993 | -0.19187 | 0.017423 | 0.0043666
32 | 0.9845 | -0.29622 | 0.0072587 | 0.0018192
33 | 0.98458 | -0.29465 | 0 | 0
34 | 0.9993 | -0.013242 | 0 | 0
35 | 0.99311 | -0.13041 | 0.0027282 | 0.00068374
36 | 0.99289 | -0.13475 | 0.0010814 | 0.00027101
37 | 0.99058 | -0.17925 | 0.0024618 | 0.00061698
38 | 1 | 0 | -0.38711 | -0.099329
39 | 0.97623 | -0.45763 | 0.0014634 | 0.00036676
40 | 0.97624 | -0.45748 | 0 | 0
41 | 0.97614 | -0.45954 | 0 | 0
42 | 0.97588 | -0.46455 | 0 | 0
43 | 0.97497 | -0.48242 | 0.0078184 | 0.0019595
44 | 0.97006 | -0.57861 | 0.00144 | 0.00036089
45 | 0.97006 | -0.57874 | 0.00021618 | 5.4181e-05
46 | 0.97013 | -0.57719 | 0.0014507 | 0.00036359
47 | 0.97021 | -0.57563 | 3.1597e-05 | 7.9191e-06
48 | 0.972 | -0.54016 | 0.0096761 | 0.0024251
49 | 0.97088 | -0.56234 | 0.0068151 | 0.001708
50 | 0.97409 | -0.49906 | 0.00018358 | 4.6011e-05
51 | 0.98693 | -0.24909 | 0.0033857 | 0.00084854
52 | 0.98683 | -0.25113 | 0.00095135 | 0.00023843
53 | 0.98713 | -0.24513 | 0 | 0
54 | 0.97582 | -0.46495 | 0.010147 | 0.0025431
55 | 0.97069 | -0.56625 | 0.0042526 | 0.0010658
56 | 0.98606 | -0.26559 | 0.0019436 | 0.00048711
57 | 0.98505 | -0.28517 | 0 | 0
58 | 0.9889 | -0.21109 | 0 | 0
59 | 0.98449 | -0.29604 | 0.00045957 | 0.00011518
60 | 0.98467 | -0.29253 | 0 | 0
61 | 0.99074 | -0.1757 | 0.001154 | 0.00028923
62 | 0.9885 | -0.21875 | 0.0014149 | 0.00035461
63 | 0.98328 | -0.31951 | 0.0020892 | 0.00052361
64 | 0.98437 | -0.29833 | 0.0025034 | 0.0006274
65 | 0.99188 | -0.15393 | 0.0010038 | 0.00025158
66 | 0.98829 | -0.22276 | 0.0038295 | 0.00095977
67 | 0.98279 | -0.32901 | 0.0014744 | 0.00036951
68 | 0.98198 | -0.34469 | 0 | 0
69 | 0.98076 | -0.3685 | 0.012601 | 0.0031581
70 | 0.98194 | -0.34537 | 0 | 0
71 | 0.9805 | -0.37349 | 0.0057404 | 0.0014387
72 | 0.98325 | -0.3201 | 0.0075793 | 0.0018996
73 | 0.98388 | -0.30785 | 0.0028314 | 0.00070962
74 | 0.98795 | -0.22935 | 0.0017005 | 0.0004262
75 | 0.97064 | -0.56726 | 0.00077008 | 0.000193
76 | 0.97033 | -0.57336 | 0.00049054 | 0.00012294
77 | 0.97073 | -0.5654 | 0.0015415 | 0.00038635
78 | 0.9702 | -0.57596 | 0 | 0
79 | 0.97096 | -0.56093 | 0 | 0
80 | 0.97008 | -0.5782 | 0.00018207 | 4.563e-05
81 | 0.97095 | -0.56108 | 0.0013769 | 0.00034509
82 | 0.97135 | -0.55305 | 7.5325e-05 | 1.8878e-05
83 | 0.97 | -0.57984 | 0.0035463 | 0.00088878
84 | 0.97152 | -0.5498 | 0.0030471 | 0.00076367
85 | 0.9745 | -0.49171 | 0.00061942 | 0.00015524
86 | 0.97425 | -0.49663 | 0 | 0
87 | 0.97424 | -0.49677 | 0.0005572 | 0.00013965
88 | 0.97408 | -0.49997 | 0.0006882 | 0.00017248
89 | 0.97373 | -0.50687 | 0 | 0
90 | 0.97293 | -0.52266 | 0.00015504 | 3.8857e-05
91 | 0.97175 | -0.54511 | 0.006121 | 0.0015341
92 | 0.97164 | -0.54734 | 0 | 0
93 | 0.97151 | -0.54987 | 0 | 0
94 | 0.97156 | -0.54901 | 0.0020209 | 0.00050649
95 | 0.97135 | -0.55305 | 0.0038163 | 0.00095646
96 | 0.97144 | -0.55142 | 0.001459 | 0.00036566
97 | 0.97141 | -0.55188 | 0.001839 | 0.00046089
98 | 0.97794 | -0.42347 | 0.0024205 | 0.00060662
99 | 0.97741 | -0.43374 | 0.0014061 | 0.00035241
100 | 0.97867 | -0.40913 | 0.00105 | 0.00026315
101 | 0.97681 | -0.44547 | 0.0015331 | 0.00038424
102 | 0.97889 | -0.40486 | 0.00032387 | 8.1171e-05
103 | 0.97638 | -0.45403 | 0.001122 | 0.0002812
104 | 0.97966 | -0.38987 | 0.013511 | 0.0033862
105 | 0.97632 | -0.45514 | 0.00063567 | 0.00015931
106 | 0.97181 | -0.54493 | 0.00078648 | 0.00019711
107 | 0.97186 | -0.5438 | 0.0023832 | 0.00059728
108 | 0.97172 | -0.54653 | 0.00055016 | 0.00013788
109 | 0.97187 | -0.54364 | 0.00040549 | 0.00010162
110 | 0.97154 | -0.55023 | 0.005978 | 0.0014982
111 | 0.97274 | -0.5265 | 0.00041266 | 0.00010342
112 | 0.97233 | -0.53455 | 0.00091168 | 0.00022849
113 | 0.97207 | -0.53971 | 0.00087469 | 0.00021922
114 | 0.97587 | -0.46398 | 0.0012393 | 0.0003106
115 | 0.97594 | -0.46261 | 0.0016383 | 0.0004106
116 | 0.97478 | -0.48546 | 0 | 0
117 | 0.97408 | -0.4993 | 0.00033234 | 8.3291e-05
118 | 0.97462 | -0.48856 | 0.0026741 | 0.00067019
119 | 0.97375 | -0.50563 | 0.007817 | 0.0019591
120 | 0.97357 | -0.5092 | 0.0034053 | 0.00085345
121 | 0.99053 | -0.18028 | 0.0046183 | 0.0011574
122 | 0.98747 | -0.23862 | 0.002729 | 0.00068396
123 | 0.98747 | -0.23862 | 0.0027823 | 0.00069731
124 | 0.98745 | -0.23889 | 0.001064 | 0.00026667
125 | 0.98761 | -0.23585 | 0 | 0
126 | 0.98688 | -0.24989 | 0.0033205 | 0.00083221
127 | 0.98553 | -0.27596 | 0 | 0
128 | 0.97325 | -0.51553 | 0.00052399 | 0.00013132
129 | 0.97289 | -0.52261 | 0.0033185 | 0.0008317
130 | 0.97235 | -0.53332 | 0.0027949 | 0.00070046
131 | 0.97212 | -0.53791 | 0 | 0
132 | 0.98682 | -0.25123 | 0.0032681 | 0.00081905
133 | 0.9855 | -0.27652 | 0 | 0
134 | 0.97865 | -0.4095 | 0 | 0
135 | 0.98542 | -0.27815 | 0.0036231 | 0.00090803
136 | 0.97718 | -0.43824 | 0.0045417 | 0.0011383
137 | 0.98294 | -0.32618 | 0.0026296 | 0.00065904
138 | 0.98332 | -0.31889 | 0 | 0
139 | 0.98167 | -0.35096 | 0 | 0
140 | 0.98136 | -0.3571 | 0 | 0
141 | 0.97882 | -0.4068 | 0.047985 | 0.012026
142 | 0.99287 | -0.13526 | 0.0022728 | 0.00056963
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.03614 | -0.0090973 | 0.036161 | 0.0091102 | 2.0624e-05 | 1.297e-05 | 0.054971 | 0.054971 | 0.054971 | 0.97854 | -0.4125 | 0.97915 | -0.40057 | 15.1018
1 | 0.026435 | 0.006665 | -0.026418 | -0.0066546 | 1.6939e-05 | 1.049e-05 | 0.040213 | 0.040213 | 0.040213 | 0.97854 | -0.4125 | 0.97785 | -0.4259 | 11.0476
2 | -0.036161 | -0.0091102 | 0.036178 | 0.0091214 | 1.7807e-05 | 1.1198e-05 | 0.054971 | 0.054971 | 0.054971 | 0.97915 | -0.40057 | 0.97967 | -0.39028 | 15.1018
3 | 0.024171 | 0.0060912 | -0.024149 | -0.0060776 | 2.2069e-05 | 1.3579e-05 | 0.036793 | 0.036793 | 0.036793 | 0.97785 | -0.4259 | 0.97688 | -0.445 | 10.108
4 | -0.052477 | -0.013206 | 0.052554 | 0.013255 | 7.6989e-05 | 4.8866e-05 | 0.079726 | 0.079726 | 0.079726 | 0.97967 | -0.39028 | 0.98124 | -0.35963 | 21.9027
5 | 0.023683 | 0.005961 | -0.023675 | -0.0059557 | 8.6115e-06 | 5.2907e-06 | 0.036084 | 0.036084 | 0.036084 | 0.97688 | -0.445 | 0.97649 | -0.45261 | 9.9133
6 | -0.069266 | -0.017443 | 0.069286 | 0.017456 | 2.05e-05 | 1.3058e-05 | 0.10507 | 0.10507 | 0.10507 | 0.98124 | -0.35963 | 0.98156 | -0.35344 | 28.865
7 | 0.023675 | 0.0059557 | -0.023669 | -0.0059523 | 5.5044e-06 | 3.3818e-06 | 0.036084 | 0.036084 | 0.036084 | 0.97649 | -0.45261 | 0.97624 | -0.45748 | 9.9133
8 | -0.071192 | -0.017934 | 0.071393 | 0.018062 | 0.00020081 | 0.00012793 | 0.10796 | 0.10796 | 0.10796 | 0.98156 | -0.35344 | 0.98458 | -0.29465 | 29.6589
9 | 0.00071208 | 0.00017795 | -0.00071206 | -0.00017846 | 1.7573e-08 | -5.0529e-07 | 0.001075 | 0.0010752 | 0.0010752 | 0.98549 | -0.27721 | 0.98546 | -0.27773 | 0.29538
10 | -0.00071208 | -0.00017795 | 0.0007121 | 0.00017742 | 1.8549e-08 | -5.3359e-07 | 0.001075 | 0.0010748 | 0.001075 | 0.98549 | -0.27721 | 0.98551 | -0.27666 | 0.29533
11 | -0.007422 | -0.0018591 | 0.0074227 | 0.0018593 | 6.6213e-07 | 2.4458e-07 | 0.011206 | 0.011206 | 0.011206 | 0.98551 | -0.27666 | 0.98561 | -0.27479 | 3.0786
12 | -0.028055 | -0.0070349 | 0.028059 | 0.0070377 | 4.4149e-06 | 2.7462e-06 | 0.042927 | 0.042927 | 0.042927 | 0.97253 | -0.52984 | 0.97269 | -0.52654 | 11.7931
13 | 0.025389 | 0.0063669 | -0.025388 | -0.0063662 | 1.0801e-06 | 6.676e-07 | 0.038848 | 0.038848 | 0.038848 | 0.97253 | -0.52984 | 0.97248 | -0.53073 | 10.6726
14 | -0.028763 | -0.0072141 | 0.028767 | 0.0072163 | 3.4887e-06 | 2.1731e-06 | 0.044004 | 0.044004 | 0.044004 | 0.97269 | -0.52654 | 0.97282 | -0.524 | 12.0889
15 | 0.024172 | 0.0060614 | -0.024171 | -0.0060605 | 1.4021e-06 | 8.6344e-07 | 0.036987 | 0.036987 | 0.036987 | 0.97248 | -0.53073 | 0.97242 | -0.53195 | 10.1614
16 | -0.030164 | -0.0075665 | 0.030168 | 0.0075692 | 4.2145e-06 | 2.6317e-06 | 0.046141 | 0.046141 | 0.046141 | 0.97282 | -0.524 | 0.97297 | -0.52107 | 12.6762
17 | 0.020121 | 0.0050455 | -0.020117 | -0.005043 | 4.0529e-06 | 2.4525e-06 | 0.03079 | 0.03079 | 0.03079 | 0.97242 | -0.53195 | 0.97221 | -0.53618 | 8.4588
18 | -0.030678 | -0.0076969 | 0.030683 | 0.0076996 | 4.3258e-06 | 2.7034e-06 | 0.046921 | 0.046921 | 0.046921 | 0.97297 | -0.52107 | 0.97312 | -0.51811 | 12.8903
19 | 0.016205 | 0.0040628 | -0.016201 | -0.0040604 | 4.2328e-06 | 2.4816e-06 | 0.024804 | 0.024804 | 0.024804 | 0.97221 | -0.53618 | 0.97193 | -0.54166 | 6.8143
20 | -0.031511 | -0.0079072 | 0.031539 | 0.0079249 | 2.8288e-05 | 1.7701e-05 | 0.048187 | 0.048187 | 0.048187 | 0.97312 | -0.51811 | 0.97408 | -0.4993 | 13.2383
21 | 0.015262 | 0.0038249 | -0.015259 | -0.0038234 | 2.5089e-06 | 1.4538e-06 | 0.023365 | 0.023365 | 0.023365 | 0.97193 | -0.54166 | 0.97175 | -0.54511 | 6.4191
22 | 0.094568 | 0.024076 | -0.094567 | -0.024076 | 6.0437e-07 | 3.7753e-07 | 0.1421 | 0.1421 | 0.1421 | 0.99124 | -0.16633 | 0.99124 | -0.16646 | 13.0124
23 | -0.10057 | -0.02558 | 0.10062 | 0.02561 | 4.753e-05 | 2.9775e-05 | 0.1511 | 0.1511 | 0.1511 | 0.99124 | -0.16633 | 0.99175 | -0.15652 | 13.8373
24 | 0.089135 | 0.022714 | -0.088993 | -0.022624 | 0.0001421 | 8.9857e-05 | 0.13394 | 0.13394 | 0.13394 | 0.99124 | -0.16646 | 0.98951 | -0.19955 | 18.3986
25 | -0.12692 | -0.032216 | 0.12708 | 0.032314 | 0.00015422 | 9.7386e-05 | 0.19058 | 0.19058 | 0.19058 | 0.99175 | -0.15652 | 0.99307 | -0.1313 | 17.4522
26 | 0.026306 | 0.0066065 | -0.026283 | -0.0065918 | 2.3738e-05 | 1.4669e-05 | 0.039475 | 0.039475 | 0.039475 | 0.99175 | -0.15652 | 0.99078 | -0.17546 | 10.8447
27 | 0.088031 | 0.022383 | -0.087713 | -0.02218 | 0.00031779 | 0.00020277 | 0.13249 | 0.13249 | 0.13249 | 0.98951 | -0.19955 | 0.98561 | -0.27479 | 36.3996
28 | -0.13171 | -0.033475 | 0.13176 | 0.033508 | 5.2129e-05 | 3.2948e-05 | 0.19752 | 0.19752 | 0.19752 | 0.99307 | -0.1313 | 0.9935 | -0.12308 | 18.0882
29 | 0.0046354 | 0.0011613 | -0.0046346 | -0.0011614 | 7.62e-07 | -5.7194e-08 | 0.0069455 | 0.0069457 | 0.0069457 | 0.99307 | -0.1313 | 0.99289 | -0.13475 | 1.9082
30 | 0.017437 | 0.0043746 | -0.017424 | -0.0043674 | 1.2282e-05 | 7.2462e-06 | 0.026189 | 0.026189 | 0.026189 | 0.99078 | -0.17546 | 0.99001 | -0.19024 | 7.1948
31 | 0.0088462 | 0.0022172 | -0.0088455 | -0.0022169 | 6.3993e-07 | 2.8506e-07 | 0.013286 | 0.013286 | 0.013286 | 0.99078 | -0.17546 | 0.9907 | -0.17697 | 3.65
32 | 0.078727 | 0.019929 | -0.078652 | -0.019882 | 7.4968e-05 | 4.78e-05 | 0.11893 | 0.11893 | 0.11893 | 0.98561 | -0.27479 | 0.98458 | -0.29465 | 32.6729
33 | -0.38317 | -0.097862 | 0.38521 | 0.09917 | 0.0020464 | 0.0013078 | 0.57454 | 0.57454 | 0.57454 | 0.9935 | -0.12308 | 0.9993 | -0.013242 | 52.6139
34 | 0.2514 | 0.064354 | -0.25131 | -0.064297 | 8.9209e-05 | 5.6899e-05 | 0.37702 | 0.37702 | 0.37702 | 0.9935 | -0.12308 | 0.99311 | -0.13041 | 34.5258
35 | 0.0033543 | 0.00084051 | -0.0033543 | -0.00084051 | 3.7927e-10 | -2.7663e-10 | 0.0050269 | 0.0050269 | 0.0050269 | 0.99289 | -0.13475 | 0.99289 | -0.13475 | 1.381
36 | 0.017424 | 0.0043674 | -0.017423 | -0.0043666 | 1.3495e-06 | 7.9625e-07 | 0.026189 | 0.026189 | 0.026189 | 0.99001 | -0.19024 | 0.98993 | -0.19187 | 7.1949
37 | 0.007081 | 0.0017747 | -0.0070803 | -0.0017744 | 7.6743e-07 | 2.5823e-07 | 0.010636 | 0.010636 | 0.010636 | 0.9907 | -0.17697 | 0.99058 | -0.17925 | 2.9219
38 | -0.0072587 | -0.0018192 | 0.0072592 | 0.0018194 | 5.4548e-07 | 1.9542e-07 | 0.010971 | 0.010971 | 0.010971 | 0.9845 | -0.29622 | 0.98458 | -0.29465 | 3.014
39 | -0.38521 | -0.09917 | 0.38546 | 0.099329 | 0.00024832 | 0.00015869 | 0.57454 | 0.57454 | 0.57454 | 0.9993 | -0.013242 | 1 | 0 | 52.6138
40 | 0.24859 | 0.063614 | -0.2483 | -0.063433 | 0.00028269 | 0.00018029 | 0.37293 | 0.37293 | 0.37293 | 0.99311 | -0.13041 | 0.99188 | -0.15393 | 34.1514
41 | 0.0022729 | 0.0005695 | -0.0022728 | -0.00056963 | 5.4535e-08 | -1.272e-07 | 0.0034063 | 0.0034063 | 0.0034063 | 0.99289 | -0.13475 | 0.99287 | -0.13526 | 0.9358
42 | 0.0046185 | 0.0011574 | -0.0046183 | -0.0011574 | 2.2691e-07 | -1.6606e-08 | 0.0069377 | 0.0069378 | 0.0069378 | 0.99058 | -0.17925 | 0.99053 | -0.18028 | 1.906
43 | -0.0014634 | -0.00036676 | 0.0014634 | 0.00036669 | 1.0205e-08 | -6.1859e-08 | 0.0022305 | 0.0022305 | 0.0022305 | 0.97623 | -0.45763 | 0.97624 | -0.45748 | 0.61278
44 | 0.022206 | 0.0055856 | -0.022203 | -0.0055843 | 2.1841e-06 | 1.3343e-06 | 0.033854 | 0.033854 | 0.033854 | 0.97624 | -0.45748 | 0.97614 | -0.45954 | 9.3005
45 | 0.022203 | 0.0055843 | -0.022198 | -0.005581 | 5.3155e-06 | 3.2474e-06 | 0.033854 | 0.033854 | 0.033854 | 0.97614 | -0.45954 | 0.97588 | -0.46455 | 9.3005
46 | 0.022198 | 0.005581 | -0.022179 | -0.0055695 | 1.8918e-05 | 1.1558e-05 | 0.033854 | 0.033854 | 0.033854 | 0.97588 | -0.46455 | 0.97497 | -0.48242 | 9.3006
47 | 0.014361 | 0.00361 | -0.014354 | -0.0036064 | 6.371e-06 | 3.6368e-06 | 0.021922 | 0.021922 | 0.021922 | 0.97497 | -0.48242 | 0.9745 | -0.49171 | 6.0224
48 | 0.00021619 | 5.3808e-05 | -0.00021618 | -5.4181e-05 | 1.247e-09 | -3.7267e-07 | 0.00033148 | 0.00033162 | 0.00033162 | 0.97006 | -0.57861 | 0.97006 | -0.57874 | 0.091103
49 | -0.0016562 | -0.0004147 | 0.0016563 | 0.0004142 | 1.1256e-07 | -5.0227e-07 | 0.0025403 | 0.0025401 | 0.0025403 | 0.97006 | -0.57861 | 0.97013 | -0.57719 | 0.69789
50 | -0.003107 | -0.00077778 | 0.0031072 | 0.0007776 | 2.3027e-07 | -1.8656e-07 | 0.0047653 | 0.0047651 | 0.0047653 | 0.97013 | -0.57719 | 0.97021 | -0.57563 | 1.3091
51 | -0.0031388 | -0.00078551 | 0.0031408 | 0.00078396 | 1.9839e-06 | -1.5525e-06 | 0.0048136 | 0.0048126 | 0.0048136 | 0.97021 | -0.57563 | 0.97088 | -0.56234 | 1.3224
52 | 0.014224 | 0.0035662 | -0.014209 | -0.0035577 | 1.5019e-05 | 8.5663e-06 | 0.021776 | 0.021776 | 0.021776 | 0.972 | -0.54016 | 0.97088 | -0.56234 | 5.9825
53 | -0.0239 | -0.0059913 | 0.023947 | 0.0060202 | 4.6903e-05 | 2.8858e-05 | 0.036589 | 0.036589 | 0.036589 | 0.972 | -0.54016 | 0.97409 | -0.49906 | 10.0519
54 | 0.0042534 | 0.0010657 | -0.0042526 | -0.0010658 | 7.9229e-07 | -1.0763e-07 | 0.0065188 | 0.006519 | 0.006519 | 0.97088 | -0.56234 | 0.97069 | -0.56625 | 1.7909
55 | -0.024131 | -0.0060662 | 0.02417 | 0.0060904 | 3.9362e-05 | 2.4229e-05 | 0.036869 | 0.036869 | 0.036869 | 0.97409 | -0.49906 | 0.97582 | -0.46495 | 10.1289
56 | 0.0042198 | 0.0010574 | -0.0042194 | -0.0010575 | 4.111e-07 | -8.2932e-08 | 0.0063623 | 0.0063624 | 0.0063624 | 0.98693 | -0.24909 | 0.98683 | -0.25113 | 1.7479
57 | -0.0076055 | -0.0019059 | 0.007607 | 0.0019065 | 1.4353e-06 | 5.4656e-07 | 0.011467 | 0.011467 | 0.011467 | 0.98693 | -0.24909 | 0.98713 | -0.24513 | 3.1503
58 | 0.0032681 | 0.00081904 | -0.0032681 | -0.00081905 | 1.5105e-08 | -1.1524e-08 | 0.0049279 | 0.0049279 | 0.0049279 | 0.98683 | -0.25113 | 0.98682 | -0.25123 | 1.3538
59 | -0.007607 | -0.0019065 | 0.0076103 | 0.0019078 | 3.3626e-06 | 1.2798e-06 | 0.011467 | 0.011467 | 0.011467 | 0.98713 | -0.24513 | 0.98761 | -0.23585 | 3.1502
60 | -0.034317 | -0.0086335 | 0.034361 | 0.008661 | 4.3861e-05 | 2.7537e-05 | 0.052342 | 0.052341 | 0.052342 | 0.97582 | -0.46495 | 0.97718 | -0.43824 | 14.3796
61 | 0.16224 | 0.041178 | -0.16209 | -0.041081 | 0.00015267 | 9.6932e-05 | 0.24502 | 0.24502 | 0.24502 | 0.98606 | -0.26559 | 0.98505 | -0.28517 | 22.4374
62 | -0.16419 | -0.041665 | 0.16462 | 0.041939 | 0.0004316 | 0.00027407 | 0.24795 | 0.24795 | 0.24795 | 0.98606 | -0.26559 | 0.9889 | -0.21109 | 22.706
63 | 0.10585 | 0.026882 | -0.1058 | -0.026848 | 5.533e-05 | 3.4752e-05 | 0.16002 | 0.16003 | 0.16003 | 0.98505 | -0.28517 | 0.98449 | -0.29604 | 14.6543
64 | 0.056239 | 0.014198 | -0.056219 | -0.014187 | 1.9805e-05 | 1.1838e-05 | 0.084992 | 0.084992 | 0.084992 | 0.98505 | -0.28517 | 0.98467 | -0.29253 | 7.7832
65 | -0.24547 | -0.062459 | 0.24589 | 0.062727 | 0.00041956 | 0.00026757 | 0.3697 | 0.36969 | 0.3697 | 0.9889 | -0.21109 | 0.99074 | -0.1757 | 33.8549
66 | 0.080848 | 0.02052 | -0.080819 | -0.020502 | 2.9747e-05 | 1.842e-05 | 0.12175 | 0.12175 | 0.12175 | 0.9889 | -0.21109 | 0.9885 | -0.21875 | 11.149
67 | 0.10534 | 0.026732 | -0.10522 | -0.026658 | 0.00011876 | 7.4582e-05 | 0.15933 | 0.15933 | 0.15933 | 0.98449 | -0.29604 | 0.98328 | -0.31951 | 14.5908
68 | 0.056219 | 0.014187 | -0.056204 | -0.014177 | 1.5613e-05 | 9.3329e-06 | 0.084992 | 0.084992 | 0.084992 | 0.98467 | -0.29253 | 0.98437 | -0.29833 | 7.7832
69 | -0.24704 | -0.063016 | 0.2473 | 0.063182 | 0.00025999 | 0.00016581 | 0.37143 | 0.37143 | 0.37143 | 0.99074 | -0.1757 | 0.99188 | -0.15393 | 34.0136
70 | 0.079404 | 0.020147 | -0.079388 | -0.020138 | 1.5326e-05 | 9.4791e-06 | 0.11962 | 0.11962 | 0.11962 | 0.9885 | -0.21875 | 0.98829 | -0.22276 | 10.9539
71 | 0.10313 | 0.026134 | -0.10308 | -0.026105 | 4.7025e-05 | 2.9509e-05 | 0.15617 | 0.15617 | 0.15617 | 0.98328 | -0.31951 | 0.98279 | -0.32901 | 14.3012
72 | 0.0537 | 0.01355 | -0.053676 | -0.013535 | 2.4463e-05 | 1.4525e-05 | 0.081208 | 0.081209 | 0.081209 | 0.98437 | -0.29833 | 0.98388 | -0.30785 | 7.4367
73 | 0.075559 | 0.019178 | -0.075535 | -0.019163 | 2.3929e-05 | 1.4747e-05 | 0.11385 | 0.11385 | 0.11385 | 0.98829 | -0.22276 | 0.98795 | -0.22935 | 10.4259
74 | 0.10161 | 0.025735 | -0.10153 | -0.025687 | 7.6496e-05 | 4.7976e-05 | 0.15394 | 0.15394 | 0.15394 | 0.98279 | -0.32901 | 0.98198 | -0.34469 | 14.0969
75 | 0.10153 | 0.025687 | -0.10141 | -0.025615 | 0.00011584 | 7.2653e-05 | 0.15394 | 0.15394 | 0.15394 | 0.98198 | -0.34469 | 0.98076 | -0.3685 | 14.0969
76 | 0.088813 | 0.022457 | -0.088722 | -0.0224 | 9.0957e-05 | 5.6698e-05 | 0.13482 | 0.13482 | 0.13482 | 0.98076 | -0.3685 | 0.97966 | -0.38987 | 12.3462
77 | 0.044824 | 0.011352 | -0.044764 | -0.011314 | 6.0447e-05 | 3.8245e-05 | 0.067968 | 0.067969 | 0.067969 | 0.98194 | -0.34537 | 0.9805 | -0.37349 | 18.6727
78 | -0.044824 | -0.011352 | 0.044879 | 0.011387 | 5.4457e-05 | 3.4454e-05 | 0.067968 | 0.067968 | 0.067968 | 0.98194 | -0.34537 | 0.98325 | -0.3201 | 18.6727
79 | 0.039024 | 0.0098755 | -0.038956 | -0.009833 | 6.7326e-05 | 4.2445e-05 | 0.059257 | 0.059257 | 0.059257 | 0.9805 | -0.37349 | 0.97865 | -0.4095 | 16.2794
80 | -0.052458 | -0.013286 | 0.05257 | 0.013357 | 0.00011148 | 7.0749e-05 | 0.079439 | 0.079438 | 0.079439 | 0.98325 | -0.3201 | 0.98553 | -0.27596 | 21.8238
81 | 0.050845 | 0.012826 | -0.050818 | -0.01281 | 2.686e-05 | 1.5808e-05 | 0.076927 | 0.076927 | 0.076927 | 0.98388 | -0.30785 | 0.98332 | -0.31889 | 7.0446
82 | 0.073834 | 0.018737 | -0.073811 | -0.018723 | 2.3096e-05 | 1.4208e-05 | 0.11129 | 0.11129 | 0.11129 | 0.98795 | -0.22935 | 0.98761 | -0.23585 | 10.1914
83 | 0.0042212 | 0.0010567 | -0.00422 | -0.0010569 | 1.2261e-06 | -1.8009e-07 | 0.0064708 | 0.0064712 | 0.0064712 | 0.97064 | -0.56726 | 0.97033 | -0.57336 | 1.7778
84 | -0.0049913 | -0.0012497 | 0.0049918 | 0.0012498 | 4.4185e-07 | 3.3994e-08 | 0.0076514 | 0.0076513 | 0.0076514 | 0.97064 | -0.56726 | 0.97073 | -0.5654 | 2.102
85 | 0.0037295 | 0.00093396 | -0.003729 | -0.00093413 | 4.6033e-07 | -1.6893e-07 | 0.0057189 | 0.0057191 | 0.0057191 | 0.97033 | -0.57336 | 0.9702 | -0.57596 | 1.5712
86 | -0.0065333 | -0.0016361 | 0.0065347 | 0.0016365 | 1.3909e-06 | 4.3284e-07 | 0.010014 | 0.010014 | 0.010014 | 0.97073 | -0.5654 | 0.97096 | -0.56093 | 2.7512
87 | 0.003729 | 0.00093413 | -0.0037286 | -0.00093428 | 3.9924e-07 | -1.4638e-07 | 0.0057191 | 0.0057193 | 0.0057193 | 0.9702 | -0.57596 | 0.97008 | -0.5782 | 1.5712
88 | 0.0013769 | 0.00034503 | -0.0013769 | -0.00034509 | 9.9231e-09 | -6.7147e-08 | 0.0021102 | 0.0021102 | 0.0021102 | 0.97096 | -0.56093 | 0.97095 | -0.56108 | 0.57973
89 | -0.0079116 | -0.0019816 | 0.0079146 | 0.0019828 | 2.969e-06 | 1.2337e-06 | 0.012124 | 0.012124 | 0.012124 | 0.97096 | -0.56093 | 0.97135 | -0.55305 | 3.3309
90 | 0.0035465 | 0.00088865 | -0.0035463 | -0.00088878 | 2.7605e-07 | -1.304e-07 | 0.00544 | 0.0054401 | 0.0054401 | 0.97008 | -0.5782 | 0.97 | -0.57984 | 1.4945
91 | -0.0079899 | -0.0020017 | 0.0079912 | 0.0020022 | 1.2373e-06 | 5.1917e-07 | 0.012239 | 0.012239 | 0.012239 | 0.97135 | -0.55305 | 0.97152 | -0.5498 | 3.3625
92 | -0.011038 | -0.0027659 | 0.011044 | 0.0027691 | 6.2547e-06 | 3.28e-06 | 0.016906 | 0.016906 | 0.016906 | 0.97152 | -0.5498 | 0.97212 | -0.53791 | 4.6446
93 | 0.013735 | 0.0034511 | -0.013732 | -0.0034493 | 3.2255e-06 | 1.8209e-06 | 0.020976 | 0.020976 | 0.020976 | 0.9745 | -0.49171 | 0.97425 | -0.49663 | 5.7626
94 | 0.0005572 | 0.00013948 | -0.0005572 | -0.00013965 | 3.7679e-09 | -1.7035e-07 | 0.00085098 | 0.00085104 | 0.00085104 | 0.97425 | -0.49663 | 0.97424 | -0.49677 | 0.2338
95 | 0.013175 | 0.0033098 | -0.013172 | -0.0033087 | 2.0956e-06 | 1.1694e-06 | 0.020125 | 0.020125 | 0.020125 | 0.97425 | -0.49663 | 0.97408 | -0.49997 | 5.5288
96 | 0.012484 | 0.0031362 | -0.01248 | -0.0031339 | 4.1107e-06 | 2.2559e-06 | 0.019074 | 0.019074 | 0.019074 | 0.97408 | -0.49997 | 0.97373 | -0.50687 | 5.2401
97 | 0.01248 | 0.0031339 | -0.012471 | -0.0031288 | 9.3951e-06 | 5.1569e-06 | 0.019074 | 0.019074 | 0.019074 | 0.97373 | -0.50687 | 0.97293 | -0.52266 | 5.2402
98 | 0.012316 | 0.0030899 | -0.012313 | -0.0030887 | 2.2582e-06 | 1.2346e-06 | 0.018837 | 0.018837 | 0.018837 | 0.97293 | -0.52266 | 0.97274 | -0.5265 | 5.175
99 | 0.0091381 | 0.0022893 | -0.0091371 | -0.0022889 | 9.6778e-07 | 4.561e-07 | 0.013993 | 0.013993 | 0.013993 | 0.97175 | -0.54511 | 0.97164 | -0.54734 | 3.8441
100 | 0.007116 | 0.0017828 | -0.0071152 | -0.0017825 | 8.5933e-07 | 3.1101e-07 | 0.010898 | 0.010898 | 0.010898 | 0.97164 | -0.54734 | 0.97151 | -0.54987 | 2.9939
101 | 0.0020211 | 0.00050604 | -0.0020209 | -0.00050649 | 1.6107e-07 | -4.5221e-07 | 0.003095 | 0.0030952 | 0.0030952 | 0.97164 | -0.54734 | 0.97156 | -0.54901 | 0.85033
102 | 0.0038169 | 0.00095627 | -0.0038163 | -0.00095646 | 5.7718e-07 | -1.8815e-07 | 0.005846 | 0.0058462 | 0.0058462 | 0.97151 | -0.54987 | 0.97135 | -0.55305 | 1.6061
103 | 0.0032983 | 0.00082625 | -0.003298 | -0.00082641 | 2.4299e-07 | -1.5887e-07 | 0.0050516 | 0.0050517 | 0.0050517 | 0.97151 | -0.54987 | 0.97144 | -0.55142 | 1.3878
104 | 0.001839 | 0.00046074 | -0.001839 | -0.00046089 | 4.011e-08 | -1.4121e-07 | 0.0028169 | 0.0028169 | 0.0028169 | 0.97144 | -0.55142 | 0.97141 | -0.55188 | 0.77388
105 | 0.071297 | 0.017989 | -0.071262 | -0.017967 | 3.5041e-05 | 2.1531e-05 | 0.10853 | 0.10853 | 0.10853 | 0.97794 | -0.42347 | 0.97741 | -0.43374 | 9.9384
106 | -0.073717 | -0.018595 | 0.073768 | 0.018627 | 5.0663e-05 | 3.1211e-05 | 0.11221 | 0.11221 | 0.11221 | 0.97794 | -0.42347 | 0.97867 | -0.40913 | 10.2757
107 | 0.069856 | 0.017615 | -0.069817 | -0.017591 | 3.9181e-05 | 2.4035e-05 | 0.10639 | 0.10639 | 0.10639 | 0.97741 | -0.43374 | 0.97681 | -0.44547 | 9.7424
108 | -0.074818 | -0.01889 | 0.074833 | 0.018899 | 1.529e-05 | 9.4292e-06 | 0.11381 | 0.11381 | 0.11381 | 0.97867 | -0.40913 | 0.97889 | -0.40486 | 10.4218
109 | 0.068283 | 0.017207 | -0.068255 | -0.017189 | 2.796e-05 | 1.7119e-05 | 0.10405 | 0.10405 | 0.10405 | 0.97681 | -0.44547 | 0.97638 | -0.45403 | 9.5286
110 | -0.075157 | -0.01898 | 0.075211 | 0.019014 | 5.4027e-05 | 3.3328e-05 | 0.1143 | 0.1143 | 0.1143 | 0.97889 | -0.40486 | 0.97966 | -0.38987 | 10.4669
111 | 0.067133 | 0.016908 | -0.06713 | -0.016906 | 3.5704e-06 | 2.1827e-06 | 0.10234 | 0.10234 | 0.10234 | 0.97638 | -0.45403 | 0.97632 | -0.45514 | 9.372
112 | 0.066494 | 0.016747 | -0.06647 | -0.016732 | 2.3732e-05 | 1.4495e-05 | 0.10137 | 0.10137 | 0.10137 | 0.97632 | -0.45514 | 0.97594 | -0.46261 | 9.2833
113 | -0.0073161 | -0.0018336 | 0.0073165 | 0.0018338 | 3.9441e-07 | 1.4858e-07 | 0.011202 | 0.011202 | 0.011202 | 0.97181 | -0.54493 | 0.97186 | -0.5438 | 3.0776
114 | 0.0065297 | 0.0016365 | -0.0065292 | -0.0016364 | 4.9648e-07 | 1.5367e-07 | 0.0099981 | 0.0099982 | 0.0099982 | 0.97181 | -0.54493 | 0.97172 | -0.54653 | 2.7468
115 | -0.0096997 | -0.0024311 | 0.0096998 | 0.0024311 | 7.3586e-08 | 3.607e-08 | 0.014851 | 0.014851 | 0.014851 | 0.97186 | -0.5438 | 0.97187 | -0.54364 | 4.08
116 | 0.005979 | 0.0014985 | -0.005978 | -0.0014982 | 1.054e-06 | 2.5929e-07 | 0.0091557 | 0.0091559 | 0.0091559 | 0.97172 | -0.54653 | 0.97154 | -0.55023 | 2.5154
117 | -0.010105 | -0.0025327 | 0.010107 | 0.0025337 | 1.8917e-06 | 9.4952e-07 | 0.015472 | 0.015472 | 0.015472 | 0.97187 | -0.54364 | 0.97207 | -0.53971 | 4.2506
118 | 0.011901 | 0.0029853 | -0.011896 | -0.0029828 | 4.5632e-06 | 2.4649e-06 | 0.018206 | 0.018206 | 0.018206 | 0.97274 | -0.5265 | 0.97233 | -0.53455 | 5.0017
119 | 0.010985 | 0.0027543 | -0.010982 | -0.0027529 | 2.7011e-06 | 1.4126e-06 | 0.016811 | 0.016811 | 0.016811 | 0.97233 | -0.53455 | 0.97207 | -0.53971 | 4.6184
120 | -0.064828 | -0.016319 | 0.064832 | 0.016322 | 4.2406e-06 | 2.5839e-06 | 0.098876 | 0.098876 | 0.098876 | 0.97587 | -0.46398 | 0.97594 | -0.46261 | 9.0546
121 | 0.063589 | 0.016008 | -0.063523 | -0.015968 | 6.5221e-05 | 4.0818e-05 | 0.096986 | 0.096987 | 0.096987 | 0.97587 | -0.46398 | 0.97478 | -0.48546 | 13.3223
122 | 0.031893 | 0.0080205 | -0.031872 | -0.0080082 | 2.1071e-05 | 1.2305e-05 | 0.048695 | 0.048695 | 0.048695 | 0.97478 | -0.48546 | 0.97408 | -0.4993 | 6.6889
123 | 0.031631 | 0.0079471 | -0.031626 | -0.0079442 | 4.6799e-06 | 2.9285e-06 | 0.048292 | 0.048292 | 0.048292 | 0.97478 | -0.48546 | 0.97462 | -0.48856 | 13.2671
124 | 0.028952 | 0.007274 | -0.028928 | -0.0072593 | 2.3574e-05 | 1.4687e-05 | 0.044209 | 0.04421 | 0.04421 | 0.97462 | -0.48856 | 0.97375 | -0.50563 | 12.1455
125 | 0.021111 | 0.0053001 | -0.021108 | -0.005298 | 3.5896e-06 | 2.1829e-06 | 0.032264 | 0.032264 | 0.032264 | 0.97375 | -0.50563 | 0.97357 | -0.5092 | 8.8638
126 | 0.017703 | 0.0044445 | -0.017697 | -0.0044413 | 5.3467e-06 | 3.1798e-06 | 0.027059 | 0.02706 | 0.02706 | 0.97357 | -0.5092 | 0.97325 | -0.51553 | 7.4339
127 | -0.0037931 | -0.00095046 | 0.0037931 | 0.00095046 | 8.25e-10 | -3.3418e-10 | 0.0057157 | 0.0057157 | 0.0057157 | 0.98747 | -0.23862 | 0.98747 | -0.23862 | 1.5703
128 | 0.0010641 | 0.0002665 | -0.001064 | -0.00026667 | 1.3758e-08 | -1.7375e-07 | 0.0016034 | 0.0016034 | 0.0016034 | 0.98747 | -0.23862 | 0.98745 | -0.23889 | 0.4405
129 | -0.0065754 | -0.0016478 | 0.0065763 | 0.001648 | 8.6577e-07 | 2.5322e-07 | 0.0099084 | 0.0099083 | 0.0099084 | 0.98747 | -0.23862 | 0.98761 | -0.23585 | 2.7221
130 | 0.059625 | 0.015167 | -0.059584 | -0.015142 | 4.03e-05 | 2.5112e-05 | 0.089916 | 0.089916 | 0.089916 | 0.98761 | -0.23585 | 0.98688 | -0.24989 | 12.3511
131 | 0.056264 | 0.01431 | -0.056193 | -0.014265 | 7.0573e-05 | 4.4834e-05 | 0.084909 | 0.084909 | 0.084909 | 0.98688 | -0.24989 | 0.98553 | -0.27596 | 23.3267
132 | 0.0036235 | 0.00090784 | -0.0036234 | -0.00090789 | 9.694e-08 | -4.8011e-08 | 0.0054708 | 0.0054709 | 0.0054709 | 0.98553 | -0.27596 | 0.9855 | -0.27652 | 1.503
133 | 0.017173 | 0.00431 | -0.017167 | -0.0043066 | 5.7986e-06 | 3.4325e-06 | 0.026258 | 0.026259 | 0.026259 | 0.97325 | -0.51553 | 0.97289 | -0.52261 | 7.2139
134 | 0.013849 | 0.0034749 | -0.013842 | -0.0034709 | 7.0663e-06 | 4.0013e-06 | 0.021183 | 0.021183 | 0.021183 | 0.97289 | -0.52261 | 0.97235 | -0.53332 | 5.8195
135 | 0.011047 | 0.0027704 | -0.011044 | -0.0027691 | 2.4155e-06 | 1.2664e-06 | 0.016906 | 0.016906 | 0.016906 | 0.97235 | -0.53332 | 0.97212 | -0.53791 | 4.6445
136 | 0.0036234 | 0.00090789 | -0.0036231 | -0.00090803 | 2.8147e-07 | -1.3936e-07 | 0.0054709 | 0.005471 | 0.005471 | 0.9855 | -0.27652 | 0.98542 | -0.27815 | 1.503
137 | 0.038956 | 0.009833 | -0.038903 | -0.0097993 | 5.3543e-05 | 3.3758e-05 | 0.059257 | 0.059257 | 0.059257 | 0.97865 | -0.4095 | 0.97718 | -0.43824 | 16.2795
138 | -0.0508 | -0.012799 | 0.050818 | 0.01281 | 1.7729e-05 | 1.0435e-05 | 0.076927 | 0.076927 | 0.076927 | 0.98294 | -0.32618 | 0.98332 | -0.31889 | 7.0446
139 | 0.04817 | 0.01214 | -0.048113 | -0.012107 | 5.7049e-05 | 3.3254e-05 | 0.072947 | 0.072948 | 0.072948 | 0.98294 | -0.32618 | 0.98167 | -0.35096 | 6.6802
140 | 0.048113 | 0.012107 | -0.048099 | -0.012098 | 1.4099e-05 | 8.6664e-06 | 0.072948 | 0.072948 | 0.072948 | 0.98167 | -0.35096 | 0.98136 | -0.3571 | 10.0203
141 | 0.048099 | 0.012098 | -0.047985 | -0.012026 | 0.00011391 | 7.2186e-05 | 0.072948 | 0.072948 | 0.072948 | 0.98136 | -0.3571 | 0.97882 | -0.4068 | 20.0407

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40464 | 0.10372

## res_load
| p_mw | q_mvar
0 | 0.0097047 | 0.0024322
1 | 0.0022477 | 0.00056334
2 | 0.016298 | 0.0040847
3 | 0.00046546 | 0.00011665
4 | 0.016712 | 0.0041884
5 | 0.0019063 | 0.00047776
6 | 0.00071206 | 0.00017846
7 | 0.0067099 | 0.0016817
8 | 0.0026657 | 0.00066808
9 | 0.00070382 | 0.00017639
10 | 0.0012162 | 0.0003048
11 | 0.0013976 | 0.00035027
12 | 0.0040501 | 0.001015
13 | 0.0005097 | 0.00012774
14 | 0.003911 | 0.0009802
15 | 0.00082843 | 0.00020762
16 | 0.00093964 | 0.00023549
17 | 0.0060008 | 0.0015039
18 | 0.0054322 | 0.0013614
19 | 0.00096231 | 0.00024118
20 | 0.0015628 | 0.00039168
21 | 0.0012804 | 0.00032089
22 | 0.0017645 | 0.00044223
23 | 0.017423 | 0.0043666
24 | 0.0072587 | 0.0018192
25 | 0.0027282 | 0.00068374
26 | 0.0010814 | 0.00027101
27 | 0.0024618 | 0.00061698
28 | 0.017523 | 0.0043918
29 | 0.0014634 | 0.00036676
30 | 0.0078184 | 0.0019595
31 | 0.00144 | 0.00036089
32 | 0.00021618 | 5.4181e-05
33 | 0.0014507 | 0.00036359
34 | 3.1597e-05 | 7.9191e-06
35 | 0.0096761 | 0.0024251
36 | 0.0068151 | 0.001708
37 | 0.00018358 | 4.6011e-05
38 | 0.0033857 | 0.00084854
39 | 0.00095135 | 0.00023843
40 | 0.010147 | 0.0025431
41 | 0.0042526 | 0.0010658
42 | 0.0019436 | 0.00048711
43 | 0.00045957 | 0.00011518
44 | 0.001154 | 0.00028923
45 | 0.0014149 | 0.00035461
46 | 0.0020892 | 0.00052361
47 | 0.0025034 | 0.0006274
48 | 0.0010038 | 0.00025158
49 | 0.0038295 | 0.00095977
50 | 0.0014744 | 0.00036951
51 | 0.012601 | 0.0031581
52 | 0.0057404 | 0.0014387
53 | 0.0075793 | 0.0018996
54 | 0.0028314 | 0.00070962
55 | 0.0017005 | 0.0004262
56 | 0.00077008 | 0.000193
57 | 0.00049054 | 0.00012294
58 | 0.0015415 | 0.00038635
59 | 0.00018207 | 4.563e-05
60 | 0.0013769 | 0.00034509
61 | 7.5325e-05 | 1.8878e-05
62 | 0.0035463 | 0.00088878
63 | 0.0030471 | 0.00076367
64 | 0.00061942 | 0.00015524
65 | 0.0005572 | 0.00013965
66 | 0.0006882 | 0.00017248
67 | 0.00015504 | 3.8857e-05
68 | 0.006121 | 0.0015341
69 | 0.0020209 | 0.00050649
70 | 0.0038163 | 0.00095646
71 | 0.001459 | 0.00036566
72 | 0.001839 | 0.00046089
73 | 0.0024205 | 0.00060662
74 | 0.0014061 | 0.00035241
75 | 0.00105 | 0.00026315
76 | 0.0015331 | 0.00038424
77 | 0.00032387 | 8.1171e-05
78 | 0.001122 | 0.0002812
79 | 0.013511 | 0.0033862
80 | 0.00063567 | 0.00015931
81 | 0.00078648 | 0.00019711
82 | 0.0023832 | 0.00059728
83 | 0.00055016 | 0.00013788
84 | 0.00040549 | 0.00010162
85 | 0.005978 | 0.0014982
86 | 0.00041266 | 0.00010342
87 | 0.00091168 | 0.00022849
88 | 0.00087469 | 0.00021922
89 | 0.0012393 | 0.0003106
90 | 0.0016383 | 0.0004106
91 | 0.00033234 | 8.3291e-05
92 | 0.0026741 | 0.00067019
93 | 0.007817 | 0.0019591
94 | 0.0034053 | 0.00085345
95 | 0.0046183 | 0.0011574
96 | 0.002729 | 0.00068396
97 | 0.0027823 | 0.00069731
98 | 0.001064 | 0.00026667
99 | 0.0033205 | 0.00083221
100 | 0.00052399 | 0.00013132
101 | 0.0033185 | 0.0008317
102 | 0.0027949 | 0.00070046
103 | 0.0032681 | 0.00081905
104 | 0.0036231 | 0.00090803
105 | 0.0045417 | 0.0011383
106 | 0.0026296 | 0.00065904
107 | 0.047985 | 0.012026
108 | 0.0022728 | 0.00056963

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1