## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2513-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2513-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2513-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2513-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2513-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2513-6_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2513-6_0_4_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_2513-6_0_4_node_103 | 0.4 | n |  | TRUE
8 | bus_LV_2513-6_0_4_node_111 | 0.4 | n |  | TRUE
9 | bus_LV_2513-6_0_4_node_151 | 0.4 | n |  | TRUE
10 | bus_LV_2513-6_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_2513-6_0_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_2513-6_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2513-6_0_4_node_77 | 0.4 | n |  | TRUE
14 | bus_LV_2513-6_0_4_node_92 | 0.4 | n |  | TRUE
15 | bus_LV_2513-6_0_4_node_108 | 0.4 | n |  | TRUE
16 | bus_LV_2513-6_0_4_node_72 | 0.4 | n |  | TRUE
17 | bus_LV_2513-6_0_4_node_78 | 0.4 | n |  | TRUE
18 | bus_LV_2513-6_0_4_node_93 | 0.4 | n |  | TRUE
19 | bus_LV_2513-6_0_4_node_6 | 0.4 | n |  | TRUE
20 | bus_LV_2513-6_0_4_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_2513-6_0_4_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_2513-6_0_4_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_2513-6_0_4_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_2513-6_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_2513-6_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_2513-6_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2513-6_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2513-6_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2513-6_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2513-6_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_2513-6_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2513-6_0_4_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_2513-6_0_4_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_2513-6_0_4_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_2513-6_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2513-6_0_4_node_50 | 0.4 | n |  | TRUE
37 | bus_LV_2513-6_0_4_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_2513-6_0_4_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_2513-6_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_2513-6_0_4_node_86 | 0.4 | n |  | TRUE
41 | bus_LV_2513-6_0_4_node_101 | 0.4 | n |  | TRUE
42 | bus_LV_2513-6_0_4_node_84 | 0.4 | n |  | TRUE
43 | bus_LV_2513-6_0_4_node_153 | 0.4 | n |  | TRUE
44 | bus_LV_2513-6_0_4_node_154 | 0.4 | n |  | TRUE
45 | bus_LV_2513-6_0_4_node_125 | 0.4 | n |  | TRUE
46 | bus_LV_2513-6_0_4_node_21 | 0.4 | n |  | TRUE
47 | bus_LV_2513-6_0_4_node_22 | 0.4 | n |  | TRUE
48 | bus_LV_2513-6_0_4_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_2513-6_0_4_node_130 | 0.4 | n |  | TRUE
50 | bus_LV_2513-6_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_2513-6_0_4_node_97 | 0.4 | n |  | TRUE
52 | bus_LV_2513-6_0_4_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_2513-6_0_4_node_25 | 0.4 | n |  | TRUE
54 | bus_LV_2513-6_0_4_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_2513-6_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2513-6_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2513-6_0_4_node_94 | 0.4 | n |  | TRUE
58 | bus_LV_2513-6_0_4_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_2513-6_0_4_node_113 | 0.4 | n |  | TRUE
60 | bus_LV_2513-6_0_4_node_114 | 0.4 | n |  | TRUE
61 | bus_LV_2513-6_0_4_node_29 | 0.4 | n |  | TRUE
62 | bus_LV_2513-6_0_4_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_2513-6_0_4_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_2513-6_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_2513-6_0_4_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_2513-6_0_4_node_100 | 0.4 | n |  | TRUE
67 | bus_LV_2513-6_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2513-6_0_4_node_33 | 0.4 | n |  | TRUE
69 | bus_LV_2513-6_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_2513-6_0_4_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_2513-6_0_4_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_2513-6_0_4_node_123 | 0.4 | n |  | TRUE
73 | bus_LV_2513-6_0_4_node_143 | 0.4 | n |  | TRUE
74 | bus_LV_2513-6_0_4_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_2513-6_0_4_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_2513-6_0_4_node_115 | 0.4 | n |  | TRUE
77 | bus_LV_2513-6_0_4_node_131 | 0.4 | n |  | TRUE
78 | bus_LV_2513-6_0_4_node_124 | 0.4 | n |  | TRUE
79 | bus_LV_2513-6_0_4_node_99 | 0.4 | n |  | TRUE
80 | bus_LV_2513-6_0_4_node_39 | 0.4 | n |  | TRUE
81 | bus_LV_2513-6_0_4_node_40 | 0.4 | n |  | TRUE
82 | bus_LV_2513-6_0_4_node_41 | 0.4 | n |  | TRUE
83 | bus_LV_2513-6_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_2513-6_0_4_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_2513-6_0_4_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_2513-6_0_4_node_43 | 0.4 | n |  | TRUE
87 | bus_LV_2513-6_0_4_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_2513-6_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2513-6_0_4_node_134 | 0.4 | n |  | TRUE
90 | bus_LV_2513-6_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_2513-6_0_4_node_138 | 0.4 | n |  | TRUE
92 | bus_LV_2513-6_0_4_node_136 | 0.4 | n |  | TRUE
93 | bus_LV_2513-6_0_4_node_46 | 0.4 | n |  | TRUE
94 | bus_LV_2513-6_0_4_node_47 | 0.4 | n |  | TRUE
95 | bus_LV_2513-6_0_4_node_49 | 0.4 | n |  | TRUE
96 | bus_LV_2513-6_0_4_node_105 | 0.4 | n |  | TRUE
97 | bus_LV_2513-6_0_4_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_2513-6_0_4_node_142 | 0.4 | n |  | TRUE
99 | bus_LV_2513-6_0_4_node_106 | 0.4 | n |  | TRUE
100 | bus_LV_2513-6_0_4_node_107 | 0.4 | n |  | TRUE
101 | bus_LV_2513-6_0_4_node_109 | 0.4 | n |  | TRUE
102 | bus_LV_2513-6_0_4_node_110 | 0.4 | n |  | TRUE
103 | bus_LV_2513-6_0_4_node_141 | 0.4 | n |  | TRUE
104 | bus_LV_2513-6_0_4_node_152 | 0.4 | n |  | TRUE
105 | bus_LV_2513-6_0_4_node_58 | 0.4 | n |  | TRUE
106 | bus_LV_2513-6_0_4_node_59 | 0.4 | n |  | TRUE
107 | bus_LV_2513-6_0_4_node_60 | 0.4 | n |  | TRUE
108 | bus_LV_2513-6_0_4_node_61 | 0.4 | n |  | TRUE
109 | bus_LV_2513-6_0_4_node_62 | 0.4 | n |  | TRUE
110 | bus_LV_2513-6_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_2513-6_0_4_node_118 | 0.4 | n |  | TRUE
112 | bus_LV_2513-6_0_4_node_140 | 0.4 | n |  | TRUE
113 | bus_LV_2513-6_0_4_node_117 | 0.4 | n |  | TRUE
114 | bus_LV_2513-6_0_4_node_66 | 0.4 | n |  | TRUE
115 | bus_LV_2513-6_0_4_node_67 | 0.4 | n |  | TRUE
116 | bus_LV_2513-6_0_4_node_68 | 0.4 | n |  | TRUE
117 | bus_LV_2513-6_0_4_node_150 | 0.4 | n |  | TRUE
118 | bus_LV_2513-6_0_4_node_149 | 0.4 | n |  | TRUE
119 | bus_LV_2513-6_0_4_node_132 | 0.4 | n |  | TRUE
120 | bus_LV_2513-6_0_4_node_75 | 0.4 | n |  | TRUE
121 | bus_LV_2513-6_0_4_node_90 | 0.4 | n |  | TRUE
122 | bus_LV_2513-6_0_4_node_88 | 0.4 | n |  | TRUE
123 | bus_LV_2513-6_0_4_node_135 | 0.4 | n |  | TRUE
124 | bus_LV_2513-6_0_4_node_79 | 0.4 | n |  | TRUE
125 | bus_LV_2513-6_0_4_node_80 | 0.4 | n |  | TRUE
126 | bus_LV_2513-6_0_4_node_81 | 0.4 | n |  | TRUE
127 | bus_LV_2513-6_0_4_node_82 | 0.4 | n |  | TRUE
128 | bus_LV_2513-6_0_4_node_83 | 0.4 | n |  | TRUE
129 | bus_LV_2513-6_0_4_node_122 | 0.4 | n |  | TRUE
130 | bus_LV_2513-6_0_4_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_2513-6_0_4_node_144 | 0.4 | n |  | TRUE
132 | bus_LV_2513-6_0_4_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_2513-6_0_4_node_85 | 0.4 | n |  | TRUE
134 | bus_LV_2513-6_0_4_node_89 | 0.4 | n |  | TRUE
135 | bus_LV_2513-6_0_4_node_91 | 0.4 | n |  | TRUE
136 | bus_LV_2513-6_0_4_node_96 | 0.4 | n |  | TRUE
137 | bus_LV_2513-6_0_4_node_116 | 0.4 | n |  | TRUE
138 | bus_LV_2513-6_0_4_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_2513-6_0_4_node_128 | 0.4 | n |  | TRUE
140 | bus_LV_2513-6_0_4_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_2513-6_0_4_node_133 | 0.4 | n |  | TRUE
142 | bus_LV_2513-6_0_4_node_121 | 0.4 | n |  | TRUE
143 | bus_LV_2513-6_0_4_node_147 | 0.4 | n |  | TRUE
144 | bus_LV_2513-6_0_4_node_137 | 0.4 | n |  | TRUE
145 | bus_LV_2513-6_0_4_node_146 | 0.4 | n |  | TRUE
146 | bus_LV_2513-6_0_4_node_127 | 0.4 | n |  | TRUE
147 | bus_LV_2513-6_0_4_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_2513-6_0_4_node_148 | 0.4 | n |  | TRUE
149 | bus_LV_2513-6_0_4_node_145 | 0.4 | n |  | TRUE
150 | bus_MV_393_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2513-6_0_4_load_0 | 0 | 0.0019793 | 0.00049605 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2513-6_0_4_load_1 | 1 | 0.002344 | 0.00058747 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2513-6_0_4_load_4 | 4 | 0.0014804 | 0.00037103 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2513-6_0_4_load_5 | 5 | 0.0016493 | 0.00041334 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2513-6_0_4_load_34 | 6 | 0.001875 | 0.00046992 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2513-6_0_4_load_103 | 7 | 0.0011763 | 0.0002948 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2513-6_0_4_load_111 | 8 | 0.0094573 | 0.0023702 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2513-6_0_4_load_151 | 9 | 0.001381 | 0.00034611 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2513-6_0_4_load_35 | 10 | 0.0024442 | 0.00061257 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2513-6_0_4_load_36 | 11 | 0.00162 | 0.00040601 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2513-6_0_4_load_77 | 13 | 0.0014885 | 0.00037304 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2513-6_0_4_load_92 | 14 | 0.0014829 | 0.00037165 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2513-6_0_4_load_72 | 16 | 0.0016022 | 0.00040154 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2513-6_0_4_load_78 | 17 | 0.0022167 | 0.00055555 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2513-6_0_4_load_93 | 18 | 0.001654 | 0.00041453 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2513-6_0_4_load_6 | 19 | 0.0020202 | 0.0005063 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2513-6_0_4_load_7 | 20 | 0.0017107 | 0.00042875 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2513-6_0_4_load_8 | 21 | 0.0033439 | 0.00083805 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2513-6_0_4_load_70 | 22 | 0.0018992 | 0.00047598 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2513-6_0_4_load_10 | 24 | 0.0035356 | 0.0008861 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2513-6_0_4_load_11 | 25 | 0.0049019 | 0.0012285 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2513-6_0_4_load_13 | 27 | 0.0040435 | 0.0010134 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2513-6_0_4_load_14 | 28 | 0.0034526 | 0.00086531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2513-6_0_4_load_15 | 29 | 0.0046888 | 0.0011751 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2513-6_0_4_load_44 | 30 | 0.002942 | 0.00073732 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2513-6_0_4_load_45 | 33 | 0.0022447 | 0.00056257 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2513-6_0_4_load_38 | 34 | 0.00183 | 0.00045865 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2513-6_0_4_load_17 | 35 | 0.0038871 | 0.0009742 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2513-6_0_4_load_50 | 36 | 0.0030898 | 0.00077437 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2513-6_0_4_load_16 | 37 | 0.0034251 | 0.00085841 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2513-6_0_4_load_18 | 38 | 0.0011752 | 0.00029454 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2513-6_0_4_load_20 | 39 | 0.0016957 | 0.00042499 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2513-6_0_4_load_86 | 40 | 0.0043328 | 0.0010859 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2513-6_0_4_load_101 | 41 | 0.0013549 | 0.00033957 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2513-6_0_4_load_84 | 42 | 0.00053764 | 0.00013474 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2513-6_0_4_load_153 | 43 | 0.00085308 | 0.0002138 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2513-6_0_4_load_154 | 44 | 0.00194 | 0.00048621 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2513-6_0_4_load_125 | 45 | 0.0011776 | 0.00029514 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2513-6_0_4_load_21 | 46 | 0.0039577 | 0.0009919 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2513-6_0_4_load_23 | 48 | 0.0040549 | 0.0010162 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2513-6_0_4_load_130 | 49 | 0.0010843 | 0.00027175 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2513-6_0_4_load_97 | 51 | 0.0013961 | 0.0003499 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2513-6_0_4_load_24 | 52 | 0.0036211 | 0.00090754 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2513-6_0_4_load_25 | 53 | 0.0015015 | 0.00037631 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2513-6_0_4_load_26 | 54 | 0.0033159 | 0.00083104 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2513-6_0_4_load_27 | 55 | 0.0017289 | 0.0004333 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2513-6_0_4_load_28 | 56 | 0.002332 | 0.00058445 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2513-6_0_4_load_94 | 57 | 0.0031378 | 0.00078641 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2513-6_0_4_load_113 | 59 | 0.0027094 | 0.00067903 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2513-6_0_4_load_114 | 60 | 0.0026361 | 0.00066067 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2513-6_0_4_load_29 | 61 | 0.0018784 | 0.00047076 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2513-6_0_4_load_55 | 64 | 0.0018004 | 0.00045122 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2513-6_0_4_load_53 | 65 | 0.0019033 | 0.00047702 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2513-6_0_4_load_100 | 66 | 0.0018167 | 0.00045531 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2513-6_0_4_load_33 | 68 | 0.0039185 | 0.00098208 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2513-6_0_4_load_51 | 69 | 0.0051052 | 0.0012795 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2513-6_0_4_load_56 | 70 | 0.0016178 | 0.00040546 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2513-6_0_4_load_57 | 71 | 0.0023975 | 0.00060088 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2513-6_0_4_load_123 | 72 | 0.00194 | 0.00048621 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2513-6_0_4_load_143 | 73 | 0.0013282 | 0.00033288 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2513-6_0_4_load_98 | 74 | 0.0020858 | 0.00052276 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2513-6_0_4_load_104 | 75 | 0.0011772 | 0.00029503 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2513-6_0_4_load_115 | 76 | 0.0068625 | 0.0017199 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2513-6_0_4_load_131 | 77 | 0.0050141 | 0.0012567 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2513-6_0_4_load_124 | 78 | 0.0018315 | 0.00045902 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2513-6_0_4_load_99 | 79 | 0.0014986 | 0.00037558 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2513-6_0_4_load_39 | 80 | 0.0026318 | 0.0006596 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2513-6_0_4_load_40 | 81 | 0.0018612 | 0.00046646 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2513-6_0_4_load_63 | 84 | 0.0016597 | 0.00041596 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2513-6_0_4_load_69 | 85 | 0.0094612 | 0.0023712 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2513-6_0_4_load_76 | 87 | 0.0066658 | 0.0016706 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2513-6_0_4_load_73 | 88 | 0.0080701 | 0.0020226 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2513-6_0_4_load_134 | 89 | 0.0019684 | 0.00049332 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2513-6_0_4_load_74 | 90 | 0.0033625 | 0.00084273 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2513-6_0_4_load_136 | 92 | 0.0041978 | 0.0010521 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2513-6_0_4_load_46 | 93 | 0.0028044 | 0.00070284 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2513-6_0_4_load_47 | 94 | 0.0031613 | 0.00079229 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2513-6_0_4_load_49 | 95 | 0.0027684 | 0.00069382 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2513-6_0_4_load_105 | 96 | 0.0010098 | 0.00025309 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2513-6_0_4_load_87 | 97 | 0.0053952 | 0.0013522 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2513-6_0_4_load_142 | 98 | 0.0025378 | 0.00063604 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2513-6_0_4_load_106 | 99 | 0.0016359 | 0.00040999 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2513-6_0_4_load_109 | 101 | 0.0013253 | 0.00033214 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2513-6_0_4_load_110 | 102 | 0.0016366 | 0.00041017 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2513-6_0_4_load_141 | 103 | 0.0013278 | 0.00033277 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2513-6_0_4_load_152 | 104 | 0.001652 | 0.00041402 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2513-6_0_4_load_58 | 105 | 0.0033986 | 0.00085177 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2513-6_0_4_load_59 | 106 | 0.002075 | 0.00052003 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2513-6_0_4_load_60 | 107 | 0.0026264 | 0.00065824 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2513-6_0_4_load_61 | 108 | 0.0018618 | 0.0004666 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2513-6_0_4_load_62 | 109 | 0.0017679 | 0.00044307 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2513-6_0_4_load_102 | 110 | 0.002116 | 0.00053032 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2513-6_0_4_load_118 | 111 | 0.0020258 | 0.00050772 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2513-6_0_4_load_140 | 112 | 0.002842 | 0.00071228 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2513-6_0_4_load_117 | 113 | 0.0026101 | 0.00065415 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2513-6_0_4_load_66 | 114 | 0.00232 | 0.00058144 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2513-6_0_4_load_67 | 115 | 0.0034197 | 0.00085706 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2513-6_0_4_load_150 | 117 | 0.00088035 | 0.00022064 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2513-6_0_4_load_149 | 118 | 0.0011941 | 0.00029928 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2513-6_0_4_load_132 | 119 | 0.002019 | 0.00050601 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2513-6_0_4_load_90 | 121 | 0.0038233 | 0.0009582 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2513-6_0_4_load_88 | 122 | 0.0016746 | 0.00041969 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2513-6_0_4_load_79 | 124 | 0.0030523 | 0.00076497 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2513-6_0_4_load_80 | 125 | 0.0018587 | 0.00046584 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2513-6_0_4_load_81 | 126 | 0.0018338 | 0.00045958 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2513-6_0_4_load_82 | 127 | 0.0042615 | 0.001068 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2513-6_0_4_load_122 | 129 | 0.0018839 | 0.00047214 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2513-6_0_4_load_119 | 130 | 0.0031307 | 0.00078463 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2513-6_0_4_load_144 | 131 | 0.0038653 | 0.00096874 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2513-6_0_4_load_120 | 132 | 0.0031101 | 0.00077946 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2513-6_0_4_load_85 | 133 | 0.0030656 | 0.0007683 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2513-6_0_4_load_89 | 134 | 0.0020017 | 0.00050168 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2513-6_0_4_load_91 | 135 | 0.0029501 | 0.00073938 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2513-6_0_4_load_96 | 136 | 0.002107 | 0.00052805 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2513-6_0_4_load_116 | 137 | 0.0028816 | 0.00072219 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2513-6_0_4_load_139 | 138 | 0.0030957 | 0.00077585 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2513-6_0_4_load_128 | 139 | 0.00097617 | 0.00024465 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2513-6_0_4_load_126 | 140 | 0.0011051 | 0.00027697 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2513-6_0_4_load_133 | 141 | 0.0023912 | 0.00059928 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2513-6_0_4_load_147 | 143 | 0.0040655 | 0.0010189 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2513-6_0_4_load_137 | 144 | 0.006063 | 0.0015195 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2513-6_0_4_load_146 | 145 | 0.0024414 | 0.00061187 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2513-6_0_4_load_127 | 146 | 0.0021383 | 0.00053591 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2513-6_0_4_load_129 | 147 | 0.0012719 | 0.00031876 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2513-6_0_4_load_148 | 148 | 0.0072556 | 0.0018184 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2513-6_0_4_load_145 | 149 | 0.0026166 | 0.00065579 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2513-6_0_4_line_0 |  | 0 | 1 | 0.032219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2513-6_0_4_line_1 |  | 0 | 2 | 0.0046501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2513-6_0_4_line_2 |  | 1 | 3 | 0.025351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2513-6_0_4_line_3 |  | 2 | 4 | 0.013885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2513-6_0_4_line_4 |  | 2 | 5 | 0.012165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2513-6_0_4_line_5 |  | 3 | 8 | 0.01924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2513-6_0_4_line_6 |  | 3 | 9 | 0.013684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2513-6_0_4_line_7 |  | 4 | 13 | 0.015126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2513-6_0_4_line_8 |  | 5 | 14 | 0.0050001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2513-6_0_4_line_9 |  | 6 | 7 | 0.035916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2513-6_0_4_line_10 |  | 7 | 75 | 0.020401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2513-6_0_4_line_11 |  | 7 | 76 | 0.042868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2513-6_0_4_line_12 |  | 8 | 15 | 0.010338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2513-6_0_4_line_13 |  | 9 | 16 | 0.021818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2513-6_0_4_line_14 |  | 10 | 11 | 0.0030193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2513-6_0_4_line_15 |  | 10 | 12 | 0.027394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2513-6_0_4_line_16 |  | 11 | 50 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2513-6_0_4_line_17 |  | 12 | 16 | 0.0093174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2513-6_0_4_line_18 |  | 12 | 22 | 0.022248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2513-6_0_4_line_19 |  | 12 | 20 | 0.023027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2513-6_0_4_line_20 |  | 13 | 17 | 0.0041342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2513-6_0_4_line_21 |  | 14 | 18 | 0.012732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2513-6_0_4_line_22 |  | 15 | 99 | 0.018161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2513-6_0_4_line_23 |  | 17 | 76 | 0.0078356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2513-6_0_4_line_24 |  | 19 | 20 | 0.0045272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2513-6_0_4_line_25 |  | 19 | 21 | 0.008772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2513-6_0_4_line_26 |  | 22 | 23 | 0.023016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2513-6_0_4_line_27 |  | 23 | 49 | 0.055382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2513-6_0_4_line_28 |  | 23 | 47 | 0.052192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2513-6_0_4_line_29 |  | 24 | 25 | 0.028174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2513-6_0_4_line_30 |  | 24 | 26 | 0.0046313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2513-6_0_4_line_31 |  | 25 | 27 | 0.024308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_2513-6_0_4_line_32 |  | 26 | 28 | 0.043036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2513-6_0_4_line_33 |  | 26 | 29 | 0.010351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2513-6_0_4_line_34 |  | 27 | 30 | 0.0050287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2513-6_0_4_line_35 |  | 28 | 31 | 0.014192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2513-6_0_4_line_36 |  | 29 | 32 | 0.011843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2513-6_0_4_line_37 |  | 30 | 33 | 0.018882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2513-6_0_4_line_38 |  | 31 | 34 | 0.023253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2513-6_0_4_line_39 |  | 31 | 35 | 0.015803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2513-6_0_4_line_40 |  | 32 | 36 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2513-6_0_4_line_41 |  | 33 | 91 | 0.00069726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2513-6_0_4_line_42 |  | 34 | 41 | 0.044216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2513-6_0_4_line_43 |  | 35 | 37 | 0.026028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2513-6_0_4_line_44 |  | 36 | 98 | 0.02613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2513-6_0_4_line_45 |  | 37 | 38 | 0.016257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2513-6_0_4_line_46 |  | 38 | 39 | 0.0056656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2513-6_0_4_line_47 |  | 39 | 40 | 0.016855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2513-6_0_4_line_48 |  | 40 | 42 | 0.01539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2513-6_0_4_line_49 |  | 41 | 79 | 0.0028889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2513-6_0_4_line_50 |  | 42 | 133 | 0.0030867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2513-6_0_4_line_51 |  | 43 | 44 | 0.00073659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2513-6_0_4_line_52 |  | 43 | 45 | 0.0091093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2513-6_0_4_line_53 |  | 45 | 78 | 0.0094271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2513-6_0_4_line_54 |  | 46 | 47 | 0.024264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2513-6_0_4_line_55 |  | 47 | 48 | 0.023655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2513-6_0_4_line_56 |  | 50 | 51 | 0.014858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2513-6_0_4_line_57 |  | 51 | 77 | 0.016908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2513-6_0_4_line_58 |  | 52 | 53 | 0.021234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2513-6_0_4_line_59 |  | 52 | 54 | 0.021487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2513-6_0_4_line_60 |  | 53 | 55 | 0.018759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2513-6_0_4_line_61 |  | 54 | 56 | 0.020572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2513-6_0_4_line_62 |  | 55 | 57 | 0.026516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2513-6_0_4_line_63 |  | 56 | 58 | 0.019527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2513-6_0_4_line_64 |  | 58 | 59 | 0.024247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2513-6_0_4_line_65 |  | 58 | 60 | 0.019741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2513-6_0_4_line_66 |  | 59 | 141 | 0.010753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2513-6_0_4_line_67 |  | 60 | 138 | 0.01706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2513-6_0_4_line_68 |  | 61 | 62 | 0.007948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2513-6_0_4_line_69 |  | 62 | 63 | 0.009614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2513-6_0_4_line_70 |  | 63 | 64 | 0.029743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2513-6_0_4_line_71 |  | 63 | 65 | 0.017286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2513-6_0_4_line_72 |  | 64 | 66 | 0.0045405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2513-6_0_4_line_73 |  | 65 | 67 | 0.010943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2513-6_0_4_line_74 |  | 66 | 74 | 0.01256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2513-6_0_4_line_75 |  | 67 | 70 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2513-6_0_4_line_76 |  | 67 | 71 | 0.035396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2513-6_0_4_line_77 |  | 68 | 69 | 0.004096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2513-6_0_4_line_78 |  | 69 | 73 | 0.032828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2513-6_0_4_line_79 |  | 70 | 72 | 0.019275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2513-6_0_4_line_80 |  | 71 | 78 | 0.020803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2513-6_0_4_line_81 |  | 73 | 104 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2513-6_0_4_line_82 |  | 73 | 98 | 0.013063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2513-6_0_4_line_83 |  | 74 | 79 | 0.0074556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2513-6_0_4_line_84 |  | 75 | 139 | 0.0013462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2513-6_0_4_line_85 |  | 77 | 119 | 0.0072135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2513-6_0_4_line_86 |  | 80 | 81 | 0.012081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2513-6_0_4_line_87 |  | 81 | 82 | 0.0095178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2513-6_0_4_line_88 |  | 82 | 83 | 0.007174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2513-6_0_4_line_89 |  | 82 | 84 | 0.021994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2513-6_0_4_line_90 |  | 83 | 85 | 0.018691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2513-6_0_4_line_91 |  | 85 | 91 | 0.035058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2513-6_0_4_line_92 |  | 86 | 87 | 0.036377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2513-6_0_4_line_93 |  | 86 | 88 | 0.025193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2513-6_0_4_line_94 |  | 87 | 89 | 0.036771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2513-6_0_4_line_95 |  | 88 | 90 | 0.035764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2513-6_0_4_line_96 |  | 89 | 123 | 0.0078701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2513-6_0_4_line_97 |  | 90 | 120 | 0.014859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2513-6_0_4_line_98 |  | 91 | 92 | 0.017917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2513-6_0_4_line_99 |  | 92 | 144 | 0.007288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_2513-6_0_4_line_100 |  | 93 | 94 | 0.020119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2513-6_0_4_line_101 |  | 94 | 95 | 0.0057736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2513-6_0_4_line_102 |  | 95 | 96 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2513-6_0_4_line_103 |  | 96 | 97 | 0.0047636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2513-6_0_4_line_104 |  | 97 | 133 | 0.019074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2513-6_0_4_line_105 |  | 98 | 103 | 0.0087915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2513-6_0_4_line_106 |  | 99 | 100 | 0.0091153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2513-6_0_4_line_107 |  | 100 | 101 | 0.0076327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2513-6_0_4_line_108 |  | 100 | 102 | 0.021511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2513-6_0_4_line_109 |  | 101 | 103 | 0.014751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2513-6_0_4_line_110 |  | 105 | 106 | 0.0015376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2513-6_0_4_line_111 |  | 105 | 107 | 0.019666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2513-6_0_4_line_112 |  | 106 | 108 | 0.023908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2513-6_0_4_line_113 |  | 107 | 109 | 0.0017507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2513-6_0_4_line_114 |  | 108 | 110 | 0.0051506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2513-6_0_4_line_115 |  | 109 | 111 | 0.017686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2513-6_0_4_line_116 |  | 110 | 112 | 0.0089527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2513-6_0_4_line_117 |  | 111 | 113 | 0.006736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2513-6_0_4_line_118 |  | 112 | 138 | 0.005296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2513-6_0_4_line_119 |  | 113 | 137 | 0.010228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2513-6_0_4_line_120 |  | 114 | 115 | 0.0048116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2513-6_0_4_line_121 |  | 115 | 116 | 0.022204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2513-6_0_4_line_122 |  | 116 | 117 | 0.012124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2513-6_0_4_line_123 |  | 116 | 118 | 0.035155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2513-6_0_4_line_124 |  | 118 | 119 | 0.009588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2513-6_0_4_line_125 |  | 120 | 121 | 0.018009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2513-6_0_4_line_126 |  | 121 | 122 | 0.014306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2513-6_0_4_line_127 |  | 122 | 134 | 0.00066007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2513-6_0_4_line_128 |  | 123 | 148 | 0.02283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2513-6_0_4_line_129 |  | 123 | 149 | 0.012046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2513-6_0_4_line_130 |  | 124 | 125 | 0.0027841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2513-6_0_4_line_131 |  | 124 | 126 | 0.020142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2513-6_0_4_line_132 |  | 125 | 127 | 0.0071036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2513-6_0_4_line_133 |  | 126 | 128 | 0.0069188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2513-6_0_4_line_134 |  | 128 | 129 | 0.011682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2513-6_0_4_line_135 |  | 128 | 130 | 0.015393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2513-6_0_4_line_136 |  | 129 | 131 | 0.013229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2513-6_0_4_line_137 |  | 130 | 132 | 0.021981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2513-6_0_4_line_138 |  | 132 | 142 | 0.0063711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2513-6_0_4_line_139 |  | 134 | 135 | 0.019421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2513-6_0_4_line_140 |  | 135 | 136 | 0.00059259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2513-6_0_4_line_141 |  | 136 | 137 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2513-6_0_4_line_142 |  | 139 | 140 | 0.027876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2513-6_0_4_line_143 |  | 140 | 146 | 0.0037497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2513-6_0_4_line_144 |  | 142 | 143 | 0.017596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
145 | LV_2513-6_0_4_line_145 |  | 142 | 144 | 0.01368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
146 | LV_2513-6_0_4_line_146 |  | 143 | 145 | 0.0088066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
147 | LV_2513-6_0_4_line_147 |  | 145 | 149 | 0.021913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2513-6_0_4_line_148 |  | 146 | 147 | 0.017783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2513-6_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 150 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2609652.7936 | 1226324.2821 | 2609636.2332 | 1226296.6453
1 | 2609655.1837 | 1226328.2709 | 2609652.7936 | 1226324.2821
2 | 2609623.2026 | 1226274.8992 | 2609636.2332 | 1226296.6453
3 | 2609655.1837 | 1226328.2709 | 2609656.9978 | 1226331.2978 | 2609663.6825 | 1226339.2082
4 | 2609655.1837 | 1226328.2709 | 2609644.7596 | 1226334.5415
5 | 2609623.2026 | 1226274.8992 | 2609607.2025 | 1226285.5837
6 | 2609623.2026 | 1226274.8992 | 2609634.5606 | 1226267.2665
7 | 2609663.6825 | 1226339.2082 | 2609667.7698 | 1226344.0449 | 2609674.141 | 1226350.1056
8 | 2609640.475 | 1226337.119 | 2609644.7596 | 1226334.5415
9 | 2609677.6087 | 1226400.9062 | 2609669.0025 | 1226392.5977 | 2609661.5434 | 1226388.7612 | 2609646.0874 | 1226386.9135
10 | 2609677.6087 | 1226400.9062 | 2609692.2862 | 1226415.076
11 | 2609677.6087 | 1226400.9062 | 2609682.8137 | 1226358.3554
12 | 2609598.6048 | 1226291.325 | 2609607.2025 | 1226285.5837
13 | 2609652.6698 | 1226255.0969 | 2609634.5606 | 1226267.2665
14 | 2609652.7733 | 1226220.4609 | 2609653.433 | 1226223.4073
15 | 2609653.433 | 1226223.4073 | 2609660.4033 | 1226249.8999
16 | 2609647.3024 | 1226196.025 | 2609652.7733 | 1226220.4609
17 | 2609660.4033 | 1226249.8999 | 2609652.6698 | 1226255.0969
18 | 2609660.4033 | 1226249.8999 | 2609664 | 1226247.3042 | 2609678.4405 | 1226236.8749
19 | 2609660.4033 | 1226249.8999 | 2609670.1657 | 1226270.7548
20 | 2609677.1364 | 1226352.9549 | 2609674.141 | 1226350.1056
21 | 2609640.475 | 1226337.119 | 2609638.1523 | 1226338.5162 | 2609628.6934 | 1226341.8269
22 | 2609598.6048 | 1226291.325 | 2609602.8658 | 1226308.9788
23 | 2609682.8137 | 1226358.3554 | 2609677.1364 | 1226352.9549
24 | 2609672.085 | 1226274.855 | 2609670.1657 | 1226270.7548
25 | 2609675.804 | 1226282.7997 | 2609672.085 | 1226274.855
26 | 2609697.0989 | 1226223.3992 | 2609678.4405 | 1226236.8749
27 | 2609697.0989 | 1226223.3992 | 2609745.2398 | 1226250.7775
28 | 2609697.0989 | 1226223.3992 | 2609733.4035 | 1226185.9027
29 | 2609523.8362 | 1226312.5141 | 2609521.5478 | 1226296.3605 | 2609518.663 | 1226284.8573
30 | 2609524.4858 | 1226317.0996 | 2609523.8362 | 1226312.5141
31 | 2609512.93 | 1226261.2354 | 2609516.901 | 1226277.8311 | 2609518.663 | 1226284.8573
32 | 2609524.4858 | 1226317.0996 | 2609520.2021 | 1226327.6434 | 2609513.2988 | 1226336.3932 | 2609497.8055 | 1226349.8323
33 | 2609524.4858 | 1226317.0996 | 2609534.1731 | 1226320.7455
34 | 2609512.93 | 1226261.2354 | 2609511.7597 | 1226256.3447
35 | 2609487.0849 | 1226359.1316 | 2609497.8055 | 1226349.8323
36 | 2609543.3551 | 1226328.2028 | 2609534.4236 | 1226320.8398 | 2609534.1731 | 1226320.7455
37 | 2609507.3657 | 1226237.9811 | 2609511.7597 | 1226256.3447
38 | 2609487.0849 | 1226359.1316 | 2609502.5234 | 1226376.5203
39 | 2609487.0849 | 1226359.1316 | 2609474.7986 | 1226369.0699
40 | 2609543.3551 | 1226328.2028 | 2609551.9956 | 1226337.4085
41 | 2609507.3657 | 1226237.9811 | 2609507.2035 | 1226237.303
42 | 2609502.5234 | 1226376.5203 | 2609538.1357 | 1226402.7272
43 | 2609454.5624 | 1226385.4388 | 2609474.7986 | 1226369.0699
44 | 2609551.9956 | 1226337.4085 | 2609577.6511 | 1226332.4489
45 | 2609441.9225 | 1226395.6632 | 2609454.5624 | 1226385.4388
46 | 2609437.5175 | 1226399.2263 | 2609441.9225 | 1226395.6632
47 | 2609437.5175 | 1226399.2263 | 2609424.4129 | 1226409.8265
48 | 2609424.4129 | 1226409.8265 | 2609415.9185 | 1226416.6976 | 2609413.143 | 1226420.1945
49 | 2609538.1357 | 1226402.7272 | 2609539.9868 | 1226404.9452
50 | 2609411.2241 | 1226422.6123 | 2609413.143 | 1226420.1945
51 | 2609497.1527 | 1226473.7952 | 2609496.5889 | 1226474.2692
52 | 2609497.1527 | 1226473.7952 | 2609504.1257 | 1226467.9337
53 | 2609511.342 | 1226461.8677 | 2609504.1257 | 1226467.9337
54 | 2609733.4035 | 1226185.9027 | 2609740.5233 | 1226162.7073
55 | 2609733.4035 | 1226185.9027 | 2609756.4541 | 1226191.2144
56 | 2609647.3024 | 1226196.025 | 2609635.0538 | 1226187.6149
57 | 2609635.0538 | 1226187.6149 | 2609626.528 | 1226181.7609 | 2609620.1462 | 1226180.216
58 | 2609317.6192 | 1226306.4535 | 2609307.5961 | 1226287.7342
59 | 2609329.9104 | 1226323.9562 | 2609321.577 | 1226313.8452 | 2609317.6192 | 1226306.4535
60 | 2609298.7413 | 1226271.1967 | 2609307.5961 | 1226287.7342
61 | 2609342.9943 | 1226339.831 | 2609329.9104 | 1226323.9562
62 | 2609298.7413 | 1226271.1967 | 2609286.2249 | 1226247.8208
63 | 2609355.414 | 1226354.8999 | 2609342.9943 | 1226339.831
64 | 2609355.414 | 1226354.8999 | 2609371.3098 | 1226373.2089
65 | 2609355.414 | 1226354.8999 | 2609366.8134 | 1226354.4952 | 2609373.8164 | 1226349.9759
66 | 2609378.3597 | 1226381.3291 | 2609371.3098 | 1226373.2089
67 | 2609388.1505 | 1226340.7253 | 2609373.8164 | 1226349.9759
68 | 2609582.1999 | 1226440.4975 | 2609587.3153 | 1226434.4145
69 | 2609574.7779 | 1226446.6337 | 2609582.1999 | 1226440.4975
70 | 2609574.7779 | 1226446.6337 | 2609555.7205 | 1226423.7981
71 | 2609574.7779 | 1226446.6337 | 2609561.4549 | 1226457.6479
72 | 2609555.7205 | 1226423.7981 | 2609552.8113 | 1226420.3121
73 | 2609553.0206 | 1226464.6206 | 2609561.4549 | 1226457.6479
74 | 2609544.7638 | 1226410.6693 | 2609552.8113 | 1226420.3121
75 | 2609553.0206 | 1226464.6206 | 2609544.8787 | 1226471.3523
76 | 2609553.0206 | 1226464.6206 | 2609538.9675 | 1226446.7433 | 2609534.6417 | 1226445.658 | 2609529.7749 | 1226446.3729 | 2609527.2659 | 1226448.4819
77 | 2609589.2967 | 1226377.1494 | 2609589.2967 | 1226377.1494 | 2609586.4935 | 1226374.1628
78 | 2609586.4935 | 1226374.1628 | 2609587.2187 | 1226341.3431
79 | 2609530.024 | 1226483.6343 | 2609544.8787 | 1226471.3523
80 | 2609511.342 | 1226461.8677 | 2609527.2659 | 1226448.4819
81 | 2609607.7707 | 1226346.2831 | 2609598.7352 | 1226347.1024 | 2609591.6439 | 1226345.4567 | 2609587.2187 | 1226341.3431
82 | 2609577.6511 | 1226332.4489 | 2609587.2187 | 1226341.3431
83 | 2609544.7638 | 1226410.6693 | 2609539.9868 | 1226404.9452
84 | 2609693.2547 | 1226416.0111 | 2609692.2862 | 1226415.076
85 | 2609613.1352 | 1226178.5188 | 2609620.1462 | 1226180.216
86 | 2609479.413 | 1226167.8797 | 2609490.2432 | 1226173.2336
87 | 2609498.4526 | 1226178.0321 | 2609492.5996 | 1226174.3985 | 2609490.2432 | 1226173.2336
88 | 2609498.4526 | 1226178.0321 | 2609502.7333 | 1226183.7978
89 | 2609498.4526 | 1226178.0321 | 2609500.7236 | 1226174.9784 | 2609499.2604 | 1226170.4623 | 2609505.6448 | 1226158.634
90 | 2609502.7333 | 1226183.7978 | 2609503.6303 | 1226191.6594 | 2609504.0347 | 1226202.4299
91 | 2609507.2035 | 1226237.303 | 2609504.6338 | 1226218.3878 | 2609504.0347 | 1226202.4299
92 | 2609377.6986 | 1226150.0922 | 2609406.4401 | 1226172.391
93 | 2609377.6986 | 1226150.0922 | 2609358.0873 | 1226165.9065
94 | 2609406.4401 | 1226172.391 | 2609435.4924 | 1226194.9309
95 | 2609330.2474 | 1226188.3563 | 2609358.0873 | 1226165.9065
96 | 2609441.7106 | 1226199.7552 | 2609435.4924 | 1226194.9309
97 | 2609318.6807 | 1226197.6836 | 2609330.2474 | 1226188.3563
98 | 2609507.2035 | 1226237.303 | 2609489.913 | 1226241.9987
99 | 2609482.8798 | 1226243.9088 | 2609489.913 | 1226241.9987
100 | 2609369.725 | 1226474.8977 | 2609382.233 | 1226459.1387
101 | 2609385.8223 | 1226454.6164 | 2609382.233 | 1226459.1387
102 | 2609385.8223 | 1226454.6164 | 2609396.4044 | 1226441.2838
103 | 2609399.3659 | 1226437.5526 | 2609396.4044 | 1226441.2838
104 | 2609399.3659 | 1226437.5526 | 2609411.2241 | 1226422.6123
105 | 2609577.6511 | 1226332.4489 | 2609584.8853 | 1226327.4533
106 | 2609605.0045 | 1226317.8397 | 2609602.8658 | 1226308.9788
107 | 2609605.0045 | 1226317.8397 | 2609597.9673 | 1226320.7955
108 | 2609626.509 | 1226316.1176 | 2609605.0045 | 1226317.8397
109 | 2609597.9673 | 1226320.7955 | 2609589.184 | 1226324.4849 | 2609584.8853 | 1226327.4533
110 | 2609388.5789 | 1226304.161 | 2609389.4227 | 1226305.4464
111 | 2609388.5789 | 1226304.161 | 2609377.7868 | 1226287.7211
112 | 2609399.3381 | 1226326.2268 | 2609399.8115 | 1226321.2718 | 2609389.4227 | 1226305.4464
113 | 2609376.826 | 1226286.2576 | 2609377.7868 | 1226287.7211
114 | 2609399.3381 | 1226326.2268 | 2609398.8483 | 1226331.354
115 | 2609367.1201 | 1226271.4724 | 2609376.826 | 1226286.2576
116 | 2609398.8483 | 1226331.354 | 2609398.8483 | 1226331.354 | 2609392.2679 | 1226337.4244
117 | 2609367.1201 | 1226271.4724 | 2609363.4236 | 1226265.8413
118 | 2609388.1505 | 1226340.7253 | 2609389.9452 | 1226339.5671 | 2609392.2679 | 1226337.4244
119 | 2609357.8106 | 1226257.2911 | 2609363.4236 | 1226265.8413
120 | 2609546.4533 | 1226176.138 | 2609541.6439 | 1226176.2815
121 | 2609568.6479 | 1226175.4756 | 2609546.4533 | 1226176.138
122 | 2609568.6479 | 1226175.4756 | 2609572.0949 | 1226163.8522
123 | 2609568.6479 | 1226175.4756 | 2609586.6935 | 1226175.8603 | 2609603.7886 | 1226176.465
124 | 2609613.1352 | 1226178.5188 | 2609604.7992 | 1226176.5008 | 2609603.7886 | 1226176.465
125 | 2609318.6807 | 1226197.6836 | 2609328.5635 | 1226212.7383
126 | 2609336.4142 | 1226224.6974 | 2609328.5635 | 1226212.7383
127 | 2609336.7764 | 1226225.2492 | 2609336.4142 | 1226224.6974
128 | 2609424.3011 | 1226214.2474 | 2609438.0498 | 1226204.5967 | 2609441.7106 | 1226199.7552
129 | 2609441.7106 | 1226199.7552 | 2609445.5031 | 1226202.6962 | 2609449.7257 | 1226208.5855
130 | 2609446.6035 | 1226290.8498 | 2609448.1395 | 1226293.1718
131 | 2609446.6035 | 1226290.8498 | 2609435.491 | 1226274.0502
132 | 2609452.0585 | 1226299.0965 | 2609448.1395 | 1226293.1718
133 | 2609431.6739 | 1226268.2796 | 2609435.491 | 1226274.0502
134 | 2609431.6739 | 1226268.2796 | 2609425.0605 | 1226258.6502
135 | 2609431.6739 | 1226268.2796 | 2609443.9481 | 1226258.9902
136 | 2609417.5712 | 1226247.7454 | 2609425.0605 | 1226258.6502
137 | 2609443.9481 | 1226258.9902 | 2609448.2389 | 1226255.7428 | 2609463.7319 | 1226249.7818
138 | 2609469.6781 | 1226247.494 | 2609463.7319 | 1226249.7818
139 | 2609336.7764 | 1226225.2492 | 2609347.4345 | 1226241.4849
140 | 2609347.7597 | 1226241.9802 | 2609347.4345 | 1226241.4849
141 | 2609357.8106 | 1226257.2911 | 2609347.7597 | 1226241.9802
142 | 2609713.3095 | 1226435.3723 | 2609693.2547 | 1226416.0111
143 | 2609713.3095 | 1226435.3723 | 2609716.0072 | 1226437.9767
144 | 2609469.6781 | 1226247.494 | 2609459.9071 | 1226232.8599
145 | 2609469.6781 | 1226247.494 | 2609482.8798 | 1226243.9088
146 | 2609459.9071 | 1226232.8599 | 2609455.0168 | 1226225.5358
147 | 2609449.7257 | 1226208.5855 | 2609459.2291 | 1226221.8402 | 2609455.0168 | 1226225.5358 | 2609455.0168 | 1226225.5358
148 | 2609728.8266 | 1226450.3012 | 2609721.0036 | 1226442.8002 | 2609716.0072 | 1226437.9767

## bus_geodata
| x | y | coords
0 | 2609652.7936 | 1226324.2821
1 | 2609636.2332 | 1226296.6453
2 | 2609655.1837 | 1226328.2709
3 | 2609623.2026 | 1226274.8992
4 | 2609663.6825 | 1226339.2082
5 | 2609644.7596 | 1226334.5415
6 | 2609646.0874 | 1226386.9135
7 | 2609677.6087 | 1226400.9062
8 | 2609607.2025 | 1226285.5837
9 | 2609634.5606 | 1226267.2665
10 | 2609653.433 | 1226223.4073
11 | 2609652.7733 | 1226220.4609
12 | 2609660.4033 | 1226249.8999
13 | 2609674.141 | 1226350.1056
14 | 2609640.475 | 1226337.119
15 | 2609598.6048 | 1226291.325
16 | 2609652.6698 | 1226255.0969
17 | 2609677.1364 | 1226352.9549
18 | 2609628.6934 | 1226341.8269
19 | 2609672.085 | 1226274.855
20 | 2609670.1657 | 1226270.7548
21 | 2609675.804 | 1226282.7997
22 | 2609678.4405 | 1226236.8749
23 | 2609697.0989 | 1226223.3992
24 | 2609523.8362 | 1226312.5141
25 | 2609518.663 | 1226284.8573
26 | 2609524.4858 | 1226317.0996
27 | 2609512.93 | 1226261.2354
28 | 2609497.8055 | 1226349.8323
29 | 2609534.1731 | 1226320.7455
30 | 2609511.7597 | 1226256.3447
31 | 2609487.0849 | 1226359.1316
32 | 2609543.3551 | 1226328.2028
33 | 2609507.3657 | 1226237.9811
34 | 2609502.5234 | 1226376.5203
35 | 2609474.7986 | 1226369.0699
36 | 2609551.9956 | 1226337.4085
37 | 2609454.5624 | 1226385.4388
38 | 2609441.9225 | 1226395.6632
39 | 2609437.5175 | 1226399.2263
40 | 2609424.4129 | 1226409.8265
41 | 2609538.1357 | 1226402.7272
42 | 2609413.143 | 1226420.1945
43 | 2609497.1527 | 1226473.7952
44 | 2609496.5889 | 1226474.2692
45 | 2609504.1257 | 1226467.9337
46 | 2609740.5233 | 1226162.7073
47 | 2609733.4035 | 1226185.9027
48 | 2609756.4541 | 1226191.2144
49 | 2609745.2398 | 1226250.7775
50 | 2609647.3024 | 1226196.025
51 | 2609635.0538 | 1226187.6149
52 | 2609317.6192 | 1226306.4535
53 | 2609307.5961 | 1226287.7342
54 | 2609329.9104 | 1226323.9562
55 | 2609298.7413 | 1226271.1967
56 | 2609342.9943 | 1226339.831
57 | 2609286.2249 | 1226247.8208
58 | 2609355.414 | 1226354.8999
59 | 2609371.3098 | 1226373.2089
60 | 2609373.8164 | 1226349.9759
61 | 2609587.3153 | 1226434.4145
62 | 2609582.1999 | 1226440.4975
63 | 2609574.7779 | 1226446.6337
64 | 2609555.7205 | 1226423.7981
65 | 2609561.4549 | 1226457.6479
66 | 2609552.8113 | 1226420.3121
67 | 2609553.0206 | 1226464.6206
68 | 2609589.2967 | 1226377.1494
69 | 2609586.4935 | 1226374.1628
70 | 2609544.8787 | 1226471.3523
71 | 2609527.2659 | 1226448.4819
72 | 2609530.024 | 1226483.6343
73 | 2609587.2187 | 1226341.3431
74 | 2609544.7638 | 1226410.6693
75 | 2609692.2862 | 1226415.076
76 | 2609682.8137 | 1226358.3554
77 | 2609620.1462 | 1226180.216
78 | 2609511.342 | 1226461.8677
79 | 2609539.9868 | 1226404.9452
80 | 2609479.413 | 1226167.8797
81 | 2609490.2432 | 1226173.2336
82 | 2609498.4526 | 1226178.0321
83 | 2609502.7333 | 1226183.7978
84 | 2609505.6448 | 1226158.634
85 | 2609504.0347 | 1226202.4299
86 | 2609377.6986 | 1226150.0922
87 | 2609406.4401 | 1226172.391
88 | 2609358.0873 | 1226165.9065
89 | 2609435.4924 | 1226194.9309
90 | 2609330.2474 | 1226188.3563
91 | 2609507.2035 | 1226237.303
92 | 2609489.913 | 1226241.9987
93 | 2609369.725 | 1226474.8977
94 | 2609382.233 | 1226459.1387
95 | 2609385.8223 | 1226454.6164
96 | 2609396.4044 | 1226441.2838
97 | 2609399.3659 | 1226437.5526
98 | 2609577.6511 | 1226332.4489
99 | 2609602.8658 | 1226308.9788
100 | 2609605.0045 | 1226317.8397
101 | 2609597.9673 | 1226320.7955
102 | 2609626.509 | 1226316.1176
103 | 2609584.8853 | 1226327.4533
104 | 2609607.7707 | 1226346.2831
105 | 2609388.5789 | 1226304.161
106 | 2609389.4227 | 1226305.4464
107 | 2609377.7868 | 1226287.7211
108 | 2609399.3381 | 1226326.2268
109 | 2609376.826 | 1226286.2576
110 | 2609398.8483 | 1226331.354
111 | 2609367.1201 | 1226271.4724
112 | 2609392.2679 | 1226337.4244
113 | 2609363.4236 | 1226265.8413
114 | 2609541.6439 | 1226176.2815
115 | 2609546.4533 | 1226176.138
116 | 2609568.6479 | 1226175.4756
117 | 2609572.0949 | 1226163.8522
118 | 2609603.7886 | 1226176.465
119 | 2609613.1352 | 1226178.5188
120 | 2609318.6807 | 1226197.6836
121 | 2609328.5635 | 1226212.7383
122 | 2609336.4142 | 1226224.6974
123 | 2609441.7106 | 1226199.7552
124 | 2609446.6035 | 1226290.8498
125 | 2609448.1395 | 1226293.1718
126 | 2609435.491 | 1226274.0502
127 | 2609452.0585 | 1226299.0965
128 | 2609431.6739 | 1226268.2796
129 | 2609425.0605 | 1226258.6502
130 | 2609443.9481 | 1226258.9902
131 | 2609417.5712 | 1226247.7454
132 | 2609463.7319 | 1226249.7818
133 | 2609411.2241 | 1226422.6123
134 | 2609336.7764 | 1226225.2492
135 | 2609347.4345 | 1226241.4849
136 | 2609347.7597 | 1226241.9802
137 | 2609357.8106 | 1226257.2911
138 | 2609388.1505 | 1226340.7253
139 | 2609693.2547 | 1226416.0111
140 | 2609713.3095 | 1226435.3723
141 | 2609378.3597 | 1226381.3291
142 | 2609469.6781 | 1226247.494
143 | 2609459.9071 | 1226232.8599
144 | 2609482.8798 | 1226243.9088
145 | 2609455.0168 | 1226225.5358
146 | 2609716.0072 | 1226437.9767
147 | 2609728.8266 | 1226450.3012
148 | 2609424.3011 | 1226214.2474
149 | 2609449.7257 | 1226208.5855
150 | 2609524.4858 | 1226317.0996

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98328 | -0.32155 | 0.0019793 | 0.00049605
1 | 0.98413 | -0.30499 | 0.002344 | 0.00058747
2 | 0.98317 | -0.32378 | 0 | 0
3 | 0.98485 | -0.29091 | 0 | 0
4 | 0.98289 | -0.32923 | 0.0014804 | 0.00037103
5 | 0.98312 | -0.32483 | 0.0016493 | 0.00041334
6 | 0.98197 | -0.34727 | 0.001875 | 0.00046992
7 | 0.98203 | -0.34605 | 0.0011763 | 0.0002948
8 | 0.98614 | -0.26596 | 0.0094573 | 0.0023702
9 | 0.98433 | -0.30109 | 0.001381 | 0.00034611
10 | 0.98268 | -0.33328 | 0.0024442 | 0.00061257
11 | 0.98263 | -0.33426 | 0.00162 | 0.00040601
12 | 0.9832 | -0.32324 | 0 | 0
13 | 0.98261 | -0.33477 | 0.0014885 | 0.00037304
14 | 0.9831 | -0.32511 | 0.0014829 | 0.00037165
15 | 0.98692 | -0.25083 | 0 | 0
16 | 0.98353 | -0.3168 | 0.0016022 | 0.00040154
17 | 0.98254 | -0.33617 | 0.0022167 | 0.00055555
18 | 0.98308 | -0.32549 | 0.001654 | 0.00041453
19 | 0.98302 | -0.32662 | 0.0020202 | 0.0005063
20 | 0.98305 | -0.32618 | 0.0017107 | 0.00042875
21 | 0.983 | -0.32715 | 0.0033439 | 0.00083805
22 | 0.98297 | -0.32766 | 0.0018992 | 0.00047598
23 | 0.98278 | -0.33144 | 0 | 0
24 | 0.99772 | -0.043352 | 0.0035356 | 0.0008861
25 | 1 | 0 | -0.3398 | -0.086374
26 | 0.99735 | -0.050354 | 0 | 0
27 | 0.99823 | -0.033489 | 0.0040435 | 0.0010134
28 | 0.99489 | -0.097716 | 0.0034526 | 0.00086531
29 | 0.9963 | -0.070321 | 0.0046888 | 0.0011751
30 | 0.99787 | -0.040254 | 0.002942 | 0.00073732
31 | 0.99412 | -0.11252 | 0 | 0
32 | 0.99516 | -0.09224 | 0 | 0
33 | 0.99656 | -0.065211 | 0.0022447 | 0.00056257
34 | 0.99357 | -0.12316 | 0.00183 | 0.00045865
35 | 0.99364 | -0.1218 | 0.0038871 | 0.0009742
36 | 0.99393 | -0.11566 | 0.0030898 | 0.00077437
37 | 0.99294 | -0.1353 | 0.0034251 | 0.00085841
38 | 0.99256 | -0.14276 | 0.0011752 | 0.00029454
39 | 0.99243 | -0.14525 | 0.0016957 | 0.00042499
40 | 0.99207 | -0.15213 | 0.0043328 | 0.0010859
41 | 0.9926 | -0.142 | 0.0013549 | 0.00033957
42 | 0.99181 | -0.15724 | 0.00053764 | 0.00013474
43 | 0.99091 | -0.17469 | 0.00085308 | 0.0002138
44 | 0.99091 | -0.17471 | 0.00194 | 0.00048621
45 | 0.99093 | -0.17424 | 0.0011776 | 0.00029514
46 | 0.9823 | -0.34072 | 0.0039577 | 0.0009919
47 | 0.98239 | -0.33899 | 0 | 0
48 | 0.9823 | -0.34072 | 0.0040549 | 0.0010162
49 | 0.98272 | -0.33252 | 0.0010843 | 0.00027175
50 | 0.98226 | -0.3416 | 0 | 0
51 | 0.98203 | -0.34597 | 0.0013961 | 0.0003499
52 | 0.97048 | -0.5703 | 0.0036211 | 0.00090754
53 | 0.97035 | -0.5728 | 0.0015015 | 0.00037631
54 | 0.97068 | -0.56632 | 0.0033159 | 0.00083104
55 | 0.97026 | -0.57449 | 0.0017289 | 0.0004333
56 | 0.97093 | -0.56126 | 0.002332 | 0.00058445
57 | 0.97019 | -0.57603 | 0.0031378 | 0.00078641
58 | 0.97122 | -0.55562 | 0 | 0
59 | 0.9711 | -0.5579 | 0.0027094 | 0.00067903
60 | 0.9716 | -0.54805 | 0.0026361 | 0.00066067
61 | 0.99165 | -0.16039 | 0.0018784 | 0.00047076
62 | 0.99166 | -0.16013 | 0 | 0
63 | 0.99168 | -0.15981 | 0 | 0
64 | 0.9921 | -0.15162 | 0.0018004 | 0.00045122
65 | 0.99146 | -0.164 | 0.0019033 | 0.00047702
66 | 0.99217 | -0.15022 | 0.0018167 | 0.00045531
67 | 0.99134 | -0.16628 | 0 | 0
68 | 0.99104 | -0.17121 | 0.0039185 | 0.00098208
69 | 0.99106 | -0.17093 | 0.0051052 | 0.0012795
70 | 0.99131 | -0.16695 | 0.0016178 | 0.00040546
71 | 0.99108 | -0.17143 | 0.0023975 | 0.00060088
72 | 0.99127 | -0.16761 | 0.00194 | 0.00048621
73 | 0.99133 | -0.16567 | 0.0013282 | 0.00033288
74 | 0.99239 | -0.14596 | 0.0020858 | 0.00052276
75 | 0.98191 | -0.34851 | 0.0011772 | 0.00029503
76 | 0.98242 | -0.33852 | 0.0068625 | 0.0017199
77 | 0.9818 | -0.3505 | 0.0050141 | 0.0012567
78 | 0.99097 | -0.17357 | 0.0018315 | 0.00045902
79 | 0.99254 | -0.14316 | 0.0014986 | 0.00037558
80 | 0.9958 | -0.079842 | 0.0026318 | 0.0006596
81 | 0.99583 | -0.079283 | 0.0018612 | 0.00046646
82 | 0.99587 | -0.078532 | 0 | 0
83 | 0.99591 | -0.077756 | 0 | 0
84 | 0.99584 | -0.079173 | 0.0016597 | 0.00041596
85 | 0.99601 | -0.075734 | 0.0094612 | 0.0023712
86 | 0.98416 | -0.30238 | 0 | 0
87 | 0.98669 | -0.25362 | 0.0066658 | 0.0016706
88 | 0.98241 | -0.3363 | 0.0080701 | 0.0020226
89 | 0.98948 | -0.20022 | 0.0019684 | 0.00049332
90 | 0.98019 | -0.37941 | 0.0033625 | 0.00084273
91 | 0.99651 | -0.06612 | 0 | 0
92 | 0.99541 | -0.087049 | 0.0041978 | 0.0010521
93 | 0.99123 | -0.16843 | 0.0028044 | 0.00070284
94 | 0.99128 | -0.16743 | 0.0031613 | 0.00079229
95 | 0.99131 | -0.16682 | 0.0027684 | 0.00069382
96 | 0.99145 | -0.16418 | 0.0010098 | 0.00025309
97 | 0.99149 | -0.16336 | 0.0053952 | 0.0013522
98 | 0.99147 | -0.16289 | 0.0025378 | 0.00063604
99 | 0.98829 | -0.2243 | 0.0016359 | 0.00040999
100 | 0.98899 | -0.21075 | 0 | 0
101 | 0.98959 | -0.1992 | 0.0013253 | 0.00033214
102 | 0.98895 | -0.21138 | 0.0016366 | 0.00041017
103 | 0.99076 | -0.17657 | 0.0013278 | 0.00033277
104 | 0.99129 | -0.16633 | 0.001652 | 0.00041402
105 | 0.97329 | -0.51462 | 0.0033986 | 0.00085177
106 | 0.97324 | -0.51562 | 0.002075 | 0.00052003
107 | 0.974 | -0.5006 | 0.0026264 | 0.00065824
108 | 0.9725 | -0.53028 | 0.0018618 | 0.0004666
109 | 0.97407 | -0.49927 | 0.0017679 | 0.00044307
110 | 0.97235 | -0.53326 | 0.002116 | 0.00053032
111 | 0.97478 | -0.48526 | 0.0020258 | 0.00050772
112 | 0.9721 | -0.5381 | 0.002842 | 0.00071228
113 | 0.97507 | -0.47967 | 0.0026101 | 0.00065415
114 | 0.98133 | -0.35986 | 0.00232 | 0.00058144
115 | 0.98134 | -0.35966 | 0.0034197 | 0.00085706
116 | 0.98145 | -0.35735 | 0 | 0
117 | 0.98144 | -0.35755 | 0.00088035 | 0.00022064
118 | 0.98167 | -0.35314 | 0.0011941 | 0.00029928
119 | 0.98174 | -0.35179 | 0.002019 | 0.00050601
120 | 0.97932 | -0.39648 | 0 | 0
121 | 0.97826 | -0.4172 | 0.0038233 | 0.0009582
122 | 0.97746 | -0.43269 | 0.0016746 | 0.00041969
123 | 0.99009 | -0.18856 | 0 | 0
124 | 0.9932 | -0.12956 | 0.0030523 | 0.00076497
125 | 0.99318 | -0.12986 | 0.0018587 | 0.00046584
126 | 0.99336 | -0.12629 | 0.0018338 | 0.00045958
127 | 0.99315 | -0.13039 | 0.0042615 | 0.001068
128 | 0.99343 | -0.12495 | 0 | 0
129 | 0.99337 | -0.12613 | 0.0018839 | 0.00047214
130 | 0.99367 | -0.12039 | 0.0031307 | 0.00078463
131 | 0.99333 | -0.12704 | 0.0038653 | 0.00096874
132 | 0.99407 | -0.11268 | 0.0031101 | 0.00077946
133 | 0.99176 | -0.15824 | 0.0030656 | 0.0007683
134 | 0.97743 | -0.43339 | 0.0020017 | 0.00050168
135 | 0.97642 | -0.45316 | 0.0029501 | 0.00073938
136 | 0.97639 | -0.45373 | 0.002107 | 0.00052805
137 | 0.97552 | -0.47071 | 0.0028816 | 0.00072219
138 | 0.97197 | -0.54069 | 0.0030957 | 0.00077585
139 | 0.9819 | -0.34864 | 0.00097617 | 0.00024465
140 | 0.98178 | -0.35092 | 0.0011051 | 0.00027697
141 | 0.97108 | -0.55838 | 0.0023912 | 0.00059928
142 | 0.9942 | -0.11009 | 0 | 0
143 | 0.99339 | -0.12557 | 0.0040655 | 0.0010189
144 | 0.99498 | -0.095306 | 0.006063 | 0.0015195
145 | 0.993 | -0.13301 | 0.0024414 | 0.00061187
146 | 0.98177 | -0.35115 | 0.0021383 | 0.00053591
147 | 0.98175 | -0.35156 | 0.0012719 | 0.00031876
148 | 0.98993 | -0.1915 | 0.0072556 | 0.0018184
149 | 0.9911 | -0.16918 | 0.0026166 | 0.00065579
150 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.028556 | -0.0071625 | 0.028578 | 0.0071765 | 2.2564e-05 | 1.4032e-05 | 0.043216 | 0.043215 | 0.043216 | 0.98328 | -0.32155 | 0.98413 | -0.30499 | 11.8724
1 | 0.026576 | 0.0066665 | -0.026574 | -0.0066647 | 2.8209e-06 | 1.7464e-06 | 0.04022 | 0.04022 | 0.04022 | 0.98328 | -0.32155 | 0.98317 | -0.32378 | 11.0496
2 | -0.030922 | -0.007764 | 0.030943 | 0.007777 | 2.0786e-05 | 1.2981e-05 | 0.04676 | 0.04676 | 0.04676 | 0.98413 | -0.30499 | 0.98485 | -0.29091 | 12.8461
3 | 0.021787 | 0.0054654 | -0.021781 | -0.0054619 | 5.6623e-06 | 3.4479e-06 | 0.032976 | 0.032976 | 0.032976 | 0.98317 | -0.32378 | 0.98289 | -0.32923 | 9.0594
4 | 0.0047865 | 0.0011993 | -0.0047862 | -0.0011993 | 2.394e-07 | -1.0455e-09 | 0.0072442 | 0.0072442 | 0.0072442 | 0.98317 | -0.32378 | 0.98312 | -0.32483 | 1.9902
5 | -0.072401 | -0.018199 | 0.072488 | 0.018254 | 8.6366e-05 | 5.5029e-05 | 0.10941 | 0.10941 | 0.10941 | 0.98485 | -0.29091 | 0.98614 | -0.26596 | 30.0577
6 | 0.041458 | 0.010422 | -0.041438 | -0.010409 | 2.0142e-05 | 1.2717e-05 | 0.06265 | 0.062651 | 0.062651 | 0.98485 | -0.29091 | 0.98433 | -0.30109 | 17.2117
7 | 0.020301 | 0.0050909 | -0.020296 | -0.0050876 | 5.3582e-06 | 3.2376e-06 | 0.030735 | 0.030735 | 0.030735 | 0.98289 | -0.32923 | 0.98261 | -0.33477 | 8.4437
8 | 0.003137 | 0.000786 | -0.0031369 | -0.00078604 | 4.2269e-08 | -3.6348e-08 | 0.0047479 | 0.004748 | 0.004748 | 0.98312 | -0.32483 | 0.9831 | -0.32511 | 1.3044
9 | -0.001875 | -0.00046992 | 0.0018751 | 0.00046953 | 1.0872e-07 | -3.8481e-07 | 0.0028412 | 0.0028411 | 0.0028412 | 0.98197 | -0.34727 | 0.98203 | -0.34605 | 0.78056
10 | 0.00667 | 0.0016713 | -0.0066692 | -0.0016711 | 7.8145e-07 | 2.4204e-07 | 0.010107 | 0.010107 | 0.010107 | 0.98203 | -0.34605 | 0.98191 | -0.34851 | 2.7766
11 | -0.0097214 | -0.0024356 | 0.0097249 | 0.0024373 | 3.4879e-06 | 1.6897e-06 | 0.01473 | 0.01473 | 0.01473 | 0.98203 | -0.34605 | 0.98242 | -0.33852 | 4.0467
12 | -0.081945 | -0.020624 | 0.082004 | 0.020662 | 5.9304e-05 | 3.7823e-05 | 0.12368 | 0.12368 | 0.12368 | 0.98614 | -0.26596 | 0.98692 | -0.25083 | 33.9781
13 | 0.040057 | 0.010063 | -0.040027 | -0.010044 | 3.001e-05 | 1.8929e-05 | 0.060563 | 0.060563 | 0.060563 | 0.98433 | -0.30109 | 0.98353 | -0.3168 | 16.6382
14 | 0.01788 | 0.0044855 | -0.017879 | -0.004485 | 8.3001e-07 | 4.9296e-07 | 0.027076 | 0.027076 | 0.027076 | 0.98268 | -0.33328 | 0.98263 | -0.33426 | 7.4383
15 | -0.020324 | -0.005098 | 0.020334 | 0.0051039 | 9.7304e-06 | 5.8802e-06 | 0.030777 | 0.030776 | 0.030777 | 0.98268 | -0.33328 | 0.9832 | -0.32324 | 8.4551
16 | 0.016259 | 0.004079 | -0.016253 | -0.0040756 | 5.693e-06 | 3.3265e-06 | 0.024622 | 0.024622 | 0.024622 | 0.98263 | -0.33426 | 0.98226 | -0.3416 | 6.7644
17 | -0.038413 | -0.0096355 | 0.038425 | 0.0096429 | 1.181e-05 | 7.4404e-06 | 0.058139 | 0.058139 | 0.058139 | 0.9832 | -0.32324 | 0.98353 | -0.3168 | 15.9723
18 | 0.011004 | 0.0027582 | -0.011001 | -0.002757 | 2.3139e-06 | 1.1988e-06 | 0.016654 | 0.016654 | 0.016654 | 0.9832 | -0.32324 | 0.98297 | -0.32766 | 4.5752
19 | 0.0070759 | 0.0017734 | -0.0070749 | -0.0017731 | 9.9031e-07 | 3.4181e-07 | 0.010709 | 0.010709 | 0.010709 | 0.9832 | -0.32324 | 0.98305 | -0.32618 | 2.9421
20 | 0.018807 | 0.0047146 | -0.018806 | -0.0047139 | 1.2576e-06 | 7.5248e-07 | 0.028481 | 0.028481 | 0.028481 | 0.98261 | -0.33477 | 0.98254 | -0.33617 | 7.8245
21 | 0.001654 | 0.00041439 | -0.001654 | -0.00041453 | 2.9925e-08 | -1.4228e-07 | 0.0025035 | 0.0025035 | 0.0025035 | 0.9831 | -0.32511 | 0.98308 | -0.32549 | 0.68779
22 | -0.082004 | -0.020662 | 0.082108 | 0.020729 | 0.00010418 | 6.644e-05 | 0.12368 | 0.12368 | 0.12368 | 0.98692 | -0.25083 | 0.98829 | -0.2243 | 33.9781
23 | 0.016589 | 0.0041583 | -0.016587 | -0.0041572 | 1.8547e-06 | 1.0878e-06 | 0.025124 | 0.025124 | 0.025124 | 0.98254 | -0.33617 | 0.98242 | -0.33852 | 6.9022
24 | -0.0053641 | -0.0013443 | 0.0053642 | 0.0013443 | 1.1193e-07 | 1.4238e-08 | 0.0081197 | 0.0081197 | 0.0081197 | 0.98302 | -0.32662 | 0.98305 | -0.32618 | 2.2307
25 | 0.0033439 | 0.00083799 | -0.0033439 | -0.00083805 | 8.4282e-08 | -5.7265e-08 | 0.0050617 | 0.0050618 | 0.0050618 | 0.98302 | -0.32662 | 0.983 | -0.32715 | 1.3906
26 | 0.0091021 | 0.002281 | -0.0091005 | -0.0022802 | 1.6386e-06 | 7.5702e-07 | 0.013779 | 0.013779 | 0.013779 | 0.98297 | -0.32766 | 0.98278 | -0.33144 | 3.7854
27 | 0.0010844 | 0.00027109 | -0.0010843 | -0.00027175 | 5.5973e-08 | -6.6589e-07 | 0.0016416 | 0.0016418 | 0.0016418 | 0.98278 | -0.33144 | 0.98272 | -0.33252 | 0.45105
28 | 0.0080161 | 0.0020091 | -0.0080133 | -0.002008 | 2.8833e-06 | 1.1842e-06 | 0.012137 | 0.012137 | 0.012137 | 0.98278 | -0.33144 | 0.98239 | -0.33899 | 3.3345
29 | -0.17772 | -0.045148 | 0.17809 | 0.045385 | 0.00037174 | 0.00023717 | 0.26527 | 0.26527 | 0.26527 | 0.99772 | -0.043352 | 1 | 0 | 36.4384
30 | 0.17419 | 0.044262 | -0.17413 | -0.044225 | 5.8701e-05 | 3.7448e-05 | 0.26 | 0.26 | 0.26 | 0.99772 | -0.043352 | 0.99735 | -0.050354 | 35.7141
31 | 0.16006 | 0.040988 | -0.1598 | -0.040823 | 0.0002592 | 0.00016525 | 0.23848 | 0.23848 | 0.23848 | 1 | 0 | 0.99823 | -0.033489 | 32.7578
32 | 0.062943 | 0.015888 | -0.0628 | -0.015797 | 0.00014244 | 9.0602e-05 | 0.093948 | 0.093948 | 0.093948 | 0.99735 | -0.050354 | 0.99489 | -0.097716 | 25.8099
33 | 0.11118 | 0.028337 | -0.11108 | -0.028269 | 0.00010702 | 6.8361e-05 | 0.16605 | 0.16605 | 0.16605 | 0.99735 | -0.050354 | 0.9963 | -0.070321 | 45.6185
34 | 0.15575 | 0.03981 | -0.1557 | -0.039777 | 5.0947e-05 | 3.2475e-05 | 0.23245 | 0.23245 | 0.23245 | 0.99823 | -0.033489 | 0.99787 | -0.040254 | 31.9299
35 | 0.059347 | 0.014932 | -0.059306 | -0.014905 | 4.1951e-05 | 2.6664e-05 | 0.088784 | 0.088784 | 0.088784 | 0.99489 | -0.097716 | 0.99412 | -0.11252 | 24.3913
36 | 0.10639 | 0.027094 | -0.10628 | -0.027022 | 0.00011234 | 7.1746e-05 | 0.15905 | 0.15905 | 0.15905 | 0.9963 | -0.070321 | 0.99516 | -0.09224 | 43.6946
37 | 0.15276 | 0.03904 | -0.15258 | -0.038922 | 0.00018414 | 0.00011736 | 0.22806 | 0.22806 | 0.22806 | 0.99787 | -0.040254 | 0.99656 | -0.065211 | 31.3273
38 | 0.025983 | 0.0065306 | -0.02597 | -0.0065225 | 1.3194e-05 | 8.1428e-06 | 0.038898 | 0.038898 | 0.038898 | 0.99412 | -0.11252 | 0.99357 | -0.12316 | 10.6863
39 | 0.033323 | 0.0083744 | -0.033308 | -0.0083651 | 1.4747e-05 | 9.2335e-06 | 0.049886 | 0.049886 | 0.049886 | 0.99412 | -0.11252 | 0.99364 | -0.1218 | 13.705
40 | 0.10628 | 0.027022 | -0.10616 | -0.026945 | 0.00011977 | 7.6487e-05 | 0.15905 | 0.15905 | 0.15905 | 0.99516 | -0.09224 | 0.99393 | -0.11566 | 43.6947
41 | 0.15033 | 0.03836 | -0.15033 | -0.038356 | 6.6016e-06 | 4.2068e-06 | 0.22471 | 0.22471 | 0.22471 | 0.99656 | -0.065211 | 0.99651 | -0.06612 | 30.867
42 | 0.02414 | 0.0060638 | -0.024118 | -0.0060505 | 2.1678e-05 | 1.3302e-05 | 0.036158 | 0.036158 | 0.036158 | 0.99357 | -0.12316 | 0.9926 | -0.142 | 9.9334
43 | 0.029421 | 0.0073909 | -0.029402 | -0.0073791 | 1.8952e-05 | 1.1792e-05 | 0.044065 | 0.044065 | 0.044065 | 0.99364 | -0.1218 | 0.99294 | -0.1353 | 12.1058
44 | 0.10307 | 0.026171 | -0.10283 | -0.026022 | 0.00023367 | 0.00014921 | 0.15442 | 0.15442 | 0.15442 | 0.99393 | -0.11566 | 0.99147 | -0.16289 | 42.4239
45 | 0.025977 | 0.0065207 | -0.025967 | -0.006515 | 9.2407e-06 | 5.7038e-06 | 0.038932 | 0.038932 | 0.038932 | 0.99294 | -0.1353 | 0.99256 | -0.14276 | 10.6957
46 | 0.024792 | 0.0062205 | -0.024789 | -0.0062187 | 2.9354e-06 | 1.8055e-06 | 0.03717 | 0.03717 | 0.03717 | 0.99256 | -0.14276 | 0.99243 | -0.14525 | 10.2117
47 | 0.023094 | 0.0057937 | -0.023086 | -0.005789 | 7.5791e-06 | 4.6329e-06 | 0.034628 | 0.034628 | 0.034628 | 0.99243 | -0.14525 | 0.99207 | -0.15213 | 9.5132
48 | 0.018753 | 0.0047031 | -0.018749 | -0.0047004 | 4.5665e-06 | 2.7239e-06 | 0.028129 | 0.028129 | 0.028129 | 0.99207 | -0.15213 | 0.99181 | -0.15724 | 7.7278
49 | 0.022763 | 0.0057109 | -0.022762 | -0.0057102 | 1.2617e-06 | 7.7014e-07 | 0.034127 | 0.034127 | 0.034127 | 0.9926 | -0.142 | 0.99254 | -0.14316 | 9.3754
50 | 0.018211 | 0.0045657 | -0.01821 | -0.0045652 | 8.6412e-07 | 5.132e-07 | 0.027323 | 0.027323 | 0.027323 | 0.99181 | -0.15724 | 0.99176 | -0.15824 | 7.5062
51 | 0.00194 | 0.0004862 | -0.00194 | -0.00048621 | 2.3442e-09 | -7.9882e-09 | 0.0029132 | 0.0029132 | 0.0029132 | 0.99091 | -0.17469 | 0.99091 | -0.17471 | 0.80034
52 | -0.0027931 | -0.00070001 | 0.0027931 | 0.00069993 | 6.0094e-08 | -7.8888e-08 | 0.0041943 | 0.0041942 | 0.0041943 | 0.99091 | -0.17469 | 0.99093 | -0.17424 | 1.1523
53 | -0.0039708 | -0.00099507 | 0.0039709 | 0.00099503 | 1.2568e-07 | -4.101e-08 | 0.0059626 | 0.0059626 | 0.0059626 | 0.99093 | -0.17424 | 0.99097 | -0.17357 | 1.6381
54 | -0.0039577 | -0.0009919 | 0.003958 | 0.0009918 | 3.2703e-07 | -9.788e-08 | 0.0059952 | 0.0059951 | 0.0059952 | 0.9823 | -0.34072 | 0.98239 | -0.33899 | 1.647
55 | 0.0040552 | 0.0010162 | -0.0040549 | -0.0010162 | 3.3467e-07 | -8.5282e-08 | 0.0061423 | 0.0061424 | 0.0061424 | 0.98239 | -0.33899 | 0.9823 | -0.34072 | 1.6875
56 | 0.016253 | 0.0040756 | -0.01625 | -0.0040737 | 3.3779e-06 | 1.9739e-06 | 0.024622 | 0.024623 | 0.024623 | 0.98226 | -0.3416 | 0.98203 | -0.34597 | 6.7644
57 | 0.014854 | 0.0037238 | -0.01485 | -0.0037219 | 3.212e-06 | 1.8418e-06 | 0.022507 | 0.022507 | 0.022507 | 0.98203 | -0.34597 | 0.9818 | -0.3505 | 6.1833
58 | 0.0063695 | 0.0015961 | -0.0063688 | -0.0015958 | 7.5948e-07 | 2.2373e-07 | 0.0097662 | 0.0097663 | 0.0097663 | 0.97048 | -0.5703 | 0.97035 | -0.5728 | 2.6831
59 | -0.0099907 | -0.0025036 | 0.0099925 | 0.0025046 | 1.8908e-06 | 9.4454e-07 | 0.015318 | 0.015318 | 0.015318 | 0.97048 | -0.5703 | 0.97068 | -0.56632 | 4.2084
60 | 0.0048673 | 0.0012195 | -0.0048669 | -0.0012195 | 3.9189e-07 | 1.9105e-08 | 0.0074638 | 0.0074639 | 0.0074639 | 0.97035 | -0.5728 | 0.97026 | -0.57449 | 2.0505
61 | -0.013308 | -0.0033356 | 0.013312 | 0.0033374 | 3.2109e-06 | 1.8006e-06 | 0.020402 | 0.020401 | 0.020402 | 0.97068 | -0.56632 | 0.97093 | -0.56126 | 5.6048
62 | 0.003138 | 0.00078623 | -0.0031378 | -0.00078641 | 2.3029e-07 | -1.8007e-07 | 0.0048125 | 0.0048126 | 0.0048126 | 0.97026 | -0.57449 | 0.97019 | -0.57603 | 1.3221
63 | -0.015644 | -0.0039219 | 0.015648 | 0.0039243 | 4.2093e-06 | 2.4523e-06 | 0.023975 | 0.023975 | 0.023975 | 0.97093 | -0.56126 | 0.97122 | -0.55562 | 6.5866
64 | 0.0051012 | 0.0012783 | -0.0051006 | -0.0012782 | 5.5539e-07 | 5.5438e-08 | 0.0078155 | 0.0078156 | 0.0078156 | 0.97122 | -0.55562 | 0.9711 | -0.5579 | 2.1471
65 | -0.020749 | -0.0052026 | 0.020757 | 0.0052071 | 7.4818e-06 | 4.544e-06 | 0.031791 | 0.031791 | 0.031791 | 0.97122 | -0.55562 | 0.9716 | -0.54805 | 8.7337
66 | 0.0023912 | 0.00059919 | -0.0023912 | -0.00059928 | 5.4138e-08 | -9.839e-08 | 0.003664 | 0.0036641 | 0.0036641 | 0.9711 | -0.5579 | 0.97108 | -0.55838 | 1.0066
67 | -0.023393 | -0.0058678 | 0.023401 | 0.0058728 | 8.212e-06 | 5.0443e-06 | 0.035828 | 0.035828 | 0.035828 | 0.9716 | -0.54805 | 0.97197 | -0.54069 | 9.8428
68 | -0.0018784 | -0.00047076 | 0.0018784 | 0.00047068 | 2.3678e-08 | -8.7384e-08 | 0.0028186 | 0.0028186 | 0.0028186 | 0.99165 | -0.16039 | 0.99166 | -0.16013 | 0.77434
69 | -0.0018784 | -0.00047068 | 0.0018784 | 0.00047057 | 2.8641e-08 | -1.0571e-07 | 0.0028186 | 0.0028185 | 0.0028186 | 0.99166 | -0.16013 | 0.99168 | -0.15981 | 0.77433
70 | -0.015546 | -0.0038971 | 0.015552 | 0.0039006 | 6.0695e-06 | 3.5006e-06 | 0.023328 | 0.023327 | 0.023328 | 0.99168 | -0.15981 | 0.9921 | -0.15162 | 6.4087
71 | 0.013668 | 0.0034265 | -0.013665 | -0.003425 | 2.7267e-06 | 1.5221e-06 | 0.020509 | 0.020509 | 0.020509 | 0.99168 | -0.15981 | 0.99146 | -0.164 | 5.6344
72 | -0.017353 | -0.0043518 | 0.017354 | 0.0043525 | 1.1535e-06 | 6.7959e-07 | 0.026028 | 0.026028 | 0.026028 | 0.9921 | -0.15162 | 0.99217 | -0.15022 | 7.1505
73 | 0.011762 | 0.0029479 | -0.011761 | -0.0029473 | 1.2788e-06 | 6.7731e-07 | 0.017653 | 0.017653 | 0.017653 | 0.99146 | -0.164 | 0.99134 | -0.16628 | 4.8496
74 | -0.019171 | -0.0048078 | 0.019175 | 0.0048101 | 3.8937e-06 | 2.3297e-06 | 0.028752 | 0.028752 | 0.028752 | 0.99217 | -0.15022 | 0.99239 | -0.14596 | 7.899
75 | 0.003558 | 0.0008914 | -0.0035579 | -0.00089147 | 1.1299e-07 | -6.3889e-08 | 0.0053405 | 0.0053405 | 0.0053405 | 0.99134 | -0.16628 | 0.99131 | -0.16695 | 1.4672
76 | 0.0082025 | 0.0020559 | -0.0082005 | -0.002055 | 2.0121e-06 | 8.3153e-07 | 0.012312 | 0.012312 | 0.012312 | 0.99134 | -0.16628 | 0.99108 | -0.17143 | 3.3825
77 | -0.0039185 | -0.00098208 | 0.0039186 | 0.00098206 | 5.3171e-08 | -1.875e-08 | 0.0058836 | 0.0058835 | 0.0058836 | 0.99104 | -0.17121 | 0.99106 | -0.17093 | 1.6164
78 | -0.0090238 | -0.0022615 | 0.009026 | 0.0022626 | 2.2598e-06 | 1.0231e-06 | 0.013549 | 0.013549 | 0.013549 | 0.99106 | -0.17093 | 0.99133 | -0.16567 | 3.7222
79 | 0.0019401 | 0.000486 | -0.00194 | -0.00048621 | 6.1297e-08 | -2.0925e-07 | 0.0029121 | 0.0029122 | 0.0029122 | 0.99131 | -0.16695 | 0.99127 | -0.16761 | 0.80005
80 | 0.005803 | 0.0014542 | -0.0058024 | -0.001454 | 5.9218e-07 | 1.1096e-07 | 0.0087126 | 0.0087127 | 0.0087127 | 0.99108 | -0.17143 | 0.99097 | -0.17357 | 2.3936
81 | 0.001652 | 0.00041377 | -0.001652 | -0.00041402 | 5.1637e-08 | -2.5566e-07 | 0.0024796 | 0.0024797 | 0.0024797 | 0.99133 | -0.16567 | 0.99129 | -0.16633 | 0.68125
82 | -0.012006 | -0.0030092 | 0.012008 | 0.0030101 | 1.591e-06 | 8.4981e-07 | 0.018022 | 0.018022 | 0.018022 | 0.99133 | -0.16567 | 0.99147 | -0.16289 | 4.9511
83 | -0.02126 | -0.0053329 | 0.021263 | 0.0053346 | 2.8415e-06 | 1.7222e-06 | 0.03188 | 0.03188 | 0.03188 | 0.99239 | -0.14596 | 0.99254 | -0.14316 | 8.7582
84 | 0.005492 | 0.001376 | -0.005492 | -0.001376 | 3.4968e-08 | 5.3518e-09 | 0.0083227 | 0.0083227 | 0.0083227 | 0.98191 | -0.34851 | 0.9819 | -0.34864 | 2.2865
85 | 0.0098363 | 0.0024653 | -0.0098357 | -0.002465 | 6.0118e-07 | 2.9354e-07 | 0.014908 | 0.014908 | 0.014908 | 0.9818 | -0.3505 | 0.98174 | -0.35179 | 4.0956
86 | -0.0026318 | -0.0006596 | 0.0026319 | 0.00065949 | 7.0069e-08 | -1.1233e-07 | 0.0039327 | 0.0039327 | 0.0039327 | 0.9958 | -0.079842 | 0.99583 | -0.079283 | 1.0804
87 | -0.0044931 | -0.0011259 | 0.0044932 | 0.0011259 | 1.6088e-07 | -2.0872e-08 | 0.0067137 | 0.0067137 | 0.0067137 | 0.99583 | -0.079283 | 0.99587 | -0.078532 | 1.8444
88 | -0.006153 | -0.0015416 | 0.0061532 | 0.0015417 | 2.2738e-07 | 5.218e-08 | 0.0091936 | 0.0091935 | 0.0091936 | 0.99587 | -0.078532 | 0.99591 | -0.077756 | 2.5257
89 | 0.0016598 | 0.00041571 | -0.0016597 | -0.00041596 | 5.0725e-08 | -2.537e-07 | 0.0024799 | 0.00248 | 0.00248 | 0.99587 | -0.078532 | 0.99584 | -0.079173 | 0.68132
90 | -0.0061532 | -0.0015417 | 0.0061538 | 0.0015418 | 5.924e-07 | 1.3591e-07 | 0.0091935 | 0.0091935 | 0.0091935 | 0.99591 | -0.077756 | 0.99601 | -0.075734 | 2.5257
91 | -0.015615 | -0.003913 | 0.015622 | 0.0039171 | 7.1545e-06 | 4.1224e-06 | 0.023328 | 0.023328 | 0.023328 | 0.99601 | -0.075734 | 0.99651 | -0.06612 | 6.4088
92 | -0.07534 | -0.019139 | 0.075517 | 0.019252 | 0.00017729 | 0.000113 | 0.114 | 0.114 | 0.114 | 0.98416 | -0.30238 | 0.98669 | -0.25362 | 31.3194
93 | 0.07534 | 0.019139 | -0.075217 | -0.019061 | 0.00012279 | 7.8263e-05 | 0.114 | 0.114 | 0.114 | 0.98416 | -0.30238 | 0.98241 | -0.3363 | 31.3195
94 | -0.082183 | -0.020923 | 0.082395 | 0.021058 | 0.00021221 | 0.00013534 | 0.12406 | 0.12405 | 0.12406 | 0.98669 | -0.25362 | 0.98948 | -0.20022 | 34.081
95 | 0.067147 | 0.017039 | -0.067008 | -0.01695 | 0.00013893 | 8.8464e-05 | 0.10178 | 0.10178 | 0.10178 | 0.98241 | -0.3363 | 0.98019 | -0.37941 | 27.9614
96 | -0.084363 | -0.021552 | 0.084411 | 0.021582 | 4.7613e-05 | 3.0371e-05 | 0.12701 | 0.12701 | 0.12701 | 0.98948 | -0.20022 | 0.99009 | -0.18856 | 34.8942
97 | 0.063645 | 0.016107 | -0.063593 | -0.016074 | 5.2077e-05 | 3.3142e-05 | 0.096675 | 0.096675 | 0.096675 | 0.98019 | -0.37941 | 0.97932 | -0.39648 | 26.5591
98 | 0.1347 | 0.034438 | -0.13457 | -0.034352 | 0.00013624 | 8.6728e-05 | 0.20138 | 0.20138 | 0.20138 | 0.99651 | -0.06612 | 0.99541 | -0.087049 | 27.6626
99 | 0.13037 | 0.0333 | -0.13032 | -0.033267 | 5.2019e-05 | 3.3103e-05 | 0.19511 | 0.19511 | 0.19511 | 0.99541 | -0.087049 | 0.99498 | -0.095306 | 26.8006
100 | -0.0028044 | -0.00070284 | 0.0028045 | 0.00070267 | 1.3371e-07 | -1.7378e-07 | 0.0042099 | 0.0042098 | 0.0042099 | 0.99123 | -0.16843 | 0.99128 | -0.16743 | 1.1566
101 | -0.0059658 | -0.001495 | 0.005966 | 0.001495 | 1.7363e-07 | 3.669e-08 | 0.0089552 | 0.0089551 | 0.0089552 | 0.99128 | -0.16743 | 0.99131 | -0.16682 | 2.4602
102 | -0.0087343 | -0.0021888 | 0.0087354 | 0.0021893 | 1.0972e-06 | 4.8272e-07 | 0.013111 | 0.013111 | 0.013111 | 0.99131 | -0.16682 | 0.99145 | -0.16418 | 3.6018
103 | -0.0097453 | -0.0024424 | 0.0097457 | 0.0024426 | 3.8214e-07 | 1.8314e-07 | 0.014626 | 0.014626 | 0.014626 | 0.99145 | -0.16418 | 0.99149 | -0.16336 | 4.0182
104 | -0.015141 | -0.0037947 | 0.015145 | 0.0037969 | 3.6933e-06 | 2.1177e-06 | 0.022723 | 0.022723 | 0.022723 | 0.99149 | -0.16336 | 0.99176 | -0.15824 | 6.2426
105 | 0.088288 | 0.022376 | -0.08823 | -0.022339 | 5.796e-05 | 3.6981e-05 | 0.13259 | 0.13259 | 0.13259 | 0.99147 | -0.16289 | 0.99076 | -0.17657 | 36.4265
106 | -0.083744 | -0.021139 | 0.083799 | 0.021173 | 5.4392e-05 | 3.4694e-05 | 0.12614 | 0.12614 | 0.12614 | 0.98829 | -0.2243 | 0.98899 | -0.21075 | 34.6548
107 | -0.085435 | -0.021583 | 0.085483 | 0.021614 | 4.734e-05 | 3.02e-05 | 0.12861 | 0.12861 | 0.12861 | 0.98899 | -0.21075 | 0.98959 | -0.1992 | 35.3312
108 | 0.0016366 | 0.00040992 | -0.0016366 | -0.00041017 | 4.8911e-08 | -2.4472e-07 | 0.0024624 | 0.0024625 | 0.0024625 | 0.98899 | -0.21075 | 0.98895 | -0.21138 | 0.6765
109 | -0.086808 | -0.021946 | 0.086902 | 0.022006 | 9.4345e-05 | 6.0191e-05 | 0.1306 | 0.1306 | 0.1306 | 0.98959 | -0.1992 | 0.99076 | -0.17657 | 35.8787
110 | 0.035431 | 0.0089027 | -0.035429 | -0.0089016 | 1.6924e-06 | 1.064e-06 | 0.054177 | 0.054177 | 0.054177 | 0.97329 | -0.51462 | 0.97324 | -0.51562 | 14.8837
111 | -0.038829 | -0.0097544 | 0.038855 | 0.0097708 | 2.5996e-05 | 1.6393e-05 | 0.059373 | 0.059372 | 0.059373 | 0.97329 | -0.51462 | 0.974 | -0.5006 | 16.3111
112 | 0.033354 | 0.0083816 | -0.033331 | -0.0083669 | 2.3323e-05 | 1.463e-05 | 0.051004 | 0.051004 | 0.051004 | 0.97324 | -0.51562 | 0.9725 | -0.53028 | 14.0121
113 | -0.041482 | -0.010429 | 0.041484 | 0.010431 | 2.6377e-06 | 1.6663e-06 | 0.063385 | 0.063385 | 0.063385 | 0.974 | -0.5006 | 0.97407 | -0.49927 | 17.4134
114 | 0.031469 | 0.0079003 | -0.031465 | -0.0078975 | 4.479e-06 | 2.8027e-06 | 0.048156 | 0.048156 | 0.048156 | 0.9725 | -0.53028 | 0.97235 | -0.53326 | 13.2296
115 | -0.043252 | -0.010874 | 0.043281 | 0.010892 | 2.8966e-05 | 1.8318e-05 | 0.066086 | 0.066085 | 0.066086 | 0.97407 | -0.49927 | 0.97478 | -0.48526 | 18.1554
116 | 0.029349 | 0.0073672 | -0.029342 | -0.007363 | 6.7735e-06 | 4.224e-06 | 0.044917 | 0.044917 | 0.044917 | 0.97235 | -0.53326 | 0.9721 | -0.5381 | 12.34
117 | -0.045307 | -0.0114 | 0.045319 | 0.011408 | 1.2088e-05 | 7.6526e-06 | 0.069178 | 0.069178 | 0.069178 | 0.97478 | -0.48526 | 0.97507 | -0.47967 | 19.0049
118 | 0.0265 | 0.0066507 | -0.026496 | -0.0066487 | 3.2684e-06 | 2.0261e-06 | 0.040567 | 0.040567 | 0.040567 | 0.9721 | -0.5381 | 0.97197 | -0.54069 | 11.1448
119 | -0.047929 | -0.012062 | 0.04795 | 0.012075 | 2.053e-05 | 1.3011e-05 | 0.073161 | 0.073161 | 0.073161 | 0.97507 | -0.47967 | 0.97552 | -0.47071 | 20.0992
120 | -0.00232 | -0.00058144 | 0.00232 | 0.00058139 | 2.2329e-08 | -4.6499e-08 | 0.0035179 | 0.0035178 | 0.0035179 | 0.98133 | -0.35986 | 0.98134 | -0.35966 | 0.96644
121 | -0.0057397 | -0.0014385 | 0.0057403 | 0.0014386 | 6.307e-07 | 1.2308e-07 | 0.0087032 | 0.0087031 | 0.0087032 | 0.98134 | -0.35966 | 0.98145 | -0.35735 | 2.391
122 | 0.00088036 | 0.00022049 | -0.00088035 | -0.00022064 | 8.0993e-09 | -1.4802e-07 | 0.0013347 | 0.0013347 | 0.0013347 | 0.98145 | -0.35735 | 0.98144 | -0.35755 | 0.36669
123 | -0.0066207 | -0.0016591 | 0.006622 | 0.0016595 | 1.3283e-06 | 4.0574e-07 | 0.010038 | 0.010038 | 0.010038 | 0.98145 | -0.35735 | 0.98167 | -0.35314 | 2.7576
124 | -0.0078162 | -0.0019588 | 0.0078167 | 0.001959 | 5.0469e-07 | 2.0178e-07 | 0.011848 | 0.011848 | 0.011848 | 0.98167 | -0.35314 | 0.98174 | -0.35179 | 3.2549
125 | 0.063593 | 0.016074 | -0.06353 | -0.016034 | 6.3117e-05 | 4.0168e-05 | 0.096675 | 0.096675 | 0.096675 | 0.97932 | -0.39648 | 0.97826 | -0.4172 | 26.5591
126 | 0.059707 | 0.015076 | -0.059662 | -0.015048 | 4.4288e-05 | 2.8165e-05 | 0.09086 | 0.09086 | 0.09086 | 0.97826 | -0.4172 | 0.97746 | -0.43269 | 24.9615
127 | 0.057988 | 0.014628 | -0.057986 | -0.014627 | 1.9304e-06 | 1.2272e-06 | 0.088311 | 0.088311 | 0.088311 | 0.97746 | -0.43269 | 0.97743 | -0.43339 | 24.2611
128 | 0.0072566 | 0.0018188 | -0.0072556 | -0.0018184 | 1.0183e-06 | 3.5816e-07 | 0.010906 | 0.010906 | 0.010906 | 0.99009 | -0.18856 | 0.98993 | -0.1915 | 2.9962
129 | -0.091667 | -0.023401 | 0.091753 | 0.023456 | 8.5927e-05 | 5.4838e-05 | 0.13792 | 0.13792 | 0.13792 | 0.99009 | -0.18856 | 0.9911 | -0.16918 | 37.8903
130 | 0.0061204 | 0.0015339 | -0.0061203 | -0.0015338 | 8.7783e-08 | 2.0152e-08 | 0.0091696 | 0.0091696 | 0.0091696 | 0.9932 | -0.12956 | 0.99318 | -0.12986 | 2.5191
131 | -0.0091727 | -0.0022988 | 0.0091741 | 0.0022995 | 1.4265e-06 | 6.5225e-07 | 0.013743 | 0.013742 | 0.013743 | 0.9932 | -0.12956 | 0.99336 | -0.12629 | 3.7754
132 | 0.0042616 | 0.001068 | -0.0042615 | -0.001068 | 1.0859e-07 | -2.2424e-08 | 0.0063848 | 0.0063849 | 0.0063849 | 0.99318 | -0.12986 | 0.99315 | -0.13039 | 1.7541
133 | -0.011008 | -0.0027591 | 0.011009 | 0.0027594 | 7.0545e-07 | 3.6191e-07 | 0.016489 | 0.016489 | 0.016489 | 0.99336 | -0.12629 | 0.99343 | -0.12495 | 4.53
134 | 0.0057497 | 0.0014409 | -0.0057494 | -0.0014408 | 3.2491e-07 | 5.67e-08 | 0.0086121 | 0.0086122 | 0.0086122 | 0.99343 | -0.12495 | 0.99337 | -0.12613 | 2.366
135 | -0.016758 | -0.0042003 | 0.016762 | 0.0042024 | 3.6371e-06 | 2.1284e-06 | 0.025101 | 0.025101 | 0.025101 | 0.99343 | -0.12495 | 0.99367 | -0.12039 | 6.896
136 | 0.0038655 | 0.00096867 | -0.0038653 | -0.00096874 | 1.6632e-07 | -6.4807e-08 | 0.0057902 | 0.0057903 | 0.0057903 | 0.99337 | -0.12613 | 0.99333 | -0.12704 | 1.5907
137 | -0.019893 | -0.0049871 | 0.0199 | 0.0049915 | 7.315e-06 | 4.3967e-06 | 0.02979 | 0.029789 | 0.02979 | 0.99367 | -0.12039 | 0.99407 | -0.11268 | 8.1839
138 | -0.02301 | -0.0057709 | 0.023013 | 0.0057726 | 2.8346e-06 | 1.7316e-06 | 0.034445 | 0.034445 | 0.034445 | 0.99407 | -0.11268 | 0.9942 | -0.11009 | 9.4629
139 | 0.055984 | 0.014125 | -0.055931 | -0.014091 | 5.2946e-05 | 3.3642e-05 | 0.085263 | 0.085263 | 0.085263 | 0.97743 | -0.43339 | 0.97642 | -0.45316 | 23.424
140 | 0.052981 | 0.013352 | -0.05298 | -0.013351 | 1.4496e-06 | 9.2035e-07 | 0.080767 | 0.080767 | 0.080767 | 0.97642 | -0.45316 | 0.97639 | -0.45373 | 22.1888
141 | 0.050873 | 0.012823 | -0.050831 | -0.012797 | 4.1312e-05 | 2.6211e-05 | 0.077556 | 0.077556 | 0.077556 | 0.97639 | -0.45373 | 0.97552 | -0.47071 | 21.3067
142 | 0.0045158 | 0.0011314 | -0.0045154 | -0.0011314 | 4.8956e-07 | -3.923e-08 | 0.0068434 | 0.0068435 | 0.0068435 | 0.9819 | -0.34864 | 0.98178 | -0.35092 | 1.8801
143 | 0.0034102 | 0.00085444 | -0.0034102 | -0.00085446 | 3.7564e-08 | -2.3376e-08 | 0.0051685 | 0.0051686 | 0.0051686 | 0.98178 | -0.35092 | 0.98177 | -0.35115 | 1.4199
144 | 0.10115 | 0.025918 | -0.10108 | -0.02587 | 7.5824e-05 | 4.8071e-05 | 0.1516 | 0.1516 | 0.1516 | 0.9942 | -0.11009 | 0.99339 | -0.12557 | 20.8238
145 | -0.12417 | -0.031691 | 0.12425 | 0.031747 | 8.8777e-05 | 5.6462e-05 | 0.18604 | 0.18604 | 0.18604 | 0.9942 | -0.11009 | 0.99498 | -0.095306 | 25.5552
146 | 0.097012 | 0.024851 | -0.096977 | -0.024829 | 3.4961e-05 | 2.2147e-05 | 0.14551 | 0.14551 | 0.14551 | 0.99339 | -0.12557 | 0.993 | -0.13301 | 19.9873
147 | 0.094535 | 0.024217 | -0.09437 | -0.024111 | 0.00016535 | 0.00010554 | 0.14185 | 0.14185 | 0.14185 | 0.993 | -0.13301 | 0.9911 | -0.16918 | 38.9696
148 | 0.0012719 | 0.00031855 | -0.0012719 | -0.00031876 | 2.478e-08 | -2.0901e-07 | 0.0019277 | 0.0019277 | 0.0019277 | 0.98177 | -0.35115 | 0.98175 | -0.35156 | 0.5296

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3447 | 0.087602

## res_load
| p_mw | q_mvar
0 | 0.0019793 | 0.00049605
1 | 0.002344 | 0.00058747
2 | 0.0014804 | 0.00037103
3 | 0.0016493 | 0.00041334
4 | 0.001875 | 0.00046992
5 | 0.0011763 | 0.0002948
6 | 0.0094573 | 0.0023702
7 | 0.001381 | 0.00034611
8 | 0.0024442 | 0.00061257
9 | 0.00162 | 0.00040601
10 | 0.0014885 | 0.00037304
11 | 0.0014829 | 0.00037165
12 | 0.0016022 | 0.00040154
13 | 0.0022167 | 0.00055555
14 | 0.001654 | 0.00041453
15 | 0.0020202 | 0.0005063
16 | 0.0017107 | 0.00042875
17 | 0.0033439 | 0.00083805
18 | 0.0018992 | 0.00047598
19 | 0.0035356 | 0.0008861
20 | 0.0049019 | 0.0012285
21 | 0.0040435 | 0.0010134
22 | 0.0034526 | 0.00086531
23 | 0.0046888 | 0.0011751
24 | 0.002942 | 0.00073732
25 | 0.0022447 | 0.00056257
26 | 0.00183 | 0.00045865
27 | 0.0038871 | 0.0009742
28 | 0.0030898 | 0.00077437
29 | 0.0034251 | 0.00085841
30 | 0.0011752 | 0.00029454
31 | 0.0016957 | 0.00042499
32 | 0.0043328 | 0.0010859
33 | 0.0013549 | 0.00033957
34 | 0.00053764 | 0.00013474
35 | 0.00085308 | 0.0002138
36 | 0.00194 | 0.00048621
37 | 0.0011776 | 0.00029514
38 | 0.0039577 | 0.0009919
39 | 0.0040549 | 0.0010162
40 | 0.0010843 | 0.00027175
41 | 0.0013961 | 0.0003499
42 | 0.0036211 | 0.00090754
43 | 0.0015015 | 0.00037631
44 | 0.0033159 | 0.00083104
45 | 0.0017289 | 0.0004333
46 | 0.002332 | 0.00058445
47 | 0.0031378 | 0.00078641
48 | 0.0027094 | 0.00067903
49 | 0.0026361 | 0.00066067
50 | 0.0018784 | 0.00047076
51 | 0.0018004 | 0.00045122
52 | 0.0019033 | 0.00047702
53 | 0.0018167 | 0.00045531
54 | 0.0039185 | 0.00098208
55 | 0.0051052 | 0.0012795
56 | 0.0016178 | 0.00040546
57 | 0.0023975 | 0.00060088
58 | 0.00194 | 0.00048621
59 | 0.0013282 | 0.00033288
60 | 0.0020858 | 0.00052276
61 | 0.0011772 | 0.00029503
62 | 0.0068625 | 0.0017199
63 | 0.0050141 | 0.0012567
64 | 0.0018315 | 0.00045902
65 | 0.0014986 | 0.00037558
66 | 0.0026318 | 0.0006596
67 | 0.0018612 | 0.00046646
68 | 0.0016597 | 0.00041596
69 | 0.0094612 | 0.0023712
70 | 0.0066658 | 0.0016706
71 | 0.0080701 | 0.0020226
72 | 0.0019684 | 0.00049332
73 | 0.0033625 | 0.00084273
74 | 0.0041978 | 0.0010521
75 | 0.0028044 | 0.00070284
76 | 0.0031613 | 0.00079229
77 | 0.0027684 | 0.00069382
78 | 0.0010098 | 0.00025309
79 | 0.0053952 | 0.0013522
80 | 0.0025378 | 0.00063604
81 | 0.0016359 | 0.00040999
82 | 0.0013253 | 0.00033214
83 | 0.0016366 | 0.00041017
84 | 0.0013278 | 0.00033277
85 | 0.001652 | 0.00041402
86 | 0.0033986 | 0.00085177
87 | 0.002075 | 0.00052003
88 | 0.0026264 | 0.00065824
89 | 0.0018618 | 0.0004666
90 | 0.0017679 | 0.00044307
91 | 0.002116 | 0.00053032
92 | 0.0020258 | 0.00050772
93 | 0.002842 | 0.00071228
94 | 0.0026101 | 0.00065415
95 | 0.00232 | 0.00058144
96 | 0.0034197 | 0.00085706
97 | 0.00088035 | 0.00022064
98 | 0.0011941 | 0.00029928
99 | 0.002019 | 0.00050601
100 | 0.0038233 | 0.0009582
101 | 0.0016746 | 0.00041969
102 | 0.0030523 | 0.00076497
103 | 0.0018587 | 0.00046584
104 | 0.0018338 | 0.00045958
105 | 0.0042615 | 0.001068
106 | 0.0018839 | 0.00047214
107 | 0.0031307 | 0.00078463
108 | 0.0038653 | 0.00096874
109 | 0.0031101 | 0.00077946
110 | 0.0030656 | 0.0007683
111 | 0.0020017 | 0.00050168
112 | 0.0029501 | 0.00073938
113 | 0.002107 | 0.00052805
114 | 0.0028816 | 0.00072219
115 | 0.0030957 | 0.00077585
116 | 0.00097617 | 0.00024465
117 | 0.0011051 | 0.00027697
118 | 0.0023912 | 0.00059928
119 | 0.0040655 | 0.0010189
120 | 0.006063 | 0.0015195
121 | 0.0024414 | 0.00061187
122 | 0.0021383 | 0.00053591
123 | 0.0012719 | 0.00031876
124 | 0.0072556 | 0.0018184
125 | 0.0026166 | 0.00065579

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1