## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2517-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2517-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2517-7_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2517-7_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2517-7_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2517-7_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2517-7_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2517-7_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2517-7_0_5_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_2517-7_0_5_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_2517-7_0_5_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2517-7_0_5_node_150 | 0.4 | n |  | TRUE
12 | bus_LV_2517-7_0_5_node_142 | 0.4 | n |  | TRUE
13 | bus_LV_2517-7_0_5_node_140 | 0.4 | n |  | TRUE
14 | bus_LV_2517-7_0_5_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_2517-7_0_5_node_53 | 0.4 | n |  | TRUE
16 | bus_LV_2517-7_0_5_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_2517-7_0_5_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_2517-7_0_5_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2517-7_0_5_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2517-7_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2517-7_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2517-7_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2517-7_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2517-7_0_5_node_77 | 0.4 | n |  | TRUE
25 | bus_LV_2517-7_0_5_node_74 | 0.4 | n |  | TRUE
26 | bus_LV_2517-7_0_5_node_131 | 0.4 | n |  | TRUE
27 | bus_LV_2517-7_0_5_node_75 | 0.4 | n |  | TRUE
28 | bus_LV_2517-7_0_5_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_2517-7_0_5_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2517-7_0_5_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2517-7_0_5_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2517-7_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2517-7_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_2517-7_0_5_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2517-7_0_5_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_2517-7_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2517-7_0_5_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2517-7_0_5_node_148 | 0.4 | n |  | TRUE
39 | bus_LV_2517-7_0_5_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2517-7_0_5_node_136 | 0.4 | n |  | TRUE
41 | bus_LV_2517-7_0_5_node_111 | 0.4 | n |  | TRUE
42 | bus_LV_2517-7_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2517-7_0_5_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2517-7_0_5_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_2517-7_0_5_node_109 | 0.4 | n |  | TRUE
46 | bus_LV_2517-7_0_5_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_2517-7_0_5_node_98 | 0.4 | n |  | TRUE
48 | bus_LV_2517-7_0_5_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_2517-7_0_5_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_2517-7_0_5_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_2517-7_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_2517-7_0_5_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_2517-7_0_5_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_2517-7_0_5_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_2517-7_0_5_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_2517-7_0_5_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_2517-7_0_5_node_144 | 0.4 | n |  | TRUE
58 | bus_LV_2517-7_0_5_node_91 | 0.4 | n |  | TRUE
59 | bus_LV_2517-7_0_5_node_139 | 0.4 | n |  | TRUE
60 | bus_LV_2517-7_0_5_node_145 | 0.4 | n |  | TRUE
61 | bus_LV_2517-7_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2517-7_0_5_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_2517-7_0_5_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_2517-7_0_5_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_2517-7_0_5_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_2517-7_0_5_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_2517-7_0_5_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_2517-7_0_5_node_112 | 0.4 | n |  | TRUE
69 | bus_LV_2517-7_0_5_node_121 | 0.4 | n |  | TRUE
70 | bus_LV_2517-7_0_5_node_134 | 0.4 | n |  | TRUE
71 | bus_LV_2517-7_0_5_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_2517-7_0_5_node_122 | 0.4 | n |  | TRUE
73 | bus_LV_2517-7_0_5_node_135 | 0.4 | n |  | TRUE
74 | bus_LV_2517-7_0_5_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_2517-7_0_5_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_2517-7_0_5_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_2517-7_0_5_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_2517-7_0_5_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_2517-7_0_5_node_96 | 0.4 | n |  | TRUE
80 | bus_LV_2517-7_0_5_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_2517-7_0_5_node_54 | 0.4 | n |  | TRUE
82 | bus_LV_2517-7_0_5_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_2517-7_0_5_node_57 | 0.4 | n |  | TRUE
84 | bus_LV_2517-7_0_5_node_133 | 0.4 | n |  | TRUE
85 | bus_LV_2517-7_0_5_node_143 | 0.4 | n |  | TRUE
86 | bus_LV_2517-7_0_5_node_132 | 0.4 | n |  | TRUE
87 | bus_LV_2517-7_0_5_node_149 | 0.4 | n |  | TRUE
88 | bus_LV_2517-7_0_5_node_141 | 0.4 | n |  | TRUE
89 | bus_LV_2517-7_0_5_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_2517-7_0_5_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_2517-7_0_5_node_63 | 0.4 | n |  | TRUE
92 | bus_LV_2517-7_0_5_node_64 | 0.4 | n |  | TRUE
93 | bus_LV_2517-7_0_5_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_2517-7_0_5_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_2517-7_0_5_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_2517-7_0_5_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_2517-7_0_5_node_104 | 0.4 | n |  | TRUE
98 | bus_LV_2517-7_0_5_node_137 | 0.4 | n |  | TRUE
99 | bus_LV_2517-7_0_5_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_2517-7_0_5_node_101 | 0.4 | n |  | TRUE
101 | bus_LV_2517-7_0_5_node_138 | 0.4 | n |  | TRUE
102 | bus_LV_2517-7_0_5_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_2517-7_0_5_node_69 | 0.4 | n |  | TRUE
104 | bus_LV_2517-7_0_5_node_70 | 0.4 | n |  | TRUE
105 | bus_LV_2517-7_0_5_node_71 | 0.4 | n |  | TRUE
106 | bus_LV_2517-7_0_5_node_72 | 0.4 | n |  | TRUE
107 | bus_LV_2517-7_0_5_node_73 | 0.4 | n |  | TRUE
108 | bus_LV_2517-7_0_5_node_117 | 0.4 | n |  | TRUE
109 | bus_LV_2517-7_0_5_node_126 | 0.4 | n |  | TRUE
110 | bus_LV_2517-7_0_5_node_120 | 0.4 | n |  | TRUE
111 | bus_LV_2517-7_0_5_node_127 | 0.4 | n |  | TRUE
112 | bus_LV_2517-7_0_5_node_76 | 0.4 | n |  | TRUE
113 | bus_LV_2517-7_0_5_node_113 | 0.4 | n |  | TRUE
114 | bus_LV_2517-7_0_5_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_2517-7_0_5_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_2517-7_0_5_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_2517-7_0_5_node_129 | 0.4 | n |  | TRUE
118 | bus_LV_2517-7_0_5_node_78 | 0.4 | n |  | TRUE
119 | bus_LV_2517-7_0_5_node_79 | 0.4 | n |  | TRUE
120 | bus_LV_2517-7_0_5_node_80 | 0.4 | n |  | TRUE
121 | bus_LV_2517-7_0_5_node_81 | 0.4 | n |  | TRUE
122 | bus_LV_2517-7_0_5_node_82 | 0.4 | n |  | TRUE
123 | bus_LV_2517-7_0_5_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_2517-7_0_5_node_84 | 0.4 | n |  | TRUE
125 | bus_LV_2517-7_0_5_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_2517-7_0_5_node_85 | 0.4 | n |  | TRUE
127 | bus_LV_2517-7_0_5_node_86 | 0.4 | n |  | TRUE
128 | bus_LV_2517-7_0_5_node_87 | 0.4 | n |  | TRUE
129 | bus_LV_2517-7_0_5_node_88 | 0.4 | n |  | TRUE
130 | bus_LV_2517-7_0_5_node_89 | 0.4 | n |  | TRUE
131 | bus_LV_2517-7_0_5_node_90 | 0.4 | n |  | TRUE
132 | bus_LV_2517-7_0_5_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_2517-7_0_5_node_124 | 0.4 | n |  | TRUE
134 | bus_LV_2517-7_0_5_node_99 | 0.4 | n |  | TRUE
135 | bus_LV_2517-7_0_5_node_100 | 0.4 | n |  | TRUE
136 | bus_LV_2517-7_0_5_node_102 | 0.4 | n |  | TRUE
137 | bus_LV_2517-7_0_5_node_103 | 0.4 | n |  | TRUE
138 | bus_LV_2517-7_0_5_node_107 | 0.4 | n |  | TRUE
139 | bus_LV_2517-7_0_5_node_114 | 0.4 | n |  | TRUE
140 | bus_LV_2517-7_0_5_node_115 | 0.4 | n |  | TRUE
141 | bus_LV_2517-7_0_5_node_116 | 0.4 | n |  | TRUE
142 | bus_LV_2517-7_0_5_node_118 | 0.4 | n |  | TRUE
143 | bus_LV_2517-7_0_5_node_125 | 0.4 | n |  | TRUE
144 | bus_LV_2517-7_0_5_node_147 | 0.4 | n |  | TRUE
145 | bus_LV_2517-7_0_5_node_146 | 0.4 | n |  | TRUE
146 | bus_LV_2517-7_0_5_node_130 | 0.4 | n |  | TRUE
147 | bus_LV_2517-7_0_5_node_151 | 0.4 | n |  | TRUE
148 | bus_LV_2517-7_0_5_node_152 | 0.4 | n |  | TRUE
149 | bus_MV_392_0_node_94 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2517-7_0_5_load_0 | 0 | 0.0045866 | 0.0011495 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2517-7_0_5_load_1 | 1 | 0.0017592 | 0.0004409 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2517-7_0_5_load_2 | 2 | 0.0036547 | 0.00091596 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2517-7_0_5_load_4 | 4 | 0.0088144 | 0.0022091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2517-7_0_5_load_6 | 6 | 0.0040579 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2517-7_0_5_load_7 | 7 | 0.0015219 | 0.00038142 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2517-7_0_5_load_60 | 9 | 0.0025981 | 0.00065113 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2517-7_0_5_load_14 | 10 | 0.0017564 | 0.0004402 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2517-7_0_5_load_150 | 11 | 0.0058045 | 0.0014547 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2517-7_0_5_load_53 | 15 | 0.0031172 | 0.00078125 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2517-7_0_5_load_49 | 16 | 0.0012494 | 0.00031314 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2517-7_0_5_load_30 | 17 | 0.0015279 | 0.00038292 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2517-7_0_5_load_8 | 18 | 0.0020404 | 0.00051137 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2517-7_0_5_load_9 | 19 | 0.0021964 | 0.00055047 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2517-7_0_5_load_10 | 20 | 0.0031411 | 0.00078724 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2517-7_0_5_load_12 | 22 | 0.002854 | 0.00071528 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2517-7_0_5_load_13 | 23 | 0.017755 | 0.0044498 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2517-7_0_5_load_77 | 24 | 0.0034795 | 0.00087204 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2517-7_0_5_load_74 | 25 | 0.0057167 | 0.0014327 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2517-7_0_5_load_131 | 26 | 0.0032444 | 0.00081311 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2517-7_0_5_load_75 | 27 | 0.0030906 | 0.00077457 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2517-7_0_5_load_31 | 28 | 0.0017633 | 0.00044193 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2517-7_0_5_load_15 | 29 | 0.0082595 | 0.00207 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2517-7_0_5_load_16 | 30 | 0.0079294 | 0.0019873 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2517-7_0_5_load_20 | 33 | 0.0034182 | 0.00085668 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2517-7_0_5_load_23 | 34 | 0.011074 | 0.0027755 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2517-7_0_5_load_24 | 35 | 0.0098297 | 0.0024636 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2517-7_0_5_load_25 | 36 | 0.0092822 | 0.0023263 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2517-7_0_5_load_21 | 37 | 0.0050427 | 0.0012638 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2517-7_0_5_load_148 | 38 | 0.0037356 | 0.00093622 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2517-7_0_5_load_29 | 39 | 0.0076019 | 0.0019052 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2517-7_0_5_load_111 | 41 | 0.010456 | 0.0026206 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2517-7_0_5_load_26 | 43 | 0.0075951 | 0.0019035 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2517-7_0_5_load_109 | 45 | 0.010484 | 0.0026275 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2517-7_0_5_load_32 | 46 | 0.0023324 | 0.00058455 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2517-7_0_5_load_98 | 47 | 0.0015088 | 0.00037813 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2517-7_0_5_load_97 | 48 | 0.0069297 | 0.0017368 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2517-7_0_5_load_33 | 49 | 0.0020815 | 0.00052166 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2517-7_0_5_load_34 | 50 | 0.000773 | 0.00019373 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2517-7_0_5_load_36 | 52 | 0.0014081 | 0.0003529 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2517-7_0_5_load_37 | 53 | 0.0013252 | 0.00033213 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2517-7_0_5_load_38 | 54 | 0.0015282 | 0.00038301 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2517-7_0_5_load_92 | 56 | 0.0012848 | 0.00032201 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2517-7_0_5_load_144 | 57 | 0.00085669 | 0.00021471 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2517-7_0_5_load_91 | 58 | 0.003425 | 0.00085838 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2517-7_0_5_load_139 | 59 | 0.0021714 | 0.0005442 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2517-7_0_5_load_145 | 60 | 0.00072145 | 0.00018081 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2517-7_0_5_load_40 | 61 | 0.091189 | 0.022854 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2517-7_0_5_load_44 | 65 | 0.0076084 | 0.0019068 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2517-7_0_5_load_45 | 66 | 0.0025264 | 0.00063317 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2517-7_0_5_load_46 | 67 | 0.010349 | 0.0025937 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2517-7_0_5_load_112 | 68 | 0.0028706 | 0.00071944 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2517-7_0_5_load_121 | 69 | 0.011969 | 0.0029998 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2517-7_0_5_load_110 | 71 | 0.017906 | 0.0044877 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2517-7_0_5_load_122 | 72 | 0.0015171 | 0.00038021 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2517-7_0_5_load_135 | 73 | 0.0051291 | 0.0012855 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2517-7_0_5_load_47 | 74 | 0.005182 | 0.0012987 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2517-7_0_5_load_48 | 75 | 0.0042265 | 0.0010593 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2517-7_0_5_load_50 | 76 | 0.0061223 | 0.0015344 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2517-7_0_5_load_52 | 77 | 0.0062375 | 0.0015633 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2517-7_0_5_load_96 | 79 | 0.0025226 | 0.00063223 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2517-7_0_5_load_54 | 81 | 0.025394 | 0.0063644 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2517-7_0_5_load_55 | 82 | 0.0029509 | 0.00073957 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2517-7_0_5_load_57 | 83 | 0.00044649 | 0.0001119 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2517-7_0_5_load_143 | 85 | 0.00572 | 0.0014336 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2517-7_0_5_load_132 | 86 | 0.0012244 | 0.00030687 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2517-7_0_5_load_149 | 87 | 0.002996 | 0.00075086 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2517-7_0_5_load_141 | 88 | 0.0018827 | 0.00047184 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2517-7_0_5_load_61 | 89 | 0.007536 | 0.0018887 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2517-7_0_5_load_62 | 90 | 0.0024679 | 0.00061852 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2517-7_0_5_load_63 | 91 | 0.0025565 | 0.00064072 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2517-7_0_5_load_64 | 92 | 0.002419 | 0.00060626 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2517-7_0_5_load_65 | 93 | 0.0017841 | 0.00044715 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2517-7_0_5_load_67 | 95 | 0.0020047 | 0.00050242 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2517-7_0_5_load_104 | 97 | 0.0039194 | 0.00098229 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2517-7_0_5_load_137 | 98 | 0.0018267 | 0.00045781 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2517-7_0_5_load_95 | 99 | 0.0049522 | 0.0012411 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2517-7_0_5_load_138 | 101 | 0.0021719 | 0.00054434 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2517-7_0_5_load_68 | 102 | 0.003515 | 0.00088094 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2517-7_0_5_load_69 | 103 | 0.0017022 | 0.0004266 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2517-7_0_5_load_70 | 104 | 0.0046257 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2517-7_0_5_load_73 | 107 | 0.0019998 | 0.00050119 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2517-7_0_5_load_126 | 109 | 0.0011838 | 0.00029669 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2517-7_0_5_load_120 | 110 | 0.0011122 | 0.00027874 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2517-7_0_5_load_127 | 111 | 0.00091758 | 0.00022997 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2517-7_0_5_load_113 | 113 | 0.0022941 | 0.00057495 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2517-7_0_5_load_105 | 115 | 0.0027866 | 0.00069838 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2517-7_0_5_load_106 | 116 | 0.0092159 | 0.0023097 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2517-7_0_5_load_129 | 117 | 0.0014885 | 0.00037306 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2517-7_0_5_load_78 | 118 | 0.002072 | 0.0005193 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2517-7_0_5_load_79 | 119 | 0.00094025 | 0.00023565 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2517-7_0_5_load_80 | 120 | 0.003569 | 0.00089447 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2517-7_0_5_load_81 | 121 | 0.00094019 | 0.00023563 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2517-7_0_5_load_82 | 122 | 0.0024592 | 0.00061632 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2517-7_0_5_load_83 | 123 | 0.0015609 | 0.0003912 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2517-7_0_5_load_84 | 124 | 0.0014272 | 0.0003577 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2517-7_0_5_load_128 | 125 | 0.0020099 | 0.00050372 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2517-7_0_5_load_85 | 126 | 0.001637 | 0.00041027 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2517-7_0_5_load_86 | 127 | 0.0020502 | 0.00051383 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2517-7_0_5_load_87 | 128 | 0.00097311 | 0.00024388 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2517-7_0_5_load_88 | 129 | 0.011432 | 0.0028651 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2517-7_0_5_load_89 | 130 | 0.00062905 | 0.00015766 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2517-7_0_5_load_123 | 132 | 0.0026573 | 0.00066599 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2517-7_0_5_load_124 | 133 | 0.00067298 | 0.00016867 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2517-7_0_5_load_99 | 134 | 0.0028902 | 0.00072434 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2517-7_0_5_load_100 | 135 | 0.0048434 | 0.0012139 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2517-7_0_5_load_102 | 136 | 0.0023926 | 0.00059964 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2517-7_0_5_load_103 | 137 | 0.0022756 | 0.00057031 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2517-7_0_5_load_107 | 138 | 0.0027122 | 0.00067973 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2517-7_0_5_load_114 | 139 | 0.0015769 | 0.0003952 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2517-7_0_5_load_115 | 140 | 0.0016476 | 0.00041292 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2517-7_0_5_load_116 | 141 | 0.00090411 | 0.00022659 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2517-7_0_5_load_118 | 142 | 0.00099533 | 0.00024945 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2517-7_0_5_load_125 | 143 | 0.00085359 | 0.00021393 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2517-7_0_5_load_147 | 144 | 0.00093942 | 0.00023544 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2517-7_0_5_load_146 | 145 | 0.0022332 | 0.0005597 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2517-7_0_5_load_130 | 146 | 0.00061785 | 0.00015485 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2517-7_0_5_load_152 | 148 | 0.0040502 | 0.0010151 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2517-7_0_5_line_0 |  | 0 | 1 | 0.0024722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2517-7_0_5_line_1 |  | 0 | 2 | 0.011521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2517-7_0_5_line_2 |  | 1 | 3 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2517-7_0_5_line_3 |  | 2 | 4 | 0.016577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2517-7_0_5_line_4 |  | 3 | 5 | 0.016831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2517-7_0_5_line_5 |  | 3 | 6 | 0.037123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2517-7_0_5_line_6 |  | 4 | 7 | 0.0033952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2517-7_0_5_line_7 |  | 5 | 8 | 0.036269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2517-7_0_5_line_8 |  | 5 | 9 | 0.038284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2517-7_0_5_line_9 |  | 7 | 10 | 0.01636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2517-7_0_5_line_10 |  | 8 | 11 | 0.031255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2517-7_0_5_line_11 |  | 8 | 12 | 0.031285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2517-7_0_5_line_12 |  | 9 | 13 | 0.015315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2517-7_0_5_line_13 |  | 10 | 17 | 0.00085235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2517-7_0_5_line_14 |  | 12 | 87 | 0.019863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2517-7_0_5_line_15 |  | 12 | 88 | 0.014301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2517-7_0_5_line_16 |  | 13 | 59 | 0.015569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2517-7_0_5_line_17 |  | 14 | 15 | 0.023543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2517-7_0_5_line_18 |  | 14 | 16 | 0.0067927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2517-7_0_5_line_19 |  | 15 | 79 | 0.0068381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2517-7_0_5_line_20 |  | 16 | 74 | 0.022124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2517-7_0_5_line_21 |  | 17 | 28 | 0.0090581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2517-7_0_5_line_22 |  | 18 | 19 | 0.00072827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2517-7_0_5_line_23 |  | 18 | 20 | 0.057352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2517-7_0_5_line_24 |  | 19 | 21 | 0.020462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2517-7_0_5_line_25 |  | 21 | 22 | 0.027837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2517-7_0_5_line_26 |  | 21 | 23 | 0.0013049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2517-7_0_5_line_27 |  | 22 | 24 | 0.0050871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2517-7_0_5_line_28 |  | 23 | 25 | 0.026699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2517-7_0_5_line_29 |  | 24 | 26 | 0.0043158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2517-7_0_5_line_30 |  | 25 | 27 | 0.0016526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2517-7_0_5_line_31 |  | 26 | 117 | 0.015319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2517-7_0_5_line_32 |  | 27 | 112 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2517-7_0_5_line_33 |  | 28 | 46 | 0.0025444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2517-7_0_5_line_34 |  | 29 | 30 | 0.0028706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2517-7_0_5_line_35 |  | 29 | 31 | 0.019179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2517-7_0_5_line_36 |  | 31 | 32 | 0.028969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2517-7_0_5_line_37 |  | 31 | 33 | 0.009656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2517-7_0_5_line_38 |  | 32 | 34 | 0.027682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2517-7_0_5_line_39 |  | 32 | 35 | 0.02301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2517-7_0_5_line_40 |  | 33 | 36 | 0.0083063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2517-7_0_5_line_41 |  | 35 | 39 | 0.029699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2517-7_0_5_line_42 |  | 37 | 38 | 0.0011911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2517-7_0_5_line_43 |  | 38 | 40 | 0.022773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2517-7_0_5_line_44 |  | 39 | 41 | 0.037177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2517-7_0_5_line_45 |  | 39 | 42 | 0.033846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2517-7_0_5_line_46 |  | 40 | 147 | 0.013971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2517-7_0_5_line_47 |  | 40 | 73 | 0.019384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2517-7_0_5_line_48 |  | 41 | 45 | 0.032617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2517-7_0_5_line_49 |  | 42 | 44 | 0.007387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2517-7_0_5_line_50 |  | 43 | 44 | 0.023198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2517-7_0_5_line_51 |  | 45 | 138 | 0.014547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2517-7_0_5_line_52 |  | 46 | 47 | 0.016982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2517-7_0_5_line_53 |  | 47 | 48 | 0.021552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2517-7_0_5_line_54 |  | 48 | 79 | 0.020982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2517-7_0_5_line_55 |  | 49 | 50 | 0.020831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2517-7_0_5_line_56 |  | 49 | 51 | 0.024205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2517-7_0_5_line_57 |  | 50 | 52 | 0.0068457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2517-7_0_5_line_58 |  | 51 | 53 | 0.021753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2517-7_0_5_line_59 |  | 52 | 54 | 0.023712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2517-7_0_5_line_60 |  | 53 | 55 | 0.033417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2517-7_0_5_line_61 |  | 54 | 56 | 0.001771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2517-7_0_5_line_62 |  | 55 | 57 | 0.014801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2517-7_0_5_line_63 |  | 56 | 58 | 0.020621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2517-7_0_5_line_64 |  | 57 | 60 | 0.0066244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2517-7_0_5_line_65 |  | 59 | 101 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2517-7_0_5_line_66 |  | 60 | 145 | 0.018415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2517-7_0_5_line_67 |  | 61 | 62 | 0.037922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2517-7_0_5_line_68 |  | 62 | 63 | 0.025835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2517-7_0_5_line_69 |  | 62 | 64 | 0.019288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2517-7_0_5_line_70 |  | 63 | 65 | 0.0019622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2517-7_0_5_line_71 |  | 63 | 66 | 0.0089028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2517-7_0_5_line_72 |  | 64 | 67 | 0.027358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2517-7_0_5_line_73 |  | 65 | 68 | 0.032188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2517-7_0_5_line_74 |  | 66 | 69 | 0.012368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2517-7_0_5_line_75 |  | 67 | 70 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2517-7_0_5_line_76 |  | 68 | 71 | 0.030794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2517-7_0_5_line_77 |  | 69 | 72 | 0.014147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2517-7_0_5_line_78 |  | 70 | 73 | 0.0094779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2517-7_0_5_line_79 |  | 71 | 114 | 0.0087176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2517-7_0_5_line_80 |  | 74 | 75 | 0.017675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2517-7_0_5_line_81 |  | 75 | 76 | 0.0094744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2517-7_0_5_line_82 |  | 76 | 77 | 0.013132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2517-7_0_5_line_83 |  | 77 | 78 | 0.026081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2517-7_0_5_line_84 |  | 78 | 80 | 0.022573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2517-7_0_5_line_85 |  | 80 | 82 | 0.053601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2517-7_0_5_line_86 |  | 81 | 82 | 0.029432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2517-7_0_5_line_87 |  | 81 | 83 | 0.070704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2517-7_0_5_line_88 |  | 84 | 85 | 0.012229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2517-7_0_5_line_89 |  | 84 | 86 | 0.029765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2517-7_0_5_line_90 |  | 85 | 131 | 0.0082938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2517-7_0_5_line_91 |  | 86 | 146 | 0.035044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2517-7_0_5_line_92 |  | 87 | 123 | 0.022895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2517-7_0_5_line_93 |  | 88 | 142 | 0.01081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2517-7_0_5_line_94 |  | 89 | 90 | 0.016902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2517-7_0_5_line_95 |  | 89 | 91 | 0.0068678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2517-7_0_5_line_96 |  | 90 | 92 | 0.025688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2517-7_0_5_line_97 |  | 91 | 93 | 0.017392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2517-7_0_5_line_98 |  | 92 | 94 | 0.019485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2517-7_0_5_line_99 |  | 93 | 95 | 0.00485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2517-7_0_5_line_100 |  | 94 | 96 | 0.040501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2517-7_0_5_line_101 |  | 94 | 97 | 0.0069605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2517-7_0_5_line_102 |  | 95 | 98 | 0.017553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2517-7_0_5_line_103 |  | 96 | 99 | 0.022235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2517-7_0_5_line_104 |  | 97 | 100 | 0.028668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2517-7_0_5_line_105 |  | 98 | 101 | 0.0027694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2517-7_0_5_line_106 |  | 99 | 132 | 0.011262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2517-7_0_5_line_107 |  | 100 | 137 | 0.013898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_2517-7_0_5_line_108 |  | 100 | 134 | 0.016279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2517-7_0_5_line_109 |  | 102 | 103 | 0.032941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2517-7_0_5_line_110 |  | 102 | 104 | 0.012005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2517-7_0_5_line_111 |  | 104 | 105 | 0.045893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2517-7_0_5_line_112 |  | 105 | 106 | 0.024139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2517-7_0_5_line_113 |  | 105 | 107 | 0.018172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2517-7_0_5_line_114 |  | 106 | 108 | 0.061994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2517-7_0_5_line_115 |  | 107 | 109 | 0.008426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2517-7_0_5_line_116 |  | 108 | 110 | 0.039943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2517-7_0_5_line_117 |  | 109 | 111 | 0.01717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2517-7_0_5_line_118 |  | 111 | 125 | 0.0041599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2517-7_0_5_line_119 |  | 112 | 113 | 0.0076641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2517-7_0_5_line_120 |  | 112 | 114 | 0.010083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2517-7_0_5_line_121 |  | 113 | 115 | 0.031235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2517-7_0_5_line_122 |  | 114 | 116 | 0.042581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2517-7_0_5_line_123 |  | 115 | 137 | 0.029662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2517-7_0_5_line_124 |  | 116 | 138 | 0.0020588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2517-7_0_5_line_125 |  | 117 | 146 | 0.0004099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2517-7_0_5_line_126 |  | 118 | 119 | 0.025062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2517-7_0_5_line_127 |  | 118 | 120 | 0.029644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2517-7_0_5_line_128 |  | 119 | 121 | 0.00072636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2517-7_0_5_line_129 |  | 120 | 122 | 0.0037827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2517-7_0_5_line_130 |  | 121 | 123 | 0.00013043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2517-7_0_5_line_131 |  | 122 | 124 | 0.020662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2517-7_0_5_line_132 |  | 124 | 125 | 0.016717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2517-7_0_5_line_133 |  | 126 | 127 | 0.00048097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2517-7_0_5_line_134 |  | 126 | 128 | 0.024021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2517-7_0_5_line_135 |  | 127 | 129 | 0.021874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2517-7_0_5_line_136 |  | 128 | 130 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2517-7_0_5_line_137 |  | 130 | 131 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2517-7_0_5_line_138 |  | 132 | 133 | 0.022229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2517-7_0_5_line_139 |  | 133 | 143 | 0.0026395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2517-7_0_5_line_140 |  | 134 | 135 | 0.02151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2517-7_0_5_line_141 |  | 135 | 136 | 0.011177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2517-7_0_5_line_142 |  | 139 | 140 | 0.012429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2517-7_0_5_line_143 |  | 140 | 141 | 0.041088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2517-7_0_5_line_144 |  | 141 | 142 | 0.025307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2517-7_0_5_line_145 |  | 143 | 144 | 0.023032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2517-7_0_5_line_146 |  | 144 | 145 | 0.002368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2517-7_0_5_line_147 |  | 147 | 148 | 0.020559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2517-7_0_5_trafo_75 | 0.63 MVA 20/0.4 kV | 149 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2610970.129 | 1226887.0956 | 2610967.8179 | 1226887.9735
1 | 2610970.129 | 1226887.0956 | 2610980.8988 | 1226883.0042 | 2610980.8988 | 1226883.0042
2 | 2610937.9984 | 1226899.3019 | 2610967.8179 | 1226887.9735
3 | 2610980.8988 | 1226883.0042 | 2610989.7089 | 1226897.0464
4 | 2610934.7017 | 1226882.7972 | 2610937.9984 | 1226899.3019
5 | 2610937.9984 | 1226899.3019 | 2610941.5477 | 1226936.2545
6 | 2610991.5133 | 1226899.9224 | 2610989.7089 | 1226897.0464
7 | 2610899.2733 | 1226878.4745 | 2610906.9582 | 1226878.1994 | 2610921.1988 | 1226877.7029 | 2610934.7017 | 1226882.7972
8 | 2610934.7017 | 1226882.7972 | 2610934.5966 | 1226873.9474 | 2610931.1807 | 1226844.7125
9 | 2610991.5133 | 1226899.9224 | 2610993.699 | 1226903.4063 | 2610996.1794 | 1226915.3997
10 | 2610899.2733 | 1226878.4745 | 2610897.8482 | 1226847.2525
11 | 2610899.2733 | 1226878.4745 | 2610876.3018 | 1226879.2999 | 2610868.0036 | 1226879.2959
12 | 2610929.4033 | 1226829.5006 | 2610931.1807 | 1226844.7125
13 | 2610996.352 | 1226916.2344 | 2610996.1794 | 1226915.3997
14 | 2610868.0036 | 1226879.2959 | 2610867.2284 | 1226899.144
15 | 2610868.0036 | 1226879.2959 | 2610853.7082 | 1226879.7005
16 | 2610929.4033 | 1226829.5006 | 2610944.7419 | 1226826.8346
17 | 2610946.201 | 1226984.7005 | 2610967.7877 | 1226975.3056
18 | 2610946.201 | 1226984.7005 | 2610948.9624 | 1226990.9067
19 | 2610967.7877 | 1226975.3056 | 2610974.0578 | 1226972.5768
20 | 2610948.9624 | 1226990.9067 | 2610951.2953 | 1226996.1499 | 2610958.2497 | 1227005.7572 | 2610961.6572 | 1227008.7342
21 | 2610996.352 | 1226916.2344 | 2610998.1864 | 1226925.1048
22 | 2611074.746 | 1226938.4896 | 2611075.2565 | 1226939.009
23 | 2611038.6996 | 1226894.9064 | 2611043.1043 | 1226906.299 | 2611074.746 | 1226938.4896
24 | 2611089.6004 | 1226953.6018 | 2611075.2565 | 1226939.009
25 | 2611089.6004 | 1226953.6018 | 2611077.8737 | 1226978.8477
26 | 2611089.6004 | 1226953.6018 | 2611090.1515 | 1226952.419
27 | 2611075.7306 | 1226983.4614 | 2611077.8737 | 1226978.8477
28 | 2611090.1515 | 1226952.419 | 2611101.428 | 1226928.2184
29 | 2611075.7306 | 1226983.4614 | 2611073.9125 | 1226987.3756
30 | 2611101.428 | 1226928.2184 | 2611102.126 | 1226926.7204
31 | 2611068.8093 | 1227001.7613 | 2611071.0203 | 1226993.6021 | 2611073.9125 | 1226987.3756
32 | 2611115.599 | 1226897.806 | 2611102.126 | 1226926.7204
33 | 2610998.7017 | 1226927.5965 | 2610998.7017 | 1226927.5965 | 2610998.1864 | 1226925.1048
34 | 2611218.4118 | 1226840.9517 | 2611220.9512 | 1226839.6134
35 | 2611201.445 | 1226849.8934 | 2611218.4118 | 1226840.9517
36 | 2611201.445 | 1226849.8934 | 2611188.9062 | 1226823.7657
37 | 2611201.445 | 1226849.8934 | 2611192.6638 | 1226853.9097
38 | 2611188.9062 | 1226823.7657 | 2611205.7874 | 1226801.8272
39 | 2611188.9062 | 1226823.7657 | 2611176.6057 | 1226804.3195
40 | 2611192.6638 | 1226853.9097 | 2611185.1101 | 1226857.3646
41 | 2611160.7294 | 1226779.2201 | 2611176.6057 | 1226804.3195
42 | 2611264.5985 | 1226870.1612 | 2611264.2513 | 1226869.0219
43 | 2611268.085 | 1226892.3658 | 2611268.3838 | 1226882.5828 | 2611264.5985 | 1226870.1612
44 | 2611160.7294 | 1226779.2201 | 2611156.3398 | 1226788.2061 | 2611136.8957 | 1226799.2542 | 2611136.0606 | 1226803.9937
45 | 2611184.2223 | 1226755.0609 | 2611175.1985 | 1226762.0037 | 2611164.4067 | 1226774.2352 | 2611160.7294 | 1226779.2201
46 | 2611268.085 | 1226892.3658 | 2611276.5572 | 1226896.5397 | 2611279.7281 | 1226898.9138 | 2611280.2048 | 1226899.2705
47 | 2611268.085 | 1226892.3658 | 2611264.0876 | 1226902.2974 | 2611258.3318 | 1226908.7917
48 | 2611130.2787 | 1226836.0929 | 2611131.1971 | 1226831.596 | 2611136.0606 | 1226803.9937
49 | 2611179.0637 | 1226749.7592 | 2611184.2223 | 1226755.0609
50 | 2611179.0637 | 1226749.7592 | 2611156.4004 | 1226744.8083
51 | 2611127.3678 | 1226850.3457 | 2611130.2787 | 1226836.0929
52 | 2610998.7017 | 1226927.5965 | 2610996.603 | 1226935.5973 | 2610989.7876 | 1226941.022
53 | 2610984.4635 | 1226959.1598 | 2610982.9042 | 1226946.5008 | 2610989.7876 | 1226941.022
54 | 2610984.4635 | 1226959.1598 | 2610985.5027 | 1226967.5958 | 2610974.0578 | 1226972.5768
55 | 2610949.4315 | 1226717.3729 | 2610928.791 | 1226720.1833
56 | 2610904.8077 | 1226723.4488 | 2610928.791 | 1226720.1833
57 | 2610949.4315 | 1226717.3729 | 2610956.2146 | 1226716.4493
58 | 2610904.8077 | 1226723.4488 | 2610911.4303 | 1226744.1687
59 | 2610979.71 | 1226713.2502 | 2610956.2146 | 1226716.4493
60 | 2610921.6043 | 1226775.9993 | 2610911.4303 | 1226744.1687
61 | 2610979.71 | 1226713.2502 | 2610981.4648 | 1226713.0112
62 | 2610921.6043 | 1226775.9993 | 2610936.2367 | 1226773.7723
63 | 2611001.8975 | 1226710.2291 | 2610981.4648 | 1226713.0112
64 | 2610942.7856 | 1226772.7756 | 2610936.2367 | 1226773.7723
65 | 2610962.3752 | 1226823.7699 | 2610944.7419 | 1226826.8346
66 | 2610942.7856 | 1226772.7756 | 2610960.9914 | 1226770.0049
67 | 2611204.222 | 1226929.0008 | 2611196.1978 | 1226936.4457 | 2611193.6481 | 1226958.5317 | 2611192.0218 | 1226962.9871
68 | 2611204.222 | 1226929.0008 | 2611190.038 | 1226907.3837
69 | 2611216.0003 | 1226944.2985 | 2611213.7701 | 1226941.4038 | 2611204.222 | 1226929.0008
70 | 2611190.038 | 1226907.3837 | 2611188.7024 | 1226905.9462
71 | 2611190.038 | 1226907.3837 | 2611196.7351 | 1226901.5178
72 | 2611216.0003 | 1226944.2985 | 2611237.1921 | 1226926.9956
73 | 2611163.581 | 1226887.2529 | 2611168.9449 | 1226888.5443 | 2611175.6757 | 1226891.9255 | 2611188.7024 | 1226905.9462
74 | 2611206.0387 | 1226893.3688 | 2611196.7351 | 1226901.5178
75 | 2611251.4983 | 1226915.3148 | 2611239.4075 | 1226925.1867 | 2611237.1921 | 1226926.9956
76 | 2611163.581 | 1226887.2529 | 2611161.8245 | 1226886.83 | 2611152.4041 | 1226887.1015 | 2611133.4495 | 1226891.942
77 | 2611206.0387 | 1226893.3688 | 2611216.6805 | 1226884.0478
78 | 2611251.4983 | 1226915.3148 | 2611255.2933 | 1226912.2201 | 2611258.3318 | 1226908.7917
79 | 2611125.003 | 1226894.0991 | 2611133.4495 | 1226891.942
80 | 2610975.0989 | 1227020.2032 | 2610972.6857 | 1227018.3689 | 2610961.6572 | 1227008.7342
81 | 2610982.6418 | 1227025.9364 | 2610975.0989 | 1227020.2032
82 | 2610982.6418 | 1227025.9364 | 2610993.0963 | 1227033.8828
83 | 2611014.9854 | 1227048.0307 | 2610997.0836 | 1227036.9135 | 2610993.0963 | 1227033.8828
84 | 2611014.9059 | 1227070.5995 | 2611014.9854 | 1227048.0307
85 | 2611014.9059 | 1227070.5995 | 2611016.4985 | 1227107.0016 | 2611008.7011 | 1227115.0031 | 2611002.7155 | 1227115.2698
86 | 2610975.3407 | 1227119.8812 | 2610977.3027 | 1227116.4018 | 2611002.7155 | 1227115.2698
87 | 2610975.3407 | 1227119.8812 | 2610936.1007 | 1227178.6965
88 | 2611058.8749 | 1227066.0557 | 2611068.0086 | 1227074.188
89 | 2611058.8749 | 1227066.0557 | 2611061.1537 | 1227059.0335 | 2611063.8006 | 1227036.8078
90 | 2611074.2028 | 1227079.7032 | 2611068.0086 | 1227074.188
91 | 2611063.8006 | 1227036.8078 | 2611067.3196 | 1227007.2588 | 2611068.7021 | 1227002.1569
92 | 2610866.3349 | 1226922.0215 | 2610867.2284 | 1226899.144
93 | 2610842.9028 | 1226880.0063 | 2610842.9028 | 1226880.0063 | 2610853.7082 | 1226879.7005
94 | 2611010.7755 | 1226814.2833 | 2611026.3305 | 1226807.671
95 | 2611010.7755 | 1226814.2833 | 2611006.5003 | 1226816.1007 | 2611004.3107 | 1226816.4812
96 | 2611026.3305 | 1226807.671 | 2611049.9714 | 1226797.6214
97 | 2610987.1755 | 1226819.4594 | 2611004.3107 | 1226816.4812
98 | 2611067.9035 | 1226789.9985 | 2611049.9714 | 1226797.6214
99 | 2610982.3971 | 1226820.2899 | 2610987.1755 | 1226819.4594
100 | 2611043.8036 | 1226757.4015 | 2611067.9035 | 1226789.9985
101 | 2611067.9035 | 1226789.9985 | 2611071.4601 | 1226795.9818
102 | 2610982.3971 | 1226820.2899 | 2610965.1036 | 1226823.2957
103 | 2611043.8036 | 1226757.4015 | 2611021.8216 | 1226760.747
104 | 2611084.6088 | 1226821.448 | 2611079.7772 | 1226811.3886 | 2611071.4694 | 1226795.9975 | 2611071.4601 | 1226795.9818
105 | 2610965.1036 | 1226823.2957 | 2610962.3752 | 1226823.7699
106 | 2611021.8216 | 1226760.747 | 2611010.6876 | 1226762.4415
107 | 2611084.6088 | 1226821.448 | 2611090.6183 | 1226833.9801
108 | 2611084.6088 | 1226821.448 | 2611069.3124 | 1226827.0194
109 | 2610851.4297 | 1227108.6397 | 2610851.7429 | 1227111.8591 | 2610851.9618 | 1227141.5651
110 | 2610850.267 | 1227096.6909 | 2610851.4297 | 1227108.6397
111 | 2610843.4712 | 1227051.3751 | 2610847.9042 | 1227072.4066 | 2610850.267 | 1227096.6909
112 | 2610836.4351 | 1227028.282 | 2610843.4712 | 1227051.3751
113 | 2610843.4712 | 1227051.3751 | 2610861.3989 | 1227048.4058
114 | 2610836.4351 | 1227028.282 | 2610833.3564 | 1227041.9512 | 2610826.7786 | 1227071.2121 | 2610823.3759 | 1227079.6554 | 2610818.5503 | 1227087.1288
115 | 2610861.3989 | 1227048.4058 | 2610861.7277 | 1227039.9862
116 | 2610818.5503 | 1227087.1288 | 2610778.7784 | 1227083.4363
117 | 2610862.3978 | 1227022.8297 | 2610861.7277 | 1227039.9862
118 | 2610862.5601 | 1227018.673 | 2610862.3978 | 1227022.8297
119 | 2611115.599 | 1226897.806 | 2611112.8648 | 1226890.6462
120 | 2611115.599 | 1226897.806 | 2611125.003 | 1226894.0991
121 | 2611101.7218 | 1226861.4663 | 2611112.8648 | 1226890.6462
122 | 2611125.003 | 1226894.0991 | 2611121.7595 | 1226877.8057 | 2611126.9558 | 1226852.3628
123 | 2611101.7218 | 1226861.4663 | 2611093.5999 | 1226840.1979 | 2611090.6183 | 1226833.9801
124 | 2611127.3678 | 1226850.3457 | 2611126.9558 | 1226852.3628
125 | 2611068.7021 | 1227002.1569 | 2611068.8093 | 1227001.7613
126 | 2610865.3234 | 1226947.9207 | 2610866.3015 | 1226922.8776
127 | 2610864.1665 | 1226977.5426 | 2610865.3234 | 1226947.9207
128 | 2610866.3015 | 1226922.8776 | 2610866.3298 | 1226922.1518
129 | 2610864.1665 | 1226977.5426 | 2610864.0189 | 1226981.3224
130 | 2610866.3298 | 1226922.1518 | 2610866.3349 | 1226922.0215
131 | 2610864.0189 | 1226981.3224 | 2610863.2125 | 1227001.969
132 | 2610863.2125 | 1227001.969 | 2610862.5601 | 1227018.673
133 | 2611110.6764 | 1227027.2608 | 2611110.951 | 1227026.8659
134 | 2611096.9609 | 1227046.9812 | 2611110.6764 | 1227027.2608
135 | 2611123.4405 | 1227008.9083 | 2611110.951 | 1227026.8659
136 | 2611096.9609 | 1227046.9812 | 2611083.5918 | 1227066.2035
137 | 2611074.2028 | 1227079.7032 | 2611083.5918 | 1227066.2035
138 | 2611010.6876 | 1226762.4415 | 2610988.7119 | 1226765.786
139 | 2610986.1025 | 1226766.1831 | 2610988.7119 | 1226765.786
140 | 2611069.3124 | 1226827.0194 | 2611049.1012 | 1226834.3811
141 | 2611038.5996 | 1226838.2061 | 2611049.1012 | 1226834.3811
142 | 2610823.1532 | 1226939.9719 | 2610825.0017 | 1226952.2622
143 | 2610823.1532 | 1226939.9719 | 2610821.6162 | 1226929.7527 | 2610830.5374 | 1226900.3216
144 | 2610842.9028 | 1226880.0063 | 2610835.301 | 1226884.6064 | 2610830.5374 | 1226900.3216
145 | 2610986.1025 | 1226766.1831 | 2610963.3325 | 1226769.6486
146 | 2610960.9914 | 1226770.0049 | 2610963.3325 | 1226769.6486
147 | 2611280.2048 | 1226899.2705 | 2611289.2983 | 1226891.5052 | 2611292.748 | 1226883.6258

## bus_geodata
| x | y | coords
0 | 2610970.129 | 1226887.0956
1 | 2610967.8179 | 1226887.9735
2 | 2610980.8988 | 1226883.0042
3 | 2610937.9984 | 1226899.3019
4 | 2610989.7089 | 1226897.0464
5 | 2610934.7017 | 1226882.7972
6 | 2610941.5477 | 1226936.2545
7 | 2610991.5133 | 1226899.9224
8 | 2610899.2733 | 1226878.4745
9 | 2610931.1807 | 1226844.7125
10 | 2610996.1794 | 1226915.3997
11 | 2610897.8482 | 1226847.2525
12 | 2610868.0036 | 1226879.2959
13 | 2610929.4033 | 1226829.5006
14 | 2610946.201 | 1226984.7005
15 | 2610967.7877 | 1226975.3056
16 | 2610948.9624 | 1226990.9067
17 | 2610996.352 | 1226916.2344
18 | 2611074.746 | 1226938.4896
19 | 2611075.2565 | 1226939.009
20 | 2611038.6996 | 1226894.9064
21 | 2611089.6004 | 1226953.6018
22 | 2611077.8737 | 1226978.8477
23 | 2611090.1515 | 1226952.419
24 | 2611075.7306 | 1226983.4614
25 | 2611101.428 | 1226928.2184
26 | 2611073.9125 | 1226987.3756
27 | 2611102.126 | 1226926.7204
28 | 2610998.1864 | 1226925.1048
29 | 2611218.4118 | 1226840.9517
30 | 2611220.9512 | 1226839.6134
31 | 2611201.445 | 1226849.8934
32 | 2611188.9061 | 1226823.7657
33 | 2611192.6638 | 1226853.9097
34 | 2611205.7874 | 1226801.8272
35 | 2611176.6057 | 1226804.3195
36 | 2611185.1101 | 1226857.3646
37 | 2611264.2513 | 1226869.0219
38 | 2611264.5985 | 1226870.1612
39 | 2611160.7294 | 1226779.2201
40 | 2611268.085 | 1226892.3658
41 | 2611136.0606 | 1226803.9937
42 | 2611184.2223 | 1226755.0609
43 | 2611156.4004 | 1226744.8083
44 | 2611179.0637 | 1226749.7592
45 | 2611130.2787 | 1226836.0929
46 | 2610998.7017 | 1226927.5965
47 | 2610989.7876 | 1226941.022
48 | 2610984.4635 | 1226959.1598
49 | 2610928.791 | 1226720.1833
50 | 2610949.4315 | 1226717.3729
51 | 2610904.8077 | 1226723.4488
52 | 2610956.2146 | 1226716.4493
53 | 2610911.4303 | 1226744.1687
54 | 2610979.71 | 1226713.2502
55 | 2610921.6043 | 1226775.9993
56 | 2610981.4648 | 1226713.0112
57 | 2610936.2367 | 1226773.7723
58 | 2611001.8975 | 1226710.2291
59 | 2610944.7419 | 1226826.8346
60 | 2610942.7856 | 1226772.7756
61 | 2611192.0218 | 1226962.9871
62 | 2611204.222 | 1226929.0008
63 | 2611190.038 | 1226907.3837
64 | 2611216.0003 | 1226944.2985
65 | 2611188.7024 | 1226905.9462
66 | 2611196.7351 | 1226901.5178
67 | 2611237.1921 | 1226926.9956
68 | 2611163.581 | 1226887.2529
69 | 2611206.0387 | 1226893.3688
70 | 2611251.4983 | 1226915.3148
71 | 2611133.4495 | 1226891.942
72 | 2611216.6805 | 1226884.0478
73 | 2611258.3318 | 1226908.7917
74 | 2610961.6572 | 1227008.7342
75 | 2610975.0989 | 1227020.2032
76 | 2610982.6418 | 1227025.9364
77 | 2610993.0963 | 1227033.8828
78 | 2611014.9854 | 1227048.0307
79 | 2610974.0578 | 1226972.5768
80 | 2611014.9059 | 1227070.5995
81 | 2610975.3407 | 1227119.8812
82 | 2611002.7155 | 1227115.2698
83 | 2610936.1007 | 1227178.6965
84 | 2611058.8749 | 1227066.0557
85 | 2611068.0086 | 1227074.188
86 | 2611063.8006 | 1227036.8078
87 | 2610867.2284 | 1226899.144
88 | 2610853.7082 | 1226879.7005
89 | 2611010.7755 | 1226814.2833
90 | 2611026.3305 | 1226807.671
91 | 2611004.3107 | 1226816.4812
92 | 2611049.9714 | 1226797.6214
93 | 2610987.1755 | 1226819.4594
94 | 2611067.9035 | 1226789.9985
95 | 2610982.3971 | 1226820.2899
96 | 2611043.8036 | 1226757.4015
97 | 2611071.4601 | 1226795.9818
98 | 2610965.1036 | 1226823.2957
99 | 2611021.8216 | 1226760.747
100 | 2611084.6088 | 1226821.448
101 | 2610962.3752 | 1226823.7699
102 | 2610851.4297 | 1227108.6397
103 | 2610851.9618 | 1227141.5651
104 | 2610850.267 | 1227096.6909
105 | 2610843.4712 | 1227051.3751
106 | 2610836.4351 | 1227028.282
107 | 2610861.3989 | 1227048.4058
108 | 2610818.5503 | 1227087.1288
109 | 2610861.7277 | 1227039.9862
110 | 2610778.7784 | 1227083.4363
111 | 2610862.3978 | 1227022.8297
112 | 2611115.599 | 1226897.806
113 | 2611112.8648 | 1226890.6462
114 | 2611125.003 | 1226894.0991
115 | 2611101.7218 | 1226861.4663
116 | 2611126.9558 | 1226852.3628
117 | 2611068.8093 | 1227001.7613
118 | 2610865.3234 | 1226947.9207
119 | 2610866.3014 | 1226922.8776
120 | 2610864.1665 | 1226977.5426
121 | 2610866.3298 | 1226922.1518
122 | 2610864.0189 | 1226981.3224
123 | 2610866.3349 | 1226922.0215
124 | 2610863.2125 | 1227001.969
125 | 2610862.5601 | 1227018.673
126 | 2611110.6764 | 1227027.2608
127 | 2611110.951 | 1227026.8659
128 | 2611096.9609 | 1227046.9812
129 | 2611123.4405 | 1227008.9083
130 | 2611083.5918 | 1227066.2035
131 | 2611074.2028 | 1227079.7032
132 | 2611010.6876 | 1226762.4415
133 | 2610988.7119 | 1226765.786
134 | 2611069.3124 | 1226827.0194
135 | 2611049.1012 | 1226834.3811
136 | 2611038.5996 | 1226838.2061
137 | 2611090.6183 | 1226833.9801
138 | 2611127.3678 | 1226850.3457
139 | 2610825.0017 | 1226952.2622
140 | 2610823.1532 | 1226939.9719
141 | 2610830.5374 | 1226900.3216
142 | 2610842.9028 | 1226880.0063
143 | 2610986.1025 | 1226766.1831
144 | 2610963.3325 | 1226769.6486
145 | 2610960.9914 | 1226770.0049
146 | 2611068.7021 | 1227002.1569
147 | 2611280.2048 | 1226899.2705
148 | 2611292.748 | 1226883.6258
149 | 2611089.6004 | 1226953.6018

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98248 | -0.33597 | 0.0045866 | 0.0011495
1 | 0.98253 | -0.33495 | 0.0017592 | 0.0004409
2 | 0.98224 | -0.34051 | 0.0036547 | 0.00091596
3 | 0.98322 | -0.32148 | 0 | 0
4 | 0.98192 | -0.34678 | 0.0088144 | 0.0022091
5 | 0.9836 | -0.31407 | 0 | 0
6 | 0.98308 | -0.32419 | 0.0040579 | 0.001017
7 | 0.98186 | -0.34792 | 0.0015219 | 0.00038142
8 | 0.98206 | -0.34408 | 0 | 0
9 | 0.98488 | -0.28935 | 0.0025981 | 0.00065113
10 | 0.98158 | -0.35334 | 0.0017564 | 0.0004402
11 | 0.9819 | -0.34736 | 0.0058045 | 0.0014547
12 | 0.9809 | -0.36675 | 0 | 0
13 | 0.9854 | -0.2793 | 0 | 0
14 | 0.97787 | -0.42583 | 0 | 0
15 | 0.979 | -0.40362 | 0.0031172 | 0.00078125
16 | 0.97754 | -0.43225 | 0.0012494 | 0.00031314
17 | 0.98157 | -0.35362 | 0.0015279 | 0.00038292
18 | 0.99824 | -0.033787 | 0.0020404 | 0.00051137
19 | 0.99824 | -0.033721 | 0.0021964 | 0.00055047
20 | 0.99808 | -0.036939 | 0.0031411 | 0.00078724
21 | 0.99838 | -0.03108 | 0 | 0
22 | 0.99748 | -0.048305 | 0.002854 | 0.00071528
23 | 0.99843 | -0.030105 | 0.017755 | 0.0044498
24 | 0.99733 | -0.051202 | 0.0034795 | 0.00087204
25 | 0.9999 | -0.0019073 | 0.0057167 | 0.0014327
26 | 0.99722 | -0.053397 | 0.0032444 | 0.00081311
27 | 1 | 0 | -0.5547 | -0.14125
28 | 0.98142 | -0.35649 | 0.0017633 | 0.00044193
29 | 0.98295 | -0.32824 | 0.0082595 | 0.00207
30 | 0.98293 | -0.32866 | 0.0079294 | 0.0019873
31 | 0.98324 | -0.32265 | 0 | 0
32 | 0.98401 | -0.30757 | 0 | 0
33 | 0.98312 | -0.32486 | 0.0034182 | 0.00085668
34 | 0.98373 | -0.31309 | 0.011074 | 0.0027755
35 | 0.98486 | -0.29103 | 0.0098297 | 0.0024636
36 | 0.98305 | -0.32625 | 0.0092822 | 0.0023263
37 | 0.98722 | -0.24547 | 0.0050427 | 0.0012638
38 | 0.98722 | -0.24536 | 0.0037356 | 0.00093622
39 | 0.98622 | -0.26449 | 0.0076019 | 0.0019052
40 | 0.98741 | -0.24178 | 0 | 0
41 | 0.98845 | -0.22128 | 0.010456 | 0.0026206
42 | 0.98598 | -0.2691 | 0 | 0
43 | 0.98577 | -0.27326 | 0.0075951 | 0.0019035
44 | 0.98593 | -0.2701 | 0 | 0
45 | 0.99071 | -0.17748 | 0.010484 | 0.0026275
46 | 0.98138 | -0.35727 | 0.0023324 | 0.00058455
47 | 0.98112 | -0.36234 | 0.0015088 | 0.00037813
48 | 0.98048 | -0.37491 | 0.0069297 | 0.0017368
49 | 0.98698 | -0.24948 | 0.0020815 | 0.00052166
50 | 0.98681 | -0.25262 | 0.000773 | 0.00019373
51 | 0.98721 | -0.24493 | 0 | 0
52 | 0.98677 | -0.25356 | 0.0014081 | 0.0003529
53 | 0.98742 | -0.24085 | 0.0013252 | 0.00033213
54 | 0.98663 | -0.2562 | 0.0015282 | 0.00038301
55 | 0.98778 | -0.23378 | 0 | 0
56 | 0.98662 | -0.25635 | 0.0012848 | 0.00032201
57 | 0.98794 | -0.23065 | 0.00085669 | 0.00021471
58 | 0.98656 | -0.25762 | 0.003425 | 0.00085838
59 | 0.98592 | -0.26909 | 0.0021714 | 0.0005442
60 | 0.98802 | -0.22915 | 0.00072145 | 0.00018081
61 | 0.98613 | -0.26661 | 0.091189 | 0.022854
62 | 0.98931 | -0.20483 | 0 | 0
63 | 0.99214 | -0.15 | 0 | 0
64 | 0.98881 | -0.21456 | 0 | 0
65 | 0.99239 | -0.1453 | 0.0076084 | 0.0019068
66 | 0.99201 | -0.15253 | 0.0025264 | 0.00063317
67 | 0.98809 | -0.22837 | 0.010349 | 0.0025937
68 | 0.99451 | -0.10462 | 0.0028706 | 0.00071944
69 | 0.99186 | -0.15548 | 0.011969 | 0.0029998
70 | 0.98779 | -0.2343 | 0 | 0
71 | 0.99554 | -0.08483 | 0.017906 | 0.0044877
72 | 0.99184 | -0.15586 | 0.0015171 | 0.00038021
73 | 0.98763 | -0.23734 | 0.0051291 | 0.0012855
74 | 0.9765 | -0.45268 | 0.005182 | 0.0012987
75 | 0.97575 | -0.46735 | 0.0042265 | 0.0010593
76 | 0.97538 | -0.47449 | 0.0061223 | 0.0015344
77 | 0.97496 | -0.48293 | 0.0062375 | 0.0015633
78 | 0.97425 | -0.49671 | 0 | 0
79 | 0.97935 | -0.39679 | 0.0025226 | 0.00063223
80 | 0.97365 | -0.50865 | 0 | 0
81 | 0.9715 | -0.55111 | 0.025394 | 0.0063644
82 | 0.97221 | -0.53707 | 0.0029509 | 0.00073957
83 | 0.97147 | -0.55169 | 0.00044649 | 0.0001119
84 | 0.99549 | -0.086799 | 0 | 0
85 | 0.99523 | -0.091628 | 0.00572 | 0.0014336
86 | 0.99609 | -0.075056 | 0.0012244 | 0.00030687
87 | 0.98029 | -0.37865 | 0.002996 | 0.00075086
88 | 0.98081 | -0.36857 | 0.0018827 | 0.00047184
89 | 0.98831 | -0.22303 | 0.007536 | 0.0018887
90 | 0.98896 | -0.21051 | 0.0024679 | 0.00061852
91 | 0.98806 | -0.2279 | 0.0025565 | 0.00064072
92 | 0.98997 | -0.19122 | 0.002419 | 0.00060626
93 | 0.98743 | -0.24002 | 0.0017841 | 0.00044715
94 | 0.99074 | -0.17641 | 0 | 0
95 | 0.98726 | -0.24337 | 0.0020047 | 0.00050242
96 | 0.98978 | -0.19493 | 0 | 0
97 | 0.99106 | -0.17033 | 0.0039194 | 0.00098229
98 | 0.98664 | -0.25533 | 0.0018267 | 0.00045781
99 | 0.98926 | -0.20511 | 0.0049522 | 0.0012411
100 | 0.99239 | -0.14483 | 0 | 0
101 | 0.98654 | -0.2572 | 0.0021719 | 0.00054434
102 | 0.9766 | -0.45113 | 0.003515 | 0.00088094
103 | 0.97655 | -0.45215 | 0.0017022 | 0.0004266
104 | 0.97666 | -0.44998 | 0.0046257 | 0.0011593
105 | 0.97708 | -0.44173 | 0 | 0
106 | 0.97705 | -0.44222 | 0 | 0
107 | 0.97726 | -0.4381 | 0.0019998 | 0.00050119
108 | 0.97699 | -0.44348 | 0 | 0
109 | 0.97737 | -0.4361 | 0.0011838 | 0.00029669
110 | 0.97695 | -0.4443 | 0.0011122 | 0.00027874
111 | 0.97759 | -0.43167 | 0.00091758 | 0.00022997
112 | 0.99647 | -0.06696 | 0 | 0
113 | 0.99609 | -0.074304 | 0.0022941 | 0.00057495
114 | 0.99587 | -0.07855 | 0 | 0
115 | 0.99453 | -0.10397 | 0.0027866 | 0.00069838
116 | 0.99203 | -0.15207 | 0.0092159 | 0.0023097
117 | 0.99686 | -0.060321 | 0.0014885 | 0.00037306
118 | 0.97902 | -0.40368 | 0.002072 | 0.0005193
119 | 0.97963 | -0.39156 | 0.00094025 | 0.00023565
120 | 0.97834 | -0.41692 | 0.003569 | 0.00089447
121 | 0.97965 | -0.3912 | 0.00094019 | 0.00023563
122 | 0.97827 | -0.41836 | 0.0024592 | 0.00061632
123 | 0.97966 | -0.39113 | 0.0015609 | 0.0003912
124 | 0.97791 | -0.42532 | 0.0014272 | 0.0003577
125 | 0.97765 | -0.43053 | 0.0020099 | 0.00050372
126 | 0.99418 | -0.11195 | 0.001637 | 0.00041027
127 | 0.99418 | -0.11207 | 0.0020502 | 0.00051383
128 | 0.99451 | -0.10555 | 0.00097311 | 0.00024388
129 | 0.99395 | -0.11648 | 0.011432 | 0.0028651
130 | 0.99486 | -0.09891 | 0.00062905 | 0.00015766
131 | 0.99511 | -0.094069 | 0 | 0
132 | 0.98904 | -0.20927 | 0.0026573 | 0.00066599
133 | 0.98867 | -0.21645 | 0.00067298 | 0.00016867
134 | 0.99224 | -0.14775 | 0.0028902 | 0.00072434
135 | 0.99209 | -0.15051 | 0.0048434 | 0.0012139
136 | 0.99207 | -0.15098 | 0.0023926 | 0.00059964
137 | 0.99306 | -0.13187 | 0.0022756 | 0.00057031
138 | 0.99186 | -0.15531 | 0.0027122 | 0.00067973
139 | 0.98052 | -0.37422 | 0.0015769 | 0.0003952
140 | 0.98054 | -0.37387 | 0.0016476 | 0.00041292
141 | 0.98066 | -0.37147 | 0.00090411 | 0.00022659
142 | 0.98076 | -0.36957 | 0.00099533 | 0.00024945
143 | 0.98863 | -0.21727 | 0.00085359 | 0.00021393
144 | 0.98828 | -0.22408 | 0.00093942 | 0.00023544
145 | 0.98825 | -0.22474 | 0.0022332 | 0.0005597
146 | 0.99685 | -0.060495 | 0.00061785 | 0.00015485
147 | 0.98735 | -0.24279 | 0 | 0
148 | 0.98728 | -0.24428 | 0.0040502 | 0.0010151
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.092333 | -0.023322 | 0.092338 | 0.023325 | 4.5368e-06 | 2.7783e-06 | 0.13991 | 0.13991 | 0.13991 | 0.98248 | -0.33597 | 0.98253 | -0.33495 | 9.6091
1 | 0.087747 | 0.022173 | -0.087728 | -0.022161 | 1.9095e-05 | 1.1637e-05 | 0.13296 | 0.13296 | 0.13296 | 0.98248 | -0.33597 | 0.98224 | -0.34051 | 9.132
2 | -0.094097 | -0.023766 | 0.094158 | 0.023803 | 6.0788e-05 | 3.7287e-05 | 0.14257 | 0.14257 | 0.14257 | 0.98253 | -0.33495 | 0.98322 | -0.32148 | 9.7921
3 | 0.084073 | 0.021245 | -0.084048 | -0.02123 | 2.5235e-05 | 1.5311e-05 | 0.12743 | 0.12743 | 0.12743 | 0.98224 | -0.34051 | 0.98192 | -0.34678 | 8.7518
4 | -0.098216 | -0.02482 | 0.098251 | 0.024842 | 3.4897e-05 | 2.148e-05 | 0.14871 | 0.14871 | 0.14871 | 0.98322 | -0.32148 | 0.9836 | -0.31407 | 10.2139
5 | 0.0040584 | 0.0010169 | -0.0040579 | -0.001017 | 5.2516e-07 | -1.3465e-07 | 0.0061419 | 0.0061421 | 0.0061421 | 0.98322 | -0.32148 | 0.98308 | -0.32419 | 1.6874
6 | 0.075233 | 0.019021 | -0.075229 | -0.019018 | 4.1416e-06 | 2.4788e-06 | 0.11407 | 0.11407 | 0.11407 | 0.98192 | -0.34678 | 0.98186 | -0.34792 | 7.8344
7 | 0.046045 | 0.011612 | -0.045979 | -0.01157 | 6.6044e-05 | 4.1808e-05 | 0.069684 | 0.069684 | 0.069684 | 0.9836 | -0.31407 | 0.98206 | -0.34408 | 19.1439
8 | -0.1443 | -0.036453 | 0.14447 | 0.036561 | 0.00017119 | 0.00010762 | 0.2184 | 0.2184 | 0.2184 | 0.9836 | -0.31407 | 0.98488 | -0.28935 | 14.9999
9 | 0.073707 | 0.018637 | -0.073688 | -0.018625 | 1.9158e-05 | 1.1434e-05 | 0.11176 | 0.11176 | 0.11176 | 0.98186 | -0.34792 | 0.98158 | -0.35334 | 7.676
10 | 0.0058054 | 0.0014549 | -0.0058045 | -0.0014547 | 9.0688e-07 | 1.8501e-07 | 0.0087963 | 0.0087964 | 0.0087964 | 0.98206 | -0.34408 | 0.9819 | -0.34736 | 2.4166
11 | 0.040174 | 0.010115 | -0.04013 | -0.010087 | 4.3493e-05 | 2.744e-05 | 0.060888 | 0.060888 | 0.060888 | 0.98206 | -0.34408 | 0.9809 | -0.36675 | 16.7274
12 | -0.14707 | -0.037212 | 0.14714 | 0.037257 | 7.0969e-05 | 4.464e-05 | 0.22232 | 0.22232 | 0.22232 | 0.98488 | -0.28935 | 0.9854 | -0.2793 | 15.2694
13 | 0.071932 | 0.018185 | -0.071931 | -0.018185 | 9.5113e-07 | 5.6563e-07 | 0.1091 | 0.1091 | 0.1091 | 0.98158 | -0.35334 | 0.98157 | -0.35362 | 7.4931
14 | 0.033122 | 0.0083317 | -0.033103 | -0.0083199 | 1.8814e-05 | 1.179e-05 | 0.050257 | 0.050257 | 0.050257 | 0.9809 | -0.36675 | 0.98029 | -0.37865 | 13.8068
15 | 0.0070081 | 0.0017557 | -0.0070075 | -0.0017555 | 6.0611e-07 | 2.074e-07 | 0.010631 | 0.010631 | 0.010631 | 0.9809 | -0.36675 | 0.98081 | -0.36857 | 2.9206
16 | -0.14714 | -0.037257 | 0.14721 | 0.037302 | 7.2141e-05 | 4.5377e-05 | 0.22232 | 0.22232 | 0.22232 | 0.9854 | -0.2793 | 0.98592 | -0.26909 | 15.2694
17 | -0.052027 | -0.013121 | 0.052083 | 0.013156 | 5.5376e-05 | 3.5145e-05 | 0.079199 | 0.079199 | 0.079199 | 0.97787 | -0.42583 | 0.979 | -0.40362 | 21.758
18 | 0.052027 | 0.013121 | -0.052011 | -0.01311 | 1.5978e-05 | 1.0141e-05 | 0.079199 | 0.079199 | 0.079199 | 0.97787 | -0.42583 | 0.97754 | -0.43225 | 21.758
19 | -0.0552 | -0.013937 | 0.055218 | 0.013948 | 1.8067e-05 | 1.1477e-05 | 0.083937 | 0.083937 | 0.083937 | 0.979 | -0.40362 | 0.97935 | -0.39679 | 23.0596
20 | 0.050762 | 0.012797 | -0.050712 | -0.012766 | 4.957e-05 | 3.1448e-05 | 0.077297 | 0.077297 | 0.077297 | 0.97754 | -0.43225 | 0.9765 | -0.45268 | 21.2355
21 | 0.070403 | 0.017802 | -0.070393 | -0.017796 | 9.6833e-06 | 5.7394e-06 | 0.10678 | 0.10678 | 0.10678 | 0.98157 | -0.35362 | 0.98142 | -0.35649 | 7.3341
22 | -0.005182 | -0.0012982 | 0.005182 | 0.0012982 | 1.6294e-08 | 9.0761e-10 | 0.0077243 | 0.0077243 | 0.0077243 | 0.99824 | -0.033787 | 0.99824 | -0.033721 | 2.1221
23 | 0.0031416 | 0.00078679 | -0.0031411 | -0.00078724 | 4.7165e-07 | -4.478e-07 | 0.0046828 | 0.0046831 | 0.0046831 | 0.99824 | -0.033787 | 0.99808 | -0.036939 | 1.2866
24 | -0.0073784 | -0.0018486 | 0.0073793 | 0.001849 | 9.2817e-07 | 3.2649e-07 | 0.010998 | 0.010998 | 0.010998 | 0.99824 | -0.033721 | 0.99838 | -0.03108 | 3.0215
25 | 0.035448 | 0.0089191 | -0.035418 | -0.0089008 | 2.9151e-05 | 1.8293e-05 | 0.052844 | 0.052845 | 0.052845 | 0.99838 | -0.03108 | 0.99748 | -0.048305 | 14.5177
26 | -0.042827 | -0.010768 | 0.042829 | 0.010769 | 1.9945e-06 | 1.2594e-06 | 0.063843 | 0.063843 | 0.063843 | 0.99838 | -0.03108 | 0.99843 | -0.030105 | 17.5392
27 | 0.032564 | 0.0081855 | -0.03256 | -0.0081827 | 4.5035e-06 | 2.8158e-06 | 0.048587 | 0.048587 | 0.048587 | 0.99748 | -0.048305 | 0.99733 | -0.051202 | 13.3481
28 | -0.060584 | -0.015219 | 0.060666 | 0.015271 | 8.1646e-05 | 5.1904e-05 | 0.090304 | 0.090304 | 0.090304 | 0.99843 | -0.030105 | 0.9999 | -0.0019073 | 24.8088
29 | 0.02908 | 0.0073107 | -0.029077 | -0.0073088 | 3.0478e-06 | 1.8943e-06 | 0.043396 | 0.043396 | 0.043396 | 0.99733 | -0.051202 | 0.99722 | -0.053397 | 11.9219
30 | -0.066382 | -0.016704 | 0.066388 | 0.016708 | 6.0508e-06 | 3.8509e-06 | 0.098811 | 0.098811 | 0.098811 | 0.9999 | -0.0019073 | 1 | 0 | 27.1459
31 | 0.025833 | 0.0064957 | -0.025824 | -0.0064904 | 8.5391e-06 | 5.2652e-06 | 0.038555 | 0.038555 | 0.038555 | 0.99722 | -0.053397 | 0.99686 | -0.060321 | 10.5919
32 | 0.48666 | 0.12454 | -0.48509 | -0.12354 | 0.0015722 | 0.0010046 | 0.72507 | 0.72507 | 0.72507 | 1 | 0 | 0.99647 | -0.06696 | 49.7988
33 | 0.06863 | 0.017354 | -0.068627 | -0.017353 | 2.5855e-06 | 1.5261e-06 | 0.10411 | 0.10411 | 0.10411 | 0.98142 | -0.35649 | 0.98138 | -0.35727 | 7.1505
34 | 0.0079296 | 0.0019874 | -0.0079294 | -0.0019873 | 1.5511e-07 | 6.2887e-08 | 0.012004 | 0.012004 | 0.012004 | 0.98295 | -0.32824 | 0.98293 | -0.32866 | 3.2978
35 | -0.016189 | -0.0040574 | 0.016193 | 0.0040599 | 4.3196e-06 | 2.5214e-06 | 0.024507 | 0.024507 | 0.024507 | 0.98295 | -0.32824 | 0.98324 | -0.32265 | 6.7328
36 | -0.028896 | -0.0072439 | 0.028916 | 0.0072569 | 2.0775e-05 | 1.2928e-05 | 0.043731 | 0.043731 | 0.043731 | 0.98324 | -0.32265 | 0.98401 | -0.30757 | 12.014
37 | 0.012702 | 0.003184 | -0.012701 | -0.0031833 | 1.3382e-06 | 7.3397e-07 | 0.019224 | 0.019224 | 0.019224 | 0.98324 | -0.32265 | 0.98312 | -0.32486 | 5.2813
38 | 0.011077 | 0.002777 | -0.011074 | -0.0027755 | 2.9129e-06 | 1.5127e-06 | 0.016751 | 0.016752 | 0.016752 | 0.98401 | -0.30757 | 0.98373 | -0.31309 | 4.6021
39 | -0.039994 | -0.010034 | 0.040025 | 0.010054 | 3.1565e-05 | 1.9909e-05 | 0.060482 | 0.060482 | 0.060482 | 0.98401 | -0.30757 | 0.98486 | -0.29103 | 16.616
40 | 0.0092828 | 0.0023266 | -0.0092822 | -0.0023263 | 6.149e-07 | 2.8822e-07 | 0.01405 | 0.01405 | 0.01405 | 0.98312 | -0.32486 | 0.98305 | -0.32625 | 3.8599
41 | -0.049855 | -0.012517 | 0.049918 | 0.012557 | 6.3205e-05 | 4.0073e-05 | 0.075334 | 0.075334 | 0.075334 | 0.98486 | -0.29103 | 0.98622 | -0.26449 | 20.6961
42 | -0.0050427 | -0.0012638 | 0.0050427 | 0.0012638 | 2.5805e-08 | 1.2852e-09 | 0.0076007 | 0.0076007 | 0.0076007 | 0.98722 | -0.24547 | 0.98722 | -0.24536 | 2.0881
43 | -0.0087783 | -0.0022 | 0.0087798 | 0.0022007 | 1.495e-06 | 6.6559e-07 | 0.013231 | 0.013231 | 0.013231 | 0.98722 | -0.24536 | 0.98741 | -0.24178 | 3.635
44 | -0.065118 | -0.016367 | 0.065253 | 0.016453 | 0.00013463 | 8.5685e-05 | 0.098268 | 0.098268 | 0.098268 | 0.98622 | -0.26449 | 0.98845 | -0.22128 | 26.9967
45 | 0.0075982 | 0.0019047 | -0.0075966 | -0.0019041 | 1.6682e-06 | 6.3587e-07 | 0.011464 | 0.011465 | 0.011465 | 0.98622 | -0.26449 | 0.98598 | -0.2691 | 3.1496
46 | 0.0040507 | 0.0010149 | -0.0040505 | -0.001015 | 1.9522e-07 | -5.375e-08 | 0.0061043 | 0.0061043 | 0.0061043 | 0.98741 | -0.24178 | 0.98735 | -0.24279 | 1.677
47 | -0.01283 | -0.0032156 | 0.012833 | 0.0032171 | 2.7175e-06 | 1.4912e-06 | 0.019335 | 0.019335 | 0.019335 | 0.98741 | -0.24178 | 0.98763 | -0.23734 | 5.3119
48 | -0.07571 | -0.019074 | 0.075868 | 0.019175 | 0.00015899 | 0.00010133 | 0.11401 | 0.11401 | 0.11401 | 0.98845 | -0.22128 | 0.99071 | -0.17748 | 31.3212
49 | 0.0075966 | 0.0019041 | -0.0075962 | -0.0019039 | 3.641e-07 | 1.3881e-07 | 0.011465 | 0.011465 | 0.011465 | 0.98598 | -0.2691 | 0.98593 | -0.2701 | 3.1496
50 | -0.0075951 | -0.0019035 | 0.0075962 | 0.0019039 | 1.1434e-06 | 4.3599e-07 | 0.011465 | 0.011465 | 0.011465 | 0.98577 | -0.27326 | 0.98593 | -0.2701 | 3.1496
51 | -0.086352 | -0.021802 | 0.086444 | 0.021861 | 9.1844e-05 | 5.8593e-05 | 0.12976 | 0.12976 | 0.12976 | 0.99071 | -0.17748 | 0.99186 | -0.15531 | 35.647
52 | 0.066295 | 0.016768 | -0.066279 | -0.016759 | 1.6104e-05 | 9.4487e-06 | 0.10057 | 0.10057 | 0.10057 | 0.98138 | -0.35727 | 0.98112 | -0.36234 | 6.9076
53 | 0.06477 | 0.01638 | -0.064731 | -0.016356 | 3.9037e-05 | 2.444e-05 | 0.098286 | 0.098286 | 0.098286 | 0.98112 | -0.36234 | 0.98048 | -0.37491 | 13.5009
54 | 0.057801 | 0.014619 | -0.057741 | -0.014581 | 6.0612e-05 | 3.8527e-05 | 0.08777 | 0.08777 | 0.08777 | 0.98048 | -0.37491 | 0.97935 | -0.39679 | 24.1125
55 | 0.0084218 | 0.0021108 | -0.0084205 | -0.0021102 | 1.2594e-06 | 5.3983e-07 | 0.012697 | 0.012697 | 0.012697 | 0.98698 | -0.24948 | 0.98681 | -0.25262 | 3.4883
56 | -0.010503 | -0.0026324 | 0.010506 | 0.0026336 | 2.276e-06 | 1.1473e-06 | 0.015835 | 0.015835 | 0.015835 | 0.98698 | -0.24948 | 0.98721 | -0.24493 | 4.3504
57 | 0.0076475 | 0.0019165 | -0.0076472 | -0.0019164 | 3.4138e-07 | 1.3103e-07 | 0.011532 | 0.011532 | 0.011532 | 0.98681 | -0.25262 | 0.98677 | -0.25356 | 3.168
58 | -0.010506 | -0.0026336 | 0.010508 | 0.0026346 | 2.0454e-06 | 1.0309e-06 | 0.015835 | 0.015835 | 0.015835 | 0.98721 | -0.24493 | 0.98742 | -0.24085 | 4.3503
59 | 0.0062391 | 0.0015635 | -0.0062383 | -0.0015633 | 7.871e-07 | 2.0088e-07 | 0.0094083 | 0.0094084 | 0.0094084 | 0.98677 | -0.25356 | 0.98663 | -0.2562 | 2.5847
60 | -0.011833 | -0.0029668 | 0.011837 | 0.0029689 | 3.9848e-06 | 2.1227e-06 | 0.017832 | 0.017832 | 0.017832 | 0.98742 | -0.24085 | 0.98778 | -0.23378 | 4.8989
61 | 0.0047101 | 0.0011803 | -0.00471 | -0.0011803 | 3.3512e-08 | -1.1693e-09 | 0.0071036 | 0.0071036 | 0.0071036 | 0.98663 | -0.2562 | 0.98662 | -0.25635 | 1.9515
62 | -0.011837 | -0.0029689 | 0.011839 | 0.0029698 | 1.7649e-06 | 9.4004e-07 | 0.017832 | 0.017832 | 0.017832 | 0.98778 | -0.23378 | 0.98794 | -0.23065 | 4.8989
63 | 0.0034252 | 0.00085825 | -0.003425 | -0.00085838 | 2.0636e-07 | -1.3126e-07 | 0.0051658 | 0.0051659 | 0.0051659 | 0.98662 | -0.25635 | 0.98656 | -0.25762 | 1.4192
64 | -0.012695 | -0.0031845 | 0.012696 | 0.003185 | 9.0835e-07 | 4.9652e-07 | 0.019122 | 0.019122 | 0.019122 | 0.98794 | -0.23065 | 0.98802 | -0.22915 | 5.2534
65 | -0.14938 | -0.037846 | 0.14947 | 0.0379 | 8.5397e-05 | 5.374e-05 | 0.2256 | 0.2256 | 0.2256 | 0.98592 | -0.26909 | 0.98654 | -0.2572 | 15.4944
66 | -0.013418 | -0.0033658 | 0.01342 | 0.0033674 | 2.8203e-06 | 1.5691e-06 | 0.020209 | 0.020209 | 0.020209 | 0.98802 | -0.22915 | 0.98825 | -0.22474 | 5.5519
67 | -0.091189 | -0.022854 | 0.091458 | 0.023026 | 0.00026925 | 0.00017183 | 0.1376 | 0.1376 | 0.1376 | 0.98613 | -0.26661 | 0.98931 | -0.20483 | 37.8022
68 | -0.11981 | -0.030147 | 0.12012 | 0.030348 | 0.00031476 | 0.00020111 | 0.18025 | 0.18025 | 0.18025 | 0.98931 | -0.20483 | 0.99214 | -0.15 | 49.5186
69 | 0.028351 | 0.0071207 | -0.028338 | -0.0071125 | 1.3156e-05 | 8.1722e-06 | 0.042648 | 0.042648 | 0.042648 | 0.98931 | -0.20483 | 0.98881 | -0.21456 | 11.7165
70 | -0.13614 | -0.034363 | 0.13617 | 0.034383 | 3.0703e-05 | 1.9625e-05 | 0.20427 | 0.20427 | 0.20427 | 0.99214 | -0.15 | 0.99239 | -0.1453 | 56.1181
71 | 0.016017 | 0.0040152 | -0.016015 | -0.0040141 | 1.9266e-06 | 1.1181e-06 | 0.024022 | 0.024022 | 0.024022 | 0.99214 | -0.15 | 0.99201 | -0.15253 | 6.5995
72 | 0.028338 | 0.0071125 | -0.028319 | -0.0071009 | 1.8661e-05 | 1.1592e-05 | 0.042648 | 0.042648 | 0.042648 | 0.98881 | -0.21456 | 0.98809 | -0.22837 | 11.7165
73 | -0.14378 | -0.036289 | 0.14406 | 0.036468 | 0.00028074 | 0.00017884 | 0.21568 | 0.21568 | 0.21568 | 0.99239 | -0.1453 | 0.99451 | -0.10462 | 29.6261
74 | 0.013488 | 0.0033809 | -0.013487 | -0.0033799 | 1.8986e-06 | 1.0555e-06 | 0.020233 | 0.020233 | 0.020233 | 0.99201 | -0.15253 | 0.99186 | -0.15548 | 5.5585
75 | 0.01797 | 0.0045072 | -0.017965 | -0.0045042 | 5.0726e-06 | 3.01e-06 | 0.027063 | 0.027063 | 0.027063 | 0.98809 | -0.22837 | 0.98779 | -0.2343 | 7.4349
76 | -0.14693 | -0.037188 | 0.14707 | 0.037276 | 0.00013969 | 8.7804e-05 | 0.21997 | 0.21997 | 0.21997 | 0.99451 | -0.10462 | 0.99554 | -0.08483 | 15.108
77 | 0.0015171 | 0.00038005 | -0.0015171 | -0.00038021 | 2.748e-08 | -1.65e-07 | 0.0022759 | 0.002276 | 0.002276 | 0.99186 | -0.15548 | 0.99184 | -0.15586 | 0.62527
78 | 0.017965 | 0.0045042 | -0.017962 | -0.0045026 | 2.6032e-06 | 1.5447e-06 | 0.027063 | 0.027063 | 0.027063 | 0.98779 | -0.2343 | 0.98763 | -0.23734 | 7.4349
79 | -0.16498 | -0.041763 | 0.16503 | 0.041795 | 4.9754e-05 | 3.1389e-05 | 0.24674 | 0.24674 | 0.24674 | 0.99554 | -0.08483 | 0.99587 | -0.07855 | 16.9462
80 | 0.04553 | 0.011467 | -0.045498 | -0.011447 | 3.1925e-05 | 2.0211e-05 | 0.069401 | 0.069401 | 0.069401 | 0.9765 | -0.45268 | 0.97575 | -0.46735 | 19.0661
81 | 0.041272 | 0.010388 | -0.041258 | -0.010379 | 1.4081e-05 | 8.8939e-06 | 0.062955 | 0.062955 | 0.062955 | 0.97575 | -0.46735 | 0.97538 | -0.47449 | 17.2954
82 | 0.035135 | 0.0088444 | -0.035121 | -0.0088355 | 1.4156e-05 | 8.8958e-06 | 0.053615 | 0.053615 | 0.053615 | 0.97538 | -0.47449 | 0.97496 | -0.48293 | 14.7295
83 | 0.028884 | 0.0072722 | -0.028865 | -0.0072604 | 1.9017e-05 | 1.1846e-05 | 0.044095 | 0.044096 | 0.044096 | 0.97496 | -0.48293 | 0.97425 | -0.49671 | 12.1142
84 | 0.028865 | 0.0072604 | -0.028848 | -0.0072501 | 1.6459e-05 | 1.0253e-05 | 0.044096 | 0.044096 | 0.044096 | 0.97425 | -0.49671 | 0.97365 | -0.50865 | 12.1142
85 | 0.028848 | 0.0072501 | -0.028809 | -0.0072258 | 3.9084e-05 | 2.4348e-05 | 0.044096 | 0.044096 | 0.044096 | 0.97365 | -0.50865 | 0.97221 | -0.53707 | 12.1143
86 | -0.025841 | -0.0064755 | 0.025858 | 0.0064862 | 1.729e-05 | 1.0701e-05 | 0.03958 | 0.039579 | 0.03958 | 0.9715 | -0.55111 | 0.97221 | -0.53707 | 10.8735
87 | 0.00044651 | 0.00011103 | -0.00044649 | -0.0001119 | 1.2395e-08 | -8.675e-07 | 0.00068359 | 0.0006839 | 0.0006839 | 0.9715 | -0.55111 | 0.97147 | -0.55169 | 0.18789
88 | 0.022464 | 0.0056377 | -0.022459 | -0.0056346 | 5.1718e-06 | 3.151e-06 | 0.033582 | 0.033582 | 0.033582 | 0.99549 | -0.086799 | 0.99523 | -0.091628 | 9.2257
89 | -0.022464 | -0.0056377 | 0.022477 | 0.0056454 | 1.2588e-05 | 7.6689e-06 | 0.033582 | 0.033582 | 0.033582 | 0.99549 | -0.086799 | 0.99609 | -0.075056 | 9.2257
90 | 0.016739 | 0.004201 | -0.016737 | -0.0041999 | 1.9485e-06 | 1.1393e-06 | 0.02503 | 0.02503 | 0.02503 | 0.99523 | -0.091628 | 0.99511 | -0.094069 | 6.8763
91 | -0.023701 | -0.0059523 | 0.023718 | 0.0059624 | 1.6478e-05 | 1.0089e-05 | 0.035411 | 0.03541 | 0.035411 | 0.99609 | -0.075056 | 0.99685 | -0.060495 | 9.7282
92 | 0.030107 | 0.007569 | -0.030089 | -0.0075578 | 1.7938e-05 | 1.1192e-05 | 0.045709 | 0.045709 | 0.045709 | 0.98029 | -0.37865 | 0.97966 | -0.39113 | 12.5575
93 | 0.0051249 | 0.0012837 | -0.0051246 | -0.0012837 | 2.4504e-07 | 2.0405e-08 | 0.0077748 | 0.0077749 | 0.0077749 | 0.98081 | -0.36857 | 0.98076 | -0.36957 | 2.136
94 | -0.1676 | -0.042542 | 0.1677 | 0.042606 | 0.00010105 | 6.3808e-05 | 0.25254 | 0.25253 | 0.25254 | 0.98831 | -0.22303 | 0.98896 | -0.21051 | 17.3444
95 | 0.16007 | 0.040654 | -0.16003 | -0.04063 | 3.7454e-05 | 2.3619e-05 | 0.24119 | 0.24119 | 0.24119 | 0.98831 | -0.22303 | 0.98806 | -0.2279 | 16.5652
96 | -0.17017 | -0.043225 | 0.17033 | 0.043325 | 0.00015813 | 9.9886e-05 | 0.25625 | 0.25625 | 0.25625 | 0.98896 | -0.21051 | 0.98997 | -0.19122 | 17.5995
97 | 0.15747 | 0.039989 | -0.15738 | -0.039932 | 9.1847e-05 | 5.7891e-05 | 0.23734 | 0.23734 | 0.23734 | 0.98806 | -0.2279 | 0.98743 | -0.24002 | 16.3008
98 | -0.17275 | -0.043931 | 0.17287 | 0.044009 | 0.00012338 | 7.7958e-05 | 0.25988 | 0.25988 | 0.25988 | 0.98997 | -0.19122 | 0.99074 | -0.17641 | 17.8491
99 | 0.1556 | 0.039484 | -0.15557 | -0.039469 | 2.5035e-05 | 1.5774e-05 | 0.23465 | 0.23465 | 0.23465 | 0.98743 | -0.24002 | 0.98726 | -0.24337 | 16.1161
100 | 0.025781 | 0.0064841 | -0.025759 | -0.00647 | 2.2782e-05 | 1.4059e-05 | 0.03873 | 0.03873 | 0.03873 | 0.99074 | -0.17641 | 0.98978 | -0.19493 | 10.6401
101 | -0.19865 | -0.050493 | 0.19871 | 0.05053 | 5.8187e-05 | 3.6881e-05 | 0.29861 | 0.29861 | 0.29861 | 0.99074 | -0.17641 | 0.99106 | -0.17033 | 20.5091
102 | 0.15357 | 0.038966 | -0.15348 | -0.038911 | 8.8289e-05 | 5.5607e-05 | 0.23163 | 0.23163 | 0.23163 | 0.98726 | -0.24337 | 0.98664 | -0.25533 | 15.9086
103 | 0.025759 | 0.00647 | -0.025746 | -0.0064623 | 1.2507e-05 | 7.7191e-06 | 0.03873 | 0.03873 | 0.03873 | 0.98978 | -0.19493 | 0.98926 | -0.20511 | 10.6401
104 | -0.20263 | -0.051512 | 0.20288 | 0.05167 | 0.00024919 | 0.000158 | 0.3045 | 0.3045 | 0.3045 | 0.99106 | -0.17033 | 0.99239 | -0.14483 | 20.9133
105 | 0.15165 | 0.038453 | -0.15164 | -0.038444 | 1.36e-05 | 8.5627e-06 | 0.22887 | 0.22887 | 0.22887 | 0.98664 | -0.25533 | 0.98654 | -0.2572 | 15.7194
106 | 0.020794 | 0.0052212 | -0.02079 | -0.0052187 | 4.1326e-06 | 2.5003e-06 | 0.031281 | 0.031281 | 0.031281 | 0.98926 | -0.20511 | 0.98904 | -0.20927 | 8.5937
107 | -0.21301 | -0.054209 | 0.21314 | 0.054293 | 0.00013316 | 8.4505e-05 | 0.31968 | 0.31968 | 0.31968 | 0.99239 | -0.14483 | 0.99306 | -0.13187 | 21.9563
108 | 0.010129 | 0.0025388 | -0.010127 | -0.0025381 | 1.4081e-06 | 6.9086e-07 | 0.015187 | 0.015187 | 0.015187 | 0.99239 | -0.14483 | 0.99224 | -0.14775 | 4.1723
109 | 0.0017022 | 0.00042624 | -0.0017022 | -0.0004266 | 8.3094e-08 | -3.5898e-07 | 0.0025935 | 0.0025937 | 0.0025937 | 0.9766 | -0.45113 | 0.97655 | -0.45215 | 0.71254
110 | -0.0052172 | -0.0013072 | 0.0052175 | 0.0013072 | 2.8448e-07 | 3.1839e-08 | 0.0079492 | 0.0079491 | 0.0079492 | 0.9766 | -0.45113 | 0.97666 | -0.44998 | 2.1838
111 | -0.0098432 | -0.0024665 | 0.0098471 | 0.0024684 | 3.8705e-06 | 1.9026e-06 | 0.014997 | 0.014997 | 0.014997 | 0.97666 | -0.44998 | 0.97708 | -0.44173 | 4.12
112 | 0.0011123 | 0.00027724 | -0.0011123 | -0.00027753 | 2.596e-08 | -2.8571e-07 | 0.0016934 | 0.0016935 | 0.0016935 | 0.97708 | -0.44173 | 0.97705 | -0.44222 | 0.46525
113 | -0.010959 | -0.0027457 | 0.010961 | 0.0027467 | 1.8982e-06 | 9.872e-07 | 0.01669 | 0.01669 | 0.01669 | 0.97708 | -0.44173 | 0.97726 | -0.4381 | 4.5852
114 | 0.0011123 | 0.00027753 | -0.0011122 | -0.00027826 | 6.6685e-08 | -7.3369e-07 | 0.0016935 | 0.0016938 | 0.0016938 | 0.97705 | -0.44222 | 0.97699 | -0.44348 | 0.46533
115 | -0.012961 | -0.0032479 | 0.012962 | 0.0032485 | 1.2306e-06 | 6.82e-07 | 0.019735 | 0.019735 | 0.019735 | 0.97726 | -0.4381 | 0.97737 | -0.4361 | 5.4216
116 | 0.0011122 | 0.00027826 | -0.0011122 | -0.00027874 | 4.2977e-08 | -4.7266e-07 | 0.0016938 | 0.001694 | 0.001694 | 0.97699 | -0.44348 | 0.97695 | -0.4443 | 0.46538
117 | -0.014146 | -0.0035452 | 0.014149 | 0.0035469 | 2.9865e-06 | 1.6961e-06 | 0.021537 | 0.021537 | 0.021537 | 0.97737 | -0.4361 | 0.97759 | -0.43167 | 5.9168
118 | -0.015067 | -0.0037769 | 0.015068 | 0.0037774 | 8.2047e-07 | 4.7294e-07 | 0.022934 | 0.022934 | 0.022934 | 0.97759 | -0.43167 | 0.97765 | -0.43053 | 6.3005
119 | 0.22118 | 0.05657 | -0.2211 | -0.05652 | 7.8573e-05 | 4.9887e-05 | 0.33069 | 0.33069 | 0.33069 | 0.99647 | -0.06696 | 0.99609 | -0.074304 | 22.7121
120 | 0.26391 | 0.06697 | -0.26376 | -0.066876 | 0.00014703 | 9.3572e-05 | 0.39438 | 0.39438 | 0.39438 | 0.99647 | -0.06696 | 0.99587 | -0.07855 | 27.0867
121 | 0.21881 | 0.055945 | -0.21849 | -0.055746 | 0.00031362 | 0.00019909 | 0.32726 | 0.32726 | 0.32726 | 0.99609 | -0.074304 | 0.99453 | -0.10397 | 22.4768
122 | 0.098734 | 0.025082 | -0.098386 | -0.024859 | 0.0003481 | 0.00022223 | 0.14765 | 0.14765 | 0.14765 | 0.99587 | -0.07855 | 0.99203 | -0.15207 | 40.5625
123 | 0.21571 | 0.055048 | -0.21542 | -0.054864 | 0.00029029 | 0.00018425 | 0.32309 | 0.32309 | 0.32309 | 0.99453 | -0.10397 | 0.99306 | -0.13187 | 22.1905
124 | 0.08917 | 0.02255 | -0.089156 | -0.022541 | 1.3826e-05 | 8.8222e-06 | 0.13382 | 0.13382 | 0.13382 | 0.99203 | -0.15207 | 0.99186 | -0.15531 | 36.7648
125 | 0.024336 | 0.0061173 | -0.024336 | -0.0061172 | 2.0291e-07 | 1.2452e-07 | 0.036333 | 0.036333 | 0.036333 | 0.99686 | -0.060321 | 0.99685 | -0.060495 | 9.9815
126 | -0.026632 | -0.0066855 | 0.026647 | 0.006695 | 1.5402e-05 | 9.542e-06 | 0.040482 | 0.040482 | 0.040482 | 0.97902 | -0.40368 | 0.97963 | -0.39156 | 11.1215
127 | 0.02456 | 0.0061662 | -0.024545 | -0.0061566 | 1.5494e-05 | 9.5436e-06 | 0.037333 | 0.037333 | 0.037333 | 0.97902 | -0.40368 | 0.97834 | -0.41692 | 10.2563
128 | -0.027588 | -0.0069307 | 0.027588 | 0.0069309 | 4.7844e-07 | 2.9705e-07 | 0.04191 | 0.04191 | 0.04191 | 0.97963 | -0.39156 | 0.97965 | -0.3912 | 11.5138
129 | 0.020976 | 0.0052622 | -0.020974 | -0.0052613 | 1.4439e-06 | 8.7662e-07 | 0.031905 | 0.031905 | 0.031905 | 0.97834 | -0.41692 | 0.97827 | -0.41836 | 8.7651
130 | -0.028528 | -0.0071666 | 0.028528 | 0.0071666 | 9.1864e-08 | 5.715e-08 | 0.043338 | 0.043338 | 0.043338 | 0.97965 | -0.3912 | 0.97966 | -0.39113 | 11.9061
131 | 0.018515 | 0.004645 | -0.018509 | -0.0046413 | 6.1462e-06 | 3.6743e-06 | 0.028164 | 0.028164 | 0.028164 | 0.97827 | -0.41836 | 0.97791 | -0.42532 | 7.7375
132 | 0.017082 | 0.0042836 | -0.017077 | -0.0042811 | 4.2353e-06 | 2.5009e-06 | 0.025993 | 0.025993 | 0.025993 | 0.97791 | -0.42532 | 0.97765 | -0.43053 | 7.1409
133 | 0.013485 | 0.0033802 | -0.013484 | -0.0033802 | 7.347e-08 | 4.0784e-08 | 0.020183 | 0.020183 | 0.020183 | 0.99418 | -0.11195 | 0.99418 | -0.11207 | 5.5448
134 | -0.015122 | -0.0037905 | 0.015126 | 0.0037931 | 4.6143e-06 | 2.6416e-06 | 0.022633 | 0.022633 | 0.022633 | 0.99418 | -0.11195 | 0.99451 | -0.10555 | 6.2179
135 | 0.011434 | 0.0028664 | -0.011432 | -0.0028651 | 2.4026e-06 | 1.2541e-06 | 0.017114 | 0.017114 | 0.017114 | 0.99418 | -0.11207 | 0.99395 | -0.11648 | 4.7018
136 | -0.016099 | -0.004037 | 0.016104 | 0.00404 | 5.095e-06 | 2.9569e-06 | 0.024089 | 0.024089 | 0.024089 | 0.99451 | -0.10555 | 0.99486 | -0.09891 | 6.6178
137 | -0.016733 | -0.0041976 | 0.016737 | 0.0041999 | 3.8631e-06 | 2.2588e-06 | 0.02503 | 0.02503 | 0.02503 | 0.99486 | -0.09891 | 0.99511 | -0.094069 | 6.8763
138 | 0.018132 | 0.0045527 | -0.018126 | -0.004549 | 6.2049e-06 | 3.686e-06 | 0.027283 | 0.027283 | 0.027283 | 0.98904 | -0.20927 | 0.98867 | -0.21645 | 7.4954
139 | 0.017453 | 0.0043803 | -0.017453 | -0.0043799 | 6.8309e-07 | 4.0333e-07 | 0.02627 | 0.02627 | 0.02627 | 0.98867 | -0.21645 | 0.98863 | -0.21727 | 7.2171
140 | 0.007237 | 0.0018137 | -0.007236 | -0.0018134 | 9.5011e-07 | 3.3028e-07 | 0.010853 | 0.010853 | 0.010853 | 0.99224 | -0.14775 | 0.99209 | -0.15051 | 2.9816
141 | 0.0023926 | 0.00059953 | -0.0023926 | -0.00059964 | 5.3976e-08 | -1.0977e-07 | 0.0035886 | 0.0035887 | 0.0035887 | 0.99209 | -0.15051 | 0.99207 | -0.15098 | 0.9859
142 | -0.0015769 | -0.0003952 | 0.0015769 | 0.00039506 | 2.6689e-08 | -1.3969e-07 | 0.002393 | 0.0023929 | 0.002393 | 0.98052 | -0.37422 | 0.98054 | -0.37387 | 0.65742
143 | -0.0032244 | -0.00080797 | 0.0032248 | 0.00080769 | 3.689e-07 | -2.8223e-07 | 0.0048932 | 0.004893 | 0.0048932 | 0.98054 | -0.37387 | 0.98066 | -0.37147 | 1.3443
144 | -0.0041289 | -0.0010343 | 0.0041293 | 0.0010342 | 3.7246e-07 | -8.0945e-08 | 0.0062649 | 0.0062647 | 0.0062649 | 0.98066 | -0.37147 | 0.98076 | -0.36957 | 1.7211
145 | 0.016599 | 0.004166 | -0.016594 | -0.0041628 | 5.392e-06 | 3.1556e-06 | 0.024986 | 0.024986 | 0.024986 | 0.98863 | -0.21727 | 0.98828 | -0.22408 | 6.8642
146 | 0.015654 | 0.0039274 | -0.015654 | -0.0039271 | 4.9339e-07 | 2.8543e-07 | 0.023571 | 0.023571 | 0.023571 | 0.98828 | -0.22408 | 0.98825 | -0.22474 | 6.4756
147 | 0.0040505 | 0.001015 | -0.0040502 | -0.0010151 | 2.8729e-07 | -7.9058e-08 | 0.0061043 | 0.0061044 | 0.0061044 | 0.98735 | -0.24279 | 0.98728 | -0.24428 | 1.677

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55779 | 0.14203

## res_load
| p_mw | q_mvar
0 | 0.0045866 | 0.0011495
1 | 0.0017592 | 0.0004409
2 | 0.0036547 | 0.00091596
3 | 0.0088144 | 0.0022091
4 | 0.0040579 | 0.001017
5 | 0.0015219 | 0.00038142
6 | 0.0025981 | 0.00065113
7 | 0.0017564 | 0.0004402
8 | 0.0058045 | 0.0014547
9 | 0.0031172 | 0.00078125
10 | 0.0012494 | 0.00031314
11 | 0.0015279 | 0.00038292
12 | 0.0020404 | 0.00051137
13 | 0.0021964 | 0.00055047
14 | 0.0031411 | 0.00078724
15 | 0.002854 | 0.00071528
16 | 0.017755 | 0.0044498
17 | 0.0034795 | 0.00087204
18 | 0.0057167 | 0.0014327
19 | 0.0032444 | 0.00081311
20 | 0.0030906 | 0.00077457
21 | 0.0017633 | 0.00044193
22 | 0.0082595 | 0.00207
23 | 0.0079294 | 0.0019873
24 | 0.0034182 | 0.00085668
25 | 0.011074 | 0.0027755
26 | 0.0098297 | 0.0024636
27 | 0.0092822 | 0.0023263
28 | 0.0050427 | 0.0012638
29 | 0.0037356 | 0.00093622
30 | 0.0076019 | 0.0019052
31 | 0.010456 | 0.0026206
32 | 0.0075951 | 0.0019035
33 | 0.010484 | 0.0026275
34 | 0.0023324 | 0.00058455
35 | 0.0015088 | 0.00037813
36 | 0.0069297 | 0.0017368
37 | 0.0020815 | 0.00052166
38 | 0.000773 | 0.00019373
39 | 0.0014081 | 0.0003529
40 | 0.0013252 | 0.00033213
41 | 0.0015282 | 0.00038301
42 | 0.0012848 | 0.00032201
43 | 0.00085669 | 0.00021471
44 | 0.003425 | 0.00085838
45 | 0.0021714 | 0.0005442
46 | 0.00072145 | 0.00018081
47 | 0.091189 | 0.022854
48 | 0.0076084 | 0.0019068
49 | 0.0025264 | 0.00063317
50 | 0.010349 | 0.0025937
51 | 0.0028706 | 0.00071944
52 | 0.011969 | 0.0029998
53 | 0.017906 | 0.0044877
54 | 0.0015171 | 0.00038021
55 | 0.0051291 | 0.0012855
56 | 0.005182 | 0.0012987
57 | 0.0042265 | 0.0010593
58 | 0.0061223 | 0.0015344
59 | 0.0062375 | 0.0015633
60 | 0.0025226 | 0.00063223
61 | 0.025394 | 0.0063644
62 | 0.0029509 | 0.00073957
63 | 0.00044649 | 0.0001119
64 | 0.00572 | 0.0014336
65 | 0.0012244 | 0.00030687
66 | 0.002996 | 0.00075086
67 | 0.0018827 | 0.00047184
68 | 0.007536 | 0.0018887
69 | 0.0024679 | 0.00061852
70 | 0.0025565 | 0.00064072
71 | 0.002419 | 0.00060626
72 | 0.0017841 | 0.00044715
73 | 0.0020047 | 0.00050242
74 | 0.0039194 | 0.00098229
75 | 0.0018267 | 0.00045781
76 | 0.0049522 | 0.0012411
77 | 0.0021719 | 0.00054434
78 | 0.003515 | 0.00088094
79 | 0.0017022 | 0.0004266
80 | 0.0046257 | 0.0011593
81 | 0.0019998 | 0.00050119
82 | 0.0011838 | 0.00029669
83 | 0.0011122 | 0.00027874
84 | 0.00091758 | 0.00022997
85 | 0.0022941 | 0.00057495
86 | 0.0027866 | 0.00069838
87 | 0.0092159 | 0.0023097
88 | 0.0014885 | 0.00037306
89 | 0.002072 | 0.0005193
90 | 0.00094025 | 0.00023565
91 | 0.003569 | 0.00089447
92 | 0.00094019 | 0.00023563
93 | 0.0024592 | 0.00061632
94 | 0.0015609 | 0.0003912
95 | 0.0014272 | 0.0003577
96 | 0.0020099 | 0.00050372
97 | 0.001637 | 0.00041027
98 | 0.0020502 | 0.00051383
99 | 0.00097311 | 0.00024388
100 | 0.011432 | 0.0028651
101 | 0.00062905 | 0.00015766
102 | 0.0026573 | 0.00066599
103 | 0.00067298 | 0.00016867
104 | 0.0028902 | 0.00072434
105 | 0.0048434 | 0.0012139
106 | 0.0023926 | 0.00059964
107 | 0.0022756 | 0.00057031
108 | 0.0027122 | 0.00067973
109 | 0.0015769 | 0.0003952
110 | 0.0016476 | 0.00041292
111 | 0.00090411 | 0.00022659
112 | 0.00099533 | 0.00024945
113 | 0.00085359 | 0.00021393
114 | 0.00093942 | 0.00023544
115 | 0.0022332 | 0.0005597
116 | 0.00061785 | 0.00015485
117 | 0.0040502 | 0.0010151

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1