## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2519-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2519-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2519-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2519-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2519-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2519-4_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2519-4_0_4_node_102 | 0.4 | n |  | TRUE
7 | bus_LV_2519-4_0_4_node_123 | 0.4 | n |  | TRUE
8 | bus_LV_2519-4_0_4_node_80 | 0.4 | n |  | TRUE
9 | bus_LV_2519-4_0_4_node_121 | 0.4 | n |  | TRUE
10 | bus_LV_2519-4_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2519-4_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2519-4_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2519-4_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2519-4_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2519-4_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2519-4_0_4_node_59 | 0.4 | n |  | TRUE
17 | bus_LV_2519-4_0_4_node_92 | 0.4 | n |  | TRUE
18 | bus_LV_2519-4_0_4_node_128 | 0.4 | n |  | TRUE
19 | bus_LV_2519-4_0_4_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_2519-4_0_4_node_93 | 0.4 | n |  | TRUE
21 | bus_LV_2519-4_0_4_node_79 | 0.4 | n |  | TRUE
22 | bus_LV_2519-4_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2519-4_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2519-4_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2519-4_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2519-4_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2519-4_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2519-4_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2519-4_0_4_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_2519-4_0_4_node_76 | 0.4 | n |  | TRUE
31 | bus_LV_2519-4_0_4_node_99 | 0.4 | n |  | TRUE
32 | bus_LV_2519-4_0_4_node_96 | 0.4 | n |  | TRUE
33 | bus_LV_2519-4_0_4_node_106 | 0.4 | n |  | TRUE
34 | bus_LV_2519-4_0_4_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_2519-4_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_2519-4_0_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_2519-4_0_4_node_109 | 0.4 | n |  | TRUE
38 | bus_LV_2519-4_0_4_node_97 | 0.4 | n |  | TRUE
39 | bus_LV_2519-4_0_4_node_104 | 0.4 | n |  | TRUE
40 | bus_LV_2519-4_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_2519-4_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2519-4_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_2519-4_0_4_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_2519-4_0_4_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_2519-4_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_2519-4_0_4_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_2519-4_0_4_node_66 | 0.4 | n |  | TRUE
48 | bus_LV_2519-4_0_4_node_94 | 0.4 | n |  | TRUE
49 | bus_LV_2519-4_0_4_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_2519-4_0_4_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_2519-4_0_4_node_67 | 0.4 | n |  | TRUE
52 | bus_LV_2519-4_0_4_node_25 | 0.4 | n |  | TRUE
53 | bus_LV_2519-4_0_4_node_26 | 0.4 | n |  | TRUE
54 | bus_LV_2519-4_0_4_node_27 | 0.4 | n |  | TRUE
55 | bus_LV_2519-4_0_4_node_28 | 0.4 | n |  | TRUE
56 | bus_LV_2519-4_0_4_node_124 | 0.4 | n |  | TRUE
57 | bus_LV_2519-4_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2519-4_0_4_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_2519-4_0_4_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_2519-4_0_4_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_2519-4_0_4_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_2519-4_0_4_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_2519-4_0_4_node_32 | 0.4 | n |  | TRUE
64 | bus_LV_2519-4_0_4_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_2519-4_0_4_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_2519-4_0_4_node_84 | 0.4 | n |  | TRUE
67 | bus_LV_2519-4_0_4_node_90 | 0.4 | n |  | TRUE
68 | bus_LV_2519-4_0_4_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_2519-4_0_4_node_34 | 0.4 | n |  | TRUE
70 | bus_LV_2519-4_0_4_node_36 | 0.4 | n |  | TRUE
71 | bus_LV_2519-4_0_4_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2519-4_0_4_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2519-4_0_4_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2519-4_0_4_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_2519-4_0_4_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_2519-4_0_4_node_44 | 0.4 | n |  | TRUE
77 | bus_LV_2519-4_0_4_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_2519-4_0_4_node_101 | 0.4 | n |  | TRUE
79 | bus_LV_2519-4_0_4_node_88 | 0.4 | n |  | TRUE
80 | bus_LV_2519-4_0_4_node_82 | 0.4 | n |  | TRUE
81 | bus_LV_2519-4_0_4_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_2519-4_0_4_node_100 | 0.4 | n |  | TRUE
83 | bus_LV_2519-4_0_4_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_2519-4_0_4_node_114 | 0.4 | n |  | TRUE
85 | bus_LV_2519-4_0_4_node_46 | 0.4 | n |  | TRUE
86 | bus_LV_2519-4_0_4_node_48 | 0.4 | n |  | TRUE
87 | bus_LV_2519-4_0_4_node_127 | 0.4 | n |  | TRUE
88 | bus_LV_2519-4_0_4_node_105 | 0.4 | n |  | TRUE
89 | bus_LV_2519-4_0_4_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_2519-4_0_4_node_64 | 0.4 | n |  | TRUE
91 | bus_LV_2519-4_0_4_node_95 | 0.4 | n |  | TRUE
92 | bus_LV_2519-4_0_4_node_54 | 0.4 | n |  | TRUE
93 | bus_LV_2519-4_0_4_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_2519-4_0_4_node_56 | 0.4 | n |  | TRUE
95 | bus_LV_2519-4_0_4_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_2519-4_0_4_node_103 | 0.4 | n |  | TRUE
97 | bus_LV_2519-4_0_4_node_60 | 0.4 | n |  | TRUE
98 | bus_LV_2519-4_0_4_node_61 | 0.4 | n |  | TRUE
99 | bus_LV_2519-4_0_4_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_2519-4_0_4_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_2519-4_0_4_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_2519-4_0_4_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_2519-4_0_4_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_2519-4_0_4_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_2519-4_0_4_node_70 | 0.4 | n |  | TRUE
106 | bus_LV_2519-4_0_4_node_72 | 0.4 | n |  | TRUE
107 | bus_LV_2519-4_0_4_node_77 | 0.4 | n |  | TRUE
108 | bus_LV_2519-4_0_4_node_78 | 0.4 | n |  | TRUE
109 | bus_LV_2519-4_0_4_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_2519-4_0_4_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_2519-4_0_4_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2519-4_0_4_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_2519-4_0_4_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_2519-4_0_4_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_2519-4_0_4_node_119 | 0.4 | n |  | TRUE
116 | bus_LV_2519-4_0_4_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_2519-4_0_4_node_126 | 0.4 | n |  | TRUE
118 | bus_LV_2519-4_0_4_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_2519-4_0_4_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_2519-4_0_4_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_2519-4_0_4_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_2519-4_0_4_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_2519-4_0_4_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_2519-4_0_4_node_120 | 0.4 | n |  | TRUE
125 | bus_MV_393_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2519-4_0_4_load_0 | 0 | 0.0016554 | 0.00041489 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2519-4_0_4_load_1 | 1 | 0.0021217 | 0.00053174 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2519-4_0_4_load_3 | 3 | 0.0019027 | 0.00047687 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2519-4_0_4_load_4 | 4 | 0.0015715 | 0.00039384 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2519-4_0_4_load_5 | 5 | 0.0017416 | 0.00043648 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2519-4_0_4_load_102 | 6 | 0.0012189 | 0.00030548 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2519-4_0_4_load_123 | 7 | 0.0020775 | 0.00052068 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2519-4_0_4_load_80 | 8 | 0.0017547 | 0.00043976 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2519-4_0_4_load_6 | 10 | 0.0022371 | 0.00056067 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2519-4_0_4_load_7 | 11 | 0.0012208 | 0.00030597 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2519-4_0_4_load_10 | 14 | 0.0033647 | 0.00084328 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2519-4_0_4_load_11 | 15 | 0.0020138 | 0.00050472 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2519-4_0_4_load_128 | 18 | 0.0015999 | 0.00040097 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2519-4_0_4_load_58 | 19 | 0.0036832 | 0.00092309 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2519-4_0_4_load_93 | 20 | 0.0013247 | 0.000332 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2519-4_0_4_load_79 | 21 | 0.0023009 | 0.00057665 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2519-4_0_4_load_12 | 22 | 0.0020563 | 0.00051536 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2519-4_0_4_load_13 | 23 | 0.0043975 | 0.0011021 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2519-4_0_4_load_15 | 25 | 0.0020609 | 0.0005165 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2519-4_0_4_load_16 | 26 | 0.0032731 | 0.00082031 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2519-4_0_4_load_18 | 28 | 0.001769 | 0.00044335 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2519-4_0_4_load_76 | 30 | 0.0039943 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2519-4_0_4_load_99 | 31 | 0.0025083 | 0.00062864 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2519-4_0_4_load_96 | 32 | 0.0021858 | 0.00054781 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2519-4_0_4_load_49 | 34 | 0.0014005 | 0.00035099 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2519-4_0_4_load_50 | 35 | 0.0013817 | 0.0003463 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2519-4_0_4_load_45 | 36 | 0.00077355 | 0.00019387 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2519-4_0_4_load_109 | 37 | 0.0021986 | 0.00055101 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2519-4_0_4_load_97 | 38 | 0.0017438 | 0.00043704 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2519-4_0_4_load_104 | 39 | 0.0021073 | 0.00052813 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2519-4_0_4_load_19 | 40 | 0.0038065 | 0.000954 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2519-4_0_4_load_22 | 43 | 0.0042358 | 0.0010616 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2519-4_0_4_load_23 | 44 | 0.0017881 | 0.00044815 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2519-4_0_4_load_24 | 45 | 0.0029681 | 0.00074386 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2519-4_0_4_load_66 | 47 | 0.0029552 | 0.00074063 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2519-4_0_4_load_94 | 48 | 0.012544 | 0.0031438 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2519-4_0_4_load_51 | 50 | 0.0011796 | 0.00029565 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2519-4_0_4_load_67 | 51 | 0.0063428 | 0.0015897 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2519-4_0_4_load_25 | 52 | 0.0011827 | 0.00029642 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2519-4_0_4_load_26 | 53 | 0.0010009 | 0.00025086 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2519-4_0_4_load_27 | 54 | 0.0018466 | 0.00046279 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2519-4_0_4_load_124 | 56 | 0.00054337 | 0.00013618 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2519-4_0_4_load_37 | 57 | 0.0014429 | 0.00036161 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2519-4_0_4_load_65 | 58 | 0.00093191 | 0.00023356 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2519-4_0_4_load_35 | 59 | 0.0018806 | 0.00047133 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2519-4_0_4_load_29 | 60 | 0.0028475 | 0.00071365 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2519-4_0_4_load_30 | 61 | 0.0054727 | 0.0013716 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2519-4_0_4_load_31 | 62 | 0.0099266 | 0.0024878 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2519-4_0_4_load_32 | 63 | 0.0021865 | 0.00054798 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2519-4_0_4_load_33 | 64 | 0.001742 | 0.00043658 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2519-4_0_4_load_68 | 65 | 0.013291 | 0.003331 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2519-4_0_4_load_84 | 66 | 0.0032154 | 0.00080586 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2519-4_0_4_load_34 | 69 | 0.00087968 | 0.00022047 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2519-4_0_4_load_36 | 70 | 0.0022253 | 0.00055772 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2519-4_0_4_load_39 | 71 | 0.00264 | 0.00066165 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2519-4_0_4_load_43 | 75 | 0.0015124 | 0.00037905 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2519-4_0_4_load_44 | 76 | 0.0095348 | 0.0023896 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2519-4_0_4_load_74 | 77 | 0.00265 | 0.00066415 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2519-4_0_4_load_88 | 79 | 0.0039227 | 0.00098312 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2519-4_0_4_load_73 | 81 | 0.0017601 | 0.00044112 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2519-4_0_4_load_100 | 82 | 0.0078885 | 0.001977 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2519-4_0_4_load_46 | 85 | 0.0031691 | 0.00079425 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2519-4_0_4_load_48 | 86 | 0.00085736 | 0.00021488 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2519-4_0_4_load_127 | 87 | 0.0014505 | 0.00036353 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2519-4_0_4_load_105 | 88 | 0.0018362 | 0.00046021 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2519-4_0_4_load_89 | 89 | 0.004128 | 0.0010346 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2519-4_0_4_load_64 | 90 | 0.0014627 | 0.00036659 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2519-4_0_4_load_95 | 91 | 0.0036767 | 0.00092147 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2519-4_0_4_load_54 | 92 | 0.0044108 | 0.0011055 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2519-4_0_4_load_56 | 94 | 0.0032864 | 0.00082364 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2519-4_0_4_load_57 | 95 | 0.0029863 | 0.00074845 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2519-4_0_4_load_103 | 96 | 0.0029612 | 0.00074214 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2519-4_0_4_load_60 | 97 | 0.0013554 | 0.0003397 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2519-4_0_4_load_61 | 98 | 0.0014977 | 0.00037536 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2519-4_0_4_load_63 | 100 | 0.0012035 | 0.00030163 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2519-4_0_4_load_69 | 102 | 0.0012134 | 0.0003041 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2519-4_0_4_load_86 | 103 | 0.0033536 | 0.0008405 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2519-4_0_4_load_91 | 104 | 0.0023351 | 0.00058522 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2519-4_0_4_load_70 | 105 | 0.0013519 | 0.00033883 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2519-4_0_4_load_72 | 106 | 0.0017236 | 0.00043197 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2519-4_0_4_load_78 | 108 | 0.0024105 | 0.00060413 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2519-4_0_4_load_83 | 109 | 0.0095159 | 0.0023849 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2519-4_0_4_load_112 | 110 | 0.0098228 | 0.0024618 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2519-4_0_4_load_107 | 112 | 0.024215 | 0.0060688 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2519-4_0_4_load_115 | 113 | 0.0081378 | 0.0020395 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2519-4_0_4_load_119 | 115 | 0.0029504 | 0.00073945 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2519-4_0_4_load_125 | 116 | 0.0020654 | 0.00051763 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2519-4_0_4_load_126 | 117 | 0.0024449 | 0.00061274 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2519-4_0_4_load_98 | 118 | 0.0037015 | 0.00092769 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2519-4_0_4_load_110 | 119 | 0.0035848 | 0.00089844 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2519-4_0_4_load_111 | 120 | 0.0071735 | 0.0017979 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2519-4_0_4_load_117 | 121 | 0.0035996 | 0.00090214 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2519-4_0_4_load_129 | 122 | 0.0025625 | 0.00064223 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2519-4_0_4_load_122 | 123 | 0.0035212 | 0.00088251 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2519-4_0_4_load_120 | 124 | 0.00195 | 0.00048871 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2519-4_0_4_line_0 |  | 0 | 1 | 0.0081526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2519-4_0_4_line_1 |  | 0 | 2 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2519-4_0_4_line_2 |  | 1 | 3 | 0.0025058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2519-4_0_4_line_3 |  | 2 | 4 | 0.01314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2519-4_0_4_line_4 |  | 2 | 5 | 0.0048685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2519-4_0_4_line_5 |  | 4 | 6 | 0.020539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2519-4_0_4_line_6 |  | 5 | 7 | 0.020924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2519-4_0_4_line_7 |  | 6 | 8 | 0.0014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2519-4_0_4_line_8 |  | 7 | 9 | 0.028801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2519-4_0_4_line_9 |  | 8 | 107 | 0.012146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2519-4_0_4_line_10 |  | 9 | 115 | 0.018324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2519-4_0_4_line_11 |  | 9 | 104 | 0.015294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2519-4_0_4_line_12 |  | 10 | 11 | 0.023778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2519-4_0_4_line_13 |  | 10 | 12 | 0.019224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2519-4_0_4_line_14 |  | 11 | 13 | 0.011709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2519-4_0_4_line_15 |  | 12 | 14 | 0.009229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2519-4_0_4_line_16 |  | 12 | 15 | 0.0019229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2519-4_0_4_line_17 |  | 13 | 16 | 0.014333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2519-4_0_4_line_18 |  | 13 | 17 | 0.018209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2519-4_0_4_line_19 |  | 15 | 18 | 0.020847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2519-4_0_4_line_20 |  | 16 | 19 | 0.025703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2519-4_0_4_line_21 |  | 17 | 20 | 0.015093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2519-4_0_4_line_22 |  | 17 | 21 | 0.015288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2519-4_0_4_line_23 |  | 20 | 116 | 0.0065066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2519-4_0_4_line_24 |  | 21 | 107 | 0.040638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2519-4_0_4_line_25 |  | 22 | 23 | 0.0029934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2519-4_0_4_line_26 |  | 22 | 24 | 0.016168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2519-4_0_4_line_27 |  | 23 | 25 | 0.028778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2519-4_0_4_line_28 |  | 24 | 26 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2519-4_0_4_line_29 |  | 24 | 27 | 0.02664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2519-4_0_4_line_30 |  | 24 | 28 | 0.03471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2519-4_0_4_line_31 |  | 25 | 29 | 0.018781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2519-4_0_4_line_32 |  | 26 | 30 | 0.02193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2519-4_0_4_line_33 |  | 27 | 31 | 0.0075827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2519-4_0_4_line_34 |  | 27 | 32 | 0.013711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2519-4_0_4_line_35 |  | 28 | 33 | 0.011781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2519-4_0_4_line_36 |  | 29 | 34 | 0.024584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2519-4_0_4_line_37 |  | 29 | 35 | 0.01628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2519-4_0_4_line_38 |  | 29 | 36 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2519-4_0_4_line_39 |  | 31 | 37 | 0.021747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2519-4_0_4_line_40 |  | 32 | 38 | 0.011479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2519-4_0_4_line_41 |  | 33 | 39 | 0.022556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2519-4_0_4_line_42 |  | 34 | 87 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2519-4_0_4_line_43 |  | 35 | 88 | 0.0081441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2519-4_0_4_line_44 |  | 36 | 85 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2519-4_0_4_line_45 |  | 37 | 119 | 0.010909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2519-4_0_4_line_46 |  | 38 | 118 | 0.0048347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2519-4_0_4_line_47 |  | 40 | 41 | 0.020316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2519-4_0_4_line_48 |  | 40 | 42 | 0.007078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2519-4_0_4_line_49 |  | 41 | 43 | 0.046406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2519-4_0_4_line_50 |  | 42 | 44 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2519-4_0_4_line_51 |  | 42 | 45 | 0.012616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2519-4_0_4_line_52 |  | 43 | 46 | 0.05209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2519-4_0_4_line_53 |  | 44 | 47 | 0.020204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2519-4_0_4_line_54 |  | 45 | 48 | 0.023226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2519-4_0_4_line_55 |  | 46 | 49 | 0.005605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2519-4_0_4_line_56 |  | 46 | 50 | 0.01333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2519-4_0_4_line_57 |  | 47 | 51 | 0.010376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2519-4_0_4_line_58 |  | 49 | 91 | 0.078719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2519-4_0_4_line_59 |  | 51 | 103 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2519-4_0_4_line_60 |  | 52 | 53 | 0.012154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2519-4_0_4_line_61 |  | 52 | 54 | 0.0029814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2519-4_0_4_line_62 |  | 53 | 55 | 0.010933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2519-4_0_4_line_63 |  | 55 | 56 | 0.036486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2519-4_0_4_line_64 |  | 55 | 57 | 0.022474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2519-4_0_4_line_65 |  | 56 | 58 | 0.0089164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2519-4_0_4_line_66 |  | 57 | 59 | 0.018256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2519-4_0_4_line_67 |  | 58 | 99 | 0.029008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2519-4_0_4_line_68 |  | 59 | 69 | 0.011762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2519-4_0_4_line_69 |  | 60 | 61 | 0.026668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2519-4_0_4_line_70 |  | 60 | 62 | 0.006138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2519-4_0_4_line_71 |  | 61 | 63 | 0.021555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2519-4_0_4_line_72 |  | 62 | 64 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2519-4_0_4_line_73 |  | 63 | 65 | 0.0031428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2519-4_0_4_line_74 |  | 64 | 66 | 0.013863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2519-4_0_4_line_75 |  | 65 | 67 | 0.026081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2519-4_0_4_line_76 |  | 66 | 68 | 0.042182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2519-4_0_4_line_77 |  | 67 | 104 | 0.023718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2519-4_0_4_line_78 |  | 67 | 103 | 0.0030293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2519-4_0_4_line_79 |  | 68 | 111 | 0.029806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2519-4_0_4_line_80 |  | 69 | 70 | 0.0093619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2519-4_0_4_line_81 |  | 71 | 72 | 0.013906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2519-4_0_4_line_82 |  | 71 | 73 | 0.018333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2519-4_0_4_line_83 |  | 72 | 74 | 0.002821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2519-4_0_4_line_84 |  | 73 | 75 | 0.019334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2519-4_0_4_line_85 |  | 73 | 76 | 0.027694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2519-4_0_4_line_86 |  | 74 | 77 | 0.016749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2519-4_0_4_line_87 |  | 74 | 78 | 0.012925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2519-4_0_4_line_88 |  | 75 | 79 | 0.017876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2519-4_0_4_line_89 |  | 76 | 80 | 0.019938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2519-4_0_4_line_90 |  | 77 | 81 | 0.02552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2519-4_0_4_line_91 |  | 78 | 82 | 0.027286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2519-4_0_4_line_92 |  | 79 | 83 | 0.013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2519-4_0_4_line_93 |  | 80 | 84 | 0.014622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2519-4_0_4_line_94 |  | 83 | 89 | 0.025292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2519-4_0_4_line_95 |  | 83 | 86 | 0.025356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2519-4_0_4_line_96 |  | 84 | 110 | 0.048709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2519-4_0_4_line_97 |  | 84 | 109 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2519-4_0_4_line_98 |  | 85 | 86 | 0.0067958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2519-4_0_4_line_99 |  | 87 | 90 | 0.0056766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2519-4_0_4_line_100 |  | 89 | 96 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2519-4_0_4_line_101 |  | 90 | 99 | 0.013007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2519-4_0_4_line_102 |  | 92 | 93 | 0.011394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2519-4_0_4_line_103 |  | 93 | 94 | 0.013935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2519-4_0_4_line_104 |  | 93 | 95 | 0.016574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2519-4_0_4_line_105 |  | 94 | 96 | 0.017763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2519-4_0_4_line_106 |  | 97 | 98 | 0.016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2519-4_0_4_line_107 |  | 97 | 99 | 0.0027409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2519-4_0_4_line_108 |  | 98 | 100 | 0.0074065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2519-4_0_4_line_109 |  | 100 | 101 | 0.042768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2519-4_0_4_line_110 |  | 101 | 102 | 0.014632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2519-4_0_4_line_111 |  | 102 | 105 | 0.020711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2519-4_0_4_line_112 |  | 105 | 106 | 0.018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2519-4_0_4_line_113 |  | 107 | 108 | 0.018281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2519-4_0_4_line_114 |  | 111 | 112 | 0.027699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2519-4_0_4_line_115 |  | 113 | 114 | 0.021801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2519-4_0_4_line_116 |  | 114 | 121 | 0.014771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2519-4_0_4_line_117 |  | 114 | 120 | 0.0056022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_2519-4_0_4_line_118 |  | 115 | 124 | 0.00077752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_2519-4_0_4_line_119 |  | 116 | 117 | 0.016113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2519-4_0_4_line_120 |  | 119 | 120 | 0.026115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_2519-4_0_4_line_121 |  | 121 | 122 | 0.022105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_2519-4_0_4_line_122 |  | 122 | 123 | 0.0049281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_2519-4_0_4_line_123 |  | 123 | 124 | 0.017986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2519-4_0_4_trafo_4 | 0.63 MVA 20/0.4 kV | 125 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2610022.3024 | 1224773.5804 | 2610022.3031 | 1224780.8003 | 2610022.1659 | 1224781.7229
1 | 2610022.301 | 1224759.3989 | 2610022.3024 | 1224773.5804
2 | 2610021.7971 | 1224784.2014 | 2610022.1659 | 1224781.7229
3 | 2610022.301 | 1224759.3989 | 2610028.303 | 1224760.6986 | 2610035.0042 | 1224762.7201
4 | 2610022.301 | 1224759.3989 | 2610017.5379 | 1224758.3916
5 | 2610035.0042 | 1224762.7201 | 2610041.9041 | 1224764.8016 | 2610047.1022 | 1224766.3 | 2610054.8558 | 1224767.9257
6 | 2609996.9734 | 1224754.5589 | 2610008.0992 | 1224756.3956 | 2610017.5379 | 1224758.3916
7 | 2610056.3136 | 1224768.2313 | 2610054.8558 | 1224767.9257
8 | 2609968.204 | 1224754.1056 | 2609989.598 | 1224753.8966 | 2609996.6019 | 1224754.4975 | 2609996.9734 | 1224754.5589
9 | 2610068.4 | 1224769.2042 | 2610061.7973 | 1224769.0041 | 2610057.0981 | 1224768.3958 | 2610056.3136 | 1224768.2313
10 | 2609968.204 | 1224754.1056 | 2609968.2647 | 1224772.4299
11 | 2609968.204 | 1224754.1056 | 2609968.2034 | 1224738.8117
12 | 2610034.8126 | 1224694.8067 | 2610058.5897 | 1224695.0015
13 | 2610015.6008 | 1224695.1057 | 2610022.5003 | 1224694.7059 | 2610034.8126 | 1224694.8067
14 | 2610070.2986 | 1224695.0974 | 2610058.5897 | 1224695.0015
15 | 2610015.6008 | 1224695.1057 | 2610014.797 | 1224704.2986
16 | 2610015.6008 | 1224695.1057 | 2610015.7526 | 1224693.1888
17 | 2610070.2986 | 1224695.0974 | 2610070.8989 | 1224680.7789
18 | 2610070.2986 | 1224695.0974 | 2610069.798 | 1224713.2961
19 | 2610017.3976 | 1224672.4065 | 2610015.7526 | 1224693.1888
20 | 2610070.8989 | 1224680.7789 | 2610096.5951 | 1224681.3884
21 | 2610069.798 | 1224713.2961 | 2610081.8971 | 1224713.5054 | 2610084.8876 | 1224713.6111
22 | 2610069.798 | 1224713.2961 | 2610069.424 | 1224728.5794
23 | 2610091.3902 | 1224713.8408 | 2610084.8876 | 1224713.6111
24 | 2610068.4 | 1224769.2042 | 2610068.6013 | 1224762.2004 | 2610069.424 | 1224728.5794
25 | 2610082.0645 | 1224846.8836 | 2610084.9858 | 1224847.5363
26 | 2610066.1974 | 1224843.7996 | 2610075.8981 | 1224845.5058 | 2610082.0645 | 1224846.8836
27 | 2610084.9858 | 1224847.5363 | 2610113.0712 | 1224853.8115
28 | 2610066.1974 | 1224843.7996 | 2610066.7037 | 1224831.2042 | 2610066.8399 | 1224826.2291
29 | 2610039.7999 | 1224839.6974 | 2610058.8006 | 1224842.4975 | 2610066.1974 | 1224843.7996
30 | 2610066.1974 | 1224843.7996 | 2610065.4542 | 1224878.502
31 | 2610131.3999 | 1224857.9067 | 2610113.0712 | 1224853.8115
32 | 2610067.4396 | 1224804.3073 | 2610066.8399 | 1224826.2291
33 | 2610039.7999 | 1224839.6974 | 2610033.1986 | 1224838.6968 | 2610032.3003 | 1224838.5792
34 | 2610039.7999 | 1224839.6974 | 2610037.2334 | 1224853.1661
35 | 2610065.202 | 1224890.2807 | 2610065.4542 | 1224878.502
36 | 2610131.3999 | 1224857.9067 | 2610137.0985 | 1224859.206 | 2610155.2056 | 1224864.0334
37 | 2610131.3999 | 1224857.9067 | 2610120.4885 | 1224869.9892
38 | 2610131.3999 | 1224857.9067 | 2610132.1027 | 1224854.706 | 2610135.8004 | 1224851.2991 | 2610139.8988 | 1224848.5044 | 2610145.776 | 1224844.2491
39 | 2610010.7211 | 1224835.9038 | 2610014.0988 | 1224836.1967 | 2610032.3003 | 1224838.5792
40 | 2610037.2334 | 1224853.1661 | 2610036.1976 | 1224858.6024 | 2610035.5035 | 1224861.1027 | 2610034.6002 | 1224861.8016 | 2610032.4014 | 1224861.998
41 | 2610065.202 | 1224890.2807 | 2610087.587 | 1224893.0524
42 | 2610175.2387 | 1224869.3744 | 2610155.2056 | 1224864.0334
43 | 2610120.4885 | 1224869.9892 | 2610115.0301 | 1224876.0334
44 | 2610155.5507 | 1224837.1716 | 2610145.776 | 1224844.2491
45 | 2610010.7211 | 1224835.9038 | 2609999.8526 | 1224834.9613
46 | 2610027.6037 | 1224861.4007 | 2610032.4014 | 1224861.998 | 2610032.4014 | 1224861.998
47 | 2609967.8979 | 1224619.204 | 2609967.8978 | 1224639.5198
48 | 2609967.8978 | 1224646.5978 | 2609967.8978 | 1224639.5198
49 | 2609967.8979 | 1224619.204 | 2609954.9037 | 1224619.2046 | 2609921.4922 | 1224619.1873
50 | 2609967.8978 | 1224646.5978 | 2609968.0028 | 1224660.9063
51 | 2609967.8978 | 1224646.5978 | 2609962.204 | 1224646.7996 | 2609958.7992 | 1224647.3053 | 2609955.4995 | 1224648.4005
52 | 2609869.4027 | 1224619.1965 | 2609876.7111 | 1224619.1641 | 2609921.4922 | 1224619.1873
53 | 2609968.0028 | 1224660.9063 | 2609968.0625 | 1224681.1103
54 | 2609943.3019 | 1224666.4018 | 2609943.7039 | 1224661.6997 | 2609944.8014 | 1224658.1995 | 2609946.2005 | 1224655.7004 | 2609948.7977 | 1224653.0031 | 2609952.1992 | 1224649.8958 | 2609955.4995 | 1224648.4005
55 | 2609869.4996 | 1224624.7999 | 2609869.4027 | 1224619.1965
56 | 2609869.4027 | 1224619.1965 | 2609869.1919 | 1224609.1236 | 2609869.1993 | 1224605.8691
57 | 2609968.0625 | 1224681.1103 | 2609968.0931 | 1224691.4862
58 | 2609869.4996 | 1224624.7999 | 2609790.9176 | 1224629.4354
59 | 2609968.1539 | 1224712.0645 | 2609968.0931 | 1224691.4862
60 | 2610216.7823 | 1224814.5992 | 2610228.9291 | 1224815.0077
61 | 2610213.8026 | 1224814.499 | 2610216.7823 | 1224814.5992
62 | 2610239.5971 | 1224816.5998 | 2610236.9003 | 1224815.4057 | 2610234.7022 | 1224815.2018 | 2610228.9291 | 1224815.0077
63 | 2610239.5971 | 1224816.5998 | 2610235.1988 | 1224821.8065 | 2610216.1656 | 1224844.568
64 | 2610239.5971 | 1224816.5998 | 2610253.9018 | 1224799.2666
65 | 2610216.1656 | 1224844.568 | 2610210.4459 | 1224851.408
66 | 2610266.7055 | 1224786.2705 | 2610264.1997 | 1224788.7034 | 2610255.6034 | 1224797.2048 | 2610253.9018 | 1224799.2666
67 | 2610193.2015 | 1224874.499 | 2610194.6027 | 1224870.7992 | 2610196.4038 | 1224868.2008 | 2610210.4459 | 1224851.408
68 | 2610266.7055 | 1224786.2705 | 2610275.144 | 1224778.0773
69 | 2609935.7381 | 1224742.6894 | 2609935.7381 | 1224742.6894 | 2609931.7483 | 1224744.028 | 2609929.5026 | 1224749.6053 | 2609928.7971 | 1224754.4959 | 2609927.9993 | 1224760.0979 | 2609926.7011 | 1224765.799 | 2609926.7011 | 1224765.799
70 | 2609924.3665 | 1224771.4757 | 2609926.7011 | 1224765.799
71 | 2609935.7381 | 1224742.6894 | 2609944.2049 | 1224722.8668
72 | 2609920.1076 | 1224781.8313 | 2609924.3665 | 1224771.4757
73 | 2609945.4394 | 1224719.9766 | 2609944.2049 | 1224722.8668
74 | 2609920.1076 | 1224781.8313 | 2609917.2017 | 1224788.8968 | 2609914.8457 | 1224794.6564
75 | 2609968.1628 | 1224715.0938 | 2609947.6108 | 1224714.8929 | 2609945.4394 | 1224719.9766
76 | 2609899.3959 | 1224833.5935 | 2609899.6001 | 1224829.3024 | 2609900.5978 | 1224826.5024 | 2609903.6019 | 1224820.704 | 2609907.2988 | 1224813.1057 | 2609914.8457 | 1224794.6564
77 | 2609968.1628 | 1224715.0938 | 2609968.203 | 1224727.4011 | 2609968.2034 | 1224738.8117
78 | 2609968.1628 | 1224715.0938 | 2609968.1539 | 1224712.0645
79 | 2609869.6014 | 1224834.4003 | 2609894.104 | 1224833.796 | 2609899.3959 | 1224833.5935
80 | 2610281.8608 | 1224771.5557 | 2610275.144 | 1224778.0773
81 | 2610220.9037 | 1224744.8037 | 2610218.504 | 1224747.201 | 2610213.4043 | 1224754.6967 | 2610212.6508 | 1224755.9333
82 | 2610203.1108 | 1224771.5891 | 2610212.6508 | 1224755.9333
83 | 2610222.9009 | 1224742.806 | 2610220.9037 | 1224744.8037
84 | 2610203.1108 | 1224771.5891 | 2610196.398 | 1224782.6063 | 2610194.6039 | 1224785.5049 | 2610193.0643 | 1224788.1073
85 | 2610203.1108 | 1224771.5891 | 2610175.4225 | 1224771.0184
86 | 2610222.9009 | 1224742.806 | 2610226.9992 | 1224740.2003 | 2610234.3042 | 1224737.6002 | 2610237.9008 | 1224735.7052 | 2610237.9613 | 1224735.6638
87 | 2610222.8241 | 1224730.0651 | 2610223.8928 | 1224734.6696 | 2610222.9009 | 1224742.806
88 | 2610183.9622 | 1224803.4923 | 2610193.0643 | 1224788.1073
89 | 2610155.4885 | 1224770.6076 | 2610175.4225 | 1224771.0184
90 | 2610258.2642 | 1224720.2075 | 2610240.1019 | 1224734.197 | 2610237.9613 | 1224735.6638
91 | 2610222.8241 | 1224730.0651 | 2610216.6323 | 1224703.4909
92 | 2610175.4977 | 1224813.4999 | 2610176.0981 | 1224812.6004 | 2610178.703 | 1224809.9033 | 2610182.599 | 1224805.7964 | 2610183.9622 | 1224803.4923
93 | 2610155.5284 | 1224755.988 | 2610155.4885 | 1224770.6076
94 | 2610175.4977 | 1224813.4999 | 2610170.1033 | 1224811.6007 | 2610150.7376 | 1224808.7582
95 | 2610175.4977 | 1224813.4999 | 2610173.8017 | 1224816.6989 | 2610172.4974 | 1224821.3994 | 2610171.5977 | 1224824.3997 | 2610169.2971 | 1224826.497 | 2610163.3989 | 1224831.1008 | 2610160.9576 | 1224833.0582
96 | 2610155.5284 | 1224755.988 | 2610155.0506 | 1224747.1709 | 2610146.4853 | 1224728.5344 | 2610146.2679 | 1224709.1671
97 | 2610155.5284 | 1224755.988 | 2610141.0904 | 1224763.1085
98 | 2610160.9576 | 1224833.0582 | 2610158.4039 | 1224835.1057 | 2610155.5507 | 1224837.1716
99 | 2610175.2387 | 1224869.3744 | 2610180.7238 | 1224870.8368
100 | 2610150.7376 | 1224808.7582 | 2610134.7013 | 1224806.4044 | 2610133.1116 | 1224806.196
101 | 2610193.2015 | 1224874.499 | 2610186.2005 | 1224872.2969 | 2610180.7238 | 1224870.8368
102 | 2610102.3088 | 1224801.3578 | 2610102.3971 | 1224802.9033 | 2610100.4667 | 1224812.5581
103 | 2610102.3088 | 1224801.3578 | 2610106.2128 | 1224801.4645 | 2610107.2036 | 1224802.8003 | 2610115.499 | 1224803.8875
104 | 2610102.3088 | 1224801.3578 | 2610102.0581 | 1224797.1438 | 2610100.952 | 1224792.2502 | 2610101.1725 | 1224784.9179
105 | 2610115.499 | 1224803.8875 | 2610133.1116 | 1224806.196
106 | 2610195.8293 | 1224875.2783 | 2610211.4884 | 1224879.9224
107 | 2610193.2015 | 1224874.499 | 2610195.8293 | 1224875.2783
108 | 2610211.4884 | 1224879.9224 | 2610216.8041 | 1224881.4989 | 2610218.5676 | 1224882.0962
109 | 2610253.8032 | 1224905.4983 | 2610236.8984 | 1224891.9059 | 2610233.0004 | 1224888.2972 | 2610228.5018 | 1224885.6991 | 2610223.6002 | 1224883.8007 | 2610218.5676 | 1224882.0962
110 | 2610253.8032 | 1224905.4983 | 2610256.9021 | 1224902.0016 | 2610260.3974 | 1224897.3048 | 2610262.725 | 1224893.9241
111 | 2610262.725 | 1224893.9241 | 2610274.47 | 1224876.8651
112 | 2610274.47 | 1224876.8651 | 2610284.6636 | 1224862.0592 | 2610285.1874 | 1224861.2984
113 | 2610068.4 | 1224769.2042 | 2610086.6321 | 1224770.5347
114 | 2609869.6014 | 1224834.4003 | 2609871.4447 | 1224819.9616 | 2609871.6144 | 1224806.8192
115 | 2609968.2015 | 1224832.9961 | 2609957.498 | 1224832.5002 | 2609946.4126 | 1224832.3835
116 | 2609968.2015 | 1224832.9961 | 2609968.3524 | 1224818.2256
117 | 2609968.2015 | 1224832.9961 | 2609973.7997 | 1224833.2091
118 | 2609968.2647 | 1224772.4299 | 2609968.2673 | 1224773.2074
119 | 2610091.3902 | 1224713.8408 | 2610107.4934 | 1224714.4098
120 | 2609999.8526 | 1224834.9613 | 2609999.1968 | 1224834.9044 | 2609978.8975 | 1224833.403 | 2609973.7997 | 1224833.2091
121 | 2609968.3524 | 1224818.2256 | 2609968.4008 | 1224813.4961 | 2609968.3432 | 1224796.121
122 | 2609968.3432 | 1224796.121 | 2609968.3269 | 1224791.1929
123 | 2609968.2673 | 1224773.2074 | 2609968.3269 | 1224791.1929

## bus_geodata
| x | y | coords
0 | 2610022.3024 | 1224773.5804
1 | 2610022.1659 | 1224781.7229
2 | 2610022.301 | 1224759.3989
3 | 2610021.7971 | 1224784.2014
4 | 2610035.0042 | 1224762.7201
5 | 2610017.5379 | 1224758.3916
6 | 2610054.8558 | 1224767.9257
7 | 2609996.9734 | 1224754.5589
8 | 2610056.3136 | 1224768.2313
9 | 2609968.204 | 1224754.1056
10 | 2610034.8126 | 1224694.8067
11 | 2610058.5897 | 1224695.0015
12 | 2610015.6008 | 1224695.1057
13 | 2610070.2986 | 1224695.0974
14 | 2610014.797 | 1224704.2986
15 | 2610015.7526 | 1224693.1888
16 | 2610070.8989 | 1224680.7789
17 | 2610069.798 | 1224713.2961
18 | 2610017.3976 | 1224672.4065
19 | 2610096.5951 | 1224681.3884
20 | 2610084.8876 | 1224713.6111
21 | 2610069.424 | 1224728.5794
22 | 2610082.0645 | 1224846.8836
23 | 2610084.9858 | 1224847.5363
24 | 2610066.1974 | 1224843.7996
25 | 2610113.0712 | 1224853.8115
26 | 2610066.8399 | 1224826.2291
27 | 2610039.7999 | 1224839.6974
28 | 2610065.4542 | 1224878.502
29 | 2610131.3999 | 1224857.9067
30 | 2610067.4396 | 1224804.3073
31 | 2610032.3003 | 1224838.5792
32 | 2610037.2334 | 1224853.1661
33 | 2610065.2019 | 1224890.2807
34 | 2610155.2056 | 1224864.0334
35 | 2610120.4885 | 1224869.9892
36 | 2610145.776 | 1224844.2491
37 | 2610010.7211 | 1224835.9038
38 | 2610032.4014 | 1224861.998
39 | 2610087.587 | 1224893.0524
40 | 2609967.8978 | 1224639.5198
41 | 2609967.8979 | 1224619.204
42 | 2609967.8978 | 1224646.5978
43 | 2609921.4922 | 1224619.1873
44 | 2609968.0028 | 1224660.9063
45 | 2609955.4995 | 1224648.4005
46 | 2609869.4027 | 1224619.1965
47 | 2609968.0625 | 1224681.1103
48 | 2609943.3019 | 1224666.4018
49 | 2609869.4996 | 1224624.7999
50 | 2609869.1993 | 1224605.8691
51 | 2609968.0931 | 1224691.4862
52 | 2610216.7823 | 1224814.5992
53 | 2610228.9291 | 1224815.0077
54 | 2610213.8026 | 1224814.499
55 | 2610239.5971 | 1224816.5998
56 | 2610216.1656 | 1224844.568
57 | 2610253.9018 | 1224799.2666
58 | 2610210.4459 | 1224851.408
59 | 2610266.7055 | 1224786.2705
60 | 2609926.7011 | 1224765.799
61 | 2609935.7381 | 1224742.6894
62 | 2609924.3665 | 1224771.4757
63 | 2609944.2049 | 1224722.8668
64 | 2609920.1076 | 1224781.8313
65 | 2609945.4394 | 1224719.9766
66 | 2609914.8457 | 1224794.6564
67 | 2609968.1628 | 1224715.0938
68 | 2609899.3959 | 1224833.5935
69 | 2610275.144 | 1224778.0773
70 | 2610281.8608 | 1224771.5557
71 | 2610212.6508 | 1224755.9333
72 | 2610220.9037 | 1224744.8037
73 | 2610203.1108 | 1224771.5891
74 | 2610222.9009 | 1224742.806
75 | 2610193.0643 | 1224788.1073
76 | 2610175.4225 | 1224771.0184
77 | 2610237.9613 | 1224735.6638
78 | 2610222.8241 | 1224730.0651
79 | 2610183.9622 | 1224803.4923
80 | 2610155.4885 | 1224770.6075
81 | 2610258.2642 | 1224720.2075
82 | 2610216.6323 | 1224703.4909
83 | 2610175.4977 | 1224813.4999
84 | 2610155.5284 | 1224755.988
85 | 2610155.5507 | 1224837.1716
86 | 2610160.9576 | 1224833.0582
87 | 2610175.2387 | 1224869.3744
88 | 2610115.0301 | 1224876.0334
89 | 2610150.7376 | 1224808.7582
90 | 2610180.7238 | 1224870.8368
91 | 2609790.9176 | 1224629.4354
92 | 2610100.4667 | 1224812.5581
93 | 2610102.3088 | 1224801.3578
94 | 2610115.499 | 1224803.8875
95 | 2610101.1725 | 1224784.9179
96 | 2610133.1116 | 1224806.196
97 | 2610195.8293 | 1224875.2783
98 | 2610211.4884 | 1224879.9224
99 | 2610193.2015 | 1224874.499
100 | 2610218.5676 | 1224882.0962
101 | 2610253.8032 | 1224905.4983
102 | 2610262.725 | 1224893.9241
103 | 2609968.1539 | 1224712.0645
104 | 2609968.2034 | 1224738.8117
105 | 2610274.47 | 1224876.8651
106 | 2610285.1874 | 1224861.2984
107 | 2610068.4 | 1224769.2042
108 | 2610086.6321 | 1224770.5347
109 | 2610141.0904 | 1224763.1085
110 | 2610146.2679 | 1224709.1671
111 | 2609869.6014 | 1224834.4003
112 | 2609871.6144 | 1224806.8192
113 | 2609946.4126 | 1224832.3835
114 | 2609968.2015 | 1224832.9961
115 | 2609968.2647 | 1224772.4299
116 | 2610091.3902 | 1224713.8408
117 | 2610107.4934 | 1224714.4098
118 | 2610027.6037 | 1224861.4007
119 | 2609999.8526 | 1224834.9613
120 | 2609973.7997 | 1224833.2091
121 | 2609968.3524 | 1224818.2256
122 | 2609968.3432 | 1224796.121
123 | 2609968.3269 | 1224791.1929
124 | 2609968.2673 | 1224773.2074
125 | 2610035.0042 | 1224762.7201

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99878 | -0.023019 | 0.0016554 | 0.00041489
1 | 0.99875 | -0.023593 | 0.0021217 | 0.00053174
2 | 0.99886 | -0.021612 | 0 | 0
3 | 0.99875 | -0.023676 | 0.0019027 | 0.00047687
4 | 1 | 0 | -0.31642 | -0.080585
5 | 0.99844 | -0.02947 | 0.0017416 | 0.00043648
6 | 0.99948 | -0.0099029 | 0.0012189 | 0.00030548
7 | 0.99667 | -0.063106 | 0.0020775 | 0.00052068
8 | 0.99945 | -0.01059 | 0.0017547 | 0.00043976
9 | 0.99424 | -0.10925 | 0 | 0
10 | 0.99753 | -0.047445 | 0.0022371 | 0.00056067
11 | 0.99773 | -0.043606 | 0.0012208 | 0.00030597
12 | 0.99741 | -0.049795 | 0 | 0
13 | 0.99784 | -0.041467 | 0 | 0
14 | 0.99738 | -0.050339 | 0.0033647 | 0.00084328
15 | 0.99741 | -0.049917 | 0.0020138 | 0.00050472
16 | 0.9978 | -0.042391 | 0 | 0
17 | 0.99808 | -0.036966 | 0 | 0
18 | 0.99737 | -0.050502 | 0.0015999 | 0.00040097
19 | 0.99771 | -0.044049 | 0.0036832 | 0.00092309
20 | 0.998 | -0.038507 | 0.0013247 | 0.000332
21 | 0.99835 | -0.031628 | 0.0023009 | 0.00057665
22 | 0.98419 | -0.30209 | 0.0020563 | 0.00051536
23 | 0.9839 | -0.30781 | 0.0043975 | 0.0011021
24 | 0.98582 | -0.27067 | 0 | 0
25 | 0.98117 | -0.36066 | 0.0020609 | 0.0005165
26 | 0.9857 | -0.27296 | 0.0032731 | 0.00082031
27 | 0.9873 | -0.24221 | 0 | 0
28 | 0.9857 | -0.27309 | 0.001769 | 0.00044335
29 | 0.97943 | -0.3946 | 0 | 0
30 | 0.98562 | -0.27454 | 0.0039943 | 0.0010011
31 | 0.98775 | -0.23361 | 0.0025083 | 0.00062864
32 | 0.9872 | -0.24408 | 0.0021858 | 0.00054781
33 | 0.98568 | -0.27353 | 0 | 0
34 | 0.97887 | -0.4056 | 0.0014005 | 0.00035099
35 | 0.97938 | -0.39556 | 0.0013817 | 0.0003463
36 | 0.97806 | -0.42143 | 0.00077355 | 0.00019387
37 | 0.98862 | -0.21686 | 0.0021986 | 0.00055101
38 | 0.98715 | -0.2452 | 0.0017438 | 0.00043704
39 | 0.98563 | -0.27438 | 0.0021073 | 0.00052813
40 | 0.98822 | -0.22557 | 0.0038065 | 0.000954
41 | 0.98805 | -0.22887 | 0 | 0
42 | 0.98831 | -0.22394 | 0 | 0
43 | 0.98767 | -0.23641 | 0.0042358 | 0.0010616
44 | 0.98868 | -0.21668 | 0.0017881 | 0.00044815
45 | 0.98813 | -0.22743 | 0.0029681 | 0.00074386
46 | 0.98743 | -0.24093 | 0 | 0
47 | 0.98924 | -0.20581 | 0.0029552 | 0.00074063
48 | 0.98786 | -0.23263 | 0.012544 | 0.0031438
49 | 0.98742 | -0.2413 | 0 | 0
50 | 0.98742 | -0.24121 | 0.0011796 | 0.00029565
51 | 0.98956 | -0.19968 | 0.0063428 | 0.0015897
52 | 0.97723 | -0.43795 | 0.0011827 | 0.00029642
53 | 0.97726 | -0.43728 | 0.0010009 | 0.00025086
54 | 0.97722 | -0.43805 | 0.0018466 | 0.00046279
55 | 0.9773 | -0.43648 | 0 | 0
56 | 0.97765 | -0.42951 | 0.00054337 | 0.00013618
57 | 0.97717 | -0.43911 | 0.0014429 | 0.00036161
58 | 0.97775 | -0.42772 | 0.00093191 | 0.00023356
59 | 0.97708 | -0.44077 | 0.0018806 | 0.00047133
60 | 0.9868 | -0.25313 | 0.0028475 | 0.00071365
61 | 0.98783 | -0.23313 | 0.0054727 | 0.0013716
62 | 0.98658 | -0.25743 | 0.0099266 | 0.0024878
63 | 0.98877 | -0.21489 | 0.0021865 | 0.00054798
64 | 0.98628 | -0.26328 | 0.001742 | 0.00043658
65 | 0.98891 | -0.21211 | 0.013291 | 0.003331
66 | 0.98593 | -0.2701 | 0.0032154 | 0.00080586
67 | 0.99042 | -0.18291 | 0 | 0
68 | 0.98498 | -0.28843 | 0 | 0
69 | 0.97705 | -0.44144 | 0.00087968 | 0.00022047
70 | 0.97703 | -0.44182 | 0.0022253 | 0.00055772
71 | 0.97284 | -0.52398 | 0.00264 | 0.00066165
72 | 0.97268 | -0.52713 | 0 | 0
73 | 0.97309 | -0.51894 | 0 | 0
74 | 0.97265 | -0.52777 | 0 | 0
75 | 0.97389 | -0.50336 | 0.0015124 | 0.00037905
76 | 0.97235 | -0.53367 | 0.0095348 | 0.0023896
77 | 0.97258 | -0.52913 | 0.00265 | 0.00066415
78 | 0.97255 | -0.52965 | 0 | 0
79 | 0.97464 | -0.48848 | 0.0039227 | 0.00098312
80 | 0.97199 | -0.54078 | 0 | 0
81 | 0.97254 | -0.52996 | 0.0017601 | 0.00044112
82 | 0.97235 | -0.53362 | 0.0078885 | 0.001977
83 | 0.97525 | -0.47658 | 0 | 0
84 | 0.97173 | -0.546 | 0 | 0
85 | 0.97726 | -0.43706 | 0.0031691 | 0.00079425
86 | 0.97683 | -0.44549 | 0.00085736 | 0.00021488
87 | 0.97843 | -0.41435 | 0.0014505 | 0.00036353
88 | 0.97937 | -0.39583 | 0.0018362 | 0.00046021
89 | 0.97483 | -0.48483 | 0.004128 | 0.0010346
90 | 0.97831 | -0.4166 | 0.0014627 | 0.00036659
91 | 0.98715 | -0.24648 | 0.0036767 | 0.00092147
92 | 0.97428 | -0.49558 | 0.0044108 | 0.0011055
93 | 0.97433 | -0.49466 | 0 | 0
94 | 0.97442 | -0.49277 | 0.0032864 | 0.00082364
95 | 0.97428 | -0.49557 | 0.0029863 | 0.00074845
96 | 0.9746 | -0.48928 | 0.0029612 | 0.00074214
97 | 0.97805 | -0.42183 | 0.0013554 | 0.0003397
98 | 0.97794 | -0.42391 | 0.0014977 | 0.00037536
99 | 0.97807 | -0.42141 | 0 | 0
100 | 0.9779 | -0.42465 | 0.0012035 | 0.00030163
101 | 0.97773 | -0.428 | 0 | 0
102 | 0.97767 | -0.42914 | 0.0012134 | 0.0003041
103 | 0.9903 | -0.18522 | 0.0033536 | 0.0008405
104 | 0.99273 | -0.13844 | 0.0023351 | 0.00058522
105 | 0.97761 | -0.4303 | 0.0013519 | 0.00033883
106 | 0.97758 | -0.4309 | 0.0017236 | 0.00043197
107 | 0.99918 | -0.01582 | 0 | 0
108 | 0.99914 | -0.01659 | 0.0024105 | 0.00060413
109 | 0.97158 | -0.54883 | 0.0095159 | 0.0023849
110 | 0.97128 | -0.55484 | 0.0098228 | 0.0024618
111 | 0.98432 | -0.30141 | 0 | 0
112 | 0.9837 | -0.31348 | 0.024215 | 0.0060688
113 | 0.99024 | -0.18579 | 0.0081378 | 0.0020395
114 | 0.9904 | -0.18264 | 0 | 0
115 | 0.99331 | -0.12705 | 0.0029504 | 0.00073945
116 | 0.99797 | -0.039021 | 0.0020654 | 0.00051763
117 | 0.99793 | -0.03971 | 0.0024449 | 0.00061274
118 | 0.98713 | -0.24552 | 0.0037015 | 0.00092769
119 | 0.98906 | -0.20832 | 0.0035848 | 0.00089844
120 | 0.99016 | -0.18737 | 0.0071735 | 0.0017979
121 | 0.99109 | -0.16948 | 0.0035996 | 0.00090214
122 | 0.99214 | -0.14934 | 0.0025625 | 0.00064223
123 | 0.99238 | -0.14478 | 0.0035212 | 0.00088251
124 | 0.99327 | -0.1278 | 0.00195 | 0.00048871
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0040245 | 0.0010085 | -0.0040244 | -0.0010086 | 1.0991e-07 | -3.6353e-08 | 0.0059958 | 0.0059958 | 0.0059958 | 0.99878 | -0.023019 | 0.99875 | -0.023593 | 1.6472
1 | -0.0056799 | -0.0014234 | 0.0056803 | 0.0014235 | 3.8081e-07 | 5.8106e-08 | 0.0084621 | 0.0084621 | 0.0084621 | 0.99878 | -0.023019 | 0.99886 | -0.021612 | 2.3248
2 | 0.0019027 | 0.00047684 | -0.0019027 | -0.00047687 | 7.5516e-09 | -2.796e-08 | 0.0028348 | 0.0028348 | 0.0028348 | 0.99875 | -0.023593 | 0.99875 | -0.023676 | 0.7788
3 | -0.28678 | -0.073438 | 0.28708 | 0.073629 | 0.00030058 | 0.00019185 | 0.42778 | 0.42778 | 0.42778 | 0.99886 | -0.021612 | 1 | 0 | 39.1737
4 | 0.2811 | 0.072014 | -0.28099 | -0.071946 | 0.000107 | 6.8289e-05 | 0.41932 | 0.41932 | 0.41932 | 0.99886 | -0.021612 | 0.99844 | -0.02947 | 38.3988
5 | 0.027689 | 0.0069552 | -0.027676 | -0.0069471 | 1.3079e-05 | 8.1011e-06 | 0.041208 | 0.041208 | 0.041208 | 1 | 0 | 0.99948 | -0.0099029 | 11.3208
6 | 0.27925 | 0.071509 | -0.2788 | -0.07122 | 0.00045419 | 0.00028986 | 0.41672 | 0.41672 | 0.41672 | 0.99844 | -0.02947 | 0.99667 | -0.063106 | 38.1612
7 | 0.026457 | 0.0066416 | -0.026456 | -0.0066411 | 8.6677e-07 | 5.3521e-07 | 0.039393 | 0.039393 | 0.039393 | 0.99948 | -0.0099029 | 0.99945 | -0.01059 | 10.8223
8 | 0.27672 | 0.070699 | -0.2761 | -0.070306 | 0.00061591 | 0.00039306 | 0.41362 | 0.41362 | 0.41362 | 0.99667 | -0.063106 | 0.99424 | -0.10925 | 37.8772
9 | 0.024702 | 0.0062013 | -0.024696 | -0.0061975 | 6.1616e-06 | 3.7843e-06 | 0.036781 | 0.036781 | 0.036781 | 0.99945 | -0.01059 | 0.99918 | -0.01582 | 10.1046
10 | 0.16731 | 0.042771 | -0.16717 | -0.042679 | 0.00014396 | 9.1425e-05 | 0.2507 | 0.2507 | 0.2507 | 0.99424 | -0.10925 | 0.99331 | -0.12705 | 22.9581
11 | 0.10879 | 0.027535 | -0.10864 | -0.027438 | 0.00015222 | 9.7225e-05 | 0.16292 | 0.16292 | 0.16292 | 0.99424 | -0.10925 | 0.99273 | -0.13844 | 44.7575
12 | -0.0092165 | -0.0023096 | 0.0092182 | 0.0023103 | 1.6853e-06 | 7.6814e-07 | 0.013748 | 0.013748 | 0.013748 | 0.99753 | -0.047445 | 0.99773 | -0.043606 | 3.7769
13 | 0.0069794 | 0.0017489 | -0.0069786 | -0.0017486 | 7.8137e-07 | 2.4915e-07 | 0.010411 | 0.010411 | 0.010411 | 0.99753 | -0.047445 | 0.99741 | -0.049795 | 2.8602
14 | -0.010439 | -0.0026163 | 0.01044 | 0.0026168 | 1.0643e-06 | 5.2822e-07 | 0.015569 | 0.015569 | 0.015569 | 0.99773 | -0.043606 | 0.99784 | -0.041467 | 4.2771
15 | 0.0033648 | 0.00084321 | -0.0033647 | -0.00084328 | 8.7211e-08 | -6.4633e-08 | 0.0050199 | 0.0050199 | 0.0050199 | 0.99741 | -0.049795 | 0.99738 | -0.050339 | 1.3791
16 | 0.0036138 | 0.00090543 | -0.0036138 | -0.00090544 | 2.0959e-08 | -1.1683e-08 | 0.0053912 | 0.0053913 | 0.0053913 | 0.99741 | -0.049795 | 0.99741 | -0.049917 | 1.4811
17 | 0.0036836 | 0.00092286 | -0.0036835 | -0.00092294 | 1.6218e-07 | -8.3425e-08 | 0.005493 | 0.0054931 | 0.0054931 | 0.99784 | -0.041467 | 0.9978 | -0.042391 | 1.5091
18 | -0.014124 | -0.0035397 | 0.014127 | 0.0035414 | 3.029e-06 | 1.7007e-06 | 0.021062 | 0.021062 | 0.021062 | 0.99784 | -0.041467 | 0.99808 | -0.036966 | 5.7862
19 | 0.0015999 | 0.00040073 | -0.0015999 | -0.00040097 | 4.4539e-08 | -2.4357e-07 | 0.0023868 | 0.0023869 | 0.0023869 | 0.99741 | -0.049917 | 0.99737 | -0.050502 | 0.65575
20 | 0.0036835 | 0.00092294 | -0.0036832 | -0.00092309 | 2.9085e-07 | -1.4956e-07 | 0.0054931 | 0.0054932 | 0.0054932 | 0.9978 | -0.042391 | 0.99771 | -0.044049 | 1.5091
21 | 0.0058355 | 0.0014623 | -0.0058351 | -0.0014622 | 4.2841e-07 | 7.6945e-08 | 0.0087 | 0.0087001 | 0.0087001 | 0.99808 | -0.036966 | 0.998 | -0.038507 | 2.3901
22 | -0.019962 | -0.0050037 | 0.019967 | 0.0050067 | 5.078e-06 | 3.0501e-06 | 0.029762 | 0.029762 | 0.029762 | 0.99808 | -0.036966 | 0.99835 | -0.031628 | 8.1763
23 | 0.0045104 | 0.0011302 | -0.0045103 | -0.0011302 | 1.1035e-07 | -1.4395e-08 | 0.006725 | 0.006725 | 0.006725 | 0.998 | -0.038507 | 0.99797 | -0.039021 | 1.8475
24 | -0.022268 | -0.0055834 | 0.022285 | 0.0055936 | 1.6788e-05 | 1.0212e-05 | 0.033191 | 0.033191 | 0.033191 | 0.99835 | -0.031628 | 0.99918 | -0.01582 | 9.1184
25 | 0.10701 | 0.027165 | -0.10698 | -0.027147 | 2.9427e-05 | 1.8796e-05 | 0.16191 | 0.16191 | 0.16191 | 0.98419 | -0.30209 | 0.9839 | -0.30781 | 44.4812
26 | -0.10906 | -0.027681 | 0.10923 | 0.027786 | 0.00016511 | 0.00010546 | 0.16502 | 0.16502 | 0.16502 | 0.98419 | -0.30209 | 0.98582 | -0.27067 | 45.3353
27 | 0.10258 | 0.026045 | -0.10232 | -0.025878 | 0.00026014 | 0.00016613 | 0.15526 | 0.15526 | 0.15526 | 0.9839 | -0.30781 | 0.98117 | -0.36066 | 42.6542
28 | 0.0072684 | 0.0018216 | -0.0072676 | -0.0018213 | 7.9362e-07 | 2.8377e-07 | 0.010971 | 0.010971 | 0.010971 | 0.98582 | -0.27067 | 0.9857 | -0.27296 | 3.0141
29 | -0.12038 | -0.030579 | 0.12054 | 0.030684 | 0.00016517 | 0.00010503 | 0.18184 | 0.18184 | 0.18184 | 0.98582 | -0.27067 | 0.9873 | -0.24221 | 24.9784
30 | 0.0038769 | 0.00097098 | -0.0038764 | -0.00097113 | 4.457e-07 | -1.5725e-07 | 0.0058516 | 0.0058517 | 0.0058517 | 0.98582 | -0.27067 | 0.9857 | -0.27309 | 1.6076
31 | 0.10026 | 0.025362 | -0.1001 | -0.025258 | 0.00016301 | 0.00010409 | 0.15214 | 0.15214 | 0.15214 | 0.98117 | -0.36066 | 0.97943 | -0.3946 | 41.7956
32 | 0.0039946 | 0.001001 | -0.0039943 | -0.0010011 | 2.9904e-07 | -8.8129e-08 | 0.0060302 | 0.0060303 | 0.0060303 | 0.9857 | -0.27296 | 0.98562 | -0.27454 | 1.6567
33 | -0.12817 | -0.032597 | 0.12823 | 0.032631 | 5.3149e-05 | 3.3821e-05 | 0.19335 | 0.19335 | 0.19335 | 0.9873 | -0.24221 | 0.98775 | -0.23361 | 26.5585
34 | 0.0076321 | 0.0019128 | -0.0076314 | -0.0019125 | 6.8032e-07 | 2.6008e-07 | 0.011503 | 0.011503 | 0.011503 | 0.9873 | -0.24221 | 0.9872 | -0.24408 | 3.1601
35 | 0.0021074 | 0.00052778 | -0.0021074 | -0.0005279 | 4.4712e-08 | -1.2155e-07 | 0.0031812 | 0.0031813 | 0.0031813 | 0.9857 | -0.27309 | 0.98568 | -0.27353 | 0.87398
36 | 0.024635 | 0.0061857 | -0.024622 | -0.0061778 | 1.2917e-05 | 7.9574e-06 | 0.037431 | 0.037431 | 0.037431 | 0.97943 | -0.3946 | 0.97887 | -0.4056 | 10.2832
37 | 0.0032182 | 0.00080631 | -0.003218 | -0.00080642 | 1.4594e-07 | -1.1148e-07 | 0.0048892 | 0.0048892 | 0.0048892 | 0.97943 | -0.3946 | 0.97938 | -0.39556 | 1.3432
38 | 0.072245 | 0.018266 | -0.072152 | -0.018207 | 9.2805e-05 | 5.9137e-05 | 0.10982 | 0.10982 | 0.10982 | 0.97943 | -0.3946 | 0.97806 | -0.42143 | 30.1693
39 | -0.13073 | -0.033259 | 0.13084 | 0.033326 | 0.00010563 | 6.6768e-05 | 0.19712 | 0.19712 | 0.19712 | 0.98775 | -0.23361 | 0.98862 | -0.21686 | 18.0517
40 | 0.0054457 | 0.0013647 | -0.0054454 | -0.0013647 | 2.9002e-07 | 3.8857e-08 | 0.0082082 | 0.0082083 | 0.0082083 | 0.9872 | -0.24408 | 0.98715 | -0.2452 | 2.255
41 | 0.0021074 | 0.0005279 | -0.0021073 | -0.00052813 | 8.5607e-08 | -2.327e-07 | 0.0031813 | 0.0031814 | 0.0031814 | 0.98568 | -0.27353 | 0.98563 | -0.27438 | 0.874
42 | 0.023221 | 0.0058268 | -0.023212 | -0.0058209 | 9.6892e-06 | 5.9406e-06 | 0.035302 | 0.035302 | 0.035302 | 0.97887 | -0.4056 | 0.97843 | -0.41435 | 9.6984
43 | 0.0018363 | 0.00046012 | -0.0018362 | -0.00046021 | 2.3771e-08 | -8.727e-08 | 0.0027899 | 0.0027899 | 0.0027899 | 0.97938 | -0.39556 | 0.97937 | -0.39583 | 0.76646
44 | 0.071378 | 0.018013 | -0.071325 | -0.017979 | 5.3412e-05 | 3.4032e-05 | 0.10864 | 0.10864 | 0.10864 | 0.97806 | -0.42143 | 0.97726 | -0.43706 | 29.846
45 | -0.13304 | -0.033877 | 0.13309 | 0.033912 | 5.4783e-05 | 3.4641e-05 | 0.20043 | 0.20043 | 0.20043 | 0.98862 | -0.21686 | 0.98906 | -0.20832 | 18.3547
46 | 0.0037016 | 0.00092766 | -0.0037015 | -0.00092769 | 5.6445e-08 | -2.5682e-08 | 0.0055797 | 0.0055797 | 0.0055797 | 0.98715 | -0.2452 | 0.98713 | -0.24552 | 1.5329
47 | 0.0090989 | 0.0022803 | -0.0090975 | -0.0022796 | 1.43e-06 | 6.5498e-07 | 0.013701 | 0.013701 | 0.013701 | 0.98822 | -0.22557 | 0.98805 | -0.22887 | 3.7639
48 | -0.012905 | -0.0032343 | 0.012906 | 0.0032348 | 1.0023e-06 | 5.5077e-07 | 0.019432 | 0.019432 | 0.019432 | 0.98822 | -0.22557 | 0.98831 | -0.22394 | 5.3385
49 | 0.0090975 | 0.0022796 | -0.0090942 | -0.0022781 | 3.2666e-06 | 1.4965e-06 | 0.013701 | 0.013701 | 0.013701 | 0.98805 | -0.22887 | 0.98767 | -0.23641 | 3.764
50 | -0.028424 | -0.0071256 | 0.028434 | 0.0071317 | 9.8276e-06 | 6.1063e-06 | 0.042796 | 0.042796 | 0.042796 | 0.98831 | -0.22394 | 0.98868 | -0.21668 | 11.7572
51 | 0.015517 | 0.0038908 | -0.015515 | -0.0038893 | 2.5826e-06 | 1.4912e-06 | 0.023364 | 0.023364 | 0.023364 | 0.98831 | -0.22394 | 0.98813 | -0.22743 | 6.4187
52 | 0.0048584 | 0.0012165 | -0.0048574 | -0.0012165 | 1.0465e-06 | 3.2762e-09 | 0.0073193 | 0.0073195 | 0.0073195 | 0.98767 | -0.23641 | 0.98743 | -0.24093 | 2.0108
53 | -0.030222 | -0.0075799 | 0.030238 | 0.0075896 | 1.5677e-05 | 9.7738e-06 | 0.045487 | 0.045487 | 0.045487 | 0.98868 | -0.21668 | 0.98924 | -0.20581 | 12.4965
54 | 0.012547 | 0.0031454 | -0.012544 | -0.0031438 | 3.1095e-06 | 1.6926e-06 | 0.018895 | 0.018895 | 0.018895 | 0.98813 | -0.22743 | 0.98786 | -0.23263 | 5.1908
55 | 0.0036777 | 0.00092102 | -0.0036776 | -0.00092105 | 6.4553e-08 | -3.0382e-08 | 0.0055419 | 0.0055419 | 0.0055419 | 0.98743 | -0.24093 | 0.98742 | -0.2413 | 1.5225
56 | 0.0011797 | 0.00029549 | -0.0011796 | -0.00029565 | 1.5796e-08 | -1.604e-07 | 0.0017776 | 0.0017777 | 0.0017777 | 0.98743 | -0.24093 | 0.98742 | -0.24121 | 0.48838
57 | -0.033193 | -0.0083303 | 0.033202 | 0.0083363 | 9.7013e-06 | 6.0756e-06 | 0.049932 | 0.049932 | 0.049932 | 0.98924 | -0.20581 | 0.98956 | -0.19968 | 13.7177
58 | 0.0036776 | 0.00092105 | -0.0036767 | -0.00092147 | 9.0667e-07 | -4.2636e-07 | 0.0055419 | 0.0055422 | 0.0055422 | 0.98742 | -0.2413 | 0.98715 | -0.24648 | 1.5226
59 | -0.039545 | -0.009926 | 0.039572 | 0.0099432 | 2.7292e-05 | 1.7203e-05 | 0.05947 | 0.05947 | 0.05947 | 0.98956 | -0.19968 | 0.9903 | -0.18522 | 16.338
60 | -0.0030293 | -0.00075918 | 0.0030294 | 0.00075909 | 9.6971e-08 | -9.0211e-08 | 0.0046127 | 0.0046126 | 0.0046127 | 0.97723 | -0.43795 | 0.97726 | -0.43728 | 1.2672
61 | 0.0018466 | 0.00046276 | -0.0018466 | -0.00046279 | 8.8389e-09 | -3.1695e-08 | 0.0028117 | 0.0028118 | 0.0028118 | 0.97723 | -0.43795 | 0.97722 | -0.43805 | 0.77246
62 | -0.0040303 | -0.00101 | 0.0040305 | 0.0010099 | 1.544e-07 | -3.8177e-08 | 0.0061367 | 0.0061367 | 0.0061367 | 0.97726 | -0.43728 | 0.9773 | -0.43648 | 1.6859
63 | -0.01046 | -0.0026211 | 0.010464 | 0.0026229 | 3.4706e-06 | 1.7638e-06 | 0.015927 | 0.015926 | 0.015927 | 0.9773 | -0.43648 | 0.97765 | -0.42951 | 4.3754
64 | 0.0064299 | 0.0016112 | -0.0064291 | -0.001611 | 8.0773e-07 | 2.3538e-07 | 0.0097899 | 0.00979 | 0.00979 | 0.9773 | -0.43648 | 0.97717 | -0.43911 | 2.6896
65 | -0.011007 | -0.0027591 | 0.011008 | 0.0027596 | 9.3848e-07 | 4.8881e-07 | 0.016753 | 0.016753 | 0.016753 | 0.97765 | -0.42951 | 0.97775 | -0.42772 | 4.6026
66 | 0.0049862 | 0.0012494 | -0.0049858 | -0.0012494 | 3.9468e-07 | 2.3924e-08 | 0.0075928 | 0.0075929 | 0.0075929 | 0.97717 | -0.43911 | 0.97708 | -0.44077 | 2.086
67 | -0.01194 | -0.0029931 | 0.011944 | 0.0029951 | 3.592e-06 | 1.9349e-06 | 0.018172 | 0.018172 | 0.018172 | 0.97775 | -0.42772 | 0.97807 | -0.42141 | 4.9922
68 | 0.0031052 | 0.00077802 | -0.0031051 | -0.0007781 | 9.8632e-08 | -8.4184e-08 | 0.0047288 | 0.0047289 | 0.0047289 | 0.97708 | -0.44077 | 0.97705 | -0.44144 | 1.2991
69 | -0.042022 | -0.010559 | 0.042062 | 0.010585 | 4.0166e-05 | 2.5365e-05 | 0.063375 | 0.063375 | 0.063375 | 0.9868 | -0.25313 | 0.98783 | -0.23313 | 17.4108
70 | 0.039174 | 0.0098456 | -0.039166 | -0.0098405 | 8.0345e-06 | 5.0637e-06 | 0.059081 | 0.059081 | 0.059081 | 0.9868 | -0.25313 | 0.98658 | -0.25743 | 16.2312
71 | -0.047534 | -0.011956 | 0.047576 | 0.011982 | 4.1461e-05 | 2.6259e-05 | 0.071619 | 0.071619 | 0.071619 | 0.98783 | -0.23313 | 0.98877 | -0.21489 | 19.6755
72 | 0.02924 | 0.0073527 | -0.029231 | -0.0073476 | 8.1697e-06 | 5.0857e-06 | 0.04411 | 0.04411 | 0.04411 | 0.98658 | -0.25743 | 0.98628 | -0.26328 | 12.118
73 | -0.049762 | -0.01253 | 0.049769 | 0.012535 | 6.6133e-06 | 4.1922e-06 | 0.074909 | 0.074909 | 0.074909 | 0.98877 | -0.21489 | 0.98891 | -0.21211 | 20.5795
74 | 0.027489 | 0.006911 | -0.02748 | -0.0069055 | 8.9451e-06 | 5.548e-06 | 0.041481 | 0.041482 | 0.041482 | 0.98628 | -0.26328 | 0.98593 | -0.2701 | 11.396
75 | -0.06306 | -0.015866 | 0.063148 | 0.015922 | 8.8097e-05 | 5.6047e-05 | 0.094908 | 0.094908 | 0.094908 | 0.98891 | -0.21211 | 0.99042 | -0.18291 | 26.0736
76 | 0.024265 | 0.0060996 | -0.024244 | -0.0060866 | 2.1223e-05 | 1.3045e-05 | 0.036629 | 0.036629 | 0.036629 | 0.98593 | -0.2701 | 0.98498 | -0.28843 | 10.0629
77 | -0.10608 | -0.026708 | 0.1063 | 0.026853 | 0.00022604 | 0.00014436 | 0.15942 | 0.15942 | 0.15942 | 0.99042 | -0.18291 | 0.99273 | -0.13844 | 43.7959
78 | 0.042931 | 0.010787 | -0.042926 | -0.010784 | 4.7274e-06 | 2.9866e-06 | 0.064509 | 0.064509 | 0.064509 | 0.99042 | -0.18291 | 0.9903 | -0.18522 | 17.7223
79 | 0.024244 | 0.0060866 | -0.024229 | -0.0060774 | 1.4996e-05 | 9.2184e-06 | 0.036629 | 0.036629 | 0.036629 | 0.98498 | -0.28843 | 0.98432 | -0.30141 | 10.0629
80 | 0.0022254 | 0.00055763 | -0.0022253 | -0.00055772 | 4.0326e-08 | -9.1438e-08 | 0.0033892 | 0.0033892 | 0.0033892 | 0.97705 | -0.44144 | 0.97703 | -0.44182 | 0.9311
81 | 0.012303 | 0.0030841 | -0.012301 | -0.0030831 | 1.8468e-06 | 1.0093e-06 | 0.018819 | 0.018819 | 0.018819 | 0.97284 | -0.52398 | 0.97268 | -0.52713 | 5.17
82 | -0.014943 | -0.0037458 | 0.014947 | 0.0037479 | 3.5918e-06 | 2.0711e-06 | 0.022857 | 0.022857 | 0.022857 | 0.97284 | -0.52398 | 0.97309 | -0.51894 | 6.2794
83 | 0.012301 | 0.0030831 | -0.012301 | -0.0030829 | 3.7465e-07 | 2.0476e-07 | 0.018819 | 0.018819 | 0.018819 | 0.97268 | -0.52713 | 0.97265 | -0.52777 | 5.1701
84 | -0.043858 | -0.011006 | 0.04389 | 0.011027 | 3.2615e-05 | 2.0633e-05 | 0.06707 | 0.06707 | 0.06707 | 0.97309 | -0.51894 | 0.97389 | -0.50336 | 18.4259
85 | 0.028911 | 0.0072585 | -0.02889 | -0.0072459 | 2.0302e-05 | 1.2649e-05 | 0.044214 | 0.044214 | 0.044214 | 0.97309 | -0.51894 | 0.97235 | -0.53367 | 12.1466
86 | 0.0044104 | 0.001105 | -0.0044101 | -0.001105 | 2.8594e-07 | -2.4863e-08 | 0.0067472 | 0.0067473 | 0.0067473 | 0.97265 | -0.52777 | 0.97258 | -0.52913 | 1.8536
87 | 0.0078907 | 0.0019779 | -0.00789 | -0.0019777 | 7.0633e-07 | 2.9165e-07 | 0.012072 | 0.012072 | 0.012072 | 0.97265 | -0.52777 | 0.97255 | -0.52965 | 3.3164
88 | -0.045403 | -0.011406 | 0.045435 | 0.011427 | 3.2269e-05 | 2.0429e-05 | 0.069381 | 0.069381 | 0.069381 | 0.97389 | -0.50336 | 0.97464 | -0.48848 | 19.0608
89 | 0.019356 | 0.0048563 | -0.019349 | -0.0048523 | 6.5608e-06 | 3.9517e-06 | 0.029622 | 0.029622 | 0.029622 | 0.97235 | -0.53367 | 0.97199 | -0.54078 | 8.138
90 | 0.0017602 | 0.00044085 | -0.0017601 | -0.00044112 | 6.9403e-08 | -2.7227e-07 | 0.0026929 | 0.002693 | 0.002693 | 0.97258 | -0.52913 | 0.97254 | -0.52996 | 0.73984
91 | 0.00789 | 0.0019777 | -0.0078885 | -0.001977 | 1.4912e-06 | 6.1582e-07 | 0.012072 | 0.012072 | 0.012072 | 0.97255 | -0.52965 | 0.97235 | -0.53362 | 3.3165
92 | -0.049358 | -0.01241 | 0.049386 | 0.012427 | 2.8053e-05 | 1.779e-05 | 0.07537 | 0.07537 | 0.07537 | 0.97464 | -0.48848 | 0.97525 | -0.47658 | 20.706
93 | 0.019349 | 0.0048523 | -0.019344 | -0.0048494 | 4.8115e-06 | 2.8982e-06 | 0.029622 | 0.029622 | 0.029622 | 0.97199 | -0.54078 | 0.97173 | -0.546 | 8.138
94 | 0.017785 | 0.0044611 | -0.017778 | -0.0044569 | 6.9852e-06 | 4.155e-06 | 0.027138 | 0.027138 | 0.027138 | 0.97525 | -0.47658 | 0.97483 | -0.48483 | 7.4555
95 | -0.067171 | -0.016889 | 0.067271 | 0.016952 | 9.9913e-05 | 6.3627e-05 | 0.10251 | 0.10251 | 0.10251 | 0.97525 | -0.47658 | 0.97683 | -0.44549 | 28.1615
96 | 0.009827 | 0.0024639 | -0.0098228 | -0.0024618 | 4.1365e-06 | 2.0442e-06 | 0.015049 | 0.015049 | 0.015049 | 0.97173 | -0.546 | 0.97128 | -0.55484 | 4.1343
97 | 0.0095172 | 0.0023855 | -0.0095159 | -0.0023849 | 1.2822e-06 | 6.2124e-07 | 0.014574 | 0.014574 | 0.014574 | 0.97173 | -0.546 | 0.97158 | -0.54883 | 4.0038
98 | 0.068156 | 0.017185 | -0.068128 | -0.017167 | 2.7465e-05 | 1.7493e-05 | 0.10381 | 0.10381 | 0.10381 | 0.97726 | -0.43706 | 0.97683 | -0.44549 | 28.5203
99 | 0.021761 | 0.0054573 | -0.021759 | -0.0054559 | 2.3317e-06 | 1.421e-06 | 0.033096 | 0.033096 | 0.033096 | 0.97843 | -0.41435 | 0.97831 | -0.4166 | 9.0923
100 | 0.01365 | 0.0034224 | -0.013647 | -0.0034207 | 2.9e-06 | 1.634e-06 | 0.020837 | 0.020837 | 0.020837 | 0.97483 | -0.48483 | 0.9746 | -0.48928 | 5.7245
101 | 0.020296 | 0.0050893 | -0.020291 | -0.0050865 | 4.6486e-06 | 2.8118e-06 | 0.030871 | 0.030871 | 0.030871 | 0.97831 | -0.4166 | 0.97807 | -0.42141 | 8.4811
102 | -0.0044108 | -0.0011055 | 0.004411 | 0.0011054 | 1.939e-07 | -1.7799e-08 | 0.0067366 | 0.0067366 | 0.0067366 | 0.97428 | -0.49558 | 0.97433 | -0.49466 | 1.8507
103 | -0.0073975 | -0.0018538 | 0.0073982 | 0.001854 | 6.6696e-07 | 2.5329e-07 | 0.011298 | 0.011297 | 0.011298 | 0.97433 | -0.49466 | 0.97442 | -0.49277 | 3.1037
104 | 0.0029865 | 0.00074832 | -0.0029863 | -0.00074845 | 1.2929e-07 | -1.2366e-07 | 0.0045609 | 0.004561 | 0.004561 | 0.97433 | -0.49466 | 0.97428 | -0.49557 | 1.253
105 | -0.010685 | -0.0026777 | 0.010686 | 0.0026786 | 1.7733e-06 | 9.1359e-07 | 0.016316 | 0.016316 | 0.016316 | 0.97442 | -0.49277 | 0.9746 | -0.48928 | 4.4824
106 | 0.0069921 | 0.0017517 | -0.0069914 | -0.0017514 | 6.9311e-07 | 2.3864e-07 | 0.010638 | 0.010638 | 0.010638 | 0.97805 | -0.42183 | 0.97794 | -0.42391 | 2.9225
107 | -0.0083475 | -0.0020914 | 0.0083477 | 0.0020914 | 1.6577e-07 | 7.1697e-08 | 0.0127 | 0.0127 | 0.0127 | 0.97805 | -0.42183 | 0.97807 | -0.42141 | 3.489
108 | 0.0054937 | 0.0013761 | -0.0054935 | -0.001376 | 1.9406e-07 | 3.1275e-08 | 0.0083589 | 0.0083589 | 0.0083589 | 0.97794 | -0.42391 | 0.9779 | -0.42465 | 2.2964
109 | 0.00429 | 0.0010744 | -0.0042893 | -0.0010745 | 6.8339e-07 | -9.9102e-08 | 0.0065276 | 0.0065278 | 0.0065278 | 0.9779 | -0.42465 | 0.97773 | -0.428 | 1.7933
110 | 0.0042893 | 0.0010745 | -0.0042891 | -0.0010745 | 2.3381e-07 | -3.3855e-08 | 0.0065278 | 0.0065278 | 0.0065278 | 0.97773 | -0.428 | 0.97767 | -0.42914 | 1.7934
111 | 0.0030757 | 0.00077044 | -0.0030756 | -0.00077059 | 1.7019e-07 | -1.5078e-07 | 0.0046811 | 0.0046812 | 0.0046812 | 0.97767 | -0.42914 | 0.97761 | -0.4303 | 1.286
112 | 0.0017236 | 0.00043176 | -0.0017236 | -0.00043197 | 4.8779e-08 | -2.0574e-07 | 0.0026234 | 0.0026235 | 0.0026235 | 0.97761 | -0.4303 | 0.97758 | -0.4309 | 0.72075
113 | 0.0024106 | 0.00060395 | -0.0024105 | -0.00060413 | 8.8348e-08 | -1.8288e-07 | 0.0035899 | 0.00359 | 0.00359 | 0.99918 | -0.01582 | 0.99914 | -0.01659 | 0.98626
114 | 0.024229 | 0.0060774 | -0.024215 | -0.0060688 | 1.3936e-05 | 8.5675e-06 | 0.036629 | 0.036629 | 0.036629 | 0.98432 | -0.30141 | 0.9837 | -0.31348 | 10.0629
115 | -0.0081378 | -0.0020395 | 0.008139 | 0.00204 | 1.2225e-06 | 5.019e-07 | 0.012229 | 0.012228 | 0.012229 | 0.99024 | -0.18579 | 0.9904 | -0.18264 | 3.3595
116 | -0.15216 | -0.038756 | 0.15226 | 0.038818 | 9.6687e-05 | 6.1309e-05 | 0.22883 | 0.22883 | 0.22883 | 0.9904 | -0.18264 | 0.99109 | -0.16948 | 20.9555
117 | 0.14402 | 0.036716 | -0.14399 | -0.036695 | 3.2856e-05 | 2.0811e-05 | 0.21661 | 0.21661 | 0.21661 | 0.9904 | -0.18264 | 0.99016 | -0.18737 | 19.8357
118 | 0.16422 | 0.04194 | -0.16421 | -0.041936 | 5.8951e-06 | 3.7427e-06 | 0.24628 | 0.24628 | 0.24628 | 0.99331 | -0.12705 | 0.99327 | -0.1278 | 22.5533
119 | 0.002445 | 0.00061258 | -0.0024449 | -0.00061274 | 8.0303e-08 | -1.5914e-07 | 0.0036455 | 0.0036455 | 0.0036455 | 0.99797 | -0.039021 | 0.99793 | -0.03971 | 1.0015
120 | -0.13668 | -0.03481 | 0.13682 | 0.034898 | 0.00013829 | 8.7499e-05 | 0.20583 | 0.20583 | 0.20583 | 0.98906 | -0.20832 | 0.99016 | -0.18737 | 18.8485
121 | -0.15586 | -0.03972 | 0.15601 | 0.039816 | 0.00015161 | 9.6172e-05 | 0.23424 | 0.23424 | 0.23424 | 0.99109 | -0.16948 | 0.99214 | -0.14934 | 21.4504
122 | -0.15857 | -0.040458 | 0.15861 | 0.04048 | 3.4918e-05 | 2.2156e-05 | 0.23808 | 0.23808 | 0.23808 | 0.99214 | -0.14934 | 0.99238 | -0.14478 | 21.8023
123 | -0.16213 | -0.041363 | 0.16226 | 0.041447 | 0.00013315 | 8.4517e-05 | 0.24336 | 0.24336 | 0.24336 | 0.99238 | -0.14478 | 0.99327 | -0.1278 | 22.2858

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31799 | 0.080979

## res_load
| p_mw | q_mvar
0 | 0.0016554 | 0.00041489
1 | 0.0021217 | 0.00053174
2 | 0.0019027 | 0.00047687
3 | 0.0015715 | 0.00039384
4 | 0.0017416 | 0.00043648
5 | 0.0012189 | 0.00030548
6 | 0.0020775 | 0.00052068
7 | 0.0017547 | 0.00043976
8 | 0.0022371 | 0.00056067
9 | 0.0012208 | 0.00030597
10 | 0.0033647 | 0.00084328
11 | 0.0020138 | 0.00050472
12 | 0.0015999 | 0.00040097
13 | 0.0036832 | 0.00092309
14 | 0.0013247 | 0.000332
15 | 0.0023009 | 0.00057665
16 | 0.0020563 | 0.00051536
17 | 0.0043975 | 0.0011021
18 | 0.0020609 | 0.0005165
19 | 0.0032731 | 0.00082031
20 | 0.001769 | 0.00044335
21 | 0.0039943 | 0.0010011
22 | 0.0025083 | 0.00062864
23 | 0.0021858 | 0.00054781
24 | 0.0014005 | 0.00035099
25 | 0.0013817 | 0.0003463
26 | 0.00077355 | 0.00019387
27 | 0.0021986 | 0.00055101
28 | 0.0017438 | 0.00043704
29 | 0.0021073 | 0.00052813
30 | 0.0038065 | 0.000954
31 | 0.0042358 | 0.0010616
32 | 0.0017881 | 0.00044815
33 | 0.0029681 | 0.00074386
34 | 0.0029552 | 0.00074063
35 | 0.012544 | 0.0031438
36 | 0.0011796 | 0.00029565
37 | 0.0063428 | 0.0015897
38 | 0.0011827 | 0.00029642
39 | 0.0010009 | 0.00025086
40 | 0.0018466 | 0.00046279
41 | 0.00054337 | 0.00013618
42 | 0.0014429 | 0.00036161
43 | 0.00093191 | 0.00023356
44 | 0.0018806 | 0.00047133
45 | 0.0028475 | 0.00071365
46 | 0.0054727 | 0.0013716
47 | 0.0099266 | 0.0024878
48 | 0.0021865 | 0.00054798
49 | 0.001742 | 0.00043658
50 | 0.013291 | 0.003331
51 | 0.0032154 | 0.00080586
52 | 0.00087968 | 0.00022047
53 | 0.0022253 | 0.00055772
54 | 0.00264 | 0.00066165
55 | 0.0015124 | 0.00037905
56 | 0.0095348 | 0.0023896
57 | 0.00265 | 0.00066415
58 | 0.0039227 | 0.00098312
59 | 0.0017601 | 0.00044112
60 | 0.0078885 | 0.001977
61 | 0.0031691 | 0.00079425
62 | 0.00085736 | 0.00021488
63 | 0.0014505 | 0.00036353
64 | 0.0018362 | 0.00046021
65 | 0.004128 | 0.0010346
66 | 0.0014627 | 0.00036659
67 | 0.0036767 | 0.00092147
68 | 0.0044108 | 0.0011055
69 | 0.0032864 | 0.00082364
70 | 0.0029863 | 0.00074845
71 | 0.0029612 | 0.00074214
72 | 0.0013554 | 0.0003397
73 | 0.0014977 | 0.00037536
74 | 0.0012035 | 0.00030163
75 | 0.0012134 | 0.0003041
76 | 0.0033536 | 0.0008405
77 | 0.0023351 | 0.00058522
78 | 0.0013519 | 0.00033883
79 | 0.0017236 | 0.00043197
80 | 0.0024105 | 0.00060413
81 | 0.0095159 | 0.0023849
82 | 0.0098228 | 0.0024618
83 | 0.024215 | 0.0060688
84 | 0.0081378 | 0.0020395
85 | 0.0029504 | 0.00073945
86 | 0.0020654 | 0.00051763
87 | 0.0024449 | 0.00061274
88 | 0.0037015 | 0.00092769
89 | 0.0035848 | 0.00089844
90 | 0.0071735 | 0.0017979
91 | 0.0035996 | 0.00090214
92 | 0.0025625 | 0.00064223
93 | 0.0035212 | 0.00088251
94 | 0.00195 | 0.00048871

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1