## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2532-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2532-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2532-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2532-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2532-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2532-2_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2532-2_0_4_node_120 | 0.4 | n |  | TRUE
7 | bus_LV_2532-2_0_4_node_102 | 0.4 | n |  | TRUE
8 | bus_LV_2532-2_0_4_node_134 | 0.4 | n |  | TRUE
9 | bus_LV_2532-2_0_4_node_99 | 0.4 | n |  | TRUE
10 | bus_LV_2532-2_0_4_node_121 | 0.4 | n |  | TRUE
11 | bus_LV_2532-2_0_4_node_96 | 0.4 | n |  | TRUE
12 | bus_LV_2532-2_0_4_node_135 | 0.4 | n |  | TRUE
13 | bus_LV_2532-2_0_4_node_100 | 0.4 | n |  | TRUE
14 | bus_LV_2532-2_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2532-2_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2532-2_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2532-2_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2532-2_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_2532-2_0_4_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_2532-2_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2532-2_0_4_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_2532-2_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2532-2_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2532-2_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2532-2_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2532-2_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2532-2_0_4_node_66 | 0.4 | n |  | TRUE
28 | bus_LV_2532-2_0_4_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_2532-2_0_4_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_2532-2_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2532-2_0_4_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_2532-2_0_4_node_82 | 0.4 | n |  | TRUE
33 | bus_LV_2532-2_0_4_node_75 | 0.4 | n |  | TRUE
34 | bus_LV_2532-2_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2532-2_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2532-2_0_4_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2532-2_0_4_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_2532-2_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2532-2_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2532-2_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_2532-2_0_4_node_109 | 0.4 | n |  | TRUE
42 | bus_LV_2532-2_0_4_node_85 | 0.4 | n |  | TRUE
43 | bus_LV_2532-2_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2532-2_0_4_node_140 | 0.4 | n |  | TRUE
45 | bus_LV_2532-2_0_4_node_147 | 0.4 | n |  | TRUE
46 | bus_LV_2532-2_0_4_node_138 | 0.4 | n |  | TRUE
47 | bus_LV_2532-2_0_4_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_2532-2_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_2532-2_0_4_node_111 | 0.4 | n |  | TRUE
50 | bus_LV_2532-2_0_4_node_107 | 0.4 | n |  | TRUE
51 | bus_LV_2532-2_0_4_node_86 | 0.4 | n |  | TRUE
52 | bus_LV_2532-2_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_2532-2_0_4_node_22 | 0.4 | n |  | TRUE
54 | bus_LV_2532-2_0_4_node_23 | 0.4 | n |  | TRUE
55 | bus_LV_2532-2_0_4_node_25 | 0.4 | n |  | TRUE
56 | bus_LV_2532-2_0_4_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_2532-2_0_4_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_2532-2_0_4_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_2532-2_0_4_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_2532-2_0_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_2532-2_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2532-2_0_4_node_29 | 0.4 | n |  | TRUE
63 | bus_LV_2532-2_0_4_node_30 | 0.4 | n |  | TRUE
64 | bus_LV_2532-2_0_4_node_31 | 0.4 | n |  | TRUE
65 | bus_LV_2532-2_0_4_node_32 | 0.4 | n |  | TRUE
66 | bus_LV_2532-2_0_4_node_33 | 0.4 | n |  | TRUE
67 | bus_LV_2532-2_0_4_node_34 | 0.4 | n |  | TRUE
68 | bus_LV_2532-2_0_4_node_137 | 0.4 | n |  | TRUE
69 | bus_LV_2532-2_0_4_node_136 | 0.4 | n |  | TRUE
70 | bus_LV_2532-2_0_4_node_106 | 0.4 | n |  | TRUE
71 | bus_LV_2532-2_0_4_node_139 | 0.4 | n |  | TRUE
72 | bus_LV_2532-2_0_4_node_37 | 0.4 | n |  | TRUE
73 | bus_LV_2532-2_0_4_node_88 | 0.4 | n |  | TRUE
74 | bus_LV_2532-2_0_4_node_87 | 0.4 | n |  | TRUE
75 | bus_LV_2532-2_0_4_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_2532-2_0_4_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_2532-2_0_4_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_2532-2_0_4_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_2532-2_0_4_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_2532-2_0_4_node_144 | 0.4 | n |  | TRUE
81 | bus_LV_2532-2_0_4_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_2532-2_0_4_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_2532-2_0_4_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_2532-2_0_4_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_2532-2_0_4_node_52 | 0.4 | n |  | TRUE
86 | bus_LV_2532-2_0_4_node_116 | 0.4 | n |  | TRUE
87 | bus_LV_2532-2_0_4_node_104 | 0.4 | n |  | TRUE
88 | bus_LV_2532-2_0_4_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_2532-2_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2532-2_0_4_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_2532-2_0_4_node_68 | 0.4 | n |  | TRUE
92 | bus_LV_2532-2_0_4_node_54 | 0.4 | n |  | TRUE
93 | bus_LV_2532-2_0_4_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_2532-2_0_4_node_56 | 0.4 | n |  | TRUE
95 | bus_LV_2532-2_0_4_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_2532-2_0_4_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_2532-2_0_4_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_2532-2_0_4_node_132 | 0.4 | n |  | TRUE
99 | bus_LV_2532-2_0_4_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_2532-2_0_4_node_130 | 0.4 | n |  | TRUE
101 | bus_LV_2532-2_0_4_node_60 | 0.4 | n |  | TRUE
102 | bus_LV_2532-2_0_4_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_2532-2_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2532-2_0_4_node_70 | 0.4 | n |  | TRUE
105 | bus_LV_2532-2_0_4_node_117 | 0.4 | n |  | TRUE
106 | bus_LV_2532-2_0_4_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_2532-2_0_4_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_2532-2_0_4_node_113 | 0.4 | n |  | TRUE
109 | bus_LV_2532-2_0_4_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_2532-2_0_4_node_73 | 0.4 | n |  | TRUE
111 | bus_LV_2532-2_0_4_node_83 | 0.4 | n |  | TRUE
112 | bus_LV_2532-2_0_4_node_77 | 0.4 | n |  | TRUE
113 | bus_LV_2532-2_0_4_node_78 | 0.4 | n |  | TRUE
114 | bus_LV_2532-2_0_4_node_79 | 0.4 | n |  | TRUE
115 | bus_LV_2532-2_0_4_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_2532-2_0_4_node_84 | 0.4 | n |  | TRUE
117 | bus_LV_2532-2_0_4_node_123 | 0.4 | n |  | TRUE
118 | bus_LV_2532-2_0_4_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_2532-2_0_4_node_93 | 0.4 | n |  | TRUE
120 | bus_LV_2532-2_0_4_node_94 | 0.4 | n |  | TRUE
121 | bus_LV_2532-2_0_4_node_95 | 0.4 | n |  | TRUE
122 | bus_LV_2532-2_0_4_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_2532-2_0_4_node_101 | 0.4 | n |  | TRUE
124 | bus_LV_2532-2_0_4_node_145 | 0.4 | n |  | TRUE
125 | bus_LV_2532-2_0_4_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_2532-2_0_4_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_2532-2_0_4_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_2532-2_0_4_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_2532-2_0_4_node_142 | 0.4 | n |  | TRUE
130 | bus_LV_2532-2_0_4_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_2532-2_0_4_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_2532-2_0_4_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_2532-2_0_4_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_2532-2_0_4_node_126 | 0.4 | n |  | TRUE
135 | bus_LV_2532-2_0_4_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_2532-2_0_4_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_2532-2_0_4_node_129 | 0.4 | n |  | TRUE
138 | bus_LV_2532-2_0_4_node_127 | 0.4 | n |  | TRUE
139 | bus_LV_2532-2_0_4_node_128 | 0.4 | n |  | TRUE
140 | bus_LV_2532-2_0_4_node_143 | 0.4 | n |  | TRUE
141 | bus_MV_392_1_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2532-2_0_4_load_0 | 0 | 0.001141 | 0.00028596 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2532-2_0_4_load_1 | 1 | 0.0018581 | 0.00046569 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2532-2_0_4_load_3 | 3 | 0.001397 | 0.00035013 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2532-2_0_4_load_5 | 5 | 0.0067808 | 0.0016994 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2532-2_0_4_load_120 | 6 | 0.0016927 | 0.00042422 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2532-2_0_4_load_102 | 7 | 0.0075659 | 0.0018962 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2532-2_0_4_load_134 | 8 | 0.0031851 | 0.00079827 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2532-2_0_4_load_99 | 9 | 0.0015755 | 0.00039485 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2532-2_0_4_load_121 | 10 | 0.0009632 | 0.0002414 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2532-2_0_4_load_135 | 12 | 0.0029112 | 0.00072962 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2532-2_0_4_load_100 | 13 | 0.0051784 | 0.0012978 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2532-2_0_4_load_6 | 14 | 0.0028002 | 0.0007018 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2532-2_0_4_load_7 | 15 | 0.0018457 | 0.00046256 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2532-2_0_4_load_28 | 18 | 0.0025002 | 0.00062661 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2532-2_0_4_load_64 | 19 | 0.0039114 | 0.00098029 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2532-2_0_4_load_65 | 21 | 0.0015867 | 0.00039767 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2532-2_0_4_load_11 | 22 | 0.0023024 | 0.00057702 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2532-2_0_4_load_15 | 26 | 0.003291 | 0.0008248 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2532-2_0_4_load_45 | 28 | 0.011809 | 0.0029597 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2532-2_0_4_load_27 | 30 | 0.0029191 | 0.00073159 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2532-2_0_4_load_82 | 32 | 0.0018797 | 0.0004711 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2532-2_0_4_load_75 | 33 | 0.0029917 | 0.00074979 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2532-2_0_4_load_16 | 34 | 0.0078531 | 0.0019682 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2532-2_0_4_load_17 | 35 | 0.0026467 | 0.00066333 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2532-2_0_4_load_20 | 38 | 0.0013813 | 0.00034619 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2532-2_0_4_load_85 | 42 | 0.0021146 | 0.00052997 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2532-2_0_4_load_39 | 43 | 0.003421 | 0.00085739 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2532-2_0_4_load_147 | 45 | 0.0040075 | 0.0010044 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2532-2_0_4_load_40 | 48 | 0.0028584 | 0.00071639 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2532-2_0_4_load_111 | 49 | 0.0043469 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2532-2_0_4_load_107 | 50 | 0.00090639 | 0.00022716 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2532-2_0_4_load_86 | 51 | 0.0010125 | 0.00025377 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2532-2_0_4_load_38 | 52 | 0.0038851 | 0.00097369 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2532-2_0_4_load_22 | 53 | 0.0027928 | 0.00069994 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2532-2_0_4_load_23 | 54 | 0.010133 | 0.0025395 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2532-2_0_4_load_25 | 55 | 0.0039357 | 0.00098639 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2532-2_0_4_load_26 | 56 | 0.0015198 | 0.00038091 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2532-2_0_4_load_35 | 58 | 0.0016375 | 0.00041039 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2532-2_0_4_load_63 | 59 | 0.0026593 | 0.00066648 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2532-2_0_4_load_59 | 60 | 0.0053484 | 0.0013404 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2532-2_0_4_load_36 | 61 | 0.0014809 | 0.00037115 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2532-2_0_4_load_29 | 62 | 0.0017232 | 0.00043187 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2532-2_0_4_load_30 | 63 | 0.001885 | 0.00047242 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2532-2_0_4_load_32 | 65 | 0.0014923 | 0.000374 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2532-2_0_4_load_34 | 67 | 0.00043564 | 0.00010918 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2532-2_0_4_load_137 | 68 | 0.0020407 | 0.00051144 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2532-2_0_4_load_136 | 69 | 0.0013907 | 0.00034855 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2532-2_0_4_load_139 | 71 | 0.003009 | 0.00075413 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2532-2_0_4_load_37 | 72 | 0.0027831 | 0.00069752 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2532-2_0_4_load_88 | 73 | 0.0027752 | 0.00069552 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2532-2_0_4_load_87 | 74 | 0.0027401 | 0.00068672 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2532-2_0_4_load_42 | 76 | 0.0028881 | 0.00072382 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2532-2_0_4_load_46 | 78 | 0.0028371 | 0.00071106 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2532-2_0_4_load_47 | 79 | 0.0016218 | 0.00040646 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2532-2_0_4_load_144 | 80 | 0.0040543 | 0.0010161 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2532-2_0_4_load_48 | 81 | 0.0012506 | 0.00031342 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2532-2_0_4_load_49 | 82 | 0.00032954 | 8.2591e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2532-2_0_4_load_116 | 86 | 0.0011126 | 0.00027884 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2532-2_0_4_load_67 | 88 | 0.0011426 | 0.00028637 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2532-2_0_4_load_103 | 90 | 0.0015265 | 0.00038257 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2532-2_0_4_load_68 | 91 | 0.0050324 | 0.0012612 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2532-2_0_4_load_54 | 92 | 0.0032289 | 0.00080924 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2532-2_0_4_load_55 | 93 | 0.0021438 | 0.0005373 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2532-2_0_4_load_56 | 94 | 0.0012086 | 0.00030291 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2532-2_0_4_load_57 | 95 | 0.0058366 | 0.0014628 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2532-2_0_4_load_92 | 97 | 0.0079774 | 0.0019993 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2532-2_0_4_load_132 | 98 | 0.0038353 | 0.00096123 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2532-2_0_4_load_91 | 99 | 0.0052145 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2532-2_0_4_load_130 | 100 | 0.0040971 | 0.0010268 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2532-2_0_4_load_60 | 101 | 0.0021268 | 0.00053302 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2532-2_0_4_load_62 | 102 | 0.005404 | 0.0013544 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2532-2_0_4_load_98 | 103 | 0.0021228 | 0.00053203 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2532-2_0_4_load_70 | 104 | 0.0017779 | 0.00044558 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2532-2_0_4_load_117 | 105 | 0.0017625 | 0.00044173 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2532-2_0_4_load_71 | 106 | 0.0024882 | 0.0006236 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2532-2_0_4_load_112 | 107 | 0.0021598 | 0.00054131 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2532-2_0_4_load_113 | 108 | 0.0018069 | 0.00045284 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2532-2_0_4_load_72 | 109 | 0.0021484 | 0.00053845 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2532-2_0_4_load_83 | 111 | 0.0014703 | 0.00036849 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2532-2_0_4_load_77 | 112 | 0.0021446 | 0.00053749 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2532-2_0_4_load_78 | 113 | 0.0011809 | 0.00029595 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2532-2_0_4_load_79 | 114 | 0.0013905 | 0.00034849 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2532-2_0_4_load_81 | 115 | 0.00077544 | 0.00019434 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2532-2_0_4_load_84 | 116 | 0.0020293 | 0.00050858 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2532-2_0_4_load_123 | 117 | 0.0019932 | 0.00049954 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2532-2_0_4_load_114 | 118 | 0.0024062 | 0.00060305 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2532-2_0_4_load_94 | 120 | 0.0030535 | 0.00076527 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2532-2_0_4_load_101 | 123 | 0.0040616 | 0.0010179 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2532-2_0_4_load_145 | 124 | 0.0016046 | 0.00040215 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2532-2_0_4_load_118 | 125 | 0.0031173 | 0.00078128 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2532-2_0_4_load_108 | 126 | 0.0021482 | 0.00053839 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2532-2_0_4_load_110 | 127 | 0.0032903 | 0.00082463 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2532-2_0_4_load_133 | 128 | 0.0014928 | 0.00037413 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2532-2_0_4_load_142 | 129 | 0.0059634 | 0.0014946 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2532-2_0_4_load_119 | 130 | 0.0020221 | 0.00050679 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2532-2_0_4_load_124 | 131 | 0.0034281 | 0.00085916 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2532-2_0_4_load_125 | 132 | 0.0018076 | 0.00045302 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2532-2_0_4_load_122 | 133 | 0.00068179 | 0.00017087 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2532-2_0_4_load_126 | 134 | 0.0011097 | 0.00027813 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2532-2_0_4_load_141 | 135 | 0.0022584 | 0.00056601 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2532-2_0_4_load_131 | 136 | 0.0014508 | 0.0003636 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2532-2_0_4_load_129 | 137 | 0.0042497 | 0.0010651 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2532-2_0_4_load_127 | 138 | 0.0027001 | 0.00067672 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2532-2_0_4_load_128 | 139 | 0.0019449 | 0.00048745 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2532-2_0_4_load_143 | 140 | 0.0057263 | 0.0014351 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 128 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2532-2_0_4_line_0 |  | 0 | 1 | 0.0035548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2532-2_0_4_line_1 |  | 0 | 2 | 0.020561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2532-2_0_4_line_2 |  | 1 | 3 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2532-2_0_4_line_3 |  | 2 | 4 | 0.024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2532-2_0_4_line_4 |  | 2 | 5 | 0.0034821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2532-2_0_4_line_5 |  | 3 | 6 | 0.01005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2532-2_0_4_line_6 |  | 4 | 7 | 0.017307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2532-2_0_4_line_7 |  | 4 | 8 | 0.023415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2532-2_0_4_line_8 |  | 5 | 9 | 0.034799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2532-2_0_4_line_9 |  | 6 | 10 | 0.013918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2532-2_0_4_line_10 |  | 7 | 11 | 0.0079785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2532-2_0_4_line_11 |  | 8 | 12 | 0.013927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2532-2_0_4_line_12 |  | 9 | 13 | 0.010799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2532-2_0_4_line_13 |  | 10 | 133 | 0.028581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2532-2_0_4_line_14 |  | 11 | 123 | 0.029983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2532-2_0_4_line_15 |  | 11 | 121 | 0.075817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2532-2_0_4_line_16 |  | 13 | 115 | 0.024038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2532-2_0_4_line_17 |  | 14 | 15 | 0.019508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2532-2_0_4_line_18 |  | 14 | 16 | 0.01169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2532-2_0_4_line_19 |  | 16 | 17 | 0.00286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2532-2_0_4_line_20 |  | 17 | 18 | 0.012501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2532-2_0_4_line_21 |  | 17 | 19 | 0.01333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2532-2_0_4_line_22 |  | 18 | 20 | 0.037371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2532-2_0_4_line_23 |  | 19 | 21 | 0.02934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2532-2_0_4_line_24 |  | 20 | 56 | 0.015634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2532-2_0_4_line_25 |  | 20 | 30 | 0.027459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2532-2_0_4_line_26 |  | 20 | 53 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2532-2_0_4_line_27 |  | 22 | 23 | 0.039856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2532-2_0_4_line_28 |  | 22 | 24 | 0.049531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2532-2_0_4_line_29 |  | 23 | 25 | 0.031252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2532-2_0_4_line_30 |  | 24 | 26 | 0.021339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2532-2_0_4_line_31 |  | 25 | 27 | 0.046277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_2532-2_0_4_line_32 |  | 25 | 28 | 0.032397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2532-2_0_4_line_33 |  | 26 | 29 | 0.051038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2532-2_0_4_line_34 |  | 27 | 30 | 0.0095894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2532-2_0_4_line_35 |  | 28 | 31 | 0.032888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2532-2_0_4_line_36 |  | 29 | 32 | 0.015831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2532-2_0_4_line_37 |  | 29 | 33 | 0.017637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2532-2_0_4_line_38 |  | 31 | 65 | 0.014624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2532-2_0_4_line_39 |  | 32 | 111 | 0.020193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2532-2_0_4_line_40 |  | 33 | 78 | 0.021385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2532-2_0_4_line_41 |  | 34 | 35 | 0.033083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2532-2_0_4_line_42 |  | 35 | 36 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2532-2_0_4_line_43 |  | 36 | 40 | 0.040941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2532-2_0_4_line_44 |  | 36 | 41 | 0.006969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2532-2_0_4_line_45 |  | 37 | 38 | 0.019961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2532-2_0_4_line_46 |  | 37 | 39 | 0.02748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2532-2_0_4_line_47 |  | 38 | 42 | 0.016177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2532-2_0_4_line_48 |  | 39 | 43 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2532-2_0_4_line_49 |  | 40 | 47 | 0.047008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2532-2_0_4_line_50 |  | 40 | 48 | 0.024925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2532-2_0_4_line_51 |  | 41 | 49 | 0.039461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2532-2_0_4_line_52 |  | 41 | 50 | 0.024286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2532-2_0_4_line_53 |  | 42 | 51 | 0.017875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2532-2_0_4_line_54 |  | 43 | 52 | 0.033764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2532-2_0_4_line_55 |  | 44 | 45 | 0.024407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2532-2_0_4_line_56 |  | 44 | 46 | 0.004357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2532-2_0_4_line_57 |  | 46 | 71 | 0.04603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2532-2_0_4_line_58 |  | 47 | 71 | 0.045766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2532-2_0_4_line_59 |  | 47 | 75 | 0.014535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2532-2_0_4_line_60 |  | 48 | 52 | 0.0045664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2532-2_0_4_line_61 |  | 49 | 95 | 0.0011852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2532-2_0_4_line_62 |  | 50 | 126 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2532-2_0_4_line_63 |  | 53 | 54 | 0.0030245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2532-2_0_4_line_64 |  | 54 | 55 | 0.017343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2532-2_0_4_line_65 |  | 55 | 57 | 0.01338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2532-2_0_4_line_66 |  | 56 | 58 | 0.016906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2532-2_0_4_line_67 |  | 57 | 59 | 0.029279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2532-2_0_4_line_68 |  | 57 | 60 | 0.012783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2532-2_0_4_line_69 |  | 58 | 61 | 0.0094301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2532-2_0_4_line_70 |  | 59 | 104 | 0.0043362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2532-2_0_4_line_71 |  | 60 | 101 | 0.0020495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2532-2_0_4_line_72 |  | 61 | 72 | 0.0035203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2532-2_0_4_line_73 |  | 62 | 63 | 0.025921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2532-2_0_4_line_74 |  | 62 | 64 | 0.032231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2532-2_0_4_line_75 |  | 63 | 65 | 0.019906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2532-2_0_4_line_76 |  | 64 | 66 | 0.016389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2532-2_0_4_line_77 |  | 64 | 67 | 0.0081908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2532-2_0_4_line_78 |  | 66 | 68 | 0.014459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2532-2_0_4_line_79 |  | 66 | 69 | 0.018012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2532-2_0_4_line_80 |  | 69 | 70 | 0.028346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2532-2_0_4_line_81 |  | 70 | 87 | 0.035704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2532-2_0_4_line_82 |  | 72 | 73 | 0.011766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2532-2_0_4_line_83 |  | 73 | 74 | 0.010148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2532-2_0_4_line_84 |  | 75 | 88 | 0.022809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2532-2_0_4_line_85 |  | 75 | 83 | 0.022132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2532-2_0_4_line_86 |  | 76 | 77 | 0.0052196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2532-2_0_4_line_87 |  | 77 | 78 | 0.016833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2532-2_0_4_line_88 |  | 77 | 79 | 0.040051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2532-2_0_4_line_89 |  | 79 | 80 | 0.021566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2532-2_0_4_line_90 |  | 81 | 82 | 0.010277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2532-2_0_4_line_91 |  | 81 | 83 | 0.017586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2532-2_0_4_line_92 |  | 82 | 84 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2532-2_0_4_line_93 |  | 83 | 85 | 0.021142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_2532-2_0_4_line_94 |  | 84 | 86 | 0.0063055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2532-2_0_4_line_95 |  | 85 | 87 | 0.025569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2532-2_0_4_line_96 |  | 86 | 89 | 0.025735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2532-2_0_4_line_97 |  | 87 | 90 | 0.0057333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2532-2_0_4_line_98 |  | 88 | 91 | 0.010708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2532-2_0_4_line_99 |  | 89 | 110 | 0.021554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2532-2_0_4_line_100 |  | 92 | 93 | 0.012452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2532-2_0_4_line_101 |  | 92 | 94 | 0.0094592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2532-2_0_4_line_102 |  | 93 | 95 | 0.029558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2532-2_0_4_line_103 |  | 94 | 96 | 0.029333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2532-2_0_4_line_104 |  | 96 | 97 | 0.024229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2532-2_0_4_line_105 |  | 96 | 98 | 0.016771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2532-2_0_4_line_106 |  | 97 | 99 | 0.0050765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2532-2_0_4_line_107 |  | 98 | 100 | 0.0018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2532-2_0_4_line_108 |  | 99 | 119 | 0.0073171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2532-2_0_4_line_109 |  | 100 | 139 | 0.037083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2532-2_0_4_line_110 |  | 102 | 103 | 0.0069359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2532-2_0_4_line_111 |  | 103 | 105 | 0.017303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2532-2_0_4_line_112 |  | 104 | 106 | 0.013302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2532-2_0_4_line_113 |  | 105 | 125 | 0.0052569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2532-2_0_4_line_114 |  | 106 | 107 | 0.010285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2532-2_0_4_line_115 |  | 107 | 108 | 0.0080401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2532-2_0_4_line_116 |  | 108 | 118 | 0.015733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2532-2_0_4_line_117 |  | 109 | 110 | 0.027099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2532-2_0_4_line_118 |  | 111 | 116 | 0.024807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2532-2_0_4_line_119 |  | 112 | 113 | 0.0057898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2532-2_0_4_line_120 |  | 112 | 114 | 0.0013341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2532-2_0_4_line_121 |  | 114 | 115 | 0.0022863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2532-2_0_4_line_122 |  | 117 | 118 | 0.0050799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2532-2_0_4_line_123 |  | 119 | 120 | 0.0099384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2532-2_0_4_line_124 |  | 120 | 121 | 0.0046735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2532-2_0_4_line_125 |  | 121 | 122 | 0.022341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2532-2_0_4_line_126 |  | 122 | 124 | 0.0124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2532-2_0_4_line_127 |  | 125 | 130 | 0.014128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2532-2_0_4_line_128 |  | 126 | 127 | 0.010558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_2532-2_0_4_line_129 |  | 127 | 128 | 0.022129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_2532-2_0_4_line_130 |  | 128 | 129 | 0.035015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2532-2_0_4_line_131 |  | 129 | 140 | 0.026971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2532-2_0_4_line_132 |  | 130 | 131 | 0.0072865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2532-2_0_4_line_133 |  | 131 | 132 | 0.012718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2532-2_0_4_line_134 |  | 132 | 136 | 0.016528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2532-2_0_4_line_135 |  | 133 | 134 | 0.0076214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2532-2_0_4_line_136 |  | 134 | 135 | 0.0018439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2532-2_0_4_line_137 |  | 136 | 137 | 0.0051645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2532-2_0_4_line_138 |  | 137 | 138 | 0.011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2532-2_0_4_line_139 |  | 138 | 139 | 0.010475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2532-2_0_4_trafo_133 | 0.63 MVA 20/0.4 kV | 141 | 128 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2613424.8741 | 1227273.0037 | 2613428.1779 | 1227271.6915
1 | 2613405.7653 | 1227280.5938 | 2613424.8741 | 1227273.0037
2 | 2613428.1779 | 1227271.6915 | 2613443.6231 | 1227265.5566
3 | 2613405.7653 | 1227280.5938 | 2613390.7976 | 1227260.9487
4 | 2613405.7653 | 1227280.5938 | 2613407.5315 | 1227283.5947
5 | 2613452.9634 | 1227261.8465 | 2613443.6231 | 1227265.5566
6 | 2613390.7976 | 1227260.9487 | 2613386.1882 | 1227255.1238 | 2613379.6104 | 1227247.7532
7 | 2613390.7976 | 1227260.9487 | 2613370.4681 | 1227272.566
8 | 2613425.1829 | 1227313.5847 | 2613407.5315 | 1227283.5947
9 | 2613452.9634 | 1227261.8465 | 2613465.8979 | 1227256.7089
10 | 2613374.298 | 1227241.8004 | 2613379.6104 | 1227247.7532
11 | 2613358.376 | 1227279.476 | 2613370.4681 | 1227272.566
12 | 2613425.1829 | 1227313.5847 | 2613429.0389 | 1227320.1361 | 2613430.2726 | 1227323.086
13 | 2613456.0206 | 1227232.6098 | 2613468.3997 | 1227252.1178 | 2613466.7457 | 1227256.3722 | 2613465.8979 | 1227256.7089
14 | 2613374.298 | 1227241.8004 | 2613346.4329 | 1227252.8679
15 | 2613326.4989 | 1227186.4721 | 2613328.4945 | 1227188.7112 | 2613329.8146 | 1227191.4046 | 2613330.3688 | 1227194.3409 | 2613329.8217 | 1227198.3976 | 2613336.9362 | 1227209.1087 | 2613356.131 | 1227222.7152 | 2613374.298 | 1227241.8004
16 | 2613430.2726 | 1227323.086 | 2613439.5477 | 1227345.262
17 | 2613391.1595 | 1226899.7745 | 2613373.3977 | 1226907.8414
18 | 2613402.2881 | 1226901.829 | 2613399.132 | 1226899.9986 | 2613391.7063 | 1226899.5261 | 2613391.1595 | 1226899.7745
19 | 2613402.2881 | 1226901.829 | 2613402.8578 | 1226904.6319
20 | 2613402.8578 | 1226904.6319 | 2613405.3339 | 1226916.8855
21 | 2613402.8578 | 1226904.6319 | 2613415.5628 | 1226900.5981
22 | 2613412.7362 | 1226953.5163 | 2613405.3339 | 1226916.8855
23 | 2613415.5628 | 1226900.5981 | 2613426.8148 | 1226897.0257 | 2613428.069 | 1226879.5362
24 | 2613412.7362 | 1226953.5163 | 2613398.3755 | 1226959.6954
25 | 2613412.7362 | 1226953.5163 | 2613428.2697 | 1226947.6255 | 2613438.4102 | 1226943.7774
26 | 2613412.7362 | 1226953.5163 | 2613416.7341 | 1226975.0679
27 | 2613502.3901 | 1226925.3348 | 2613509.5022 | 1226923.6944 | 2613539.3987 | 1226910.8029
28 | 2613584.8817 | 1226891.1905 | 2613539.3987 | 1226910.8029
29 | 2613483.4775 | 1226947.583 | 2613485.1884 | 1226938.3036 | 2613490.1554 | 1226933.5343 | 2613498.5841 | 1226929.4398 | 2613502.3901 | 1226925.3348
30 | 2613584.8817 | 1226891.1905 | 2613593.8776 | 1226910.5403
31 | 2613447.3757 | 1226940.3752 | 2613451.5857 | 1226938.5614 | 2613461.6671 | 1226934.2038 | 2613465.7406 | 1226932.4452 | 2613467.5536 | 1226931.66 | 2613478.6287 | 1226947.0273 | 2613481.6313 | 1226946.2781 | 2613483.4775 | 1226947.583
32 | 2613483.4775 | 1226947.583 | 2613490.6741 | 1226975.6269 | 2613492.3713 | 1226978.6238
33 | 2613615.394 | 1226956.8209 | 2613593.8776 | 1226910.5403
34 | 2613447.3757 | 1226940.3752 | 2613438.4102 | 1226943.7774
35 | 2613508.5782 | 1227007.2416 | 2613492.3713 | 1226978.6238
36 | 2613615.394 | 1226956.8209 | 2613622.0345 | 1226971.1916
37 | 2613615.394 | 1226956.8209 | 2613599.4447 | 1226964.3499
38 | 2613508.5782 | 1227007.2416 | 2613514.9142 | 1227020.422
39 | 2613622.0345 | 1226971.1916 | 2613630.5049 | 1226989.5227
40 | 2613580.1059 | 1226973.4789 | 2613599.4447 | 1226964.3499
41 | 2613518.8679 | 1227229.1164 | 2613517.4025 | 1227226.8024 | 2613505.9418 | 1227198.7063
42 | 2613502.7852 | 1227179.6637 | 2613502.187 | 1227189.5015 | 2613505.9418 | 1227198.7063
43 | 2613502.7852 | 1227179.6637 | 2613519.2384 | 1227185.7378 | 2613529.3649 | 1227188.051 | 2613534.8258 | 1227189.2974 | 2613542.2207 | 1227189.8256
44 | 2613496.2891 | 1227177.0919 | 2613502.7852 | 1227179.6637
45 | 2613547.1001 | 1227273.6973 | 2613528.7201 | 1227281.4826
46 | 2613547.1001 | 1227273.6973 | 2613549.9839 | 1227278.5178 | 2613555.3213 | 1227274.0161 | 2613562.3451 | 1227267.7506 | 2613566.5058 | 1227264.2024
47 | 2613513.8239 | 1227287.7922 | 2613528.7201 | 1227281.4826
48 | 2613566.5058 | 1227264.2024 | 2613557.7126 | 1227250.2742
49 | 2613542.2207 | 1227189.8256 | 2613554.9106 | 1227187.8643 | 2613567.2101 | 1227184.3012 | 2613573.8102 | 1227181.1032 | 2613586.2534 | 1227174.3719
50 | 2613542.2207 | 1227189.8256 | 2613543.5688 | 1227210.1962 | 2613544.4586 | 1227214.6174
51 | 2613496.2891 | 1227177.0919 | 2613482.3846 | 1227173.2805 | 2613472.7892 | 1227170.6462 | 2613457.7079 | 1227170.0532
52 | 2613496.2891 | 1227177.0919 | 2613489.7167 | 1227153.7127
53 | 2613497.3645 | 1227294.7639 | 2613513.8239 | 1227287.7922
54 | 2613557.7126 | 1227250.2742 | 2613554.1981 | 1227244.7074 | 2613546.761 | 1227226.0573 | 2613545.3596 | 1227219.094
55 | 2613523.8476 | 1227151.4836 | 2613548.2364 | 1227153.5734
56 | 2613523.8476 | 1227151.4836 | 2613525.5011 | 1227147.4516
57 | 2613525.5011 | 1227147.4516 | 2613558.4577 | 1227150.8838 | 2613561.6338 | 1227150.4686 | 2613563.1968 | 1227149.6161 | 2613564.0938 | 1227148.384 | 2613564.471 | 1227142.4814 | 2613564.8358 | 1227142.1801
58 | 2613586.2534 | 1227174.3719 | 2613580.2969 | 1227157.8042 | 2613578.201 | 1227146.4038 | 2613572.9011 | 1227140.9997 | 2613567.599 | 1227139.8981 | 2613564.8358 | 1227142.1801
59 | 2613599.0608 | 1227167.4303 | 2613586.2534 | 1227174.3719
60 | 2613544.4586 | 1227214.6174 | 2613545.3596 | 1227219.094
61 | 2613457.7079 | 1227170.0532 | 2613456.5236 | 1227170.0066
62 | 2613489.7167 | 1227153.7127 | 2613485.1931 | 1227137.6214 | 2613484.0572 | 1227130.5479
63 | 2613417.2858 | 1226978.0417 | 2613416.7341 | 1226975.0679
64 | 2613417.2858 | 1226978.0417 | 2613420.4489 | 1226995.0935
65 | 2613422.8894 | 1227008.2492 | 2613420.4489 | 1226995.0935
66 | 2613398.3755 | 1226959.6954 | 2613382.8459 | 1226966.3776
67 | 2613422.8894 | 1227008.2492 | 2613396.0998 | 1227020.0638
68 | 2613422.8894 | 1227008.2492 | 2613427.4747 | 1227020.1815
69 | 2613374.1836 | 1226970.1048 | 2613382.8459 | 1226966.3776
70 | 2613396.0998 | 1227020.0638 | 2613392.1323 | 1227021.8136
71 | 2613427.4747 | 1227020.1815 | 2613428.2099 | 1227022.0946
72 | 2613374.1836 | 1226970.1048 | 2613370.9499 | 1226971.4962
73 | 2613523.5385 | 1227038.3628 | 2613527.6838 | 1227046.9861 | 2613533.3821 | 1227062.3139
74 | 2613543.236 | 1227092.9484 | 2613540.255 | 1227080.8012 | 2613533.3821 | 1227062.3139
75 | 2613523.5385 | 1227038.3628 | 2613514.9142 | 1227020.422
76 | 2613543.236 | 1227092.9484 | 2613557.871 | 1227085.4883
77 | 2613543.236 | 1227092.9484 | 2613543.9343 | 1227101.1094
78 | 2613557.871 | 1227085.4883 | 2613567.2421 | 1227096.4988
79 | 2613557.871 | 1227085.4883 | 2613572.2561 | 1227074.6479
80 | 2613591.123 | 1227095.8033 | 2613572.2561 | 1227074.6479
81 | 2613591.123 | 1227095.8033 | 2613603.089 | 1227108.9827 | 2613615.1079 | 1227122.2513
82 | 2613360.1415 | 1226976.1469 | 2613370.9499 | 1226971.4962
83 | 2613350.82 | 1226980.1578 | 2613360.1415 | 1226976.1469
84 | 2613599.0608 | 1227167.4303 | 2613612.7606 | 1227185.6665
85 | 2613599.0608 | 1227167.4303 | 2613618.1603 | 1227156.156
86 | 2613564.8839 | 1226980.6645 | 2613560.1637 | 1226982.8925
87 | 2613564.8839 | 1226980.6645 | 2613580.1059 | 1226973.4789
88 | 2613564.8839 | 1226980.6645 | 2613584.2514 | 1227015.721
89 | 2613594.68 | 1227034.5974 | 2613584.2514 | 1227015.721
90 | 2613642.1556 | 1227141.9947 | 2613633.3052 | 1227147.2179
91 | 2613618.1603 | 1227156.156 | 2613633.3052 | 1227147.2179
92 | 2613661.8343 | 1227132.1081 | 2613646.9653 | 1227139.1561 | 2613642.1556 | 1227141.9947
93 | 2613618.1603 | 1227156.156 | 2613613.3547 | 1227150.0303 | 2613612.0774 | 1227148.5377 | 2613604.8606 | 1227139.6938
94 | 2613661.8343 | 1227132.1081 | 2613667.5314 | 1227129.406
95 | 2613604.8606 | 1227139.6938 | 2613608.2006 | 1227137.1777 | 2613604.0523 | 1227131.8984 | 2613615.1079 | 1227122.2513
96 | 2613690.7836 | 1227118.3774 | 2613667.5314 | 1227129.406
97 | 2613615.1079 | 1227122.2513 | 2613619.4863 | 1227118.5498
98 | 2613618.2622 | 1227194.7765 | 2613616.2788 | 1227190.3497 | 2613612.7606 | 1227185.6665
99 | 2613690.7836 | 1227118.3774 | 2613697.9987 | 1227114.7251 | 2613710.0618 | 1227108.6269
100 | 2613414.9038 | 1227174.8509 | 2613427.2171 | 1227173.0011
101 | 2613414.9038 | 1227174.8509 | 2613405.5495 | 1227176.2561
102 | 2613427.2171 | 1227173.0011 | 2613449.095 | 1227169.7145 | 2613456.5236 | 1227170.0066
103 | 2613376.5417 | 1227180.6137 | 2613405.5495 | 1227176.2561
104 | 2613376.5417 | 1227180.6137 | 2613352.9561 | 1227186.1583
105 | 2613376.5417 | 1227180.6137 | 2613373.3083 | 1227164.1574
106 | 2613348.0143 | 1227187.3201 | 2613352.9561 | 1227186.1583
107 | 2613373.3083 | 1227164.1574 | 2613372.9456 | 1227162.3113
108 | 2613340.8914 | 1227188.9946 | 2613348.0143 | 1227187.3201
109 | 2613365.7962 | 1227125.9239 | 2613372.9456 | 1227162.3113
110 | 2613435.4058 | 1227066.7229 | 2613429.024 | 1227069.4394
111 | 2613413.1033 | 1227076.2163 | 2613429.024 | 1227069.4394
112 | 2613392.1323 | 1227021.8136 | 2613379.961 | 1227027.1813
113 | 2613413.1033 | 1227076.2163 | 2613408.2664 | 1227078.2752
114 | 2613370.5506 | 1227031.3315 | 2613379.961 | 1227027.1813
115 | 2613370.5506 | 1227031.3315 | 2613363.1941 | 1227034.5758
116 | 2613363.1941 | 1227034.5758 | 2613348.799 | 1227040.9243
117 | 2613710.0618 | 1227108.6269 | 2613724.4739 | 1227131.5757
118 | 2613640.9107 | 1227012.0421 | 2613630.5049 | 1226989.5227
119 | 2613440.9447 | 1227348.602 | 2613443.1787 | 1227353.9434
120 | 2613440.9447 | 1227348.602 | 2613440.4299 | 1227347.3712
121 | 2613440.4299 | 1227347.3712 | 2613439.5477 | 1227345.262
122 | 2613344.1511 | 1227042.9741 | 2613348.799 | 1227040.9243
123 | 2613340.8914 | 1227188.9946 | 2613331.1022 | 1227187.2789
124 | 2613326.4989 | 1227186.4721 | 2613331.1022 | 1227187.2789
125 | 2613306.1938 | 1227177.9551 | 2613318.0248 | 1227183.9295 | 2613321.3665 | 1227184.0036 | 2613324.0926 | 1227184.8991 | 2613326.4989 | 1227186.4721
126 | 2613306.1938 | 1227177.9551 | 2613298.93 | 1227167.9059
127 | 2613395.2674 | 1227083.8084 | 2613408.2664 | 1227078.2752
128 | 2613484.0572 | 1227130.5479 | 2613482.3831 | 1227120.1236
129 | 2613482.3831 | 1227120.1236 | 2613478.8742 | 1227098.2745
130 | 2613472.98 | 1227063.7603 | 2613477.3539 | 1227088.8082 | 2613478.8742 | 1227098.2745
131 | 2613472.98 | 1227063.7603 | 2613468.3404 | 1227037.1911
132 | 2613395.2674 | 1227083.8084 | 2613388.563 | 1227086.6622
133 | 2613376.8609 | 1227091.6433 | 2613388.563 | 1227086.6622
134 | 2613376.8609 | 1227091.6433 | 2613365.3856 | 1227096.528 | 2613362.5903 | 1227099.4679 | 2613362.5903 | 1227099.4679
135 | 2613456.0206 | 1227232.6098 | 2613451.9371 | 1227226.1747
136 | 2613450.9492 | 1227224.6178 | 2613451.9371 | 1227226.1747
137 | 2613361.5938 | 1227104.5354 | 2613361.5938 | 1227104.5354 | 2613362.5903 | 1227099.4679
138 | 2613363.7767 | 1227115.6454 | 2613361.5938 | 1227104.5354
139 | 2613363.7767 | 1227115.6454 | 2613365.7962 | 1227125.9239

## bus_geodata
| x | y | coords
0 | 2613424.8741 | 1227273.0037
1 | 2613428.1779 | 1227271.6915
2 | 2613405.7653 | 1227280.5938
3 | 2613443.6231 | 1227265.5566
4 | 2613390.7976 | 1227260.9487
5 | 2613407.5315 | 1227283.5947
6 | 2613452.9634 | 1227261.8465
7 | 2613379.6104 | 1227247.7532
8 | 2613370.4681 | 1227272.566
9 | 2613425.1829 | 1227313.5847
10 | 2613465.8979 | 1227256.7089
11 | 2613374.298 | 1227241.8004
12 | 2613358.376 | 1227279.476
13 | 2613430.2726 | 1227323.086
14 | 2613391.1595 | 1226899.7745
15 | 2613373.3977 | 1226907.8414
16 | 2613402.2881 | 1226901.829
17 | 2613402.8578 | 1226904.6319
18 | 2613405.3339 | 1226916.8855
19 | 2613415.5628 | 1226900.5981
20 | 2613412.7362 | 1226953.5163
21 | 2613428.069 | 1226879.5362
22 | 2613539.3987 | 1226910.8029
23 | 2613502.3901 | 1226925.3348
24 | 2613584.8817 | 1226891.1905
25 | 2613483.4775 | 1226947.583
26 | 2613593.8776 | 1226910.5403
27 | 2613447.3757 | 1226940.3752
28 | 2613492.3713 | 1226978.6238
29 | 2613615.394 | 1226956.8209
30 | 2613438.4102 | 1226943.7774
31 | 2613508.5782 | 1227007.2416
32 | 2613622.0345 | 1226971.1916
33 | 2613599.4447 | 1226964.3499
34 | 2613518.8679 | 1227229.1164
35 | 2613505.9418 | 1227198.7063
36 | 2613502.7852 | 1227179.6637
37 | 2613547.1001 | 1227273.6973
38 | 2613528.7201 | 1227281.4826
39 | 2613566.5058 | 1227264.2024
40 | 2613542.2207 | 1227189.8256
41 | 2613496.2891 | 1227177.0919
42 | 2613513.8239 | 1227287.7922
43 | 2613557.7126 | 1227250.2742
44 | 2613523.8476 | 1227151.4836
45 | 2613548.2364 | 1227153.5734
46 | 2613525.5011 | 1227147.4516
47 | 2613586.2534 | 1227174.3719
48 | 2613544.4586 | 1227214.6174
49 | 2613457.7079 | 1227170.0532
50 | 2613489.7167 | 1227153.7127
51 | 2613497.3645 | 1227294.7639
52 | 2613545.3596 | 1227219.094
53 | 2613416.7341 | 1226975.0679
54 | 2613417.2858 | 1226978.0416
55 | 2613420.4489 | 1226995.0935
56 | 2613398.3755 | 1226959.6954
57 | 2613422.8894 | 1227008.2492
58 | 2613382.8459 | 1226966.3776
59 | 2613396.0998 | 1227020.0638
60 | 2613427.4747 | 1227020.1815
61 | 2613374.1836 | 1226970.1048
62 | 2613533.3821 | 1227062.3139
63 | 2613523.5385 | 1227038.3628
64 | 2613543.236 | 1227092.9484
65 | 2613514.9142 | 1227020.422
66 | 2613557.871 | 1227085.4883
67 | 2613543.9343 | 1227101.1094
68 | 2613567.2421 | 1227096.4988
69 | 2613572.2561 | 1227074.6479
70 | 2613591.123 | 1227095.8033
71 | 2613564.8358 | 1227142.1801
72 | 2613370.9499 | 1226971.4962
73 | 2613360.1415 | 1226976.1469
74 | 2613350.82 | 1226980.1578
75 | 2613599.0608 | 1227167.4303
76 | 2613560.1637 | 1226982.8925
77 | 2613564.8839 | 1226980.6645
78 | 2613580.1059 | 1226973.4789
79 | 2613584.2514 | 1227015.721
80 | 2613594.68 | 1227034.5974
81 | 2613633.3052 | 1227147.2179
82 | 2613642.1556 | 1227141.9947
83 | 2613618.1603 | 1227156.156
84 | 2613661.8343 | 1227132.1081
85 | 2613604.8606 | 1227139.6938
86 | 2613667.5314 | 1227129.406
87 | 2613615.1079 | 1227122.2513
88 | 2613612.7606 | 1227185.6665
89 | 2613690.7836 | 1227118.3774
90 | 2613619.4863 | 1227118.5498
91 | 2613618.2622 | 1227194.7765
92 | 2613414.9038 | 1227174.8508
93 | 2613427.2171 | 1227173.0011
94 | 2613405.5495 | 1227176.2561
95 | 2613456.5236 | 1227170.0066
96 | 2613376.5417 | 1227180.6137
97 | 2613352.9561 | 1227186.1583
98 | 2613373.3083 | 1227164.1574
99 | 2613348.0143 | 1227187.3201
100 | 2613372.9456 | 1227162.3113
101 | 2613428.2099 | 1227022.0946
102 | 2613435.4058 | 1227066.7229
103 | 2613429.024 | 1227069.4394
104 | 2613392.1323 | 1227021.8136
105 | 2613413.1033 | 1227076.2163
106 | 2613379.961 | 1227027.1813
107 | 2613370.5506 | 1227031.3315
108 | 2613363.1941 | 1227034.5758
109 | 2613724.4739 | 1227131.5757
110 | 2613710.0618 | 1227108.6269
111 | 2613630.5049 | 1226989.5227
112 | 2613440.9447 | 1227348.602
113 | 2613443.1787 | 1227353.9434
114 | 2613440.4299 | 1227347.3712
115 | 2613439.5477 | 1227345.262
116 | 2613640.9107 | 1227012.0421
117 | 2613344.1511 | 1227042.9741
118 | 2613348.799 | 1227040.9243
119 | 2613340.8914 | 1227188.9946
120 | 2613331.1022 | 1227187.2789
121 | 2613326.4989 | 1227186.4721
122 | 2613306.1938 | 1227177.9551
123 | 2613346.4329 | 1227252.8679
124 | 2613298.93 | 1227167.9059
125 | 2613408.2664 | 1227078.2752
126 | 2613484.0572 | 1227130.5479
127 | 2613482.3831 | 1227120.1236
128 | 2613478.8742 | 1227098.2745
129 | 2613472.98 | 1227063.7603
130 | 2613395.2674 | 1227083.8084
131 | 2613388.563 | 1227086.6622
132 | 2613376.8609 | 1227091.6433
133 | 2613456.0206 | 1227232.6098
134 | 2613451.9371 | 1227226.1747
135 | 2613450.9492 | 1227224.6178
136 | 2613362.5903 | 1227099.4679
137 | 2613361.5938 | 1227104.5354
138 | 2613363.7767 | 1227115.6454
139 | 2613365.7962 | 1227125.9239
140 | 2613468.3404 | 1227037.1911
141 | 2613496.2891 | 1227177.0919

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97236 | -0.53282 | 0.001141 | 0.00028596
1 | 0.97232 | -0.53347 | 0.0018581 | 0.00046569
2 | 0.97257 | -0.52861 | 0 | 0
3 | 0.9722 | -0.53595 | 0.001397 | 0.00035013
4 | 0.97326 | -0.51492 | 0 | 0
5 | 0.97251 | -0.52983 | 0.0067808 | 0.0016994
6 | 0.97214 | -0.5372 | 0.0016927 | 0.00042422
7 | 0.97385 | -0.50339 | 0.0075659 | 0.0018962
8 | 0.97313 | -0.51755 | 0.0031851 | 0.00079827
9 | 0.97211 | -0.53769 | 0.0015755 | 0.00039485
10 | 0.97207 | -0.53848 | 0.0009632 | 0.0002414
11 | 0.97417 | -0.49697 | 0 | 0
12 | 0.97309 | -0.51829 | 0.0029112 | 0.00072962
13 | 0.972 | -0.53981 | 0.0051784 | 0.0012978
14 | 0.97222 | -0.53481 | 0.0028002 | 0.0007018
15 | 0.97219 | -0.53548 | 0.0018457 | 0.00046256
16 | 0.97228 | -0.53381 | 0 | 0
17 | 0.97229 | -0.53356 | 0 | 0
18 | 0.97241 | -0.53123 | 0.0025002 | 0.00062661
19 | 0.97222 | -0.53492 | 0.0039114 | 0.00098029
20 | 0.97285 | -0.52252 | 0 | 0
21 | 0.97218 | -0.53577 | 0.0015867 | 0.00039767
22 | 0.97492 | -0.48178 | 0.0023024 | 0.00057702
23 | 0.97586 | -0.46326 | 0 | 0
24 | 0.97385 | -0.50276 | 0 | 0
25 | 0.9766 | -0.44875 | 0 | 0
26 | 0.97339 | -0.51182 | 0.003291 | 0.0008248
27 | 0.97513 | -0.47761 | 0 | 0
28 | 0.97801 | -0.42111 | 0.011809 | 0.0029597
29 | 0.97245 | -0.5304 | 0 | 0
30 | 0.97452 | -0.48959 | 0.0029191 | 0.00073159
31 | 0.97909 | -0.40009 | 0 | 0
32 | 0.97237 | -0.53197 | 0.0018797 | 0.0004711
33 | 0.97221 | -0.53508 | 0.0029917 | 0.00074979
34 | 0.99217 | -0.14818 | 0.0078531 | 0.0019682
35 | 0.99241 | -0.14359 | 0.0026467 | 0.00066333
36 | 0.9926 | -0.13991 | 0 | 0
37 | 0.98991 | -0.19159 | 0 | 0
38 | 0.98982 | -0.19319 | 0.0013813 | 0.00034619
39 | 0.99002 | -0.18939 | 0 | 0
40 | 0.99072 | -0.17585 | 0 | 0
41 | 0.99294 | -0.13337 | 0 | 0
42 | 0.98978 | -0.19409 | 0.0021146 | 0.00052997
43 | 0.99009 | -0.18807 | 0.003421 | 0.00085739
44 | 0.98829 | -0.22251 | 0 | 0
45 | 0.9882 | -0.22426 | 0.0040075 | 0.0010044
46 | 0.9883 | -0.2222 | 0 | 0
47 | 0.98876 | -0.21318 | 0 | 0
48 | 0.99038 | -0.18235 | 0.0028584 | 0.00071639
49 | 0.98853 | -0.21776 | 0.0043469 | 0.0010894
50 | 0.99504 | -0.093455 | 0.00090639 | 0.00022716
51 | 0.98976 | -0.19442 | 0.0010125 | 0.00025377
52 | 0.99033 | -0.1833 | 0.0038851 | 0.00097369
53 | 0.97204 | -0.53853 | 0.0027928 | 0.00069994
54 | 0.97193 | -0.54058 | 0.010133 | 0.0025395
55 | 0.9715 | -0.54913 | 0.0039357 | 0.00098639
56 | 0.97266 | -0.52624 | 0.0015198 | 0.00038091
57 | 0.97121 | -0.55476 | 0 | 0
58 | 0.97248 | -0.5298 | 0.0016375 | 0.00041039
59 | 0.9708 | -0.56304 | 0.0026593 | 0.00066648
60 | 0.97113 | -0.55653 | 0.0053484 | 0.0013404
61 | 0.97239 | -0.5315 | 0.0014809 | 0.00037115
62 | 0.9811 | -0.36087 | 0.0017232 | 0.00043187
63 | 0.98023 | -0.37789 | 0.001885 | 0.00047242
64 | 0.98221 | -0.3394 | 0 | 0
65 | 0.97957 | -0.39076 | 0.0014923 | 0.000374
66 | 0.98277 | -0.32847 | 0 | 0
67 | 0.98221 | -0.33947 | 0.00043564 | 0.00010918
68 | 0.98275 | -0.329 | 0.0020407 | 0.00051144
69 | 0.98341 | -0.31624 | 0.0013907 | 0.00034855
70 | 0.98441 | -0.29679 | 0 | 0
71 | 0.98847 | -0.21891 | 0.003009 | 0.00075413
72 | 0.97236 | -0.53204 | 0.0027831 | 0.00069752
73 | 0.9723 | -0.53324 | 0.0027752 | 0.00069552
74 | 0.97228 | -0.53375 | 0.0027401 | 0.00068672
75 | 0.98819 | -0.22414 | 0 | 0
76 | 0.97184 | -0.54252 | 0.0028881 | 0.00072382
77 | 0.97185 | -0.54224 | 0 | 0
78 | 0.97199 | -0.53958 | 0.0028371 | 0.00071106
79 | 0.97164 | -0.54644 | 0.0016218 | 0.00040646
80 | 0.97156 | -0.54805 | 0.0040543 | 0.0010161
81 | 0.98728 | -0.24157 | 0.0012506 | 0.00031342
82 | 0.98725 | -0.24223 | 0.00032954 | 8.2591e-05
83 | 0.98736 | -0.24005 | 0 | 0
84 | 0.98719 | -0.24352 | 0 | 0
85 | 0.9866 | -0.25466 | 0 | 0
86 | 0.98717 | -0.24389 | 0.0011126 | 0.00027884
87 | 0.98568 | -0.27235 | 0 | 0
88 | 0.98806 | -0.22666 | 0.0011426 | 0.00028637
89 | 0.98712 | -0.24488 | 0 | 0
90 | 0.98567 | -0.27251 | 0.0015265 | 0.00038257
91 | 0.98801 | -0.22762 | 0.0050324 | 0.0012612
92 | 0.98412 | -0.30272 | 0.0032289 | 0.00080924
93 | 0.98537 | -0.27853 | 0.0021438 | 0.0005373
94 | 0.9832 | -0.32059 | 0.0012086 | 0.00030291
95 | 0.9884 | -0.22021 | 0.0058366 | 0.0014628
96 | 0.98037 | -0.37558 | 0 | 0
97 | 0.97889 | -0.40449 | 0.0079774 | 0.0019993
98 | 0.97978 | -0.38713 | 0.0038353 | 0.00096123
99 | 0.97862 | -0.40983 | 0.0052145 | 0.0013069
100 | 0.97972 | -0.38829 | 0.0040971 | 0.0010268
101 | 0.97112 | -0.55661 | 0.0021268 | 0.00053302
102 | 0.97708 | -0.44023 | 0.005404 | 0.0013544
103 | 0.97711 | -0.43954 | 0.0021228 | 0.00053203
104 | 0.97075 | -0.56405 | 0.0017779 | 0.00044558
105 | 0.97723 | -0.43717 | 0.0017625 | 0.00044173
106 | 0.97061 | -0.56672 | 0.0024882 | 0.0006236
107 | 0.97053 | -0.56832 | 0.0021598 | 0.00054131
108 | 0.97048 | -0.56924 | 0.0018069 | 0.00045284
109 | 0.98702 | -0.24675 | 0.0021484 | 0.00053845
110 | 0.98707 | -0.24571 | 0 | 0
111 | 0.97231 | -0.53328 | 0.0014703 | 0.00036849
112 | 0.97187 | -0.54253 | 0.0021446 | 0.00053749
113 | 0.97186 | -0.54266 | 0.0011809 | 0.00029595
114 | 0.97187 | -0.54245 | 0.0013905 | 0.00034849
115 | 0.97188 | -0.54225 | 0.00077544 | 0.00019434
116 | 0.97226 | -0.53421 | 0.0020293 | 0.00050858
117 | 0.97041 | -0.57071 | 0.0019932 | 0.00049954
118 | 0.97042 | -0.57052 | 0.0024062 | 0.00060305
119 | 0.97826 | -0.41682 | 0 | 0
120 | 0.97777 | -0.42634 | 0.0030535 | 0.00076527
121 | 0.97756 | -0.43055 | 0 | 0
122 | 0.97752 | -0.43121 | 0 | 0
123 | 0.97406 | -0.4992 | 0.0040616 | 0.0010179
124 | 0.9775 | -0.43157 | 0.0016046 | 0.00040215
125 | 0.97728 | -0.43628 | 0.0031173 | 0.00078128
126 | 0.99712 | -0.054243 | 0.0021482 | 0.00053839
127 | 0.99804 | -0.036826 | 0.0032903 | 0.00082463
128 | 1 | 0 | -0.30498 | -0.078268
129 | 0.99963 | -0.0071375 | 0.0059634 | 0.0014946
130 | 0.97744 | -0.43308 | 0.0020221 | 0.00050679
131 | 0.97754 | -0.43116 | 0.0034281 | 0.00085916
132 | 0.97775 | -0.42702 | 0.0018076 | 0.00045302
133 | 0.97196 | -0.54062 | 0.00068179 | 0.00017087
134 | 0.97194 | -0.54109 | 0.0011097 | 0.00027813
135 | 0.97194 | -0.54117 | 0.0022584 | 0.00056601
136 | 0.97805 | -0.42109 | 0.0014508 | 0.0003636
137 | 0.97815 | -0.41911 | 0.0042497 | 0.0010651
138 | 0.97842 | -0.41387 | 0.0027001 | 0.00067672
139 | 0.97869 | -0.40852 | 0.0019449 | 0.00048745
140 | 0.99949 | -0.009832 | 0.0057263 | 0.0014351
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0099634 | 0.002497 | -0.0099631 | -0.0024969 | 3.0991e-07 | 1.5425e-07 | 0.015247 | 0.015247 | 0.015247 | 0.97236 | -0.53282 | 0.97232 | -0.53347 | 4.1888
1 | -0.011104 | -0.002783 | 0.011107 | 0.0027841 | 2.2265e-06 | 1.1699e-06 | 0.016993 | 0.016993 | 0.016993 | 0.97236 | -0.53282 | 0.97257 | -0.52861 | 4.6685
2 | 0.008105 | 0.0020312 | -0.008104 | -0.0020308 | 9.5881e-07 | 4.0753e-07 | 0.012404 | 0.012404 | 0.012404 | 0.97232 | -0.53347 | 0.9722 | -0.53595 | 3.4076
3 | -0.03014 | -0.0075563 | 0.03016 | 0.0075686 | 1.9676e-05 | 1.2286e-05 | 0.046115 | 0.046115 | 0.046115 | 0.97257 | -0.52861 | 0.97326 | -0.51492 | 12.6689
4 | 0.019034 | 0.0047721 | -0.019032 | -0.0047715 | 1.1074e-06 | 6.6553e-07 | 0.029122 | 0.029122 | 0.029122 | 0.97257 | -0.52861 | 0.97251 | -0.52983 | 8.0005
5 | 0.006707 | 0.0016806 | -0.0067066 | -0.0016805 | 3.9716e-07 | 1.2956e-07 | 0.010265 | 0.010265 | 0.010265 | 0.9722 | -0.53595 | 0.97214 | -0.5372 | 2.8202
6 | -0.036257 | -0.0090966 | 0.036277 | 0.0091091 | 1.9946e-05 | 1.255e-05 | 0.055437 | 0.055437 | 0.055437 | 0.97326 | -0.51492 | 0.97385 | -0.50339 | 15.2299
7 | 0.0060972 | 0.001528 | -0.0060965 | -0.0015278 | 7.6303e-07 | 1.974e-07 | 0.009322 | 0.0093221 | 0.0093221 | 0.97326 | -0.51492 | 0.97313 | -0.51755 | 2.561
8 | 0.012252 | 0.003072 | -0.012247 | -0.0030695 | 4.5861e-06 | 2.5035e-06 | 0.018747 | 0.018747 | 0.018747 | 0.97251 | -0.52983 | 0.97211 | -0.53769 | 5.1502
9 | 0.0050139 | 0.0012563 | -0.0050136 | -0.0012563 | 3.074e-07 | 2.4191e-08 | 0.0076745 | 0.0076746 | 0.0076746 | 0.97214 | -0.5372 | 0.97207 | -0.53848 | 2.1084
10 | -0.043843 | -0.011005 | 0.043856 | 0.011014 | 1.343e-05 | 8.4957e-06 | 0.066997 | 0.066997 | 0.066997 | 0.97385 | -0.50339 | 0.97417 | -0.49697 | 18.4058
11 | 0.0029113 | 0.00072951 | -0.0029112 | -0.00072962 | 1.035e-07 | -1.0678e-07 | 0.0044517 | 0.0044517 | 0.0044517 | 0.97313 | -0.51755 | 0.97309 | -0.51829 | 1.223
12 | 0.010672 | 0.0026747 | -0.01067 | -0.0026741 | 1.0806e-06 | 5.5773e-07 | 0.016335 | 0.016335 | 0.016335 | 0.97211 | -0.53769 | 0.972 | -0.53981 | 4.4877
13 | 0.0040504 | 0.0010149 | -0.00405 | -0.0010149 | 4.1202e-07 | -9.0575e-08 | 0.0062002 | 0.0062003 | 0.0062003 | 0.97207 | -0.53848 | 0.97196 | -0.54062 | 1.7034
14 | 0.004062 | 0.0010178 | -0.0040616 | -0.0010179 | 4.3283e-07 | -9.624e-08 | 0.0062045 | 0.0062046 | 0.0062046 | 0.97417 | -0.49697 | 0.97406 | -0.4992 | 1.7046
15 | -0.047918 | -0.012032 | 0.048071 | 0.012128 | 0.00015235 | 9.6555e-05 | 0.073202 | 0.073201 | 0.073202 | 0.97417 | -0.49697 | 0.97756 | -0.43055 | 20.1103
16 | 0.0054921 | 0.0013763 | -0.0054915 | -0.0013762 | 6.372e-07 | 1.099e-07 | 0.0084077 | 0.0084078 | 0.0084078 | 0.972 | -0.53981 | 0.97188 | -0.54225 | 2.3098
17 | 0.0018457 | 0.00046236 | -0.0018457 | -0.00046256 | 5.8377e-08 | -2.0454e-07 | 0.0028248 | 0.0028249 | 0.0028249 | 0.97222 | -0.53481 | 0.97219 | -0.53548 | 0.77608
18 | -0.0046459 | -0.0011642 | 0.0046461 | 0.0011642 | 2.2164e-07 | -3.1182e-09 | 0.0071106 | 0.0071106 | 0.0071106 | 0.97222 | -0.53481 | 0.97228 | -0.53381 | 1.9535
19 | -0.0046461 | -0.0011642 | 0.0046462 | 0.0011642 | 5.4226e-08 | -7.6551e-10 | 0.0071106 | 0.0071106 | 0.0071106 | 0.97228 | -0.53381 | 0.97229 | -0.53356 | 1.9535
20 | -0.010145 | -0.0025419 | 0.010146 | 0.0025424 | 1.13e-06 | 5.6814e-07 | 0.015526 | 0.015526 | 0.015526 | 0.97229 | -0.53356 | 0.97241 | -0.53123 | 4.2653
21 | 0.0054986 | 0.0013777 | -0.0054982 | -0.0013776 | 3.5398e-07 | 6.1235e-08 | 0.008415 | 0.0084151 | 0.0084151 | 0.97229 | -0.53356 | 0.97222 | -0.53492 | 2.3118
22 | -0.012646 | -0.003169 | 0.012651 | 0.0031719 | 5.248e-06 | 2.8949e-06 | 0.019351 | 0.019351 | 0.019351 | 0.97241 | -0.53123 | 0.97285 | -0.52252 | 5.3163
23 | 0.0015868 | 0.00039735 | -0.0015867 | -0.00039767 | 6.4894e-08 | -3.2228e-07 | 0.0024285 | 0.0024287 | 0.0024287 | 0.97222 | -0.53492 | 0.97218 | -0.53577 | 0.66722
24 | 0.012942 | 0.003245 | -0.01294 | -0.0032437 | 2.2975e-06 | 1.2763e-06 | 0.019796 | 0.019796 | 0.019796 | 0.97285 | -0.52252 | 0.97266 | -0.52624 | 5.4385
25 | -0.065282 | -0.016386 | 0.065385 | 0.016451 | 0.00010268 | 6.5377e-05 | 0.099861 | 0.099861 | 0.099861 | 0.97285 | -0.52252 | 0.97452 | -0.48959 | 27.4343
26 | 0.039689 | 0.0099686 | -0.039658 | -0.0099495 | 3.0299e-05 | 1.9119e-05 | 0.060714 | 0.060714 | 0.060714 | 0.97285 | -0.52252 | 0.97204 | -0.53853 | 16.6796
27 | -0.025425 | -0.0063916 | 0.025448 | 0.0064055 | 2.2516e-05 | 1.3913e-05 | 0.038813 | 0.038813 | 0.038813 | 0.97492 | -0.48178 | 0.97586 | -0.46326 | 10.663
28 | 0.023123 | 0.0058145 | -0.0231 | -0.0058003 | 2.3145e-05 | 1.4196e-05 | 0.035299 | 0.0353 | 0.0353 | 0.97492 | -0.48178 | 0.97385 | -0.50276 | 9.6977
29 | -0.025448 | -0.0064055 | 0.025465 | 0.0064164 | 1.7655e-05 | 1.0908e-05 | 0.038813 | 0.038813 | 0.038813 | 0.97586 | -0.46326 | 0.9766 | -0.44875 | 10.663
30 | 0.0231 | 0.0058003 | -0.02309 | -0.0057942 | 9.9711e-06 | 6.1161e-06 | 0.0353 | 0.0353 | 0.0353 | 0.97385 | -0.50276 | 0.97339 | -0.51182 | 9.6977
31 | 0.068437 | 0.017267 | -0.068343 | -0.017207 | 9.4425e-05 | 5.9276e-05 | 0.10432 | 0.10432 | 0.10432 | 0.9766 | -0.44875 | 0.97513 | -0.47761 | 14.3294
32 | -0.093903 | -0.023683 | 0.094027 | 0.023762 | 0.00012444 | 7.8831e-05 | 0.14313 | 0.14313 | 0.14313 | 0.9766 | -0.44875 | 0.97801 | -0.42111 | 19.6608
33 | 0.019799 | 0.0049694 | -0.019781 | -0.0049588 | 1.7535e-05 | 1.0589e-05 | 0.030269 | 0.030269 | 0.030269 | 0.97339 | -0.51182 | 0.97245 | -0.5304 | 8.3157
34 | 0.068343 | 0.017207 | -0.068304 | -0.017182 | 3.9133e-05 | 2.4925e-05 | 0.10432 | 0.10432 | 0.10432 | 0.97513 | -0.47761 | 0.97452 | -0.48959 | 28.6588
35 | -0.10584 | -0.026722 | 0.10594 | 0.026789 | 0.00010669 | 6.7043e-05 | 0.1611 | 0.1611 | 0.1611 | 0.97801 | -0.42111 | 0.97909 | -0.40009 | 14.7525
36 | 0.00538 | 0.0013479 | -0.0053796 | -0.0013478 | 4.0231e-07 | 6.1089e-08 | 0.0082321 | 0.0082322 | 0.0082322 | 0.97245 | -0.5304 | 0.97237 | -0.53197 | 2.2616
37 | 0.014401 | 0.003611 | -0.014398 | -0.0036091 | 3.2119e-06 | 1.8369e-06 | 0.022037 | 0.022037 | 0.022037 | 0.97245 | -0.5304 | 0.97221 | -0.53508 | 6.0541
38 | -0.10594 | -0.026789 | 0.10599 | 0.026818 | 4.7441e-05 | 2.9811e-05 | 0.1611 | 0.1611 | 0.1611 | 0.97909 | -0.40009 | 0.97957 | -0.39076 | 14.7525
39 | 0.0034999 | 0.00087671 | -0.0034996 | -0.00087682 | 2.1721e-07 | -1.1146e-07 | 0.0053557 | 0.0053557 | 0.0053557 | 0.97237 | -0.53197 | 0.97231 | -0.53328 | 1.4714
40 | 0.011406 | 0.0028593 | -0.011404 | -0.002858 | 2.4442e-06 | 1.2992e-06 | 0.017458 | 0.017458 | 0.017458 | 0.97221 | -0.53508 | 0.97199 | -0.53958 | 4.7962
41 | -0.0078531 | -0.0019682 | 0.0078548 | 0.0019689 | 1.7209e-06 | 6.7401e-07 | 0.011778 | 0.011778 | 0.011778 | 0.99217 | -0.14818 | 0.99241 | -0.14359 | 3.2356
42 | -0.010502 | -0.0026322 | 0.010503 | 0.0026331 | 1.8407e-06 | 9.2218e-07 | 0.015746 | 0.015746 | 0.015746 | 0.99241 | -0.14359 | 0.9926 | -0.13991 | 4.3258
43 | 0.1507 | 0.03859 | -0.15043 | -0.038424 | 0.00026186 | 0.000166 | 0.2262 | 0.2262 | 0.2262 | 0.9926 | -0.13991 | 0.99072 | -0.17585 | 20.7146
44 | -0.1612 | -0.041223 | 0.16125 | 0.041255 | 5.0995e-05 | 3.2366e-05 | 0.24195 | 0.24195 | 0.24195 | 0.9926 | -0.13991 | 0.99294 | -0.13337 | 22.1565
45 | 0.004509 | 0.0011296 | -0.0045086 | -0.0011296 | 3.4385e-07 | -3.6524e-08 | 0.0067777 | 0.0067777 | 0.0067777 | 0.98991 | -0.19159 | 0.98982 | -0.19319 | 1.862
46 | -0.004509 | -0.0011296 | 0.0045094 | 0.0011295 | 4.7337e-07 | -5.0362e-08 | 0.0067777 | 0.0067775 | 0.0067777 | 0.98991 | -0.19159 | 0.99002 | -0.18939 | 1.862
47 | 0.0031273 | 0.0007834 | -0.0031272 | -0.00078352 | 1.3408e-07 | -1.2212e-07 | 0.0047012 | 0.0047013 | 0.0047013 | 0.98982 | -0.19319 | 0.98978 | -0.19409 | 1.2916
48 | -0.0045094 | -0.0011295 | 0.0045097 | 0.0011295 | 2.8373e-07 | -3.0231e-08 | 0.0067775 | 0.0067775 | 0.0067775 | 0.99002 | -0.18939 | 0.99009 | -0.18807 | 1.862
49 | 0.13575 | 0.034743 | -0.13551 | -0.034588 | 0.0002449 | 0.00015493 | 0.20415 | 0.20415 | 0.20415 | 0.99072 | -0.17585 | 0.98876 | -0.21318 | 18.6954
50 | 0.014681 | 0.0036805 | -0.014677 | -0.0036779 | 4.5449e-06 | 2.5879e-06 | 0.022051 | 0.022051 | 0.022051 | 0.99072 | -0.17585 | 0.99038 | -0.18235 | 6.058
51 | 0.12218 | 0.031304 | -0.12169 | -0.030986 | 0.00049744 | 0.00031786 | 0.18335 | 0.18335 | 0.18335 | 0.99294 | -0.13337 | 0.98853 | -0.21776 | 50.37
52 | -0.28343 | -0.072559 | 0.28398 | 0.072909 | 0.00054908 | 0.00035047 | 0.4253 | 0.4253 | 0.4253 | 0.99294 | -0.13337 | 0.99504 | -0.093455 | 38.9465
53 | 0.0010126 | 0.00025355 | -0.0010125 | -0.00025377 | 1.5532e-08 | -2.1979e-07 | 0.0015222 | 0.0015223 | 0.0015223 | 0.98978 | -0.19409 | 0.98976 | -0.19442 | 0.41821
54 | -0.0079308 | -0.0019869 | 0.0079326 | 0.0019876 | 1.7987e-06 | 7.1685e-07 | 0.011919 | 0.011919 | 0.011919 | 0.99009 | -0.18807 | 0.99033 | -0.1833 | 3.2744
55 | 0.0040079 | 0.0010043 | -0.0040075 | -0.0010044 | 3.3329e-07 | -9.941e-08 | 0.0060344 | 0.0060345 | 0.0060345 | 0.98829 | -0.22251 | 0.9882 | -0.22426 | 1.6578
56 | -0.0040079 | -0.0010043 | 0.0040079 | 0.0010043 | 5.9496e-08 | -1.7753e-08 | 0.0060344 | 0.0060344 | 0.0060344 | 0.98829 | -0.22251 | 0.9883 | -0.2222 | 1.6578
57 | -0.0040079 | -0.0010043 | 0.0040086 | 0.0010041 | 6.2853e-07 | -1.8768e-07 | 0.0060344 | 0.0060342 | 0.0060344 | 0.9883 | -0.2222 | 0.98847 | -0.21891 | 1.6578
58 | 0.0070195 | 0.0017588 | -0.0070176 | -0.0017582 | 1.9152e-06 | 6.3889e-07 | 0.010564 | 0.010564 | 0.010564 | 0.98876 | -0.21318 | 0.98847 | -0.21891 | 2.9022
59 | 0.12849 | 0.032829 | -0.12842 | -0.032786 | 6.8091e-05 | 4.302e-05 | 0.19359 | 0.19359 | 0.19359 | 0.98876 | -0.21318 | 0.98819 | -0.22414 | 17.7281
60 | 0.011818 | 0.0029616 | -0.011818 | -0.0029613 | 5.3989e-07 | 2.8677e-07 | 0.017756 | 0.017756 | 0.017756 | 0.99038 | -0.18235 | 0.99033 | -0.1833 | 4.8781
61 | 0.11734 | 0.029896 | -0.11733 | -0.029888 | 1.3894e-05 | 8.8767e-06 | 0.1768 | 0.1768 | 0.1768 | 0.98853 | -0.21776 | 0.9884 | -0.22021 | 48.5724
62 | -0.28489 | -0.073136 | 0.28543 | 0.073483 | 0.00054334 | 0.00034681 | 0.42665 | 0.42665 | 0.42665 | 0.99504 | -0.093455 | 0.99712 | -0.054243 | 39.0706
63 | 0.036866 | 0.0092496 | -0.036862 | -0.0092473 | 3.6127e-06 | 2.2746e-06 | 0.056438 | 0.056438 | 0.056438 | 0.97204 | -0.53853 | 0.97193 | -0.54058 | 15.505
64 | 0.026729 | 0.0067078 | -0.026718 | -0.0067011 | 1.0893e-05 | 6.7565e-06 | 0.040925 | 0.040925 | 0.040925 | 0.97193 | -0.54058 | 0.9715 | -0.54913 | 11.2433
65 | 0.022783 | 0.0057147 | -0.022777 | -0.0057109 | 6.1105e-06 | 3.7451e-06 | 0.034897 | 0.034897 | 0.034897 | 0.9715 | -0.54913 | 0.97121 | -0.55476 | 9.5872
66 | 0.01142 | 0.0028628 | -0.011418 | -0.0028618 | 1.9352e-06 | 1.0287e-06 | 0.017471 | 0.017471 | 0.017471 | 0.97266 | -0.52624 | 0.97248 | -0.5298 | 4.7998
67 | 0.015301 | 0.0038372 | -0.015295 | -0.0038337 | 6.0343e-06 | 3.4998e-06 | 0.023443 | 0.023443 | 0.023443 | 0.97121 | -0.55476 | 0.9708 | -0.56304 | 6.4405
68 | 0.0074758 | 0.0018737 | -0.0074752 | -0.0018734 | 6.2889e-07 | 2.4432e-07 | 0.011454 | 0.011454 | 0.011454 | 0.97121 | -0.55476 | 0.97113 | -0.55653 | 3.1467
69 | 0.0097806 | 0.0024514 | -0.0097799 | -0.002451 | 7.9203e-07 | 3.8991e-07 | 0.014966 | 0.014966 | 0.014966 | 0.97248 | -0.5298 | 0.97239 | -0.5315 | 4.1115
70 | 0.012635 | 0.0031673 | -0.012635 | -0.0031669 | 6.0993e-07 | 3.3675e-07 | 0.019367 | 0.019367 | 0.019367 | 0.9708 | -0.56304 | 0.97075 | -0.56405 | 5.3207
71 | 0.0021268 | 0.000533 | -0.0021268 | -0.00053302 | 8.1618e-09 | -2.0134e-08 | 0.0032588 | 0.0032588 | 0.0032588 | 0.97113 | -0.55653 | 0.97112 | -0.55661 | 0.89527
72 | 0.008299 | 0.0020798 | -0.0082987 | -0.0020797 | 2.1291e-07 | 9.2593e-08 | 0.0127 | 0.0127 | 0.0127 | 0.97239 | -0.5315 | 0.97236 | -0.53204 | 3.4889
73 | 0.10952 | 0.027763 | -0.10943 | -0.027707 | 8.9526e-05 | 5.6315e-05 | 0.16622 | 0.16623 | 0.16623 | 0.9811 | -0.36087 | 0.98023 | -0.37789 | 15.2221
74 | -0.11125 | -0.028195 | 0.11136 | 0.028267 | 0.00011485 | 7.2281e-05 | 0.16884 | 0.16884 | 0.16884 | 0.9811 | -0.36087 | 0.98221 | -0.3394 | 15.4614
75 | 0.10755 | 0.027234 | -0.10748 | -0.027192 | 6.6406e-05 | 4.1747e-05 | 0.16336 | 0.16336 | 0.16336 | 0.98023 | -0.37789 | 0.97957 | -0.39076 | 14.9601
76 | -0.1118 | -0.028376 | 0.11186 | 0.028413 | 5.8856e-05 | 3.7045e-05 | 0.1695 | 0.1695 | 0.1695 | 0.98221 | -0.3394 | 0.98277 | -0.32847 | 15.5218
77 | 0.00043565 | 0.00010908 | -0.00043564 | -0.00010918 | 1.3378e-09 | -1.0281e-07 | 0.00065995 | 0.00065999 | 0.00065999 | 0.98221 | -0.3394 | 0.98221 | -0.33947 | 0.18132
78 | 0.0020407 | 0.00051129 | -0.0020407 | -0.00051144 | 5.1762e-08 | -1.5007e-07 | 0.0030898 | 0.0030898 | 0.0030898 | 0.98277 | -0.32847 | 0.98275 | -0.329 | 0.84885
79 | -0.1139 | -0.028924 | 0.11396 | 0.028967 | 6.7065e-05 | 4.2237e-05 | 0.17259 | 0.17259 | 0.17259 | 0.98277 | -0.32847 | 0.98341 | -0.31624 | 15.8047
80 | -0.11535 | -0.029315 | 0.11546 | 0.029383 | 0.00010813 | 6.8123e-05 | 0.17469 | 0.17469 | 0.17469 | 0.98341 | -0.31624 | 0.98441 | -0.29679 | 15.9974
81 | -0.11546 | -0.029383 | 0.1156 | 0.029469 | 0.0001362 | 8.5802e-05 | 0.17469 | 0.17469 | 0.17469 | 0.98441 | -0.29679 | 0.98568 | -0.27235 | 15.9973
82 | 0.0055156 | 0.0013822 | -0.0055153 | -0.0013822 | 3.1435e-07 | 5.5242e-08 | 0.0084405 | 0.0084406 | 0.0084406 | 0.97236 | -0.53204 | 0.9723 | -0.53324 | 2.3188
83 | 0.0027401 | 0.00068664 | -0.0027401 | -0.00068672 | 6.6919e-08 | -8.3028e-08 | 0.0041935 | 0.0041935 | 0.0041935 | 0.9723 | -0.53324 | 0.97228 | -0.53375 | 1.1521
84 | 0.006176 | 0.0015478 | -0.0061753 | -0.0015476 | 7.3975e-07 | 1.8127e-07 | 0.0092998 | 0.0092999 | 0.0092999 | 0.98819 | -0.22414 | 0.98806 | -0.22666 | 2.5549
85 | 0.12224 | 0.031239 | -0.12215 | -0.031179 | 9.3959e-05 | 5.9284e-05 | 0.18429 | 0.18429 | 0.18429 | 0.98819 | -0.22414 | 0.98736 | -0.24005 | 16.8765
86 | -0.0028881 | -0.00072382 | 0.0028881 | 0.00072378 | 3.8275e-08 | -4.018e-08 | 0.004422 | 0.004422 | 0.004422 | 0.97184 | -0.54252 | 0.97185 | -0.54224 | 1.2148
87 | -0.0085656 | -0.0021465 | 0.0085667 | 0.002147 | 1.0857e-06 | 4.8625e-07 | 0.013115 | 0.013115 | 0.013115 | 0.97185 | -0.54224 | 0.97199 | -0.53958 | 3.603
88 | 0.0056775 | 0.0014227 | -0.0056764 | -0.0014225 | 1.1349e-06 | 2.302e-07 | 0.0086928 | 0.008693 | 0.008693 | 0.97185 | -0.54224 | 0.97164 | -0.54644 | 2.3882
89 | 0.0040546 | 0.001016 | -0.0040543 | -0.0010161 | 3.1181e-07 | -6.7523e-08 | 0.0062094 | 0.0062095 | 0.0062095 | 0.97164 | -0.54644 | 0.97156 | -0.54805 | 1.7059
90 | 0.0035912 | 0.00089886 | -0.0035911 | -0.00089892 | 1.1288e-07 | -5.9166e-08 | 0.0054122 | 0.0054122 | 0.0054122 | 0.98728 | -0.24157 | 0.98725 | -0.24223 | 1.4869
91 | -0.0048418 | -0.0012123 | 0.0048421 | 0.0012123 | 3.5114e-07 | -1.7238e-10 | 0.007297 | 0.0072969 | 0.007297 | 0.98728 | -0.24157 | 0.98736 | -0.24005 | 2.0047
92 | 0.0032616 | 0.00081632 | -0.0032614 | -0.00081648 | 1.997e-07 | -1.5399e-07 | 0.0049155 | 0.0049156 | 0.0049156 | 0.98725 | -0.24223 | 0.98719 | -0.24352 | 1.3504
93 | 0.11731 | 0.029967 | -0.11723 | -0.029915 | 8.2789e-05 | 5.2175e-05 | 0.17699 | 0.17699 | 0.17699 | 0.98736 | -0.24005 | 0.9866 | -0.25466 | 16.2083
94 | 0.0032614 | 0.00081648 | -0.0032613 | -0.00081652 | 5.7136e-08 | -4.4048e-08 | 0.0049156 | 0.0049157 | 0.0049157 | 0.98719 | -0.24352 | 0.98717 | -0.24389 | 1.3505
95 | 0.11723 | 0.029915 | -0.11713 | -0.029852 | 0.00010012 | 6.3101e-05 | 0.17699 | 0.17699 | 0.17699 | 0.9866 | -0.25466 | 0.98568 | -0.27235 | 16.2083
96 | 0.0021487 | 0.00053768 | -0.0021486 | -0.00053795 | 1.0122e-07 | -2.6421e-07 | 0.0032386 | 0.0032387 | 0.0032387 | 0.98717 | -0.24389 | 0.98712 | -0.24488 | 0.88976
97 | 0.0015265 | 0.00038251 | -0.0015265 | -0.00038257 | 1.1417e-08 | -6.5771e-08 | 0.0023044 | 0.0023044 | 0.0023044 | 0.98568 | -0.27235 | 0.98567 | -0.27251 | 0.63309
98 | 0.0050327 | 0.0012613 | -0.0050324 | -0.0012612 | 2.3067e-07 | 1.0486e-08 | 0.0075791 | 0.0075792 | 0.0075792 | 0.98806 | -0.22666 | 0.98801 | -0.22762 | 2.0822
99 | 0.0021486 | 0.00053795 | -0.0021485 | -0.00053817 | 8.4785e-08 | -2.2126e-07 | 0.0032387 | 0.0032388 | 0.0032388 | 0.98712 | -0.24488 | 0.98707 | -0.24571 | 0.88978
100 | -0.10891 | -0.027607 | 0.10903 | 0.027688 | 0.00012678 | 8.0983e-05 | 0.16478 | 0.16478 | 0.16478 | 0.98412 | -0.30272 | 0.98537 | -0.27853 | 45.2691
101 | 0.10568 | 0.026797 | -0.10559 | -0.026739 | 9.0692e-05 | 5.7923e-05 | 0.1599 | 0.1599 | 0.1599 | 0.98412 | -0.30272 | 0.9832 | -0.32059 | 43.9279
102 | -0.11118 | -0.028225 | 0.11149 | 0.028425 | 0.0003129 | 0.00019988 | 0.16802 | 0.16802 | 0.16802 | 0.98537 | -0.27853 | 0.9884 | -0.22021 | 46.1585
103 | 0.10438 | 0.026437 | -0.1041 | -0.026261 | 0.00027484 | 0.00017553 | 0.15807 | 0.15807 | 0.15807 | 0.9832 | -0.32059 | 0.98037 | -0.37558 | 43.4254
104 | 0.066079 | 0.016702 | -0.065987 | -0.016644 | 9.1486e-05 | 5.8246e-05 | 0.10035 | 0.10035 | 0.10035 | 0.98037 | -0.37558 | 0.97889 | -0.40449 | 27.5675
105 | 0.038024 | 0.0095591 | -0.038003 | -0.0095459 | 2.0955e-05 | 1.32e-05 | 0.057723 | 0.057723 | 0.057723 | 0.98037 | -0.37558 | 0.97978 | -0.38713 | 15.858
106 | 0.05801 | 0.014644 | -0.057995 | -0.014635 | 1.4816e-05 | 9.4183e-06 | 0.088219 | 0.088219 | 0.088219 | 0.97889 | -0.40449 | 0.97862 | -0.40983 | 24.236
107 | 0.034167 | 0.0085847 | -0.034165 | -0.0085835 | 1.9003e-06 | 1.1925e-06 | 0.051898 | 0.051898 | 0.051898 | 0.97978 | -0.38713 | 0.97972 | -0.38829 | 14.2578
108 | 0.052781 | 0.013328 | -0.052763 | -0.013317 | 1.7689e-05 | 1.1229e-05 | 0.08029 | 0.080291 | 0.080291 | 0.97862 | -0.40983 | 0.97826 | -0.41682 | 22.0578
109 | 0.030068 | 0.0075567 | -0.030039 | -0.0075386 | 2.9012e-05 | 1.8101e-05 | 0.045676 | 0.045676 | 0.045676 | 0.97972 | -0.38829 | 0.97869 | -0.40852 | 12.5483
110 | -0.005404 | -0.0013544 | 0.0054042 | 0.0013544 | 1.7617e-07 | 2.5873e-08 | 0.0082299 | 0.0082299 | 0.0082299 | 0.97708 | -0.44023 | 0.97711 | -0.43954 | 2.261
111 | -0.007527 | -0.0018864 | 0.0075278 | 0.0018868 | 8.5255e-07 | 3.2887e-07 | 0.011463 | 0.011463 | 0.011463 | 0.97711 | -0.43954 | 0.97723 | -0.43717 | 3.1491
112 | 0.010857 | 0.0027213 | -0.010855 | -0.0027206 | 1.3816e-06 | 7.1979e-07 | 0.016642 | 0.016642 | 0.016642 | 0.97075 | -0.56405 | 0.97061 | -0.56672 | 4.572
113 | -0.0092904 | -0.0023285 | 0.0092908 | 0.0023287 | 3.945e-07 | 1.8661e-07 | 0.014146 | 0.014146 | 0.014146 | 0.97723 | -0.43717 | 0.97728 | -0.43628 | 3.8864
114 | 0.0083673 | 0.002097 | -0.0083666 | -0.0020967 | 6.3464e-07 | 2.7906e-07 | 0.012828 | 0.012828 | 0.012828 | 0.97061 | -0.56672 | 0.97053 | -0.56832 | 3.5241
115 | 0.0062068 | 0.0015554 | -0.0062065 | -0.0015554 | 2.7304e-07 | 7.5395e-08 | 0.0095162 | 0.0095163 | 0.0095163 | 0.97053 | -0.56832 | 0.97048 | -0.56924 | 2.6144
116 | 0.0043997 | 0.0011025 | -0.0043994 | -0.0011025 | 2.6848e-07 | -2.2557e-08 | 0.0067459 | 0.0067459 | 0.0067459 | 0.97048 | -0.56924 | 0.97042 | -0.57052 | 1.8533
117 | -0.0021484 | -0.00053845 | 0.0021485 | 0.00053817 | 1.066e-07 | -2.7814e-07 | 0.0032389 | 0.0032388 | 0.0032389 | 0.98702 | -0.24675 | 0.98707 | -0.24571 | 0.88982
118 | 0.0020294 | 0.00050833 | -0.0020293 | -0.00050858 | 8.9727e-08 | -2.5024e-07 | 0.0031056 | 0.0031057 | 0.0031057 | 0.97231 | -0.53328 | 0.97226 | -0.53421 | 0.85322
119 | 0.0011809 | 0.00029588 | -0.0011809 | -0.00029595 | 7.0973e-09 | -6.7202e-08 | 0.001808 | 0.001808 | 0.001808 | 0.97187 | -0.54253 | 0.97186 | -0.54266 | 0.49671
120 | -0.0033255 | -0.00083337 | 0.0033255 | 0.00083336 | 1.297e-08 | -8.2312e-09 | 0.0050916 | 0.0050916 | 0.0050916 | 0.97187 | -0.54253 | 0.97187 | -0.54245 | 1.3988
121 | -0.004716 | -0.0011819 | 0.004716 | 0.0011819 | 4.4699e-08 | 2.7641e-10 | 0.0072205 | 0.0072205 | 0.0072205 | 0.97187 | -0.54245 | 0.97188 | -0.54225 | 1.9837
122 | -0.0019932 | -0.00049954 | 0.0019932 | 0.00049949 | 1.7795e-08 | -5.1371e-08 | 0.0030564 | 0.0030563 | 0.0030564 | 0.97041 | -0.57071 | 0.97042 | -0.57052 | 0.83966
123 | 0.052763 | 0.013317 | -0.052739 | -0.013302 | 2.4026e-05 | 1.5252e-05 | 0.080291 | 0.080291 | 0.080291 | 0.97826 | -0.41682 | 0.97777 | -0.42634 | 22.0578
124 | 0.049685 | 0.012536 | -0.049675 | -0.01253 | 1.0028e-05 | 6.3594e-06 | 0.075644 | 0.075644 | 0.075644 | 0.97777 | -0.42634 | 0.97756 | -0.43055 | 20.7812
125 | 0.0016047 | 0.00040177 | -0.0016046 | -0.00040202 | 4.9981e-08 | -2.4809e-07 | 0.0024425 | 0.0024426 | 0.0024426 | 0.97756 | -0.43055 | 0.97752 | -0.43121 | 0.67104
126 | 0.0016046 | 0.00040202 | -0.0016046 | -0.00040215 | 2.7743e-08 | -1.3768e-07 | 0.0024426 | 0.0024426 | 0.0024426 | 0.97752 | -0.43121 | 0.9775 | -0.43157 | 0.67106
127 | -0.012408 | -0.0031099 | 0.01241 | 0.003111 | 1.891e-06 | 1.0332e-06 | 0.018893 | 0.018893 | 0.018893 | 0.97728 | -0.43628 | 0.97744 | -0.43308 | 5.1903
128 | -0.28758 | -0.074022 | 0.28782 | 0.074177 | 0.00024385 | 0.00015565 | 0.42986 | 0.42986 | 0.42986 | 0.99712 | -0.054243 | 0.99804 | -0.036826 | 39.3641
129 | -0.29112 | -0.075002 | 0.29164 | 0.075336 | 0.00052285 | 0.00033375 | 0.43476 | 0.43476 | 0.43476 | 0.99804 | -0.036826 | 1 | 0 | 39.8133
130 | 0.011694 | 0.0029319 | -0.01169 | -0.0029298 | 3.9762e-06 | 2.0856e-06 | 0.017402 | 0.017402 | 0.017402 | 1 | 0 | 0.99963 | -0.0071375 | 4.7807
131 | 0.005727 | 0.0014353 | -0.0057263 | -0.0014351 | 7.3507e-07 | 1.1691e-07 | 0.008525 | 0.0085251 | 0.0085251 | 0.99963 | -0.0071375 | 0.99949 | -0.009832 | 2.3421
132 | -0.014432 | -0.0036178 | 0.014433 | 0.0036185 | 1.319e-06 | 7.5284e-07 | 0.021971 | 0.021971 | 0.021971 | 0.97744 | -0.43308 | 0.97754 | -0.43116 | 6.036
133 | -0.017862 | -0.0044777 | 0.017865 | 0.0044798 | 3.5258e-06 | 2.097e-06 | 0.027189 | 0.027189 | 0.027189 | 0.97754 | -0.43116 | 0.97775 | -0.42702 | 7.4696
134 | -0.019673 | -0.0049328 | 0.019678 | 0.0049362 | 5.5561e-06 | 3.3486e-06 | 0.02994 | 0.02994 | 0.02994 | 0.97775 | -0.42702 | 0.97805 | -0.42109 | 8.2253
135 | 0.0033682 | 0.00084407 | -0.0033681 | -0.00084412 | 7.5994e-08 | -4.5821e-08 | 0.0051565 | 0.0051565 | 0.0051565 | 0.97196 | -0.54062 | 0.97194 | -0.54109 | 1.4166
136 | 0.0022584 | 0.00056599 | -0.0022584 | -0.00056601 | 8.2662e-09 | -1.7562e-08 | 0.0034575 | 0.0034576 | 0.0034576 | 0.97194 | -0.54109 | 0.97194 | -0.54117 | 0.94988
137 | -0.021129 | -0.0052998 | 0.021131 | 0.005301 | 2.0015e-06 | 1.2161e-06 | 0.032147 | 0.032147 | 0.032147 | 0.97805 | -0.42109 | 0.97815 | -0.41911 | 8.8317
138 | -0.025381 | -0.006366 | 0.025387 | 0.0063699 | 6.3303e-06 | 3.9092e-06 | 0.038612 | 0.038612 | 0.038612 | 0.97815 | -0.41911 | 0.97842 | -0.41387 | 10.6077
139 | -0.028087 | -0.0070467 | 0.028094 | 0.0070511 | 7.1684e-06 | 4.4562e-06 | 0.042719 | 0.042719 | 0.042719 | 0.97842 | -0.41387 | 0.97869 | -0.40852 | 11.7359

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30648 | 0.078642

## res_load
| p_mw | q_mvar
0 | 0.001141 | 0.00028596
1 | 0.0018581 | 0.00046569
2 | 0.001397 | 0.00035013
3 | 0.0067808 | 0.0016994
4 | 0.0016927 | 0.00042422
5 | 0.0075659 | 0.0018962
6 | 0.0031851 | 0.00079827
7 | 0.0015755 | 0.00039485
8 | 0.0009632 | 0.0002414
9 | 0.0029112 | 0.00072962
10 | 0.0051784 | 0.0012978
11 | 0.0028002 | 0.0007018
12 | 0.0018457 | 0.00046256
13 | 0.0025002 | 0.00062661
14 | 0.0039114 | 0.00098029
15 | 0.0015867 | 0.00039767
16 | 0.0023024 | 0.00057702
17 | 0.003291 | 0.0008248
18 | 0.011809 | 0.0029597
19 | 0.0029191 | 0.00073159
20 | 0.0018797 | 0.0004711
21 | 0.0029917 | 0.00074979
22 | 0.0078531 | 0.0019682
23 | 0.0026467 | 0.00066333
24 | 0.0013813 | 0.00034619
25 | 0.0021146 | 0.00052997
26 | 0.003421 | 0.00085739
27 | 0.0040075 | 0.0010044
28 | 0.0028584 | 0.00071639
29 | 0.0043469 | 0.0010894
30 | 0.00090639 | 0.00022716
31 | 0.0010125 | 0.00025377
32 | 0.0038851 | 0.00097369
33 | 0.0027928 | 0.00069994
34 | 0.010133 | 0.0025395
35 | 0.0039357 | 0.00098639
36 | 0.0015198 | 0.00038091
37 | 0.0016375 | 0.00041039
38 | 0.0026593 | 0.00066648
39 | 0.0053484 | 0.0013404
40 | 0.0014809 | 0.00037115
41 | 0.0017232 | 0.00043187
42 | 0.001885 | 0.00047242
43 | 0.0014923 | 0.000374
44 | 0.00043564 | 0.00010918
45 | 0.0020407 | 0.00051144
46 | 0.0013907 | 0.00034855
47 | 0.003009 | 0.00075413
48 | 0.0027831 | 0.00069752
49 | 0.0027752 | 0.00069552
50 | 0.0027401 | 0.00068672
51 | 0.0028881 | 0.00072382
52 | 0.0028371 | 0.00071106
53 | 0.0016218 | 0.00040646
54 | 0.0040543 | 0.0010161
55 | 0.0012506 | 0.00031342
56 | 0.00032954 | 8.2591e-05
57 | 0.0011126 | 0.00027884
58 | 0.0011426 | 0.00028637
59 | 0.0015265 | 0.00038257
60 | 0.0050324 | 0.0012612
61 | 0.0032289 | 0.00080924
62 | 0.0021438 | 0.0005373
63 | 0.0012086 | 0.00030291
64 | 0.0058366 | 0.0014628
65 | 0.0079774 | 0.0019993
66 | 0.0038353 | 0.00096123
67 | 0.0052145 | 0.0013069
68 | 0.0040971 | 0.0010268
69 | 0.0021268 | 0.00053302
70 | 0.005404 | 0.0013544
71 | 0.0021228 | 0.00053203
72 | 0.0017779 | 0.00044558
73 | 0.0017625 | 0.00044173
74 | 0.0024882 | 0.0006236
75 | 0.0021598 | 0.00054131
76 | 0.0018069 | 0.00045284
77 | 0.0021484 | 0.00053845
78 | 0.0014703 | 0.00036849
79 | 0.0021446 | 0.00053749
80 | 0.0011809 | 0.00029595
81 | 0.0013905 | 0.00034849
82 | 0.00077544 | 0.00019434
83 | 0.0020293 | 0.00050858
84 | 0.0019932 | 0.00049954
85 | 0.0024062 | 0.00060305
86 | 0.0030535 | 0.00076527
87 | 0.0040616 | 0.0010179
88 | 0.0016046 | 0.00040215
89 | 0.0031173 | 0.00078128
90 | 0.0021482 | 0.00053839
91 | 0.0032903 | 0.00082463
92 | 0.0014928 | 0.00037413
93 | 0.0059634 | 0.0014946
94 | 0.0020221 | 0.00050679
95 | 0.0034281 | 0.00085916
96 | 0.0018076 | 0.00045302
97 | 0.00068179 | 0.00017087
98 | 0.0011097 | 0.00027813
99 | 0.0022584 | 0.00056601
100 | 0.0014508 | 0.0003636
101 | 0.0042497 | 0.0010651
102 | 0.0027001 | 0.00067672
103 | 0.0019449 | 0.00048745
104 | 0.0057263 | 0.0014351

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1