## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2532-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2532-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2532-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2532-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2532-3_0_4_node_58 | 0.4 | n |  | TRUE
5 | bus_LV_2532-3_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2532-3_0_4_node_59 | 0.4 | n |  | TRUE
7 | bus_LV_2532-3_0_4_node_101 | 0.4 | n |  | TRUE
8 | bus_LV_2532-3_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2532-3_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2532-3_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2532-3_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2532-3_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_2532-3_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2532-3_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2532-3_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2532-3_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2532-3_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2532-3_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2532-3_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2532-3_0_4_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_2532-3_0_4_node_105 | 0.4 | n |  | TRUE
22 | bus_LV_2532-3_0_4_node_91 | 0.4 | n |  | TRUE
23 | bus_LV_2532-3_0_4_node_103 | 0.4 | n |  | TRUE
24 | bus_LV_2532-3_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2532-3_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2532-3_0_4_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_2532-3_0_4_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_2532-3_0_4_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_2532-3_0_4_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_2532-3_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_2532-3_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2532-3_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2532-3_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2532-3_0_4_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2532-3_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_2532-3_0_4_node_79 | 0.4 | n |  | TRUE
37 | bus_LV_2532-3_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2532-3_0_4_node_99 | 0.4 | n |  | TRUE
39 | bus_LV_2532-3_0_4_node_73 | 0.4 | n |  | TRUE
40 | bus_LV_2532-3_0_4_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_2532-3_0_4_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_2532-3_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2532-3_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2532-3_0_4_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_2532-3_0_4_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_2532-3_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2532-3_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2532-3_0_4_node_124 | 0.4 | n |  | TRUE
49 | bus_LV_2532-3_0_4_node_48 | 0.4 | n |  | TRUE
50 | bus_LV_2532-3_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_2532-3_0_4_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_2532-3_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_2532-3_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_2532-3_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_2532-3_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2532-3_0_4_node_109 | 0.4 | n |  | TRUE
57 | bus_LV_2532-3_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_2532-3_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_2532-3_0_4_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_2532-3_0_4_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_2532-3_0_4_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_2532-3_0_4_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_2532-3_0_4_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_2532-3_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_2532-3_0_4_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_2532-3_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2532-3_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2532-3_0_4_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_2532-3_0_4_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_2532-3_0_4_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_2532-3_0_4_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_2532-3_0_4_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_2532-3_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_2532-3_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_2532-3_0_4_node_118 | 0.4 | n |  | TRUE
76 | bus_LV_2532-3_0_4_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_2532-3_0_4_node_93 | 0.4 | n |  | TRUE
78 | bus_LV_2532-3_0_4_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_2532-3_0_4_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2532-3_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2532-3_0_4_node_61 | 0.4 | n |  | TRUE
82 | bus_LV_2532-3_0_4_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_2532-3_0_4_node_100 | 0.4 | n |  | TRUE
84 | bus_LV_2532-3_0_4_node_84 | 0.4 | n |  | TRUE
85 | bus_LV_2532-3_0_4_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_2532-3_0_4_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_2532-3_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_2532-3_0_4_node_131 | 0.4 | n |  | TRUE
89 | bus_LV_2532-3_0_4_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_2532-3_0_4_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_2532-3_0_4_node_68 | 0.4 | n |  | TRUE
92 | bus_LV_2532-3_0_4_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_2532-3_0_4_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_2532-3_0_4_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_2532-3_0_4_node_113 | 0.4 | n |  | TRUE
96 | bus_LV_2532-3_0_4_node_114 | 0.4 | n |  | TRUE
97 | bus_LV_2532-3_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_2532-3_0_4_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_2532-3_0_4_node_107 | 0.4 | n |  | TRUE
100 | bus_LV_2532-3_0_4_node_111 | 0.4 | n |  | TRUE
101 | bus_LV_2532-3_0_4_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_2532-3_0_4_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_2532-3_0_4_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2532-3_0_4_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_2532-3_0_4_node_89 | 0.4 | n |  | TRUE
106 | bus_LV_2532-3_0_4_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_2532-3_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_2532-3_0_4_node_117 | 0.4 | n |  | TRUE
109 | bus_LV_2532-3_0_4_node_119 | 0.4 | n |  | TRUE
110 | bus_LV_2532-3_0_4_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_2532-3_0_4_node_116 | 0.4 | n |  | TRUE
112 | bus_LV_2532-3_0_4_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_2532-3_0_4_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_2532-3_0_4_node_98 | 0.4 | n |  | TRUE
115 | bus_LV_2532-3_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_2532-3_0_4_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_2532-3_0_4_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_2532-3_0_4_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2532-3_0_4_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_2532-3_0_4_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_2532-3_0_4_node_136 | 0.4 | n |  | TRUE
122 | bus_LV_2532-3_0_4_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_2532-3_0_4_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_2532-3_0_4_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_2532-3_0_4_node_133 | 0.4 | n |  | TRUE
126 | bus_LV_2532-3_0_4_node_132 | 0.4 | n |  | TRUE
127 | bus_LV_2532-3_0_4_node_134 | 0.4 | n |  | TRUE
128 | bus_LV_2532-3_0_4_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_2532-3_0_4_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_2532-3_0_4_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_2532-3_0_4_node_127 | 0.4 | n |  | TRUE
132 | bus_LV_2532-3_0_4_node_128 | 0.4 | n |  | TRUE
133 | bus_LV_2532-3_0_4_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_2532-3_0_4_node_135 | 0.4 | n |  | TRUE
135 | bus_MV_392_1_node_113 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2532-3_0_4_load_0 | 0 | 0.0011366 | 0.00028487 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2532-3_0_4_load_2 | 2 | 0.0024287 | 0.00060869 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2532-3_0_4_load_3 | 3 | 0.00058002 | 0.00014537 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2532-3_0_4_load_58 | 4 | 0.0008663 | 0.00021711 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2532-3_0_4_load_8 | 5 | 0.00044946 | 0.00011265 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2532-3_0_4_load_101 | 7 | 0.0022373 | 0.00056073 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2532-3_0_4_load_4 | 9 | 0.001418 | 0.0003554 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2532-3_0_4_load_5 | 10 | 0.0011412 | 0.00028601 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2532-3_0_4_load_7 | 11 | 0.0018437 | 0.00046206 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2532-3_0_4_load_17 | 12 | 0.0025041 | 0.00062759 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2532-3_0_4_load_15 | 13 | 0.0014632 | 0.00036671 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2532-3_0_4_load_9 | 14 | 0.0095978 | 0.0024054 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2532-3_0_4_load_10 | 15 | 0.0010064 | 0.00025222 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2532-3_0_4_load_12 | 17 | 0.0059762 | 0.0014978 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2532-3_0_4_load_13 | 18 | 0.0070749 | 0.0017731 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2532-3_0_4_load_14 | 19 | 0.0010299 | 0.00025813 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2532-3_0_4_load_90 | 20 | 0.0054341 | 0.0013619 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2532-3_0_4_load_105 | 21 | 0.00098989 | 0.00024809 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2532-3_0_4_load_103 | 23 | 0.00083748 | 0.00020989 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2532-3_0_4_load_16 | 24 | 0.0018639 | 0.00046715 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2532-3_0_4_load_57 | 26 | 0.0017091 | 0.00042833 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2532-3_0_4_load_96 | 27 | 0.00077406 | 0.000194 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2532-3_0_4_load_56 | 28 | 0.0013797 | 0.00034579 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2532-3_0_4_load_97 | 29 | 0.00079697 | 0.00019974 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2532-3_0_4_load_19 | 30 | 0.011071 | 0.0027747 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2532-3_0_4_load_20 | 31 | 0.0036312 | 0.00091006 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2532-3_0_4_load_21 | 32 | 0.0023149 | 0.00058016 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2532-3_0_4_load_23 | 34 | 0.012364 | 0.0030986 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2532-3_0_4_load_79 | 36 | 0.0038722 | 0.00097046 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2532-3_0_4_load_99 | 38 | 0.00035774 | 8.9658e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2532-3_0_4_load_67 | 40 | 0.00034521 | 8.6518e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2532-3_0_4_load_28 | 42 | 0.0024086 | 0.00060366 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2532-3_0_4_load_29 | 43 | 0.010961 | 0.0027471 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2532-3_0_4_load_24 | 44 | 0.0039902 | 0.001 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2532-3_0_4_load_25 | 45 | 0.0034954 | 0.00087602 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2532-3_0_4_load_27 | 46 | 0.0024326 | 0.00060966 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2532-3_0_4_load_30 | 47 | 0.0036299 | 0.00090974 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2532-3_0_4_load_124 | 48 | 0.0015352 | 0.00038476 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2532-3_0_4_load_50 | 50 | 0.0045515 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2532-3_0_4_load_47 | 51 | 0.0025843 | 0.00064769 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2532-3_0_4_load_45 | 53 | 0.0047463 | 0.0011895 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2532-3_0_4_load_46 | 54 | 0.011479 | 0.0028768 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2532-3_0_4_load_41 | 55 | 0.025884 | 0.006487 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2532-3_0_4_load_109 | 56 | 0.0025601 | 0.00064163 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2532-3_0_4_load_31 | 57 | 0.0024194 | 0.00060636 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2532-3_0_4_load_32 | 58 | 0.0012739 | 0.00031926 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2532-3_0_4_load_33 | 59 | 0.0014322 | 0.00035894 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2532-3_0_4_load_34 | 60 | 0.00076879 | 0.00019268 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2532-3_0_4_load_35 | 61 | 0.015846 | 0.0039715 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2532-3_0_4_load_36 | 62 | 0.0097703 | 0.0024487 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2532-3_0_4_load_39 | 64 | 0.030936 | 0.0077534 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2532-3_0_4_load_40 | 65 | 0.034796 | 0.0087208 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2532-3_0_4_load_53 | 66 | 0.0097505 | 0.0024437 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2532-3_0_4_load_54 | 67 | 0.025605 | 0.0064173 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2532-3_0_4_load_42 | 68 | 0.023857 | 0.0059792 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2532-3_0_4_load_51 | 71 | 0.0025283 | 0.00063366 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2532-3_0_4_load_52 | 72 | 0.0026656 | 0.00066806 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2532-3_0_4_load_65 | 73 | 0.001799 | 0.00045088 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2532-3_0_4_load_60 | 74 | 0.011218 | 0.0028115 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2532-3_0_4_load_118 | 75 | 0.0025497 | 0.00063902 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2532-3_0_4_load_75 | 76 | 0.0019332 | 0.0004845 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2532-3_0_4_load_93 | 77 | 0.0027189 | 0.00068142 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2532-3_0_4_load_76 | 78 | 0.0027296 | 0.0006841 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2532-3_0_4_load_55 | 79 | 0.012041 | 0.0030177 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2532-3_0_4_load_64 | 80 | 0.012071 | 0.0030252 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2532-3_0_4_load_100 | 83 | 0.001261 | 0.00031603 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2532-3_0_4_load_84 | 84 | 0.0027323 | 0.00068478 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2532-3_0_4_load_80 | 85 | 0.00094963 | 0.000238 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2532-3_0_4_load_63 | 86 | 0.013773 | 0.0034518 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2532-3_0_4_load_77 | 87 | 0.011483 | 0.0028779 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2532-3_0_4_load_131 | 88 | 0.0018021 | 0.00045165 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2532-3_0_4_load_78 | 89 | 0.011482 | 0.0028777 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2532-3_0_4_load_66 | 90 | 0.00075099 | 0.00018822 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2532-3_0_4_load_68 | 91 | 0.00050962 | 0.00012772 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2532-3_0_4_load_74 | 92 | 0.00054308 | 0.00013611 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2532-3_0_4_load_71 | 93 | 0.00072471 | 0.00018163 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2532-3_0_4_load_72 | 94 | 0.0013076 | 0.00032772 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2532-3_0_4_load_113 | 95 | 0.0036125 | 0.00090538 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2532-3_0_4_load_81 | 97 | 0.00079758 | 0.00019989 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2532-3_0_4_load_83 | 98 | 0.0028791 | 0.00072158 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2532-3_0_4_load_107 | 99 | 0.000336 | 8.4209e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2532-3_0_4_load_111 | 100 | 0.00035091 | 8.7946e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2532-3_0_4_load_85 | 101 | 0.0041231 | 0.0010334 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2532-3_0_4_load_86 | 102 | 0.0023276 | 0.00058336 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2532-3_0_4_load_87 | 103 | 0.002237 | 0.00056064 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2532-3_0_4_load_88 | 104 | 0.0022684 | 0.00056851 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2532-3_0_4_load_120 | 106 | 0.0030556 | 0.00076581 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2532-3_0_4_load_95 | 107 | 0.0020863 | 0.00052287 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2532-3_0_4_load_117 | 108 | 0.0022827 | 0.00057209 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2532-3_0_4_load_119 | 109 | 0.0028176 | 0.00070616 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2532-3_0_4_load_94 | 110 | 0.0019258 | 0.00048265 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2532-3_0_4_load_116 | 111 | 0.0033212 | 0.00083238 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2532-3_0_4_load_92 | 112 | 0.0063645 | 0.0015951 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2532-3_0_4_load_108 | 113 | 0.0036594 | 0.00091713 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2532-3_0_4_load_98 | 114 | 0.0066364 | 0.0016632 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2532-3_0_4_load_115 | 115 | 0.0014608 | 0.00036611 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2532-3_0_4_load_112 | 116 | 0.0028761 | 0.00072083 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2532-3_0_4_load_102 | 117 | 0.00079955 | 0.00020039 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2532-3_0_4_load_104 | 118 | 0.00082529 | 0.00020684 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2532-3_0_4_load_110 | 120 | 0.0032477 | 0.00081396 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2532-3_0_4_load_136 | 121 | 0.0031656 | 0.00079337 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2532-3_0_4_load_123 | 124 | 0.003187 | 0.00079875 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2532-3_0_4_load_133 | 125 | 0.0025757 | 0.00064553 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2532-3_0_4_load_132 | 126 | 0.0021257 | 0.00053276 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2532-3_0_4_load_134 | 127 | 0.0021039 | 0.00052728 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2532-3_0_4_load_125 | 129 | 0.0052388 | 0.001313 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2532-3_0_4_load_126 | 130 | 0.0019779 | 0.00049571 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2532-3_0_4_load_128 | 132 | 0.0024267 | 0.00060818 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2532-3_0_4_load_130 | 133 | 0.0022022 | 0.00055192 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2532-3_0_4_load_135 | 134 | 0.0013834 | 0.00034672 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2532-3_0_4_line_0 |  | 0 | 1 | 0.0046996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2532-3_0_4_line_1 |  | 1 | 2 | 0.023127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2532-3_0_4_line_2 |  | 1 | 3 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2532-3_0_4_line_3 |  | 2 | 4 | 0.018962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2532-3_0_4_line_4 |  | 3 | 5 | 0.0012285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2532-3_0_4_line_5 |  | 4 | 6 | 0.0039065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2532-3_0_4_line_6 |  | 4 | 7 | 0.042619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2532-3_0_4_line_7 |  | 5 | 8 | 0.015936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2532-3_0_4_line_8 |  | 6 | 82 | 0.005201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2532-3_0_4_line_9 |  | 7 | 83 | 0.023869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2532-3_0_4_line_10 |  | 8 | 9 | 0.0079485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2532-3_0_4_line_11 |  | 9 | 10 | 0.021111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2532-3_0_4_line_12 |  | 10 | 11 | 0.020826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2532-3_0_4_line_13 |  | 11 | 12 | 0.00096375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2532-3_0_4_line_14 |  | 12 | 13 | 0.020936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2532-3_0_4_line_15 |  | 13 | 24 | 0.019651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2532-3_0_4_line_16 |  | 14 | 15 | 0.01387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2532-3_0_4_line_17 |  | 14 | 16 | 0.019213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2532-3_0_4_line_18 |  | 15 | 17 | 0.0078003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2532-3_0_4_line_19 |  | 16 | 18 | 0.0061477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2532-3_0_4_line_20 |  | 16 | 19 | 0.014573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2532-3_0_4_line_21 |  | 17 | 20 | 0.025898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2532-3_0_4_line_22 |  | 19 | 21 | 0.024674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2532-3_0_4_line_23 |  | 20 | 22 | 0.0050498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2532-3_0_4_line_24 |  | 21 | 23 | 0.020059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2532-3_0_4_line_25 |  | 22 | 112 | 0.01792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2532-3_0_4_line_26 |  | 22 | 77 | 0.023553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2532-3_0_4_line_27 |  | 23 | 117 | 0.023174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2532-3_0_4_line_28 |  | 24 | 25 | 0.012783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2532-3_0_4_line_29 |  | 25 | 26 | 0.0099781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2532-3_0_4_line_30 |  | 25 | 27 | 0.015089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2532-3_0_4_line_31 |  | 26 | 28 | 0.023733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2532-3_0_4_line_32 |  | 27 | 29 | 0.00025797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2532-3_0_4_line_33 |  | 28 | 71 | 0.0011627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2532-3_0_4_line_34 |  | 30 | 31 | 0.0086042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2532-3_0_4_line_35 |  | 30 | 32 | 0.013183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2532-3_0_4_line_36 |  | 31 | 33 | 0.012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2532-3_0_4_line_37 |  | 32 | 34 | 0.023788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2532-3_0_4_line_38 |  | 33 | 35 | 0.050985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2532-3_0_4_line_39 |  | 33 | 36 | 0.050578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2532-3_0_4_line_40 |  | 34 | 37 | 0.018314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2532-3_0_4_line_41 |  | 35 | 38 | 0.025033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2532-3_0_4_line_42 |  | 35 | 39 | 0.012603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2532-3_0_4_line_43 |  | 35 | 40 | 0.030577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2532-3_0_4_line_44 |  | 36 | 41 | 0.026832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2532-3_0_4_line_45 |  | 37 | 42 | 0.016638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2532-3_0_4_line_46 |  | 37 | 43 | 0.026291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2532-3_0_4_line_47 |  | 37 | 44 | 0.01643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2532-3_0_4_line_48 |  | 38 | 60 | 0.012041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2532-3_0_4_line_49 |  | 39 | 92 | 0.0089966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2532-3_0_4_line_50 |  | 39 | 93 | 0.028367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2532-3_0_4_line_51 |  | 40 | 90 | 0.013703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2532-3_0_4_line_52 |  | 41 | 68 | 0.043224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2532-3_0_4_line_53 |  | 41 | 65 | 0.035595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2532-3_0_4_line_54 |  | 44 | 45 | 0.014541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2532-3_0_4_line_55 |  | 45 | 46 | 0.00084652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2532-3_0_4_line_56 |  | 46 | 47 | 0.016179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2532-3_0_4_line_57 |  | 47 | 48 | 0.0001113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2532-3_0_4_line_58 |  | 48 | 56 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2532-3_0_4_line_59 |  | 49 | 50 | 0.0030038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2532-3_0_4_line_60 |  | 49 | 51 | 0.026388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2532-3_0_4_line_61 |  | 50 | 75 | 0.012941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2532-3_0_4_line_62 |  | 52 | 53 | 0.026626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_2532-3_0_4_line_63 |  | 52 | 54 | 0.045335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2532-3_0_4_line_64 |  | 52 | 55 | 0.027941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2532-3_0_4_line_65 |  | 53 | 69 | 0.029197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2532-3_0_4_line_66 |  | 54 | 70 | 0.027934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2532-3_0_4_line_67 |  | 56 | 119 | 0.011357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2532-3_0_4_line_68 |  | 57 | 58 | 0.020392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2532-3_0_4_line_69 |  | 57 | 59 | 0.026492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2532-3_0_4_line_70 |  | 58 | 60 | 0.010625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2532-3_0_4_line_71 |  | 61 | 62 | 0.0011929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2532-3_0_4_line_72 |  | 61 | 63 | 0.02004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2532-3_0_4_line_73 |  | 63 | 64 | 0.033821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2532-3_0_4_line_74 |  | 63 | 65 | 0.036275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2532-3_0_4_line_75 |  | 64 | 66 | 0.01889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2532-3_0_4_line_76 |  | 66 | 67 | 0.02481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2532-3_0_4_line_77 |  | 67 | 79 | 0.0062589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2532-3_0_4_line_78 |  | 69 | 71 | 0.019687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2532-3_0_4_line_79 |  | 69 | 72 | 0.037775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2532-3_0_4_line_80 |  | 70 | 73 | 0.010719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2532-3_0_4_line_81 |  | 70 | 74 | 0.017682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2532-3_0_4_line_82 |  | 72 | 76 | 0.026882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2532-3_0_4_line_83 |  | 73 | 88 | 0.0073585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2532-3_0_4_line_84 |  | 74 | 81 | 0.023737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2532-3_0_4_line_85 |  | 75 | 77 | 0.015789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2532-3_0_4_line_86 |  | 76 | 78 | 0.019745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2532-3_0_4_line_87 |  | 79 | 80 | 0.037841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2532-3_0_4_line_88 |  | 80 | 81 | 0.015611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2532-3_0_4_line_89 |  | 81 | 86 | 0.025975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2532-3_0_4_line_90 |  | 82 | 84 | 0.025338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2532-3_0_4_line_91 |  | 82 | 85 | 0.01215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2532-3_0_4_line_92 |  | 85 | 97 | 0.031377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2532-3_0_4_line_93 |  | 86 | 87 | 0.021801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2532-3_0_4_line_94 |  | 87 | 89 | 0.0063885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2532-3_0_4_line_95 |  | 90 | 91 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2532-3_0_4_line_96 |  | 92 | 95 | 0.03447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2532-3_0_4_line_97 |  | 93 | 94 | 0.023206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2532-3_0_4_line_98 |  | 95 | 96 | 0.015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2532-3_0_4_line_99 |  | 96 | 111 | 0.023123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2532-3_0_4_line_100 |  | 97 | 98 | 0.016872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2532-3_0_4_line_101 |  | 98 | 99 | 0.007805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2532-3_0_4_line_102 |  | 99 | 100 | 0.018446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2532-3_0_4_line_103 |  | 100 | 116 | 0.018158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2532-3_0_4_line_104 |  | 101 | 102 | 0.0027221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2532-3_0_4_line_105 |  | 101 | 103 | 0.018823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2532-3_0_4_line_106 |  | 102 | 104 | 0.020234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2532-3_0_4_line_107 |  | 103 | 105 | 0.0015052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2532-3_0_4_line_108 |  | 104 | 106 | 0.0041475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2532-3_0_4_line_109 |  | 105 | 107 | 0.010952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2532-3_0_4_line_110 |  | 105 | 108 | 0.019253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2532-3_0_4_line_111 |  | 106 | 109 | 0.01855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2532-3_0_4_line_112 |  | 107 | 110 | 0.025315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2532-3_0_4_line_113 |  | 108 | 111 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2532-3_0_4_line_114 |  | 109 | 122 | 0.03062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2532-3_0_4_line_115 |  | 112 | 113 | 0.004865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2532-3_0_4_line_116 |  | 114 | 115 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2532-3_0_4_line_117 |  | 115 | 116 | 0.0030818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2532-3_0_4_line_118 |  | 117 | 118 | 0.0004486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2532-3_0_4_line_119 |  | 118 | 119 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2532-3_0_4_line_120 |  | 119 | 120 | 0.041215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2532-3_0_4_line_121 |  | 120 | 121 | 0.009284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2532-3_0_4_line_122 |  | 122 | 123 | 0.051187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2532-3_0_4_line_123 |  | 122 | 124 | 0.023696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2532-3_0_4_line_124 |  | 123 | 125 | 0.031025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2532-3_0_4_line_125 |  | 124 | 126 | 0.024354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2532-3_0_4_line_126 |  | 125 | 127 | 0.0093336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2532-3_0_4_line_127 |  | 126 | 128 | 0.043526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2532-3_0_4_line_128 |  | 127 | 134 | 0.010669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2532-3_0_4_line_129 |  | 128 | 131 | 0.007134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2532-3_0_4_line_130 |  | 129 | 130 | 0.002169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2532-3_0_4_line_131 |  | 129 | 131 | 0.052107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2532-3_0_4_line_132 |  | 130 | 132 | 0.026304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2532-3_0_4_line_133 |  | 132 | 133 | 0.0038901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2532-3_0_4_trafo_42 | 0.63 MVA 20/0.4 kV | 135 | 68 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2613315.4728 | 1227594.4665 | 2613319.948 | 1227595.9017
1 | 2613315.4728 | 1227594.4665 | 2613307.7798 | 1227616.2766
2 | 2613315.4728 | 1227594.4665 | 2613311.3614 | 1227593.0676 | 2613301.8007 | 1227589.8179
3 | 2613307.7798 | 1227616.2766 | 2613301.4723 | 1227634.1588
4 | 2613300.6376 | 1227589.4225 | 2613301.8007 | 1227589.8179
5 | 2613298.4207 | 1227636.5979 | 2613301.4723 | 1227634.1588
6 | 2613301.4723 | 1227634.1588 | 2613332.6199 | 1227663.2479
7 | 2613285.5494 | 1227584.2939 | 2613300.6376 | 1227589.4225
8 | 2613293.2521 | 1227636.9978 | 2613296.1995 | 1227637.0599 | 2613298.4207 | 1227636.5979
9 | 2613325.0826 | 1227685.8952 | 2613332.6199 | 1227663.2479
10 | 2613285.5494 | 1227584.2939 | 2613278.0016 | 1227581.8021
11 | 2613278.0016 | 1227581.8021 | 2613257.955 | 1227575.184
12 | 2613257.955 | 1227575.184 | 2613238.1789 | 1227568.6553
13 | 2613237.2638 | 1227568.3531 | 2613238.1789 | 1227568.6553
14 | 2613217.383 | 1227561.7898 | 2613237.2638 | 1227568.3531
15 | 2613217.383 | 1227561.7898 | 2613198.7227 | 1227555.6294
16 | 2612948.7467 | 1227501.5447 | 2612962.3745 | 1227504.1224
17 | 2612929.8688 | 1227497.974 | 2612948.7467 | 1227501.5447
18 | 2612970.0389 | 1227505.5721 | 2612962.3745 | 1227504.1224
19 | 2612929.8688 | 1227497.974 | 2612923.8162 | 1227496.8972
20 | 2612929.8688 | 1227497.974 | 2612933.902 | 1227483.9706
21 | 2612995.4856 | 1227510.3853 | 2612970.0389 | 1227505.5721
22 | 2612940.731 | 1227460.2602 | 2612933.902 | 1227483.9706
23 | 2613000.4475 | 1227511.3239 | 2612995.4856 | 1227510.3853
24 | 2612951.7353 | 1227446.6132 | 2612951.7353 | 1227446.6132 | 2612946.3163 | 1227447.0795 | 2612943.7187 | 1227449.8867 | 2612940.731 | 1227460.2602
25 | 2613000.4475 | 1227511.3239 | 2612996.6266 | 1227528.8314
26 | 2613000.4475 | 1227511.3239 | 2613023.6191 | 1227515.5423
27 | 2612974.6069 | 1227450.3478 | 2612951.7353 | 1227446.6132
28 | 2613186.5842 | 1227551.6221 | 2613198.7227 | 1227555.6294
29 | 2613186.5842 | 1227551.6221 | 2613177.0547 | 1227548.6641
30 | 2613186.5842 | 1227551.6221 | 2613182.4596 | 1227566.1367
31 | 2613177.0547 | 1227548.6641 | 2613161.8379 | 1227543.9408 | 2613154.3228 | 1227541.8511
32 | 2613182.3891 | 1227566.3848 | 2613182.4596 | 1227566.1367
33 | 2613153.2026 | 1227541.5396 | 2613154.3228 | 1227541.8511
34 | 2613058.7137 | 1227409.4202 | 2613057.5414 | 1227400.8962
35 | 2613060.5099 | 1227422.4805 | 2613058.7137 | 1227409.4202
36 | 2613055.8648 | 1227388.7055 | 2613057.5414 | 1227400.8962
37 | 2613060.5099 | 1227422.4805 | 2613060.8326 | 1227424.8266 | 2613061.276 | 1227446.242
38 | 2613041.2859 | 1227339.8448 | 2613055.8648 | 1227388.7055
39 | 2613055.8648 | 1227388.7055 | 2613097.8098 | 1227373.7551 | 2613103.1048 | 1227370.832
40 | 2613061.655 | 1227464.5518 | 2613061.276 | 1227446.242
41 | 2613041.2859 | 1227339.8448 | 2613018.6406 | 1227350.5152
42 | 2613035.5968 | 1227328.5924 | 2613041.2859 | 1227339.8448
43 | 2613041.2859 | 1227339.8448 | 2613057.6498 | 1227331.3088 | 2613068.3957 | 1227325.7021
44 | 2613126.5946 | 1227357.8644 | 2613103.1048 | 1227370.832
45 | 2613061.655 | 1227464.5518 | 2613059.6682 | 1227481.0709
46 | 2613061.655 | 1227464.5518 | 2613087.3819 | 1227469.9714
47 | 2613061.655 | 1227464.5518 | 2613045.4393 | 1227461.9062
48 | 2613018.6406 | 1227350.5152 | 2613007.7478 | 1227355.6479
49 | 2613035.5968 | 1227328.5924 | 2613031.8111 | 1227320.431
50 | 2613035.5968 | 1227328.5924 | 2613021.0468 | 1227328.9164 | 2613007.3935 | 1227326.8166
51 | 2613080.5448 | 1227319.3633 | 2613068.3957 | 1227325.7021
52 | 2613126.5946 | 1227357.8644 | 2613128.3239 | 1227364.0496 | 2613136.7073 | 1227393.9857 | 2613137.6642 | 1227399.6183
53 | 2613126.5946 | 1227357.8644 | 2613127.452 | 1227357.3882 | 2613133.1118 | 1227354.2543 | 2613157.7505 | 1227340.6498
54 | 2613045.4393 | 1227461.9062 | 2613031.0884 | 1227459.5649
55 | 2613031.0884 | 1227459.5649 | 2613030.2529 | 1227459.4285
56 | 2613014.2849 | 1227456.8233 | 2613030.2529 | 1227459.4285
57 | 2613014.2849 | 1227456.8233 | 2613014.1751 | 1227456.8054
58 | 2613014.1751 | 1227456.8054 | 2613000.1371 | 1227454.5151
59 | 2613054.8402 | 1227521.226 | 2613051.885 | 1227520.688
60 | 2613054.8402 | 1227521.226 | 2613080.7372 | 1227526.2944
61 | 2613039.1528 | 1227518.3702 | 2613051.885 | 1227520.688
62 | 2613144.2657 | 1227481.9543 | 2613140.8854 | 1227508.3651
63 | 2613144.2657 | 1227481.9543 | 2613145.1064 | 1227482.1341 | 2613149.8932 | 1227483.1341 | 2613188.6282 | 1227491.2955
64 | 2613144.2657 | 1227481.9543 | 2613144.4658 | 1227470.1923 | 2613144.4624 | 1227454.0148
65 | 2613134.1201 | 1227536.7422 | 2613135.1749 | 1227532.6088 | 2613140.4106 | 1227512.0748 | 2613140.8854 | 1227508.3651
66 | 2613215.9617 | 1227497.0547 | 2613188.6282 | 1227491.2955
67 | 2612988.9283 | 1227452.6864 | 2613000.1371 | 1227454.5151
68 | 2612998.1362 | 1227360.1768 | 2612979.6894 | 1227368.869
69 | 2612955.4065 | 1227379.4423 | 2612970.4523 | 1227373.2215 | 2612979.6894 | 1227368.869
70 | 2612998.1362 | 1227360.1768 | 2613007.7478 | 1227355.6479
71 | 2613207.7346 | 1227312.2278 | 2613206.7104 | 1227312.8395
72 | 2613189.506 | 1227323.1156 | 2613206.7104 | 1227312.8395
73 | 2613189.506 | 1227323.1156 | 2613201.2146 | 1227350.113 | 2613202.235 | 1227354.3869
74 | 2613189.506 | 1227323.1156 | 2613157.7505 | 1227340.6498
75 | 2613206.6216 | 1227372.7604 | 2613202.235 | 1227354.3869
76 | 2613206.6216 | 1227372.7604 | 2613210.2094 | 1227387.7885 | 2613211.382 | 1227397.0738
77 | 2613211.382 | 1227397.0738 | 2613212.1662 | 1227403.2834
78 | 2613134.1201 | 1227536.7422 | 2613135.9606 | 1227537.1131 | 2613141.0428 | 1227538.1583 | 2613153.2026 | 1227541.5396
79 | 2613134.1201 | 1227536.7422 | 2613128.5344 | 1227564.8021 | 2613126.0798 | 1227573.6321
80 | 2613215.9617 | 1227497.0547 | 2613226.253 | 1227500.0505
81 | 2613215.9617 | 1227497.0547 | 2613219.3134 | 1227489.0907 | 2613219.1892 | 1227480.05
82 | 2613126.0798 | 1227573.6321 | 2613121.9277 | 1227588.5683 | 2613118.8735 | 1227599.5301
83 | 2613233.3182 | 1227502.1072 | 2613226.253 | 1227500.0505
84 | 2613218.8631 | 1227456.3148 | 2613219.1892 | 1227480.05
85 | 2613023.6191 | 1227515.5423 | 2613039.1528 | 1227518.3702
86 | 2613113.5739 | 1227618.5507 | 2613118.8735 | 1227599.5301
87 | 2613212.1662 | 1227403.2834 | 2613216.9072 | 1227440.8267
88 | 2613218.8631 | 1227456.3148 | 2613216.9072 | 1227440.8267
89 | 2613218.8631 | 1227456.3148 | 2613193.7691 | 1227449.6069
90 | 2613293.2521 | 1227636.9978 | 2613284.8932 | 1227660.9171
91 | 2613293.2521 | 1227636.9978 | 2613281.5731 | 1227633.6472
92 | 2613281.5731 | 1227633.6472 | 2613251.4125 | 1227624.9945
93 | 2613193.7691 | 1227449.6069 | 2613172.7077 | 1227443.977
94 | 2613172.7077 | 1227443.977 | 2613166.5359 | 1227442.3272
95 | 2613080.5448 | 1227319.3633 | 2613091.4645 | 1227313.666
96 | 2613031.8111 | 1227320.431 | 2613017.3065 | 1227289.1609
97 | 2613007.3935 | 1227326.8166 | 2612984.4575 | 1227323.289
98 | 2613010.7824 | 1227275.0956 | 2613017.3065 | 1227289.1609
99 | 2613010.7824 | 1227275.0956 | 2613028.73 | 1227260.516
100 | 2613235.1951 | 1227620.342 | 2613251.4125 | 1227624.9945
101 | 2613235.1951 | 1227620.342 | 2613227.6927 | 1227618.1896
102 | 2613227.6927 | 1227618.1896 | 2613209.9621 | 1227613.1029
103 | 2613192.5083 | 1227608.0956 | 2613209.9621 | 1227613.1029
104 | 2613073.476 | 1227224.4818 | 2613075.6093 | 1227222.7911
105 | 2613073.476 | 1227224.4818 | 2613058.7246 | 1227236.1735
106 | 2613075.6093 | 1227222.7911 | 2613091.4663 | 1227210.2232
107 | 2613057.545 | 1227237.1084 | 2613058.7246 | 1227236.1735
108 | 2613094.7167 | 1227207.647 | 2613091.4663 | 1227210.2232
109 | 2613057.545 | 1227237.1084 | 2613051.9779 | 1227227.6772
110 | 2613057.545 | 1227237.1084 | 2613042.6013 | 1227249.2478
111 | 2613109.2544 | 1227196.1248 | 2613094.7167 | 1227207.647
112 | 2613039.1098 | 1227205.8771 | 2613051.9779 | 1227227.6772
113 | 2613028.73 | 1227260.516 | 2613042.6013 | 1227249.2478
114 | 2613133.2512 | 1227177.1055 | 2613109.2544 | 1227196.1248
115 | 2612995.5893 | 1227533.5845 | 2612996.6266 | 1227528.8314
116 | 2613174.1941 | 1227600.1568 | 2613174.1941 | 1227600.1568 | 2613176.8779 | 1227602.9644 | 2613181.5563 | 1227604.9537 | 2613189.546 | 1227607.2458
117 | 2613192.5083 | 1227608.0956 | 2613189.546 | 1227607.2458
118 | 2612975.0496 | 1227450.4201 | 2612974.6069 | 1227450.3478
119 | 2612988.9283 | 1227452.6864 | 2612975.0496 | 1227450.4201
120 | 2612988.9283 | 1227452.6864 | 2612995.1125 | 1227417.4456 | 2613000.441 | 1227418.5206
121 | 2613009.5416 | 1227420.3565 | 2613000.441 | 1227418.5206
122 | 2613104.3201 | 1227134.9282 | 2613114.4216 | 1227152.1828 | 2613133.2512 | 1227177.1055
123 | 2613133.2512 | 1227177.1055 | 2613141.6635 | 1227199.258
124 | 2613104.3201 | 1227134.9282 | 2613076.6901 | 1227149.0389
125 | 2613141.6635 | 1227199.258 | 2613150.3093 | 1227222.0254
126 | 2613067.8421 | 1227151.0468 | 2613072.7375 | 1227151.0575 | 2613076.6901 | 1227149.0389
127 | 2613165.7615 | 1227262.7165 | 2613150.3093 | 1227222.0254
128 | 2613067.8421 | 1227151.0468 | 2613067.8421 | 1227151.0468 | 2613062.275 | 1227141.9448
129 | 2613165.7615 | 1227262.7165 | 2613159.9552 | 1227266.8839
130 | 2613124.8499 | 1227251.0432 | 2613123.1026 | 1227252.3283
131 | 2613159.9552 | 1227266.8839 | 2613144.7024 | 1227242.1469 | 2613140.7033 | 1227241.2042 | 2613137.3904 | 1227241.8195 | 2613124.8499 | 1227251.0432
132 | 2613101.9132 | 1227267.9133 | 2613123.1026 | 1227252.3283
133 | 2613098.7795 | 1227270.2182 | 2613101.9132 | 1227267.9133

## bus_geodata
| x | y | coords
0 | 2613319.948 | 1227595.9017
1 | 2613315.4728 | 1227594.4665
2 | 2613307.7798 | 1227616.2766
3 | 2613301.8007 | 1227589.8179
4 | 2613301.4723 | 1227634.1588
5 | 2613300.6376 | 1227589.4225
6 | 2613298.4207 | 1227636.5979
7 | 2613332.6199 | 1227663.2479
8 | 2613285.5494 | 1227584.2939
9 | 2613278.0016 | 1227581.8021
10 | 2613257.955 | 1227575.184
11 | 2613238.1789 | 1227568.6553
12 | 2613237.2638 | 1227568.3531
13 | 2613217.383 | 1227561.7898
14 | 2612948.7467 | 1227501.5447
15 | 2612962.3746 | 1227504.1224
16 | 2612929.8688 | 1227497.974
17 | 2612970.0389 | 1227505.5721
18 | 2612923.8162 | 1227496.8972
19 | 2612933.902 | 1227483.9706
20 | 2612995.4856 | 1227510.3853
21 | 2612940.731 | 1227460.2602
22 | 2613000.4475 | 1227511.3239
23 | 2612951.7353 | 1227446.6132
24 | 2613198.7227 | 1227555.6294
25 | 2613186.5842 | 1227551.6221
26 | 2613177.0547 | 1227548.6641
27 | 2613182.4596 | 1227566.1367
28 | 2613154.3228 | 1227541.8511
29 | 2613182.3891 | 1227566.3848
30 | 2613058.7137 | 1227409.4202
31 | 2613057.5414 | 1227400.8962
32 | 2613060.5099 | 1227422.4805
33 | 2613055.8648 | 1227388.7055
34 | 2613061.276 | 1227446.242
35 | 2613041.2859 | 1227339.8448
36 | 2613103.1048 | 1227370.832
37 | 2613061.655 | 1227464.5518
38 | 2613018.6406 | 1227350.5152
39 | 2613035.5968 | 1227328.5924
40 | 2613068.3957 | 1227325.7021
41 | 2613126.5946 | 1227357.8644
42 | 2613059.6682 | 1227481.0709
43 | 2613087.3819 | 1227469.9714
44 | 2613045.4393 | 1227461.9062
45 | 2613031.0884 | 1227459.5649
46 | 2613030.2529 | 1227459.4285
47 | 2613014.2849 | 1227456.8233
48 | 2613014.1751 | 1227456.8054
49 | 2613054.8402 | 1227521.226
50 | 2613051.885 | 1227520.688
51 | 2613080.7372 | 1227526.2944
52 | 2613144.2657 | 1227481.9543
53 | 2613140.8854 | 1227508.3651
54 | 2613188.6282 | 1227491.2955
55 | 2613144.4624 | 1227454.0148
56 | 2613000.1371 | 1227454.5151
57 | 2612979.6894 | 1227368.869
58 | 2612998.1362 | 1227360.1768
59 | 2612955.4065 | 1227379.4423
60 | 2613007.7478 | 1227355.6479
61 | 2613206.7104 | 1227312.8395
62 | 2613207.7346 | 1227312.2278
63 | 2613189.506 | 1227323.1156
64 | 2613202.235 | 1227354.3869
65 | 2613157.7505 | 1227340.6498
66 | 2613206.6216 | 1227372.7604
67 | 2613211.382 | 1227397.0738
68 | 2613137.6642 | 1227399.6183
69 | 2613134.1201 | 1227536.7422
70 | 2613215.9617 | 1227497.0547
71 | 2613153.2026 | 1227541.5396
72 | 2613126.0798 | 1227573.6321
73 | 2613226.253 | 1227500.0505
74 | 2613219.1892 | 1227480.05
75 | 2613039.1528 | 1227518.3702
76 | 2613118.8735 | 1227599.5301
77 | 2613023.6191 | 1227515.5423
78 | 2613113.5739 | 1227618.5507
79 | 2613212.1662 | 1227403.2834
80 | 2613216.9072 | 1227440.8267
81 | 2613218.8631 | 1227456.3148
82 | 2613293.2521 | 1227636.9978
83 | 2613325.0826 | 1227685.8952
84 | 2613284.8932 | 1227660.9171
85 | 2613281.5731 | 1227633.6472
86 | 2613193.7691 | 1227449.6069
87 | 2613172.7077 | 1227443.977
88 | 2613233.3182 | 1227502.1072
89 | 2613166.5359 | 1227442.3272
90 | 2613080.5448 | 1227319.3633
91 | 2613091.4645 | 1227313.666
92 | 2613031.8111 | 1227320.431
93 | 2613007.3935 | 1227326.8166
94 | 2612984.4575 | 1227323.289
95 | 2613017.3065 | 1227289.1609
96 | 2613010.7824 | 1227275.0956
97 | 2613251.4125 | 1227624.9945
98 | 2613235.1951 | 1227620.342
99 | 2613227.6927 | 1227618.1896
100 | 2613209.9621 | 1227613.1029
101 | 2613073.476 | 1227224.4818
102 | 2613075.6093 | 1227222.7911
103 | 2613058.7246 | 1227236.1735
104 | 2613091.4663 | 1227210.2232
105 | 2613057.545 | 1227237.1084
106 | 2613094.7167 | 1227207.647
107 | 2613051.9779 | 1227227.6772
108 | 2613042.6013 | 1227249.2478
109 | 2613109.2544 | 1227196.1248
110 | 2613039.1098 | 1227205.8771
111 | 2613028.73 | 1227260.516
112 | 2612996.6266 | 1227528.8314
113 | 2612995.5893 | 1227533.5845
114 | 2613174.1941 | 1227600.1568
115 | 2613189.546 | 1227607.2458
116 | 2613192.5083 | 1227608.0956
117 | 2612974.6069 | 1227450.3478
118 | 2612975.0496 | 1227450.4201
119 | 2612988.9283 | 1227452.6864
120 | 2613000.441 | 1227418.5206
121 | 2613009.5416 | 1227420.3565
122 | 2613133.2512 | 1227177.1055
123 | 2613104.3201 | 1227134.9282
124 | 2613141.6635 | 1227199.258
125 | 2613076.6901 | 1227149.0389
126 | 2613150.3093 | 1227222.0254
127 | 2613067.8421 | 1227151.0468
128 | 2613165.7615 | 1227262.7165
129 | 2613124.8499 | 1227251.0432
130 | 2613123.1026 | 1227252.3283
131 | 2613159.9552 | 1227266.8839
132 | 2613101.9132 | 1227267.9133
133 | 2613098.7795 | 1227270.2182
134 | 2613062.275 | 1227141.9448
135 | 2613126.5946 | 1227357.8644

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97273 | -0.52702 | 0.0011366 | 0.00028487
1 | 0.97274 | -0.52692 | 0 | 0
2 | 0.97218 | -0.53793 | 0.0024287 | 0.00060869
3 | 0.9731 | -0.51976 | 0.00058002 | 0.00014537
4 | 0.97176 | -0.54611 | 0.0008663 | 0.00021711
5 | 0.97313 | -0.51913 | 0.00044946 | 0.00011265
6 | 0.9717 | -0.54748 | 0 | 0
7 | 0.97163 | -0.54887 | 0.0022373 | 0.00056073
8 | 0.97355 | -0.51093 | 0 | 0
9 | 0.97376 | -0.50684 | 0.001418 | 0.0003554
10 | 0.97433 | -0.49543 | 0.0011412 | 0.00028601
11 | 0.97493 | -0.48376 | 0.0018437 | 0.00046206
12 | 0.97496 | -0.48319 | 0.0025041 | 0.00062759
13 | 0.97564 | -0.4698 | 0.0014632 | 0.00036671
14 | 0.97211 | -0.53799 | 0.0095978 | 0.0024054
15 | 0.97166 | -0.54691 | 0.0010064 | 0.00025222
16 | 0.9729 | -0.52226 | 0 | 0
17 | 0.97141 | -0.55179 | 0.0059762 | 0.0014978
18 | 0.97286 | -0.52306 | 0.0070749 | 0.0017731
19 | 0.97361 | -0.50844 | 0.0010299 | 0.00025813
20 | 0.97073 | -0.56513 | 0.0054341 | 0.0013619
21 | 0.97482 | -0.48463 | 0.00098989 | 0.00024809
22 | 0.97063 | -0.56722 | 0 | 0
23 | 0.97582 | -0.46495 | 0.00083748 | 0.00020989
24 | 0.97631 | -0.45672 | 0.0018639 | 0.00046715
25 | 0.97676 | -0.44779 | 0 | 0
26 | 0.97713 | -0.44054 | 0.0017091 | 0.00042833
27 | 0.97674 | -0.44823 | 0.00077406 | 0.000194
28 | 0.97805 | -0.42258 | 0.0013797 | 0.00034579
29 | 0.97674 | -0.44823 | 0.00079697 | 0.00019974
30 | 0.98791 | -0.23018 | 0.011071 | 0.0027747
31 | 0.98887 | -0.21188 | 0.0036312 | 0.00091006
32 | 0.98659 | -0.25567 | 0.0023149 | 0.00058016
33 | 0.98957 | -0.19842 | 0 | 0
34 | 0.98425 | -0.30085 | 0.012364 | 0.0030986
35 | 0.98656 | -0.25644 | 0 | 0
36 | 0.99394 | -0.11482 | 0.0038722 | 0.00097046
37 | 0.98266 | -0.33168 | 0 | 0
38 | 0.98642 | -0.25924 | 0.00035774 | 8.9658e-05
39 | 0.98591 | -0.26906 | 0 | 0
40 | 0.98651 | -0.25732 | 0.00034521 | 8.6518e-05
41 | 0.99513 | -0.092307 | 0 | 0
42 | 0.98262 | -0.33241 | 0.0024086 | 0.00060366
43 | 0.98239 | -0.33689 | 0.010961 | 0.0027471
44 | 0.98143 | -0.35546 | 0.0039902 | 0.001
45 | 0.9804 | -0.3755 | 0.0034954 | 0.00087602
46 | 0.98034 | -0.37661 | 0.0024326 | 0.00060966
47 | 0.97928 | -0.39722 | 0.0036299 | 0.00090974
48 | 0.97928 | -0.39735 | 0.0015352 | 0.00038476
49 | 0.97012 | -0.57731 | 0 | 0
50 | 0.97013 | -0.57717 | 0.0045515 | 0.0011407
51 | 0.97006 | -0.57858 | 0.0025843 | 0.00064769
52 | 0.98108 | -0.36355 | 0 | 0
53 | 0.98036 | -0.37742 | 0.0047463 | 0.0011895
54 | 0.98283 | -0.32939 | 0.011479 | 0.0028768
55 | 0.98041 | -0.37666 | 0.025884 | 0.006487
56 | 0.97842 | -0.41417 | 0.0025601 | 0.00064163
57 | 0.98623 | -0.2629 | 0.0024194 | 0.00060636
58 | 0.9863 | -0.26149 | 0.0012739 | 0.00031926
59 | 0.98619 | -0.26358 | 0.0014322 | 0.00035894
60 | 0.98635 | -0.26052 | 0.00076879 | 0.00019268
61 | 0.99002 | -0.1903 | 0.015846 | 0.0039715
62 | 0.99001 | -0.19051 | 0.0097703 | 0.0024487
63 | 0.99049 | -0.18117 | 0 | 0
64 | 0.98864 | -0.21682 | 0.030936 | 0.0077534
65 | 0.99269 | -0.13898 | 0.034796 | 0.0087208
66 | 0.98774 | -0.23418 | 0.0097505 | 0.0024437
67 | 0.98662 | -0.25593 | 0.025605 | 0.0064173
68 | 1 | 0 | -0.49741 | -0.12738
69 | 0.97893 | -0.40539 | 0 | 0
70 | 0.98345 | -0.31744 | 0 | 0
71 | 0.9781 | -0.42167 | 0.0025283 | 0.00063366
72 | 0.97867 | -0.41043 | 0.0026656 | 0.00066806
73 | 0.98341 | -0.31814 | 0.001799 | 0.00045088
74 | 0.98385 | -0.3096 | 0.011218 | 0.0028115
75 | 0.97021 | -0.57546 | 0.0025497 | 0.00063902
76 | 0.97856 | -0.41271 | 0.0019332 | 0.0004845
77 | 0.97036 | -0.57263 | 0.0027189 | 0.00068142
78 | 0.97851 | -0.41369 | 0.0027296 | 0.0006841
79 | 0.98637 | -0.26071 | 0.012041 | 0.0030177
80 | 0.98498 | -0.28761 | 0.012071 | 0.0030252
81 | 0.98445 | -0.29789 | 0 | 0
82 | 0.9716 | -0.54931 | 0 | 0
83 | 0.9716 | -0.54942 | 0.001261 | 0.00031603
84 | 0.97154 | -0.55059 | 0.0027323 | 0.00068478
85 | 0.97142 | -0.55297 | 0.00094963 | 0.000238
86 | 0.98358 | -0.31506 | 0.013773 | 0.0034518
87 | 0.98311 | -0.32409 | 0.011483 | 0.0028779
88 | 0.9834 | -0.31838 | 0.0018021 | 0.00045165
89 | 0.98305 | -0.32541 | 0.011482 | 0.0028777
90 | 0.9865 | -0.25763 | 0.00075099 | 0.00018822
91 | 0.98649 | -0.25774 | 0.00050962 | 0.00012772
92 | 0.98546 | -0.27775 | 0.00054308 | 0.00013611
93 | 0.98585 | -0.27009 | 0.00072471 | 0.00018163
94 | 0.98583 | -0.27064 | 0.0013076 | 0.00032772
95 | 0.98376 | -0.31078 | 0.0036125 | 0.00090538
96 | 0.98304 | -0.32466 | 0 | 0
97 | 0.97097 | -0.56186 | 0.00079758 | 0.00019989
98 | 0.97074 | -0.5664 | 0.0028791 | 0.00072158
99 | 0.97065 | -0.56808 | 0.000336 | 8.4209e-05
100 | 0.97046 | -0.57195 | 0.00035091 | 8.7946e-05
101 | 0.97971 | -0.38978 | 0.0041231 | 0.0010334
102 | 0.97962 | -0.39144 | 0.0023276 | 0.00058336
103 | 0.98037 | -0.37686 | 0.002237 | 0.00056064
104 | 0.97903 | -0.40298 | 0.0022684 | 0.00056851
105 | 0.98042 | -0.37576 | 0 | 0
106 | 0.97892 | -0.40518 | 0.0030556 | 0.00076581
107 | 0.98038 | -0.37656 | 0.0020863 | 0.00052287
108 | 0.98121 | -0.36039 | 0.0022827 | 0.00057209
109 | 0.97847 | -0.41397 | 0.0028176 | 0.00070616
110 | 0.98034 | -0.37745 | 0.0019258 | 0.00048265
111 | 0.98198 | -0.3454 | 0.0033212 | 0.00083238
112 | 0.97046 | -0.57054 | 0.0063645 | 0.0015951
113 | 0.97044 | -0.57087 | 0.0036594 | 0.00091713
114 | 0.97014 | -0.57822 | 0.0066364 | 0.0016632
115 | 0.97025 | -0.5761 | 0.0014608 | 0.00036611
116 | 0.97027 | -0.57563 | 0.0028761 | 0.00072083
117 | 0.977 | -0.44191 | 0.00079955 | 0.00020039
118 | 0.97702 | -0.44145 | 0.00082529 | 0.00020684
119 | 0.97775 | -0.42708 | 0 | 0
120 | 0.97751 | -0.4319 | 0.0032477 | 0.00081396
121 | 0.97748 | -0.43244 | 0.0031656 | 0.00079337
122 | 0.97781 | -0.42693 | 0 | 0
123 | 0.97752 | -0.43259 | 0 | 0
124 | 0.97744 | -0.43434 | 0.003187 | 0.00079875
125 | 0.97735 | -0.43602 | 0.0025757 | 0.00064553
126 | 0.97712 | -0.44056 | 0.0021257 | 0.00053276
127 | 0.97732 | -0.43661 | 0.0021039 | 0.00052728
128 | 0.97664 | -0.44997 | 0 | 0
129 | 0.97599 | -0.46281 | 0.0052388 | 0.001313
130 | 0.97597 | -0.46307 | 0.0019779 | 0.00049571
131 | 0.97656 | -0.45152 | 0 | 0
132 | 0.97586 | -0.4653 | 0.0024267 | 0.00060818
133 | 0.97585 | -0.46546 | 0.0022022 | 0.00055192
134 | 0.97731 | -0.43688 | 0.0013834 | 0.00034672
135 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0011366 | -0.00028487 | 0.0011367 | 0.00028482 | 5.3281e-09 | -5.493e-08 | 0.0017388 | 0.0017387 | 0.0017388 | 0.97273 | -0.52702 | 0.97274 | -0.52692 | 0.47768
1 | 0.025857 | 0.0064944 | -0.025843 | -0.006486 | 1.3572e-05 | 8.399e-06 | 0.039559 | 0.039559 | 0.039559 | 0.97274 | -0.52692 | 0.97218 | -0.53793 | 10.8678
2 | -0.026993 | -0.0067792 | 0.027003 | 0.0067849 | 9.2357e-06 | 5.7315e-06 | 0.041298 | 0.041297 | 0.041298 | 0.97274 | -0.52692 | 0.9731 | -0.51976 | 11.3455
3 | 0.023415 | 0.0058773 | -0.023405 | -0.0058717 | 9.1346e-06 | 5.6111e-06 | 0.035841 | 0.035842 | 0.035842 | 0.97218 | -0.53793 | 0.97176 | -0.54611 | 9.8466
4 | -0.027583 | -0.0069303 | 0.027584 | 0.0069308 | 8.1978e-07 | 5.094e-07 | 0.042184 | 0.042184 | 0.042184 | 0.9731 | -0.51976 | 0.97313 | -0.51913 | 11.5891
5 | 0.01904 | 0.0047783 | -0.019039 | -0.0047775 | 1.2455e-06 | 7.4871e-07 | 0.029158 | 0.029158 | 0.029158 | 0.97176 | -0.54611 | 0.9717 | -0.54748 | 8.0104
6 | 0.0034988 | 0.00087625 | -0.0034983 | -0.00087648 | 4.5871e-07 | -2.3435e-07 | 0.0053573 | 0.0053575 | 0.0053575 | 0.97176 | -0.54611 | 0.97163 | -0.54887 | 1.4718
7 | -0.028033 | -0.0070434 | 0.028044 | 0.0070503 | 1.0984e-05 | 6.8315e-06 | 0.042872 | 0.042872 | 0.042872 | 0.97313 | -0.51913 | 0.97355 | -0.51093 | 11.7779
8 | 0.019039 | 0.0047775 | -0.019037 | -0.0047765 | 1.6582e-06 | 9.9681e-07 | 0.029158 | 0.029158 | 0.029158 | 0.9717 | -0.54748 | 0.9716 | -0.54931 | 8.0104
9 | 0.001261 | 0.00031575 | -0.001261 | -0.00031603 | 3.338e-08 | -2.7425e-07 | 0.0019311 | 0.0019312 | 0.0019312 | 0.97163 | -0.54887 | 0.9716 | -0.54942 | 0.53055
10 | -0.028044 | -0.0070503 | 0.028049 | 0.0070537 | 5.4784e-06 | 3.4073e-06 | 0.042872 | 0.042872 | 0.042872 | 0.97355 | -0.51093 | 0.97376 | -0.50684 | 11.7779
11 | -0.029468 | -0.0074091 | 0.029484 | 0.0074191 | 1.6058e-05 | 1.0015e-05 | 0.045039 | 0.045038 | 0.045039 | 0.97376 | -0.50684 | 0.97433 | -0.49543 | 12.3732
12 | -0.030625 | -0.0077051 | 0.030642 | 0.0077158 | 1.7091e-05 | 1.0679e-05 | 0.046781 | 0.046781 | 0.046781 | 0.97433 | -0.49543 | 0.97493 | -0.48376 | 12.852
13 | -0.032485 | -0.0081778 | 0.032486 | 0.0081784 | 8.8895e-07 | 5.5691e-07 | 0.049595 | 0.049595 | 0.049595 | 0.97493 | -0.48376 | 0.97496 | -0.48319 | 13.625
14 | -0.03499 | -0.008806 | 0.035013 | 0.00882 | 2.2402e-05 | 1.4076e-05 | 0.053417 | 0.053417 | 0.053417 | 0.97496 | -0.48319 | 0.97564 | -0.4698 | 14.675
15 | -0.036476 | -0.0091868 | 0.036499 | 0.0092011 | 2.282e-05 | 1.4359e-05 | 0.055648 | 0.055648 | 0.055648 | 0.97564 | -0.4698 | 0.97631 | -0.45672 | 15.288
16 | 0.034895 | 0.0087628 | -0.03488 | -0.0087534 | 1.4842e-05 | 9.3271e-06 | 0.05342 | 0.05342 | 0.05342 | 0.97211 | -0.53799 | 0.97166 | -0.54691 | 14.6758
17 | -0.044492 | -0.011168 | 0.044526 | 0.011189 | 3.3424e-05 | 2.1153e-05 | 0.068111 | 0.068111 | 0.068111 | 0.97211 | -0.53799 | 0.9729 | -0.52226 | 18.7119
18 | 0.033873 | 0.0085012 | -0.033865 | -0.0084963 | 7.8726e-06 | 4.9419e-06 | 0.051879 | 0.051879 | 0.051879 | 0.97166 | -0.54691 | 0.97141 | -0.55179 | 14.2524
19 | 0.0070752 | 0.0017732 | -0.0070749 | -0.0017731 | 2.6996e-07 | 9.6436e-08 | 0.010821 | 0.010821 | 0.010821 | 0.9729 | -0.52226 | 0.97286 | -0.52306 | 2.9729
20 | -0.051601 | -0.012963 | 0.051635 | 0.012984 | 3.4047e-05 | 2.1609e-05 | 0.078932 | 0.078932 | 0.078932 | 0.9729 | -0.52226 | 0.97361 | -0.50844 | 21.6847
21 | 0.027889 | 0.0069985 | -0.027872 | -0.0069875 | 1.7727e-05 | 1.1025e-05 | 0.042724 | 0.042724 | 0.042724 | 0.97141 | -0.55179 | 0.97073 | -0.56513 | 11.7375
22 | -0.052665 | -0.013242 | 0.052725 | 0.01328 | 5.997e-05 | 3.8074e-05 | 0.080506 | 0.080506 | 0.080506 | 0.97361 | -0.50844 | 0.97482 | -0.48463 | 22.1172
23 | 0.022437 | 0.0056256 | -0.022435 | -0.0056242 | 2.2402e-06 | 1.3713e-06 | 0.034395 | 0.034395 | 0.034395 | 0.97073 | -0.56513 | 0.97063 | -0.56722 | 9.4491
24 | -0.053715 | -0.013528 | 0.053765 | 0.013561 | 5.06e-05 | 3.2134e-05 | 0.082017 | 0.082017 | 0.082017 | 0.97482 | -0.48463 | 0.97582 | -0.46495 | 22.5322
25 | 0.010026 | 0.002513 | -0.010024 | -0.0025122 | 1.5874e-06 | 7.945e-07 | 0.01537 | 0.01537 | 0.01537 | 0.97063 | -0.56722 | 0.97046 | -0.57054 | 4.2225
26 | 0.01241 | 0.0031112 | -0.012406 | -0.0031094 | 3.1968e-06 | 1.7549e-06 | 0.019025 | 0.019025 | 0.019025 | 0.97063 | -0.56722 | 0.97036 | -0.57263 | 5.2267
27 | -0.054603 | -0.013771 | 0.054663 | 0.013809 | 6.0294e-05 | 3.8298e-05 | 0.083294 | 0.083294 | 0.083294 | 0.97582 | -0.46495 | 0.977 | -0.44191 | 22.8831
28 | -0.038363 | -0.0096683 | 0.038379 | 0.0096786 | 1.6399e-05 | 1.0335e-05 | 0.058489 | 0.058489 | 0.058489 | 0.97631 | -0.45672 | 0.97676 | -0.44779 | 16.0685
29 | -0.03995 | -0.010072 | 0.039964 | 0.010081 | 1.387e-05 | 8.7516e-06 | 0.060883 | 0.060883 | 0.060883 | 0.97676 | -0.44779 | 0.97713 | -0.44054 | 16.726
30 | 0.0015711 | 0.00039357 | -0.001571 | -0.00039374 | 3.2413e-08 | -1.6812e-07 | 0.0023933 | 0.0023934 | 0.0023934 | 0.97676 | -0.44779 | 0.97674 | -0.44823 | 0.65753
31 | -0.041673 | -0.010509 | 0.041709 | 0.010532 | 3.587e-05 | 2.2659e-05 | 0.063485 | 0.063485 | 0.063485 | 0.97713 | -0.44054 | 0.97805 | -0.42258 | 17.441
32 | 0.00079697 | 0.00019974 | -0.00079697 | -0.00019974 | 1.4267e-10 | -3.1371e-09 | 0.0012142 | 0.0012142 | 0.0012142 | 0.97674 | -0.44823 | 0.97674 | -0.44823 | 0.33356
33 | -0.043089 | -0.010878 | 0.043091 | 0.010879 | 1.8754e-06 | 1.1857e-06 | 0.065584 | 0.065584 | 0.065584 | 0.97805 | -0.42258 | 0.9781 | -0.42167 | 18.0176
34 | -0.12035 | -0.030611 | 0.12045 | 0.030679 | 0.00010621 | 6.7862e-05 | 0.18143 | 0.18143 | 0.18143 | 0.98791 | -0.23018 | 0.98887 | -0.21188 | 49.843
35 | 0.10927 | 0.027836 | -0.10914 | -0.02775 | 0.00013419 | 8.5713e-05 | 0.16475 | 0.16475 | 0.16475 | 0.98791 | -0.23018 | 0.98659 | -0.25567 | 45.2618
36 | -0.12408 | -0.031589 | 0.12416 | 0.03164 | 8.0591e-05 | 5.1262e-05 | 0.18689 | 0.18689 | 0.18689 | 0.98887 | -0.21188 | 0.98957 | -0.19842 | 25.6721
37 | 0.10683 | 0.02717 | -0.10659 | -0.027022 | 0.00023198 | 0.00014817 | 0.16126 | 0.16126 | 0.16126 | 0.98659 | -0.25567 | 0.98425 | -0.30085 | 44.3027
38 | 0.064283 | 0.016323 | -0.064104 | -0.016209 | 0.00017893 | 0.00011386 | 0.096739 | 0.096739 | 0.096739 | 0.98957 | -0.19842 | 0.98656 | -0.25644 | 26.5767
39 | -0.18845 | -0.047963 | 0.18921 | 0.04845 | 0.0007629 | 0.00048695 | 0.28363 | 0.28363 | 0.28363 | 0.98957 | -0.19842 | 0.99394 | -0.11482 | 38.9603
40 | 0.09423 | 0.023923 | -0.094091 | -0.023834 | 0.00013959 | 8.9108e-05 | 0.14257 | 0.14257 | 0.14257 | 0.98425 | -0.30085 | 0.98266 | -0.33168 | 39.1676
41 | 0.0062537 | 0.0015668 | -0.0062529 | -0.0015666 | 8.3519e-07 | 2.1492e-07 | 0.0094322 | 0.0094324 | 0.0094324 | 0.98656 | -0.25644 | 0.98642 | -0.25924 | 2.5913
42 | 0.056245 | 0.014241 | -0.056211 | -0.014219 | 3.4054e-05 | 2.1634e-05 | 0.084885 | 0.084885 | 0.084885 | 0.98656 | -0.25644 | 0.98591 | -0.26906 | 23.32
43 | 0.0016059 | 0.00040179 | -0.0016058 | -0.00040214 | 6.7263e-08 | -3.4737e-07 | 0.0024219 | 0.0024221 | 0.0024221 | 0.98656 | -0.25644 | 0.98651 | -0.25732 | 0.6654
44 | -0.19308 | -0.04942 | 0.19329 | 0.049554 | 0.00021072 | 0.00013347 | 0.28943 | 0.28943 | 0.28943 | 0.99394 | -0.11482 | 0.99513 | -0.092307 | 19.8783
45 | 0.0024087 | 0.0006035 | -0.0024086 | -0.00060366 | 8.3005e-08 | -1.5764e-07 | 0.0036474 | 0.0036475 | 0.0036475 | 0.98266 | -0.33168 | 0.98262 | -0.33241 | 1.002
46 | 0.010964 | 0.0027485 | -0.010961 | -0.0027471 | 2.7177e-06 | 1.4064e-06 | 0.016603 | 0.016603 | 0.016603 | 0.98266 | -0.33168 | 0.98239 | -0.33689 | 4.5612
47 | 0.080718 | 0.020482 | -0.080626 | -0.020424 | 9.2187e-05 | 5.8792e-05 | 0.12232 | 0.12232 | 0.12232 | 0.98266 | -0.33168 | 0.98143 | -0.35546 | 33.6045
48 | 0.0058952 | 0.0014769 | -0.0058948 | -0.0014769 | 3.5709e-07 | 7.4837e-08 | 0.0088927 | 0.0088928 | 0.0088928 | 0.98642 | -0.25924 | 0.98635 | -0.26052 | 2.4431
49 | 0.054178 | 0.01371 | -0.054156 | -0.013696 | 2.2584e-05 | 1.4339e-05 | 0.081818 | 0.081818 | 0.081818 | 0.98591 | -0.26906 | 0.98546 | -0.27775 | 22.4774
50 | 0.0020325 | 0.00050877 | -0.0020324 | -0.00050907 | 1.0009e-07 | -2.9767e-07 | 0.0030673 | 0.0030675 | 0.0030675 | 0.98591 | -0.26906 | 0.98585 | -0.27009 | 0.84271
51 | 0.0012606 | 0.00031562 | -0.0012606 | -0.00031578 | 1.8578e-08 | -1.6307e-07 | 0.0019014 | 0.0019014 | 0.0019014 | 0.98651 | -0.25732 | 0.9865 | -0.25763 | 0.52237
52 | -0.49354 | -0.12596 | 0.49576 | 0.12738 | 0.0022118 | 0.0014133 | 0.7388 | 0.7388 | 0.7388 | 0.99513 | -0.092307 | 1 | 0 | 50.742
53 | 0.30025 | 0.076408 | -0.29958 | -0.075979 | 0.00067389 | 0.00042944 | 0.44938 | 0.44938 | 0.44938 | 0.99513 | -0.092307 | 0.99269 | -0.13898 | 30.8638
54 | 0.076636 | 0.019424 | -0.076562 | -0.019377 | 7.3715e-05 | 4.6994e-05 | 0.11627 | 0.11627 | 0.11627 | 0.98143 | -0.35546 | 0.9804 | -0.3755 | 31.9425
55 | 0.073066 | 0.0185 | -0.073063 | -0.018498 | 3.9088e-06 | 2.491e-06 | 0.11097 | 0.11097 | 0.11097 | 0.9804 | -0.3755 | 0.98034 | -0.37661 | 30.485
56 | 0.07063 | 0.017888 | -0.07056 | -0.017844 | 6.9818e-05 | 4.448e-05 | 0.10727 | 0.10727 | 0.10727 | 0.98034 | -0.37661 | 0.97928 | -0.39722 | 29.4707
57 | 0.06693 | 0.016934 | -0.06693 | -0.016934 | 4.3217e-07 | 2.7518e-07 | 0.10176 | 0.10176 | 0.10176 | 0.97928 | -0.39722 | 0.97928 | -0.39735 | 27.9554
58 | 0.065395 | 0.016549 | -0.065342 | -0.016516 | 5.2727e-05 | 3.3566e-05 | 0.099425 | 0.099425 | 0.099425 | 0.97928 | -0.39735 | 0.97842 | -0.41417 | 27.3146
59 | -0.0025845 | -0.00064746 | 0.0025845 | 0.00064744 | 1.77e-08 | -2.576e-08 | 0.0039641 | 0.0039641 | 0.0039641 | 0.97012 | -0.57731 | 0.97013 | -0.57717 | 1.089
60 | 0.0025845 | 0.00064746 | -0.0025843 | -0.00064769 | 1.555e-07 | -2.2627e-07 | 0.0039641 | 0.0039642 | 0.0039642 | 0.97012 | -0.57731 | 0.97006 | -0.57858 | 1.0891
61 | -0.007136 | -0.0017881 | 0.0071365 | 0.0017884 | 5.8139e-07 | 2.1228e-07 | 0.010945 | 0.010945 | 0.010945 | 0.97013 | -0.57717 | 0.97021 | -0.57546 | 3.0069
62 | 0.057841 | 0.014631 | -0.057803 | -0.014607 | 3.8466e-05 | 2.3946e-05 | 0.087777 | 0.087777 | 0.087777 | 0.98108 | -0.36355 | 0.98036 | -0.37742 | 12.0573
63 | -0.083741 | -0.021128 | 0.083878 | 0.021215 | 0.00013724 | 8.6684e-05 | 0.12706 | 0.12706 | 0.12706 | 0.98108 | -0.36355 | 0.98283 | -0.32939 | 17.4535
64 | 0.0259 | 0.006497 | -0.025884 | -0.006487 | 1.6171e-05 | 9.9966e-06 | 0.039285 | 0.039285 | 0.039285 | 0.98108 | -0.36355 | 0.98041 | -0.37666 | 10.7926
65 | 0.053056 | 0.013417 | -0.052985 | -0.013372 | 7.108e-05 | 4.5124e-05 | 0.080573 | 0.080573 | 0.080573 | 0.98036 | -0.37742 | 0.97893 | -0.40539 | 22.1356
66 | -0.095357 | -0.024091 | 0.095411 | 0.024125 | 5.4635e-05 | 3.355e-05 | 0.14444 | 0.14444 | 0.14444 | 0.98283 | -0.32939 | 0.98345 | -0.31744 | 9.9203
67 | 0.062782 | 0.015874 | -0.062743 | -0.015849 | 3.8868e-05 | 2.4733e-05 | 0.095531 | 0.095531 | 0.095531 | 0.97842 | -0.41417 | 0.97775 | -0.42708 | 26.2449
68 | -0.0038516 | -0.00096499 | 0.0038519 | 0.0009649 | 2.5824e-07 | -9.4958e-08 | 0.0058112 | 0.0058111 | 0.0058112 | 0.98623 | -0.2629 | 0.9863 | -0.26149 | 1.5965
69 | 0.0014322 | 0.00035863 | -0.0014322 | -0.00035894 | 4.639e-08 | -3.0835e-07 | 0.0021608 | 0.002161 | 0.002161 | 0.98623 | -0.2629 | 0.98619 | -0.26358 | 0.59367
70 | -0.0051258 | -0.0012842 | 0.005126 | 0.0012842 | 2.3827e-07 | 1.6882e-08 | 0.007733 | 0.007733 | 0.007733 | 0.9863 | -0.26149 | 0.98635 | -0.26052 | 2.1245
71 | 0.0097704 | 0.0024487 | -0.0097703 | -0.0024487 | 9.6471e-08 | 4.6402e-08 | 0.014685 | 0.014685 | 0.014685 | 0.99002 | -0.1903 | 0.99001 | -0.19051 | 4.0344
72 | -0.025617 | -0.0064202 | 0.025628 | 0.006427 | 1.114e-05 | 6.872e-06 | 0.038502 | 0.038502 | 0.038502 | 0.99002 | -0.1903 | 0.99049 | -0.18117 | 10.5775
73 | 0.23862 | 0.060489 | -0.23821 | -0.06023 | 0.000408 | 0.00025938 | 0.35872 | 0.35872 | 0.35872 | 0.99049 | -0.18117 | 0.98864 | -0.21682 | 24.6372
74 | -0.26424 | -0.066917 | 0.26478 | 0.067258 | 0.00053658 | 0.00034154 | 0.39722 | 0.39722 | 0.39722 | 0.99049 | -0.18117 | 0.99269 | -0.13898 | 27.2815
75 | 0.20727 | 0.052477 | -0.2071 | -0.052367 | 0.00017256 | 0.00010947 | 0.31215 | 0.31216 | 0.31216 | 0.98864 | -0.21682 | 0.98774 | -0.23418 | 21.4392
76 | 0.19735 | 0.049924 | -0.19714 | -0.049793 | 0.00020581 | 0.00013045 | 0.29747 | 0.29747 | 0.29747 | 0.98774 | -0.23418 | 0.98662 | -0.25593 | 20.4304
77 | 0.17154 | 0.043376 | -0.1715 | -0.043351 | 3.9316e-05 | 2.4842e-05 | 0.25885 | 0.25885 | 0.25885 | 0.98662 | -0.25593 | 0.98637 | -0.26071 | 17.7781
78 | 0.045655 | 0.011535 | -0.045619 | -0.011513 | 3.5589e-05 | 2.253e-05 | 0.06943 | 0.069431 | 0.069431 | 0.97893 | -0.40539 | 0.9781 | -0.42167 | 19.0743
79 | 0.0073308 | 0.0018371 | -0.007329 | -0.0018365 | 1.7589e-06 | 6.5093e-07 | 0.011143 | 0.011143 | 0.011143 | 0.97893 | -0.40539 | 0.97867 | -0.41043 | 3.0613
80 | 0.0036013 | 0.00090239 | -0.0036011 | -0.00090244 | 1.1934e-07 | -5.9621e-08 | 0.0054489 | 0.0054489 | 0.0054489 | 0.98345 | -0.31744 | 0.98341 | -0.31814 | 1.497
81 | -0.099013 | -0.025027 | 0.09905 | 0.02505 | 3.7243e-05 | 2.2937e-05 | 0.14989 | 0.14989 | 0.14989 | 0.98345 | -0.31744 | 0.98385 | -0.3096 | 10.2945
82 | 0.0046634 | 0.0011684 | -0.0046629 | -0.0011684 | 5.068e-07 | -1.34e-08 | 0.0070903 | 0.0070905 | 0.0070905 | 0.97867 | -0.41043 | 0.97856 | -0.41271 | 1.9479
83 | 0.0018021 | 0.00045157 | -0.0018021 | -0.00045165 | 2.0518e-08 | -8.023e-08 | 0.0027268 | 0.0027268 | 0.0027268 | 0.98341 | -0.31814 | 0.9834 | -0.31838 | 0.74913
84 | -0.11027 | -0.027862 | 0.11033 | 0.0279 | 6.1956e-05 | 3.8445e-05 | 0.16685 | 0.16685 | 0.16685 | 0.98385 | -0.3096 | 0.98445 | -0.29789 | 11.4598
85 | -0.0096863 | -0.0024274 | 0.0096876 | 0.002428 | 1.3067e-06 | 6.4127e-07 | 0.014856 | 0.014856 | 0.014856 | 0.97021 | -0.57546 | 0.97036 | -0.57263 | 4.0813
86 | 0.0027297 | 0.00068393 | -0.0027296 | -0.0006841 | 1.2757e-07 | -1.6639e-07 | 0.0041508 | 0.0041509 | 0.0041509 | 0.97856 | -0.41271 | 0.97851 | -0.41369 | 1.1404
87 | 0.15946 | 0.040333 | -0.15925 | -0.040204 | 0.00020551 | 0.0001296 | 0.24069 | 0.24069 | 0.24069 | 0.98637 | -0.26071 | 0.98498 | -0.28761 | 16.5306
88 | 0.14718 | 0.037178 | -0.14711 | -0.037133 | 7.2422e-05 | 4.5556e-05 | 0.22245 | 0.22245 | 0.22245 | 0.98498 | -0.28761 | 0.98445 | -0.29789 | 15.2782
89 | 0.036778 | 0.0092327 | -0.036748 | -0.0092138 | 3.0108e-05 | 1.8939e-05 | 0.055597 | 0.055597 | 0.055597 | 0.98445 | -0.29789 | 0.98358 | -0.31506 | 15.2738
90 | 0.0027325 | 0.00068457 | -0.0027323 | -0.00068478 | 1.664e-07 | -2.0729e-07 | 0.0041847 | 0.0041848 | 0.0041848 | 0.9716 | -0.54931 | 0.97154 | -0.55059 | 1.1497
91 | 0.016305 | 0.004092 | -0.016302 | -0.0040903 | 2.8415e-06 | 1.6681e-06 | 0.024973 | 0.024973 | 0.024973 | 0.9716 | -0.54931 | 0.97142 | -0.55297 | 6.8608
92 | 0.015352 | 0.0038523 | -0.015346 | -0.0038485 | 6.5083e-06 | 3.7771e-06 | 0.023519 | 0.023519 | 0.023519 | 0.97142 | -0.55297 | 0.97097 | -0.56186 | 6.4612
93 | 0.022976 | 0.005762 | -0.022966 | -0.005756 | 9.8782e-06 | 6.0455e-06 | 0.03476 | 0.034761 | 0.034761 | 0.98358 | -0.31506 | 0.98311 | -0.32409 | 9.5496
94 | 0.011483 | 0.0028781 | -0.011482 | -0.0028777 | 7.2366e-07 | 3.8214e-07 | 0.01738 | 0.01738 | 0.01738 | 0.98311 | -0.32409 | 0.98305 | -0.32541 | 4.7748
95 | 0.00050962 | 0.00012757 | -0.00050962 | -0.00012772 | 2.729e-09 | -1.555e-07 | 0.00076864 | 0.0007687 | 0.0007687 | 0.9865 | -0.25763 | 0.98649 | -0.25774 | 0.21118
96 | 0.053613 | 0.01356 | -0.053528 | -0.013506 | 8.4805e-05 | 5.3837e-05 | 0.080998 | 0.080998 | 0.080998 | 0.98546 | -0.27775 | 0.98376 | -0.31078 | 22.2521
97 | 0.0013076 | 0.00032744 | -0.0013076 | -0.00032772 | 3.3898e-08 | -2.7419e-07 | 0.0019736 | 0.0019737 | 0.0019737 | 0.98585 | -0.27009 | 0.98583 | -0.27064 | 0.54223
98 | 0.049915 | 0.012601 | -0.049882 | -0.01258 | 3.3172e-05 | 2.1034e-05 | 0.075534 | 0.075534 | 0.075534 | 0.98376 | -0.31078 | 0.98304 | -0.32466 | 20.751
99 | 0.049882 | 0.01258 | -0.049833 | -0.012548 | 4.9472e-05 | 3.1369e-05 | 0.075534 | 0.075534 | 0.075534 | 0.98304 | -0.32466 | 0.98198 | -0.3454 | 20.751
100 | 0.014548 | 0.0036486 | -0.014545 | -0.0036468 | 3.1453e-06 | 1.8043e-06 | 0.022296 | 0.022296 | 0.022296 | 0.97097 | -0.56186 | 0.97074 | -0.5664 | 6.1254
101 | 0.011666 | 0.0029253 | -0.011665 | -0.0029248 | 9.3604e-07 | 5.0258e-07 | 0.017883 | 0.017883 | 0.017883 | 0.97074 | -0.5664 | 0.97065 | -0.56808 | 4.913
102 | 0.011329 | 0.0028405 | -0.011327 | -0.0028394 | 2.0866e-06 | 1.1075e-06 | 0.017368 | 0.017368 | 0.017368 | 0.97065 | -0.56808 | 0.97046 | -0.57195 | 4.7715
103 | 0.010976 | 0.0027515 | -0.010974 | -0.0027505 | 1.9287e-06 | 1.0101e-06 | 0.01683 | 0.01683 | 0.01683 | 0.97046 | -0.57195 | 0.97027 | -0.57563 | 4.6237
104 | 0.033765 | 0.0084868 | -0.033762 | -0.0084851 | 2.6856e-06 | 1.6845e-06 | 0.051292 | 0.051292 | 0.051292 | 0.97971 | -0.38978 | 0.97962 | -0.39144 | 14.0913
105 | -0.037888 | -0.0095201 | 0.037912 | 0.0095349 | 2.3382e-05 | 1.4727e-05 | 0.057555 | 0.057555 | 0.057555 | 0.97971 | -0.38978 | 0.98037 | -0.37686 | 15.8117
106 | 0.031435 | 0.0079017 | -0.031417 | -0.0078909 | 1.7305e-05 | 1.0821e-05 | 0.047757 | 0.047757 | 0.047757 | 0.97962 | -0.39144 | 0.97903 | -0.40298 | 13.12
107 | -0.040149 | -0.010096 | 0.040151 | 0.010097 | 2.0969e-06 | 1.3231e-06 | 0.06095 | 0.06095 | 0.06095 | 0.98037 | -0.37686 | 0.98042 | -0.37576 | 16.7445
108 | 0.029149 | 0.0073224 | -0.029146 | -0.0073205 | 3.0535e-06 | 1.9021e-06 | 0.044309 | 0.044309 | 0.044309 | 0.97903 | -0.40298 | 0.97892 | -0.40518 | 12.1729
109 | 0.0040123 | 0.0010052 | -0.0040122 | -0.0010053 | 1.5229e-07 | -4.0635e-08 | 0.0060895 | 0.0060895 | 0.0060895 | 0.98042 | -0.37576 | 0.98038 | -0.37656 | 1.673
110 | -0.044163 | -0.011102 | 0.044195 | 0.011123 | 3.2448e-05 | 2.0524e-05 | 0.06704 | 0.067039 | 0.06704 | 0.98042 | -0.37576 | 0.98121 | -0.36039 | 18.4174
111 | 0.02609 | 0.0065547 | -0.026079 | -0.0065479 | 1.0944e-05 | 6.7712e-06 | 0.039664 | 0.039665 | 0.039665 | 0.97892 | -0.40518 | 0.97847 | -0.41397 | 10.8969
112 | 0.0019259 | 0.00048239 | -0.0019258 | -0.00048265 | 8.111e-08 | -2.6728e-07 | 0.002923 | 0.0029231 | 0.0029231 | 0.98038 | -0.37656 | 0.98034 | -0.37745 | 0.80305
113 | -0.046478 | -0.011695 | 0.046511 | 0.011716 | 3.331e-05 | 2.1093e-05 | 0.070501 | 0.070501 | 0.070501 | 0.98121 | -0.36039 | 0.98198 | -0.3454 | 19.3684
114 | 0.023262 | 0.0058418 | -0.023247 | -0.0058329 | 1.4373e-05 | 8.8143e-06 | 0.03538 | 0.03538 | 0.03538 | 0.97847 | -0.41397 | 0.97781 | -0.42693 | 9.7197
115 | 0.0036595 | 0.00091711 | -0.0036594 | -0.00091713 | 5.7438e-08 | -2.3348e-08 | 0.0056111 | 0.0056111 | 0.0056111 | 0.97046 | -0.57054 | 0.97044 | -0.57087 | 1.5415
116 | -0.0066364 | -0.0016632 | 0.0066371 | 0.0016635 | 6.7139e-07 | 2.1631e-07 | 0.010179 | 0.010179 | 0.010179 | 0.97014 | -0.57822 | 0.97025 | -0.5761 | 2.7964
117 | -0.0080979 | -0.0020296 | 0.0080981 | 0.0020297 | 1.7825e-07 | 7.6018e-08 | 0.012419 | 0.012419 | 0.012419 | 0.97025 | -0.5761 | 0.97027 | -0.57563 | 3.4119
118 | -0.055463 | -0.014009 | 0.055464 | 0.01401 | 1.2015e-06 | 7.6335e-07 | 0.084512 | 0.084512 | 0.084512 | 0.977 | -0.44191 | 0.97702 | -0.44145 | 23.2176
119 | -0.056289 | -0.014217 | 0.056328 | 0.014241 | 3.8793e-05 | 2.4651e-05 | 0.085769 | 0.085769 | 0.085769 | 0.97702 | -0.44145 | 0.97775 | -0.42708 | 23.5629
120 | 0.0064149 | 0.0016077 | -0.0064134 | -0.0016073 | 1.4731e-06 | 4.2598e-07 | 0.0097626 | 0.0097628 | 0.0097628 | 0.97775 | -0.42708 | 0.97751 | -0.4319 | 2.6821
121 | 0.0031657 | 0.0007933 | -0.0031656 | -0.00079337 | 8.0847e-08 | -6.4636e-08 | 0.0048189 | 0.0048189 | 0.0048189 | 0.97751 | -0.4319 | 0.97748 | -0.43244 | 1.3239
122 | 0.0060657 | 0.00152 | -0.0060641 | -0.0015196 | 1.6356e-06 | 4.0488e-07 | 0.0092306 | 0.0092309 | 0.0092309 | 0.97781 | -0.42693 | 0.97752 | -0.43259 | 2.536
123 | 0.017182 | 0.0043129 | -0.017176 | -0.0043094 | 6.0761e-06 | 3.5916e-06 | 0.026149 | 0.026149 | 0.026149 | 0.97781 | -0.42693 | 0.97744 | -0.43434 | 7.1839
124 | 0.0060641 | 0.0015196 | -0.0060631 | -0.0015194 | 9.9135e-07 | 2.4561e-07 | 0.0092309 | 0.009231 | 0.009231 | 0.97752 | -0.43259 | 0.97735 | -0.43602 | 2.536
125 | 0.013989 | 0.0035106 | -0.013984 | -0.0035083 | 4.1424e-06 | 2.346e-06 | 0.021297 | 0.021298 | 0.021298 | 0.97744 | -0.43434 | 0.97712 | -0.44056 | 5.851
126 | 0.0034874 | 0.00087382 | -0.0034873 | -0.00087388 | 9.8672e-08 | -5.3813e-08 | 0.0053095 | 0.0053095 | 0.0053095 | 0.97735 | -0.43602 | 0.97732 | -0.43661 | 1.4587
127 | 0.011859 | 0.0029755 | -0.011853 | -0.0029726 | 5.324e-06 | 2.8624e-06 | 0.01806 | 0.018061 | 0.018061 | 0.97712 | -0.44056 | 0.97664 | -0.44997 | 4.9617
128 | 0.0013835 | 0.0003466 | -0.0013834 | -0.00034672 | 1.7751e-08 | -1.2234e-07 | 0.0021063 | 0.0021064 | 0.0021064 | 0.97732 | -0.43661 | 0.97731 | -0.43688 | 0.57867
129 | 0.011853 | 0.0029726 | -0.011852 | -0.0029722 | 8.7262e-07 | 4.6921e-07 | 0.018061 | 0.018061 | 0.018061 | 0.97664 | -0.44997 | 0.97656 | -0.45152 | 4.9617
130 | 0.0066073 | 0.0016558 | -0.0066073 | -0.0016558 | 8.2542e-08 | 2.5721e-08 | 0.010074 | 0.010074 | 0.010074 | 0.97599 | -0.46281 | 0.97597 | -0.46307 | 2.7675
131 | -0.011846 | -0.0029687 | 0.011852 | 0.0029722 | 6.3738e-06 | 3.4277e-06 | 0.018061 | 0.018061 | 0.018061 | 0.97599 | -0.46281 | 0.97656 | -0.45152 | 4.9618
132 | 0.0046294 | 0.00116 | -0.0046289 | -0.0011601 | 4.9139e-07 | -1.4175e-08 | 0.0070581 | 0.0070582 | 0.0070582 | 0.97597 | -0.46307 | 0.97586 | -0.4653 | 1.9391
133 | 0.0022022 | 0.00055188 | -0.0022022 | -0.00055192 | 1.6449e-08 | -3.8073e-08 | 0.003358 | 0.003358 | 0.003358 | 0.97586 | -0.4653 | 0.97585 | -0.46546 | 0.92252

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52126 | 0.13335

## res_load
| p_mw | q_mvar
0 | 0.0011366 | 0.00028487
1 | 0.0024287 | 0.00060869
2 | 0.00058002 | 0.00014537
3 | 0.0008663 | 0.00021711
4 | 0.00044946 | 0.00011265
5 | 0.0022373 | 0.00056073
6 | 0.001418 | 0.0003554
7 | 0.0011412 | 0.00028601
8 | 0.0018437 | 0.00046206
9 | 0.0025041 | 0.00062759
10 | 0.0014632 | 0.00036671
11 | 0.0095978 | 0.0024054
12 | 0.0010064 | 0.00025222
13 | 0.0059762 | 0.0014978
14 | 0.0070749 | 0.0017731
15 | 0.0010299 | 0.00025813
16 | 0.0054341 | 0.0013619
17 | 0.00098989 | 0.00024809
18 | 0.00083748 | 0.00020989
19 | 0.0018639 | 0.00046715
20 | 0.0017091 | 0.00042833
21 | 0.00077406 | 0.000194
22 | 0.0013797 | 0.00034579
23 | 0.00079697 | 0.00019974
24 | 0.011071 | 0.0027747
25 | 0.0036312 | 0.00091006
26 | 0.0023149 | 0.00058016
27 | 0.012364 | 0.0030986
28 | 0.0038722 | 0.00097046
29 | 0.00035774 | 8.9658e-05
30 | 0.00034521 | 8.6518e-05
31 | 0.0024086 | 0.00060366
32 | 0.010961 | 0.0027471
33 | 0.0039902 | 0.001
34 | 0.0034954 | 0.00087602
35 | 0.0024326 | 0.00060966
36 | 0.0036299 | 0.00090974
37 | 0.0015352 | 0.00038476
38 | 0.0045515 | 0.0011407
39 | 0.0025843 | 0.00064769
40 | 0.0047463 | 0.0011895
41 | 0.011479 | 0.0028768
42 | 0.025884 | 0.006487
43 | 0.0025601 | 0.00064163
44 | 0.0024194 | 0.00060636
45 | 0.0012739 | 0.00031926
46 | 0.0014322 | 0.00035894
47 | 0.00076879 | 0.00019268
48 | 0.015846 | 0.0039715
49 | 0.0097703 | 0.0024487
50 | 0.030936 | 0.0077534
51 | 0.034796 | 0.0087208
52 | 0.0097505 | 0.0024437
53 | 0.025605 | 0.0064173
54 | 0.023857 | 0.0059792
55 | 0.0025283 | 0.00063366
56 | 0.0026656 | 0.00066806
57 | 0.001799 | 0.00045088
58 | 0.011218 | 0.0028115
59 | 0.0025497 | 0.00063902
60 | 0.0019332 | 0.0004845
61 | 0.0027189 | 0.00068142
62 | 0.0027296 | 0.0006841
63 | 0.012041 | 0.0030177
64 | 0.012071 | 0.0030252
65 | 0.001261 | 0.00031603
66 | 0.0027323 | 0.00068478
67 | 0.00094963 | 0.000238
68 | 0.013773 | 0.0034518
69 | 0.011483 | 0.0028779
70 | 0.0018021 | 0.00045165
71 | 0.011482 | 0.0028777
72 | 0.00075099 | 0.00018822
73 | 0.00050962 | 0.00012772
74 | 0.00054308 | 0.00013611
75 | 0.00072471 | 0.00018163
76 | 0.0013076 | 0.00032772
77 | 0.0036125 | 0.00090538
78 | 0.00079758 | 0.00019989
79 | 0.0028791 | 0.00072158
80 | 0.000336 | 8.4209e-05
81 | 0.00035091 | 8.7946e-05
82 | 0.0041231 | 0.0010334
83 | 0.0023276 | 0.00058336
84 | 0.002237 | 0.00056064
85 | 0.0022684 | 0.00056851
86 | 0.0030556 | 0.00076581
87 | 0.0020863 | 0.00052287
88 | 0.0022827 | 0.00057209
89 | 0.0028176 | 0.00070616
90 | 0.0019258 | 0.00048265
91 | 0.0033212 | 0.00083238
92 | 0.0063645 | 0.0015951
93 | 0.0036594 | 0.00091713
94 | 0.0066364 | 0.0016632
95 | 0.0014608 | 0.00036611
96 | 0.0028761 | 0.00072083
97 | 0.00079955 | 0.00020039
98 | 0.00082529 | 0.00020684
99 | 0.0032477 | 0.00081396
100 | 0.0031656 | 0.00079337
101 | 0.003187 | 0.00079875
102 | 0.0025757 | 0.00064553
103 | 0.0021257 | 0.00053276
104 | 0.0021039 | 0.00052728
105 | 0.0052388 | 0.001313
106 | 0.0019779 | 0.00049571
107 | 0.0024267 | 0.00060818
108 | 0.0022022 | 0.00055192
109 | 0.0013834 | 0.00034672

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1