## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2534-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2534-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2534-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2534-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2534-12_0_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2534-12_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_2534-12_0_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2534-12_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2534-12_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2534-12_0_3_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_2534-12_0_3_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_2534-12_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2534-12_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_2534-12_0_3_node_33 | 0.4 | n |  | TRUE
14 | bus_LV_2534-12_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_2534-12_0_3_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_2534-12_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2534-12_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2534-12_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_2534-12_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_2534-12_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_2534-12_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2534-12_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_2534-12_0_3_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_2534-12_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2534-12_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2534-12_0_3_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2534-12_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2534-12_0_3_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_2534-12_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_2534-12_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_MV_394_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2534-12_0_3_load_0 | 0 | 0.022471 | 0.0056317 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2534-12_0_3_load_9 | 4 | 0.021888 | 0.0054856 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2534-12_0_3_load_13 | 6 | 0.0049262 | 0.0012346 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2534-12_0_3_load_27 | 9 | 0.0057039 | 0.0014295 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2534-12_0_3_load_31 | 10 | 0.0081705 | 0.0020477 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2534-12_0_3_load_33 | 13 | 0.014999 | 0.0037591 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2534-12_0_3_load_21 | 14 | 0.078822 | 0.019755 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2534-12_0_3_load_32 | 15 | 0.015174 | 0.003803 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2534-12_0_3_load_19 | 18 | 0.013453 | 0.0033717 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2534-12_0_3_load_29 | 19 | 0.041696 | 0.01045 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2534-12_0_3_load_15 | 22 | 0.013408 | 0.0033604 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2534-12_0_3_load_23 | 24 | 0.033116 | 0.0082996 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2534-12_0_3_load_14 | 27 | 0.013423 | 0.003364 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2534-12_0_3_load_35 | 28 | 0.016324 | 0.0040911 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2534-12_0_3_load_30 | 29 | 0.014943 | 0.0037451 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2534-12_0_3_line_0 |  | 0 | 1 | 0.016797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2534-12_0_3_line_1 |  | 0 | 2 | 0.024932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2534-12_0_3_line_2 |  | 1 | 3 | 0.03078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2534-12_0_3_line_3 |  | 2 | 4 | 0.029092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2534-12_0_3_line_4 |  | 2 | 5 | 0.018824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2534-12_0_3_line_5 |  | 3 | 6 | 0.013164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2534-12_0_3_line_6 |  | 4 | 14 | 0.016076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2534-12_0_3_line_7 |  | 5 | 15 | 0.017393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2534-12_0_3_line_8 |  | 7 | 8 | 0.025597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2534-12_0_3_line_9 |  | 7 | 9 | 0.017327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2534-12_0_3_line_10 |  | 8 | 10 | 0.016677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2534-12_0_3_line_11 |  | 10 | 21 | 0.015512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2534-12_0_3_line_12 |  | 11 | 12 | 0.031988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2534-12_0_3_line_13 |  | 11 | 13 | 0.0040431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2534-12_0_3_line_14 |  | 12 | 22 | 0.028984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2534-12_0_3_line_15 |  | 13 | 23 | 0.0067541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2534-12_0_3_line_16 |  | 14 | 20 | 0.022603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_2534-12_0_3_line_17 |  | 16 | 17 | 0.007031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2534-12_0_3_line_18 |  | 16 | 18 | 0.0086904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2534-12_0_3_line_19 |  | 17 | 24 | 0.044435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2534-12_0_3_line_20 |  | 18 | 25 | 0.011358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2534-12_0_3_line_21 |  | 19 | 20 | 0.014556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2534-12_0_3_line_22 |  | 20 | 29 | 0.029812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2534-12_0_3_line_23 |  | 21 | 29 | 0.012762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2534-12_0_3_line_24 |  | 21 | 30 | 0.04662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2534-12_0_3_line_25 |  | 22 | 27 | 0.0049051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2534-12_0_3_line_26 |  | 23 | 28 | 0.023073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2534-12_0_3_line_27 |  | 24 | 30 | 0.0040948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2534-12_0_3_line_28 |  | 25 | 26 | 0.04456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2534-12_0_3_line_29 |  | 26 | 27 | 0.0055762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2534-12_0_3_trafo_9 | 0.63 MVA 20/0.4 kV | 31 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2608970.3036 | 1228145.1999 | 2608983.8848 | 1228155.0836
1 | 2609004.0437 | 1228169.754 | 2608983.8848 | 1228155.0836
2 | 2608970.3036 | 1228145.1999 | 2608989.4635 | 1228121.0699
3 | 2609004.0437 | 1228169.754 | 2608986.6761 | 1228193.0933
4 | 2609004.0437 | 1228169.754 | 2609009.8108 | 1228173.954 | 2609015.6828 | 1228163.8457
5 | 2608989.4635 | 1228121.0699 | 2609000.6933 | 1228127.9396
6 | 2608986.6761 | 1228193.0933 | 2608984.1527 | 1228196.4844 | 2608973.6217 | 1228191.0543
7 | 2609015.6828 | 1228163.8457 | 2609029.8404 | 1228173.9498
8 | 2608894.304 | 1228250.7046 | 2608908.3344 | 1228231.2695 | 2608909.2986 | 1228229.9591
9 | 2608894.304 | 1228250.7046 | 2608892.9837 | 1228257.1065 | 2608886.2879 | 1228265.5684
10 | 2608909.2986 | 1228229.9591 | 2608922.6293 | 1228239.9794
11 | 2608935.8486 | 1228244.1626 | 2608930.5802 | 1228245.9558 | 2608922.6293 | 1228239.9794
12 | 2609095.3009 | 1228227.2147 | 2609094.7351 | 1228205.6677 | 2609098.7426 | 1228196.0348
13 | 2609098.7426 | 1228196.0348 | 2609094.6997 | 1228196.0661
14 | 2609095.3009 | 1228227.2147 | 2609071.0777 | 1228232.7701 | 2609066.9475 | 1228232.6507
15 | 2609087.9458 | 1228196.1185 | 2609094.6997 | 1228196.0661
16 | 2608960.8801 | 1228209.724 | 2608973.6217 | 1228191.0543
17 | 2609009.0893 | 1228235.5116 | 2609004.838 | 1228241.1196
18 | 2609009.0893 | 1228235.5116 | 2609016.2266 | 1228240.4697
19 | 2609004.838 | 1228241.1196 | 2608993.2988 | 1228256.3002 | 2608969.0592 | 1228263.7782
20 | 2609023.4679 | 1228231.7199 | 2609016.2266 | 1228240.4697
21 | 2608960.8801 | 1228209.724 | 2608955.8241 | 1228206.2811 | 2608948.7779 | 1228201.6364
22 | 2608960.8801 | 1228209.724 | 2608943.3521 | 1228233.8392
23 | 2608935.8486 | 1228244.1626 | 2608943.3521 | 1228233.8392
24 | 2608965.1464 | 1228264.9853 | 2608950.6042 | 1228266.8647 | 2608935.1477 | 1228256.8913 | 2608933.289 | 1228248.3946 | 2608935.8486 | 1228244.1626
25 | 2609062.0445 | 1228232.509 | 2609066.9475 | 1228232.6507
26 | 2609087.9458 | 1228196.1185 | 2609064.8734 | 1228196.2874
27 | 2608965.1464 | 1228264.9853 | 2608969.0592 | 1228263.7782
28 | 2609023.4679 | 1228231.7199 | 2609035.3697 | 1228217.3404 | 2609056.4706 | 1228232.3478
29 | 2609056.4706 | 1228232.3478 | 2609062.0445 | 1228232.509

## bus_geodata
| x | y | coords
0 | 2608983.8848 | 1228155.0836
1 | 2608970.3036 | 1228145.1999
2 | 2609004.0437 | 1228169.754
3 | 2608989.4635 | 1228121.0699
4 | 2608986.6761 | 1228193.0933
5 | 2609015.6828 | 1228163.8457
6 | 2609000.6933 | 1228127.9396
7 | 2608894.304 | 1228250.7046
8 | 2608909.2986 | 1228229.9591
9 | 2608886.2879 | 1228265.5684
10 | 2608922.6293 | 1228239.9794
11 | 2609098.7426 | 1228196.0348
12 | 2609095.3009 | 1228227.2147
13 | 2609094.6997 | 1228196.0661
14 | 2608973.6217 | 1228191.0543
15 | 2609029.8404 | 1228173.9498
16 | 2609009.0893 | 1228235.5116
17 | 2609004.838 | 1228241.1196
18 | 2609016.2266 | 1228240.4697
19 | 2608948.7779 | 1228201.6364
20 | 2608960.8801 | 1228209.724
21 | 2608935.8486 | 1228244.1626
22 | 2609066.9475 | 1228232.6507
23 | 2609087.9458 | 1228196.1185
24 | 2608969.0592 | 1228263.7782
25 | 2609023.4679 | 1228231.7199
26 | 2609056.4706 | 1228232.3478
27 | 2609062.0445 | 1228232.509
28 | 2609064.8734 | 1228196.2874
29 | 2608943.3521 | 1228233.8392
30 | 2608965.1464 | 1228264.9853
31 | 2609004.0437 | 1228169.754

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99825 | -0.033553 | 0.022471 | 0.0056317
1 | 0.99818 | -0.035001 | 0 | 0
2 | 0.99888 | -0.021613 | 0 | 0
3 | 0.99804 | -0.037654 | 0 | 0
4 | 1 | 0 | -0.30072 | -0.075895
5 | 0.99862 | -0.026604 | 0 | 0
6 | 0.99798 | -0.038789 | 0.0049262 | 0.0012346
7 | 0.99081 | -0.17546 | 0 | 0
8 | 0.99095 | -0.17287 | 0 | 0
9 | 0.99072 | -0.17721 | 0.0057039 | 0.0014295
10 | 0.99103 | -0.17118 | 0.0081705 | 0.0020477
11 | 0.97703 | -0.44316 | 0 | 0
12 | 0.97796 | -0.42488 | 0 | 0
13 | 0.97692 | -0.44547 | 0.014999 | 0.0037591
14 | 0.99813 | -0.035661 | 0.078822 | 0.019755
15 | 0.99838 | -0.031218 | 0.015174 | 0.003803
16 | 0.9829 | -0.32831 | 0 | 0
17 | 0.98337 | -0.31923 | 0 | 0
18 | 0.98233 | -0.33954 | 0.013453 | 0.0033717
19 | 0.99575 | -0.081038 | 0.041696 | 0.01045
20 | 0.99631 | -0.070375 | 0 | 0
21 | 0.99123 | -0.16736 | 0 | 0
22 | 0.97881 | -0.40835 | 0.013408 | 0.0033604
23 | 0.97681 | -0.44749 | 0 | 0
24 | 0.98632 | -0.26205 | 0.033116 | 0.0082996
25 | 0.98171 | -0.35148 | 0 | 0
26 | 0.97931 | -0.39846 | 0 | 0
27 | 0.97901 | -0.40436 | 0.013423 | 0.003364
28 | 0.97646 | -0.45437 | 0.016324 | 0.0040911
29 | 0.99263 | -0.14054 | 0.014943 | 0.0037451
30 | 0.98672 | -0.25437 | 0 | 0
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0049274 | 0.0012346 | -0.0049271 | -0.0012346 | 3.398e-07 | -2.1081e-09 | 0.0073448 | 0.0073448 | 0.0073448 | 0.99825 | -0.033553 | 0.99818 | -0.035001 | 2.0178
1 | -0.027398 | -0.0068663 | 0.027414 | 0.0068759 | 1.5594e-05 | 9.6539e-06 | 0.04084 | 0.04084 | 0.04084 | 0.99825 | -0.033553 | 0.99888 | -0.021613 | 11.2197
2 | 0.0049271 | 0.0012346 | -0.0049264 | -0.0012346 | 6.2269e-07 | -3.7653e-09 | 0.0073448 | 0.007345 | 0.007345 | 0.99818 | -0.035001 | 0.99804 | -0.037654 | 2.0179
3 | -0.042595 | -0.010683 | 0.042638 | 0.010711 | 4.3928e-05 | 2.7733e-05 | 0.063455 | 0.063455 | 0.063455 | 0.99888 | -0.021613 | 1 | 0 | 17.4328
4 | 0.015181 | 0.0038069 | -0.015177 | -0.0038049 | 3.6106e-06 | 2.0644e-06 | 0.022616 | 0.022616 | 0.022616 | 0.99888 | -0.021613 | 0.99862 | -0.026604 | 6.2131
5 | 0.0049264 | 0.0012346 | -0.0049262 | -0.0012346 | 2.6633e-07 | -1.5718e-09 | 0.007345 | 0.007345 | 0.007345 | 0.99804 | -0.037654 | 0.99798 | -0.038789 | 2.0179
6 | 0.25643 | 0.065185 | -0.25599 | -0.064904 | 0.0004396 | 0.00028092 | 0.3819 | 0.3819 | 0.3819 | 1 | 0 | 0.99813 | -0.035661 | 52.4583
7 | 0.015177 | 0.0038049 | -0.015174 | -0.003803 | 3.3361e-06 | 1.9076e-06 | 0.022616 | 0.022616 | 0.022616 | 0.99862 | -0.026604 | 0.99838 | -0.031218 | 6.2131
8 | -0.0057044 | -0.0014296 | 0.0057051 | 0.0014297 | 7.0447e-07 | 1.2114e-07 | 0.0085669 | 0.0085667 | 0.0085669 | 0.99081 | -0.17546 | 0.99095 | -0.17287 | 2.3535
9 | 0.0057044 | 0.0014296 | -0.0057039 | -0.0014295 | 4.7688e-07 | 8.2058e-08 | 0.0085669 | 0.0085669 | 0.0085669 | 0.99081 | -0.17546 | 0.99072 | -0.17721 | 2.3536
10 | -0.0057051 | -0.0014297 | 0.0057055 | 0.0014298 | 4.5896e-07 | 7.8868e-08 | 0.0085667 | 0.0085667 | 0.0085667 | 0.99095 | -0.17287 | 0.99103 | -0.17118 | 2.3535
11 | -0.013876 | -0.0034775 | 0.013879 | 0.003479 | 2.525e-06 | 1.4161e-06 | 0.020835 | 0.020834 | 0.020835 | 0.99103 | -0.17118 | 0.99123 | -0.16736 | 5.7238
12 | -0.031333 | -0.0078564 | 0.03136 | 0.0078735 | 2.7318e-05 | 1.7082e-05 | 0.047722 | 0.047721 | 0.047722 | 0.97703 | -0.44316 | 0.97796 | -0.42488 | 13.1103
13 | 0.031333 | 0.0078564 | -0.03133 | -0.0078543 | 3.4528e-06 | 2.1592e-06 | 0.047722 | 0.047722 | 0.047722 | 0.97703 | -0.44316 | 0.97692 | -0.44547 | 13.1103
14 | -0.03136 | -0.0078735 | 0.031385 | 0.007889 | 2.4752e-05 | 1.5477e-05 | 0.047721 | 0.047721 | 0.047721 | 0.97796 | -0.42488 | 0.97881 | -0.40835 | 13.1103
15 | 0.016331 | 0.0040952 | -0.016329 | -0.0040943 | 1.5673e-06 | 9.1849e-07 | 0.024875 | 0.024876 | 0.024876 | 0.97692 | -0.44547 | 0.97681 | -0.44749 | 6.8339
16 | 0.17717 | 0.045149 | -0.17687 | -0.04496 | 0.00029625 | 0.00018901 | 0.26439 | 0.26439 | 0.26439 | 0.99813 | -0.035661 | 0.99631 | -0.070375 | 36.3171
17 | -0.071897 | -0.01813 | 0.071929 | 0.01815 | 3.126e-05 | 1.9917e-05 | 0.10888 | 0.10888 | 0.10888 | 0.9829 | -0.32831 | 0.98337 | -0.31923 | 29.9134
18 | 0.071897 | 0.01813 | -0.071859 | -0.018105 | 3.8637e-05 | 2.4618e-05 | 0.10888 | 0.10888 | 0.10888 | 0.9829 | -0.32831 | 0.98233 | -0.33954 | 29.9134
19 | -0.071929 | -0.01815 | 0.072126 | 0.018276 | 0.00019756 | 0.00012587 | 0.10888 | 0.10888 | 0.10888 | 0.98337 | -0.31923 | 0.98632 | -0.26205 | 29.9134
20 | 0.058405 | 0.014734 | -0.058372 | -0.014713 | 3.3363e-05 | 2.1209e-05 | 0.088506 | 0.088506 | 0.088506 | 0.98233 | -0.33954 | 0.98171 | -0.35148 | 24.3149
21 | -0.041696 | -0.01045 | 0.041718 | 0.010463 | 2.1193e-05 | 1.3374e-05 | 0.06231 | 0.06231 | 0.06231 | 0.99575 | -0.081038 | 0.99631 | -0.070375 | 17.118
22 | 0.13515 | 0.034496 | -0.1347 | -0.034205 | 0.00045653 | 0.00029179 | 0.20208 | 0.20208 | 0.20208 | 0.99631 | -0.070375 | 0.99263 | -0.14054 | 55.5164
23 | -0.1196 | -0.030361 | 0.11975 | 0.03046 | 0.00015451 | 9.8721e-05 | 0.17968 | 0.17968 | 0.17968 | 0.99123 | -0.16736 | 0.99263 | -0.14054 | 49.3624
24 | 0.10572 | 0.026882 | -0.10528 | -0.0266 | 0.00044111 | 0.00028171 | 0.15884 | 0.15885 | 0.15885 | 0.99123 | -0.16736 | 0.98672 | -0.25437 | 43.6388
25 | -0.044794 | -0.011249 | 0.044802 | 0.011255 | 8.5317e-06 | 5.3986e-06 | 0.068105 | 0.068105 | 0.068105 | 0.97881 | -0.40835 | 0.97901 | -0.40436 | 18.7102
26 | 0.016329 | 0.0040943 | -0.016324 | -0.0040911 | 5.354e-06 | 3.1379e-06 | 0.024876 | 0.024876 | 0.024876 | 0.97681 | -0.44749 | 0.97646 | -0.45437 | 6.834
27 | -0.10524 | -0.026575 | 0.10528 | 0.0266 | 3.8745e-05 | 2.4744e-05 | 0.15885 | 0.15885 | 0.15885 | 0.98632 | -0.26205 | 0.98672 | -0.25437 | 43.6388
28 | 0.058372 | 0.014713 | -0.058241 | -0.014629 | 0.00013089 | 8.321e-05 | 0.088506 | 0.088506 | 0.088506 | 0.98171 | -0.35148 | 0.97931 | -0.39846 | 24.3149
29 | 0.058241 | 0.014629 | -0.058225 | -0.014619 | 1.638e-05 | 1.0413e-05 | 0.088506 | 0.088506 | 0.088506 | 0.97931 | -0.39846 | 0.97901 | -0.40436 | 24.3149

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32261 | 0.081381

## res_load
| p_mw | q_mvar
0 | 0.022471 | 0.0056317
1 | 0.021888 | 0.0054856
2 | 0.0049262 | 0.0012346
3 | 0.0057039 | 0.0014295
4 | 0.0081705 | 0.0020477
5 | 0.014999 | 0.0037591
6 | 0.078822 | 0.019755
7 | 0.015174 | 0.003803
8 | 0.013453 | 0.0033717
9 | 0.041696 | 0.01045
10 | 0.013408 | 0.0033604
11 | 0.033116 | 0.0082996
12 | 0.013423 | 0.003364
13 | 0.016324 | 0.0040911
14 | 0.014943 | 0.0037451

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1