## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2534-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2534-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2534-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2534-2_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2534-2_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2534-2_0_5_node_113 | 0.4 | n |  | TRUE
6 | bus_LV_2534-2_0_5_node_110 | 0.4 | n |  | TRUE
7 | bus_LV_2534-2_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2534-2_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2534-2_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2534-2_0_5_node_143 | 0.4 | n |  | TRUE
11 | bus_LV_2534-2_0_5_node_140 | 0.4 | n |  | TRUE
12 | bus_LV_2534-2_0_5_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2534-2_0_5_node_137 | 0.4 | n |  | TRUE
14 | bus_LV_2534-2_0_5_node_108 | 0.4 | n |  | TRUE
15 | bus_LV_2534-2_0_5_node_109 | 0.4 | n |  | TRUE
16 | bus_LV_2534-2_0_5_node_107 | 0.4 | n |  | TRUE
17 | bus_LV_2534-2_0_5_node_112 | 0.4 | n |  | TRUE
18 | bus_LV_2534-2_0_5_node_134 | 0.4 | n |  | TRUE
19 | bus_LV_2534-2_0_5_node_115 | 0.4 | n |  | TRUE
20 | bus_LV_2534-2_0_5_node_119 | 0.4 | n |  | TRUE
21 | bus_LV_2534-2_0_5_node_136 | 0.4 | n |  | TRUE
22 | bus_LV_2534-2_0_5_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_2534-2_0_5_node_138 | 0.4 | n |  | TRUE
24 | bus_LV_2534-2_0_5_node_117 | 0.4 | n |  | TRUE
25 | bus_LV_2534-2_0_5_node_116 | 0.4 | n |  | TRUE
26 | bus_LV_2534-2_0_5_node_135 | 0.4 | n |  | TRUE
27 | bus_LV_2534-2_0_5_node_139 | 0.4 | n |  | TRUE
28 | bus_LV_2534-2_0_5_node_151 | 0.4 | n |  | TRUE
29 | bus_LV_2534-2_0_5_node_118 | 0.4 | n |  | TRUE
30 | bus_LV_2534-2_0_5_node_150 | 0.4 | n |  | TRUE
31 | bus_LV_2534-2_0_5_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2534-2_0_5_node_133 | 0.4 | n |  | TRUE
33 | bus_LV_2534-2_0_5_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_2534-2_0_5_node_111 | 0.4 | n |  | TRUE
35 | bus_LV_2534-2_0_5_node_141 | 0.4 | n |  | TRUE
36 | bus_LV_2534-2_0_5_node_142 | 0.4 | n |  | TRUE
37 | bus_LV_2534-2_0_5_node_9 | 0.4 | n |  | TRUE
38 | bus_LV_2534-2_0_5_node_146 | 0.4 | n |  | TRUE
39 | bus_LV_2534-2_0_5_node_147 | 0.4 | n |  | TRUE
40 | bus_LV_2534-2_0_5_node_145 | 0.4 | n |  | TRUE
41 | bus_LV_2534-2_0_5_node_144 | 0.4 | n |  | TRUE
42 | bus_LV_2534-2_0_5_node_10 | 0.4 | n |  | TRUE
43 | bus_LV_2534-2_0_5_node_11 | 0.4 | n |  | TRUE
44 | bus_LV_2534-2_0_5_node_12 | 0.4 | n |  | TRUE
45 | bus_LV_2534-2_0_5_node_13 | 0.4 | n |  | TRUE
46 | bus_LV_2534-2_0_5_node_16 | 0.4 | n |  | TRUE
47 | bus_LV_2534-2_0_5_node_106 | 0.4 | n |  | TRUE
48 | bus_LV_2534-2_0_5_node_104 | 0.4 | n |  | TRUE
49 | bus_LV_2534-2_0_5_node_14 | 0.4 | n |  | TRUE
50 | bus_LV_2534-2_0_5_node_65 | 0.4 | n |  | TRUE
51 | bus_LV_2534-2_0_5_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_2534-2_0_5_node_132 | 0.4 | n |  | TRUE
53 | bus_LV_2534-2_0_5_node_130 | 0.4 | n |  | TRUE
54 | bus_LV_2534-2_0_5_node_131 | 0.4 | n |  | TRUE
55 | bus_LV_2534-2_0_5_node_17 | 0.4 | n |  | TRUE
56 | bus_LV_2534-2_0_5_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_2534-2_0_5_node_18 | 0.4 | n |  | TRUE
58 | bus_LV_2534-2_0_5_node_148 | 0.4 | n |  | TRUE
59 | bus_LV_2534-2_0_5_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_2534-2_0_5_node_149 | 0.4 | n |  | TRUE
61 | bus_LV_2534-2_0_5_node_105 | 0.4 | n |  | TRUE
62 | bus_LV_2534-2_0_5_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_2534-2_0_5_node_68 | 0.4 | n |  | TRUE
64 | bus_LV_2534-2_0_5_node_129 | 0.4 | n |  | TRUE
65 | bus_LV_2534-2_0_5_node_21 | 0.4 | n |  | TRUE
66 | bus_LV_2534-2_0_5_node_22 | 0.4 | n |  | TRUE
67 | bus_LV_2534-2_0_5_node_23 | 0.4 | n |  | TRUE
68 | bus_LV_2534-2_0_5_node_24 | 0.4 | n |  | TRUE
69 | bus_LV_2534-2_0_5_node_25 | 0.4 | n |  | TRUE
70 | bus_LV_2534-2_0_5_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2534-2_0_5_node_84 | 0.4 | n |  | TRUE
72 | bus_LV_2534-2_0_5_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2534-2_0_5_node_78 | 0.4 | n |  | TRUE
74 | bus_LV_2534-2_0_5_node_35 | 0.4 | n |  | TRUE
75 | bus_LV_2534-2_0_5_node_82 | 0.4 | n |  | TRUE
76 | bus_LV_2534-2_0_5_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_2534-2_0_5_node_26 | 0.4 | n |  | TRUE
78 | bus_LV_2534-2_0_5_node_27 | 0.4 | n |  | TRUE
79 | bus_LV_2534-2_0_5_node_28 | 0.4 | n |  | TRUE
80 | bus_LV_2534-2_0_5_node_29 | 0.4 | n |  | TRUE
81 | bus_LV_2534-2_0_5_node_31 | 0.4 | n |  | TRUE
82 | bus_LV_2534-2_0_5_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_2534-2_0_5_node_43 | 0.4 | n |  | TRUE
84 | bus_LV_2534-2_0_5_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_2534-2_0_5_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_2534-2_0_5_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_2534-2_0_5_node_32 | 0.4 | n |  | TRUE
88 | bus_LV_2534-2_0_5_node_33 | 0.4 | n |  | TRUE
89 | bus_LV_2534-2_0_5_node_36 | 0.4 | n |  | TRUE
90 | bus_LV_2534-2_0_5_node_94 | 0.4 | n |  | TRUE
91 | bus_LV_2534-2_0_5_node_95 | 0.4 | n |  | TRUE
92 | bus_LV_2534-2_0_5_node_39 | 0.4 | n |  | TRUE
93 | bus_LV_2534-2_0_5_node_40 | 0.4 | n |  | TRUE
94 | bus_LV_2534-2_0_5_node_62 | 0.4 | n |  | TRUE
95 | bus_LV_2534-2_0_5_node_61 | 0.4 | n |  | TRUE
96 | bus_LV_2534-2_0_5_node_41 | 0.4 | n |  | TRUE
97 | bus_LV_2534-2_0_5_node_42 | 0.4 | n |  | TRUE
98 | bus_LV_2534-2_0_5_node_48 | 0.4 | n |  | TRUE
99 | bus_LV_2534-2_0_5_node_54 | 0.4 | n |  | TRUE
100 | bus_LV_2534-2_0_5_node_49 | 0.4 | n |  | TRUE
101 | bus_LV_2534-2_0_5_node_56 | 0.4 | n |  | TRUE
102 | bus_LV_2534-2_0_5_node_52 | 0.4 | n |  | TRUE
103 | bus_LV_2534-2_0_5_node_46 | 0.4 | n |  | TRUE
104 | bus_LV_2534-2_0_5_node_47 | 0.4 | n |  | TRUE
105 | bus_LV_2534-2_0_5_node_71 | 0.4 | n |  | TRUE
106 | bus_LV_2534-2_0_5_node_128 | 0.4 | n |  | TRUE
107 | bus_LV_2534-2_0_5_node_51 | 0.4 | n |  | TRUE
108 | bus_LV_2534-2_0_5_node_53 | 0.4 | n |  | TRUE
109 | bus_LV_2534-2_0_5_node_55 | 0.4 | n |  | TRUE
110 | bus_LV_2534-2_0_5_node_57 | 0.4 | n |  | TRUE
111 | bus_LV_2534-2_0_5_node_60 | 0.4 | n |  | TRUE
112 | bus_LV_2534-2_0_5_node_63 | 0.4 | n |  | TRUE
113 | bus_LV_2534-2_0_5_node_64 | 0.4 | n |  | TRUE
114 | bus_LV_2534-2_0_5_node_66 | 0.4 | n |  | TRUE
115 | bus_LV_2534-2_0_5_node_73 | 0.4 | n |  | TRUE
116 | bus_LV_2534-2_0_5_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_2534-2_0_5_node_123 | 0.4 | n |  | TRUE
118 | bus_LV_2534-2_0_5_node_127 | 0.4 | n |  | TRUE
119 | bus_LV_2534-2_0_5_node_125 | 0.4 | n |  | TRUE
120 | bus_LV_2534-2_0_5_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_2534-2_0_5_node_92 | 0.4 | n |  | TRUE
122 | bus_LV_2534-2_0_5_node_93 | 0.4 | n |  | TRUE
123 | bus_LV_2534-2_0_5_node_79 | 0.4 | n |  | TRUE
124 | bus_LV_2534-2_0_5_node_80 | 0.4 | n |  | TRUE
125 | bus_LV_2534-2_0_5_node_81 | 0.4 | n |  | TRUE
126 | bus_LV_2534-2_0_5_node_83 | 0.4 | n |  | TRUE
127 | bus_LV_2534-2_0_5_node_98 | 0.4 | n |  | TRUE
128 | bus_LV_2534-2_0_5_node_103 | 0.4 | n |  | TRUE
129 | bus_LV_2534-2_0_5_node_97 | 0.4 | n |  | TRUE
130 | bus_LV_2534-2_0_5_node_85 | 0.4 | n |  | TRUE
131 | bus_LV_2534-2_0_5_node_86 | 0.4 | n |  | TRUE
132 | bus_LV_2534-2_0_5_node_88 | 0.4 | n |  | TRUE
133 | bus_LV_2534-2_0_5_node_96 | 0.4 | n |  | TRUE
134 | bus_LV_2534-2_0_5_node_90 | 0.4 | n |  | TRUE
135 | bus_LV_2534-2_0_5_node_89 | 0.4 | n |  | TRUE
136 | bus_LV_2534-2_0_5_node_91 | 0.4 | n |  | TRUE
137 | bus_LV_2534-2_0_5_node_102 | 0.4 | n |  | TRUE
138 | bus_LV_2534-2_0_5_node_99 | 0.4 | n |  | TRUE
139 | bus_LV_2534-2_0_5_node_101 | 0.4 | n |  | TRUE
140 | bus_LV_2534-2_0_5_node_120 | 0.4 | n |  | TRUE
141 | bus_MV_394_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2534-2_0_5_load_0 | 0 | 0.026253 | 0.0065796 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2534-2_0_5_load_1 | 1 | 0.0035568 | 0.00089141 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2534-2_0_5_load_110 | 6 | 0.026894 | 0.0067402 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2534-2_0_5_load_7 | 8 | 0.0266 | 0.0066667 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2534-2_0_5_load_143 | 10 | 0.010587 | 0.0026535 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2534-2_0_5_load_137 | 13 | 0.010553 | 0.0026449 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2534-2_0_5_load_109 | 15 | 0.0070989 | 0.0017792 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2534-2_0_5_load_134 | 18 | 0.0086418 | 0.0021658 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2534-2_0_5_load_136 | 21 | 0.0099534 | 0.0024946 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2534-2_0_5_load_138 | 23 | 0.0067073 | 0.001681 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2534-2_0_5_load_135 | 26 | 0.010494 | 0.00263 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2534-2_0_5_load_139 | 27 | 0.0085957 | 0.0021543 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2534-2_0_5_load_151 | 28 | 0.0062765 | 0.001573 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2534-2_0_5_load_150 | 30 | 0.0090854 | 0.002277 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2534-2_0_5_load_133 | 32 | 0.0091903 | 0.0023033 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2534-2_0_5_load_111 | 34 | 0.0041665 | 0.0010442 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2534-2_0_5_load_141 | 35 | 0.0089472 | 0.0022424 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2534-2_0_5_load_146 | 38 | 0.0068782 | 0.0017238 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2534-2_0_5_load_147 | 39 | 0.0068749 | 0.001723 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2534-2_0_5_load_145 | 40 | 0.0099986 | 0.0025059 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2534-2_0_5_load_144 | 41 | 0.0090892 | 0.002278 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2534-2_0_5_load_10 | 42 | 0.016681 | 0.0041807 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2534-2_0_5_load_106 | 47 | 0.018279 | 0.0045811 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2534-2_0_5_load_104 | 48 | 0.034515 | 0.0086503 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2534-2_0_5_load_76 | 51 | 0.020534 | 0.0051464 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2534-2_0_5_load_132 | 52 | 0.0085477 | 0.0021422 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2534-2_0_5_load_130 | 53 | 0.00072413 | 0.00018148 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2534-2_0_5_load_131 | 54 | 0.00068255 | 0.00017106 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2534-2_0_5_load_148 | 58 | 0.0090836 | 0.0022766 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2534-2_0_5_load_149 | 60 | 0.0085462 | 0.0021419 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2534-2_0_5_load_105 | 61 | 0.016691 | 0.0041832 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2534-2_0_5_load_67 | 62 | 0.012837 | 0.0032172 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2534-2_0_5_load_129 | 64 | 0.0084863 | 0.0021269 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2534-2_0_5_load_21 | 65 | 0.0053707 | 0.001346 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2534-2_0_5_load_22 | 66 | 0.0061354 | 0.0015377 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2534-2_0_5_load_23 | 67 | 0.0042818 | 0.0010731 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2534-2_0_5_load_25 | 69 | 0.0031677 | 0.00079389 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2534-2_0_5_load_58 | 72 | 0.0015872 | 0.00039778 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2534-2_0_5_load_78 | 73 | 0.0022801 | 0.00057144 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2534-2_0_5_load_35 | 74 | 0.0054037 | 0.0013543 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2534-2_0_5_load_82 | 75 | 0.0049931 | 0.0012514 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2534-2_0_5_load_59 | 76 | 0.0033753 | 0.00084594 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2534-2_0_5_load_26 | 77 | 0.0011925 | 0.00029887 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2534-2_0_5_load_27 | 78 | 0.0011909 | 0.00029847 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2534-2_0_5_load_29 | 80 | 0.0011913 | 0.00029858 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2534-2_0_5_load_31 | 81 | 0.0011892 | 0.00029803 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2534-2_0_5_load_75 | 84 | 0.0019266 | 0.00048285 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2534-2_0_5_load_70 | 85 | 0.0036942 | 0.00092584 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2534-2_0_5_load_44 | 86 | 0.0011829 | 0.00029647 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2534-2_0_5_load_32 | 87 | 0.0051727 | 0.0012964 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2534-2_0_5_load_94 | 90 | 0.0025127 | 0.00062974 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2534-2_0_5_load_95 | 91 | 0.0031304 | 0.00078455 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2534-2_0_5_load_39 | 92 | 0.0020467 | 0.00051296 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2534-2_0_5_load_62 | 94 | 0.0051616 | 0.0012936 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2534-2_0_5_load_41 | 96 | 0.0044063 | 0.0011043 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2534-2_0_5_load_42 | 97 | 0.0023867 | 0.00059817 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2534-2_0_5_load_48 | 98 | 0.024629 | 0.0061727 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2534-2_0_5_load_49 | 100 | 0.0043635 | 0.0010936 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2534-2_0_5_load_56 | 101 | 0.0019613 | 0.00049155 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2534-2_0_5_load_52 | 102 | 0.0051974 | 0.0013026 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2534-2_0_5_load_47 | 104 | 0.0021576 | 0.00054074 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2534-2_0_5_load_128 | 106 | 0.0016276 | 0.00040793 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2534-2_0_5_load_51 | 107 | 0.0023843 | 0.00059755 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2534-2_0_5_load_53 | 108 | 0.0020672 | 0.00051809 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2534-2_0_5_load_55 | 109 | 0.0015494 | 0.00038831 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2534-2_0_5_load_60 | 111 | 0.0022754 | 0.00057026 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2534-2_0_5_load_63 | 112 | 0.0021577 | 0.00054078 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2534-2_0_5_load_64 | 113 | 0.0042481 | 0.0010647 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2534-2_0_5_load_66 | 114 | 0.0040367 | 0.0010117 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2534-2_0_5_load_73 | 115 | 0.0019266 | 0.00048284 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2534-2_0_5_load_122 | 116 | 0.0046677 | 0.0011698 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2534-2_0_5_load_127 | 118 | 0.0016127 | 0.00040419 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2534-2_0_5_load_126 | 120 | 0.0016039 | 0.00040197 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2534-2_0_5_load_92 | 121 | 0.0024936 | 0.00062495 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2534-2_0_5_load_93 | 122 | 0.0034758 | 0.00087113 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2534-2_0_5_load_79 | 123 | 0.0027635 | 0.00069259 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2534-2_0_5_load_80 | 124 | 0.0040337 | 0.0010109 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2534-2_0_5_load_81 | 125 | 0.0032346 | 0.00081066 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2534-2_0_5_load_83 | 126 | 0.0032841 | 0.00082307 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2534-2_0_5_load_103 | 128 | 0.0055147 | 0.0013821 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2534-2_0_5_load_97 | 129 | 0.0014872 | 0.00037273 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2534-2_0_5_load_85 | 130 | 0.0019284 | 0.00048331 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2534-2_0_5_load_86 | 131 | 0.0029766 | 0.00074602 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2534-2_0_5_load_96 | 133 | 0.0021391 | 0.00053611 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2534-2_0_5_load_90 | 134 | 0.0018781 | 0.00047069 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2534-2_0_5_load_89 | 135 | 0.0016362 | 0.00041006 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2534-2_0_5_load_91 | 136 | 0.0018792 | 0.00047098 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2534-2_0_5_load_99 | 138 | 0.0029587 | 0.00074152 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2534-2_0_5_load_120 | 140 | 0.0048714 | 0.0012209 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2534-2_0_5_line_0 |  | 0 | 1 | 0.035767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2534-2_0_5_line_1 |  | 0 | 2 | 0.052694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2534-2_0_5_line_2 |  | 2 | 3 | 0.042828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2534-2_0_5_line_3 |  | 2 | 4 | 0.040002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2534-2_0_5_line_4 |  | 3 | 5 | 0.065307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2534-2_0_5_line_5 |  | 3 | 6 | 0.055538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2534-2_0_5_line_6 |  | 4 | 7 | 0.078052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2534-2_0_5_line_7 |  | 4 | 8 | 0.055334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2534-2_0_5_line_8 |  | 5 | 21 | 0.005617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2534-2_0_5_line_9 |  | 5 | 19 | 0.05175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2534-2_0_5_line_10 |  | 5 | 12 | 0.016027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2534-2_0_5_line_11 |  | 6 | 34 | 0.034401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2534-2_0_5_line_12 |  | 7 | 35 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2534-2_0_5_line_13 |  | 7 | 36 | 0.01633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2534-2_0_5_line_14 |  | 7 | 37 | 0.081999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2534-2_0_5_line_15 |  | 9 | 10 | 0.00981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2534-2_0_5_line_16 |  | 9 | 11 | 0.016677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2534-2_0_5_line_17 |  | 9 | 12 | 0.060304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2534-2_0_5_line_18 |  | 11 | 40 | 0.006375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2534-2_0_5_line_19 |  | 11 | 25 | 0.034496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2534-2_0_5_line_20 |  | 12 | 13 | 0.004513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2534-2_0_5_line_21 |  | 14 | 15 | 0.013073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2534-2_0_5_line_22 |  | 14 | 16 | 0.01147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2534-2_0_5_line_23 |  | 15 | 71 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2534-2_0_5_line_24 |  | 16 | 47 | 0.030299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2534-2_0_5_line_25 |  | 16 | 114 | 0.004021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2534-2_0_5_line_26 |  | 17 | 18 | 0.003812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2534-2_0_5_line_27 |  | 17 | 19 | 0.016648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2534-2_0_5_line_28 |  | 17 | 20 | 0.054893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2534-2_0_5_line_29 |  | 19 | 26 | 0.004064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2534-2_0_5_line_30 |  | 20 | 32 | 0.003633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2534-2_0_5_line_31 |  | 20 | 33 | 0.014536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2534-2_0_5_line_32 |  | 22 | 23 | 0.004514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2534-2_0_5_line_33 |  | 22 | 24 | 0.016357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2534-2_0_5_line_34 |  | 22 | 25 | 0.040523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2534-2_0_5_line_35 |  | 24 | 28 | 0.006628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2534-2_0_5_line_36 |  | 24 | 29 | 0.033169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2534-2_0_5_line_37 |  | 25 | 27 | 0.004769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2534-2_0_5_line_38 |  | 29 | 30 | 0.007056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2534-2_0_5_line_39 |  | 29 | 31 | 0.015973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2534-2_0_5_line_40 |  | 31 | 60 | 0.005368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2534-2_0_5_line_41 |  | 31 | 57 | 0.036872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2534-2_0_5_line_42 |  | 33 | 52 | 0.004287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2534-2_0_5_line_43 |  | 33 | 46 | 0.030522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2534-2_0_5_line_44 |  | 36 | 41 | 0.010083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2534-2_0_5_line_45 |  | 37 | 38 | 0.027008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2534-2_0_5_line_46 |  | 37 | 39 | 0.009895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2534-2_0_5_line_47 |  | 42 | 43 | 0.013586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2534-2_0_5_line_48 |  | 42 | 44 | 0.038914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2534-2_0_5_line_49 |  | 43 | 45 | 0.046575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2534-2_0_5_line_50 |  | 44 | 46 | 0.05654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2534-2_0_5_line_51 |  | 45 | 47 | 0.021701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2534-2_0_5_line_52 |  | 45 | 48 | 0.014595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2534-2_0_5_line_53 |  | 46 | 53 | 0.003584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2534-2_0_5_line_54 |  | 46 | 54 | 0.019787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2534-2_0_5_line_55 |  | 48 | 61 | 0.016656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2534-2_0_5_line_56 |  | 49 | 50 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2534-2_0_5_line_57 |  | 49 | 51 | 0.022414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2534-2_0_5_line_58 |  | 50 | 62 | 0.005362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2534-2_0_5_line_59 |  | 51 | 55 | 0.04258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2534-2_0_5_line_60 |  | 55 | 56 | 0.029244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2534-2_0_5_line_61 |  | 56 | 63 | 0.02688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2534-2_0_5_line_62 |  | 57 | 58 | 0.005327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2534-2_0_5_line_63 |  | 57 | 59 | 0.015259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2534-2_0_5_line_64 |  | 59 | 64 | 0.008447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2534-2_0_5_line_65 |  | 63 | 105 | 0.038514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2534-2_0_5_line_66 |  | 63 | 106 | 0.032912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2534-2_0_5_line_67 |  | 65 | 66 | 0.023152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2534-2_0_5_line_68 |  | 65 | 67 | 0.0039913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2534-2_0_5_line_69 |  | 66 | 68 | 0.023532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2534-2_0_5_line_70 |  | 67 | 69 | 0.013871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2534-2_0_5_line_71 |  | 68 | 70 | 0.040082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2534-2_0_5_line_72 |  | 68 | 71 | 0.00345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2534-2_0_5_line_73 |  | 69 | 72 | 0.018925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2534-2_0_5_line_74 |  | 70 | 73 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2534-2_0_5_line_75 |  | 70 | 74 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2534-2_0_5_line_76 |  | 71 | 75 | 0.014666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2534-2_0_5_line_77 |  | 72 | 76 | 0.00042575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2534-2_0_5_line_78 |  | 73 | 121 | 0.0023361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2534-2_0_5_line_79 |  | 74 | 88 | 0.02108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2534-2_0_5_line_80 |  | 75 | 124 | 0.018778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2534-2_0_5_line_81 |  | 76 | 110 | 0.012747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2534-2_0_5_line_82 |  | 77 | 78 | 0.01649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2534-2_0_5_line_83 |  | 77 | 79 | 0.01606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2534-2_0_5_line_84 |  | 78 | 80 | 0.016907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2534-2_0_5_line_85 |  | 79 | 81 | 0.00059817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2534-2_0_5_line_86 |  | 80 | 82 | 0.016577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2534-2_0_5_line_87 |  | 81 | 83 | 0.029575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2534-2_0_5_line_88 |  | 82 | 84 | 0.013223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2534-2_0_5_line_89 |  | 82 | 85 | 0.019794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2534-2_0_5_line_90 |  | 83 | 86 | 0.019689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2534-2_0_5_line_91 |  | 85 | 105 | 0.0080082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2534-2_0_5_line_92 |  | 86 | 103 | 0.022988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2534-2_0_5_line_93 |  | 87 | 88 | 0.044325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2534-2_0_5_line_94 |  | 88 | 89 | 0.004512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2534-2_0_5_line_95 |  | 89 | 90 | 0.011475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2534-2_0_5_line_96 |  | 90 | 91 | 0.021629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2534-2_0_5_line_97 |  | 92 | 93 | 0.027904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2534-2_0_5_line_98 |  | 93 | 96 | 0.039455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2534-2_0_5_line_99 |  | 93 | 97 | 0.023052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2534-2_0_5_line_100 |  | 94 | 95 | 0.0017241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2534-2_0_5_line_101 |  | 95 | 111 | 0.020307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2534-2_0_5_line_102 |  | 96 | 98 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2534-2_0_5_line_103 |  | 97 | 99 | 0.018186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2534-2_0_5_line_104 |  | 98 | 100 | 0.023185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2534-2_0_5_line_105 |  | 99 | 101 | 0.025354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2534-2_0_5_line_106 |  | 99 | 102 | 0.0018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2534-2_0_5_line_107 |  | 101 | 104 | 0.027455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2534-2_0_5_line_108 |  | 102 | 107 | 0.0083087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
109 | LV_2534-2_0_5_line_109 |  | 103 | 104 | 0.0158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2534-2_0_5_line_110 |  | 105 | 115 | 0.016887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2534-2_0_5_line_111 |  | 107 | 108 | 0.015981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2534-2_0_5_line_112 |  | 108 | 109 | 0.016108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2534-2_0_5_line_113 |  | 109 | 110 | 0.012015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2534-2_0_5_line_114 |  | 110 | 111 | 0.018329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2534-2_0_5_line_115 |  | 112 | 113 | 0.047701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2534-2_0_5_line_116 |  | 113 | 114 | 0.011647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2534-2_0_5_line_117 |  | 115 | 116 | 0.017865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2534-2_0_5_line_118 |  | 116 | 117 | 0.014678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2534-2_0_5_line_119 |  | 117 | 119 | 0.034066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2534-2_0_5_line_120 |  | 118 | 119 | 0.020033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2534-2_0_5_line_121 |  | 119 | 120 | 0.055486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2534-2_0_5_line_122 |  | 119 | 140 | 0.058873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2534-2_0_5_line_123 |  | 121 | 122 | 0.0056521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2534-2_0_5_line_124 |  | 123 | 124 | 0.020032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2534-2_0_5_line_125 |  | 123 | 125 | 0.0077498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2534-2_0_5_line_126 |  | 125 | 126 | 0.023967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2534-2_0_5_line_127 |  | 126 | 127 | 0.0092715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2534-2_0_5_line_128 |  | 127 | 128 | 0.0096785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2534-2_0_5_line_129 |  | 127 | 129 | 0.018211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2534-2_0_5_line_130 |  | 128 | 137 | 0.023742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2534-2_0_5_line_131 |  | 129 | 133 | 0.023255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2534-2_0_5_line_132 |  | 130 | 131 | 0.020696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2534-2_0_5_line_133 |  | 131 | 132 | 0.015004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2534-2_0_5_line_134 |  | 132 | 133 | 0.011498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2534-2_0_5_line_135 |  | 132 | 134 | 0.031816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2534-2_0_5_line_136 |  | 134 | 135 | 0.0028723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2534-2_0_5_line_137 |  | 135 | 136 | 0.002975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2534-2_0_5_line_138 |  | 137 | 139 | 0.052906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2534-2_0_5_line_139 |  | 138 | 139 | 0.016232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2534-2_0_5_trafo_104 | 0.63 MVA 20/0.4 kV | 141 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2609338.7224 | 1229047.909 | 2609371.3571 | 1229062.547
1 | 2609419.4361 | 1229084.1125 | 2609371.3571 | 1229062.547
2 | 2609433.083 | 1229043.5099 | 2609419.4361 | 1229084.1125
3 | 2609419.4361 | 1229084.1125 | 2609417.5495 | 1229089.1347 | 2609405.3323 | 1229121.5459
4 | 2609433.083 | 1229043.5099 | 2609435.5795 | 1229036.1094 | 2609462.4288 | 1229044.7791 | 2609472.0697 | 1229046.5843 | 2609466.881 | 1229065.3539
5 | 2609433.083 | 1229043.5099 | 2609381.8694 | 1229022.0236
6 | 2609405.3323 | 1229121.5459 | 2609398.0902 | 1229140.8015 | 2609435.8127 | 1229157.2928 | 2609442.7902 | 1229142.5506
7 | 2609405.3323 | 1229121.5459 | 2609354.4548 | 1229099.7887
8 | 2609466.881 | 1229065.3539 | 2609461.4669 | 1229063.8
9 | 2609466.881 | 1229065.3539 | 2609472.0697 | 1229046.5843 | 2609477.5432 | 1229024.9023 | 2609479.9675 | 1229015.2893
10 | 2609466.881 | 1229065.3539 | 2609465.7535 | 1229069.3768 | 2609466.4195 | 1229074.5253 | 2609464.6291 | 1229080.9374
11 | 2609350.147 | 1229008.7147 | 2609381.8694 | 1229022.0236
12 | 2609442.7902 | 1229142.5506 | 2609432.5852 | 1229138.2765
13 | 2609449.3136 | 1229127.5742 | 2609442.7902 | 1229142.5506
14 | 2609442.7902 | 1229142.5506 | 2609435.8127 | 1229157.2928 | 2609432.4334 | 1229167.349 | 2609437.5816 | 1229174.0611 | 2609455.5053 | 1229183.4839 | 2609465.5996 | 1229181.0428 | 2609473.2351 | 1229176.5745 | 2609477.0551 | 1229170.5436
15 | 2609485.5606 | 1229099.9151 | 2609493.6423 | 1229105.509
16 | 2609502.3237 | 1229091.2588 | 2609499.9385 | 1229095.3685 | 2609493.6423 | 1229105.509
17 | 2609464.6291 | 1229080.9374 | 2609461.2313 | 1229093.0726 | 2609464.8005 | 1229106.7085 | 2609477.5718 | 1229112.0986 | 2609485.1532 | 1229113.1779 | 2609489.4203 | 1229111.8505 | 2609493.6423 | 1229105.509
18 | 2609502.3237 | 1229091.2588 | 2609497.2923 | 1229087.3262
19 | 2609502.3237 | 1229091.2588 | 2609508.5916 | 1229070.3341 | 2609512.1108 | 1229058.1769
20 | 2609464.6291 | 1229080.9374 | 2609460.2142 | 1229079.9409
21 | 2609355.2792 | 1228972.5679 | 2609342.9881 | 1228968.1146
22 | 2609355.2792 | 1228972.5679 | 2609358.41 | 1228961.5329
23 | 2609322.7979 | 1228960.7992 | 2609342.9881 | 1228968.1146
24 | 2609358.41 | 1228961.5329 | 2609377.7046 | 1228957.0938 | 2609387.9258 | 1228954.6881
25 | 2609358.41 | 1228961.5329 | 2609357.2934 | 1228958.6183 | 2609357.5044 | 1228957.7436
26 | 2609486.499 | 1229000.1018 | 2609482.7884 | 1228999.1843
27 | 2609479.9675 | 1229015.2893 | 2609484.693 | 1229006.8029 | 2609486.499 | 1229000.1018
28 | 2609486.499 | 1229000.1018 | 2609492.5874 | 1228977.7537 | 2609494.4395 | 1228970.6747 | 2609499.1346 | 1228952.727 | 2609499.8863 | 1228946.9137
29 | 2609475.9917 | 1229014.3936 | 2609479.9675 | 1229015.2893
30 | 2609499.8863 | 1228946.9137 | 2609496.3879 | 1228945.8964
31 | 2609501.4092 | 1228932.463 | 2609500.7223 | 1228940.4222 | 2609499.8863 | 1228946.9137
32 | 2609523.4973 | 1229019.8055 | 2609518.9828 | 1229019.4648
33 | 2609524.7657 | 1229003.509 | 2609524.1573 | 1229014.4701 | 2609523.4973 | 1229019.8055
34 | 2609512.1108 | 1229058.1769 | 2609518.7217 | 1229045.5354 | 2609521.4252 | 1229036.6011 | 2609523.4973 | 1229019.8055
35 | 2609524.7657 | 1229003.509 | 2609518.1301 | 1229003.1093
36 | 2609533.7324 | 1228972.0157 | 2609527.5686 | 1228984.5133 | 2609525.0776 | 1228997.9284 | 2609524.7657 | 1229003.509
37 | 2609512.1108 | 1229058.1769 | 2609507.7276 | 1229056.2688
38 | 2609527.2521 | 1228969.1815 | 2609533.7324 | 1228972.0157
39 | 2609541.4288 | 1228958.0085 | 2609536.4296 | 1228967.0948 | 2609533.7324 | 1228972.0157
40 | 2609541.4288 | 1228958.0085 | 2609536.6069 | 1228955.6216
41 | 2609541.4288 | 1228958.0085 | 2609545.3916 | 1228948.0978 | 2609547.1472 | 1228939.8291 | 2609552.0001 | 1228922.76
42 | 2609501.4092 | 1228932.463 | 2609497.2442 | 1228931.4003
43 | 2609501.4092 | 1228932.463 | 2609502.0928 | 1228926.5717 | 2609503.2214 | 1228921.8707 | 2609505.9201 | 1228916.0605 | 2609512.8927 | 1228904.6759
44 | 2609449.3136 | 1229127.5742 | 2609440.1388 | 1229123.335
45 | 2609478.4123 | 1229145.8644 | 2609482.9143 | 1229154.0097 | 2609482.6814 | 1229157.5893 | 2609477.0551 | 1229170.5436
46 | 2609469.6264 | 1229163.9835 | 2609477.0551 | 1229170.5436
47 | 2609423.8827 | 1228920.6669 | 2609437.1223 | 1228917.6193
48 | 2609471.5895 | 1228914.3606 | 2609438.1607 | 1228922.1013 | 2609437.1223 | 1228917.6193
49 | 2609423.8827 | 1228920.6669 | 2609402.8373 | 1228925.5256 | 2609409.0493 | 1228949.7164
50 | 2609471.5895 | 1228914.3606 | 2609474.2027 | 1228905.0926 | 2609478.314 | 1228906.5111 | 2609488.2707 | 1228909.9622 | 2609505.9201 | 1228916.0605 | 2609512.8927 | 1228904.6759
51 | 2609409.0493 | 1228949.7164 | 2609387.9258 | 1228954.6881
52 | 2609409.0493 | 1228949.7164 | 2609412.6785 | 1228963.8527 | 2609412.6785 | 1228963.8527
53 | 2609509.8275 | 1228902.8033 | 2609512.8927 | 1228904.6759
54 | 2609520.6807 | 1228890.2908 | 2609523.4508 | 1228891.9518 | 2609519.6313 | 1228897.5268 | 2609512.8927 | 1228904.6759
55 | 2609412.6785 | 1228963.8527 | 2609429.0838 | 1228966.7293
56 | 2609425.0901 | 1228875.5976 | 2609423.1507 | 1228865.9444 | 2609413.2756 | 1228868.3859
57 | 2609425.0901 | 1228875.5976 | 2609446.9465 | 1228870.6291
58 | 2609411.9883 | 1228863.1807 | 2609413.2756 | 1228868.3859
59 | 2609484.6262 | 1228867.3089 | 2609448.0901 | 1228875.6116 | 2609446.9465 | 1228870.6291
60 | 2609493.3523 | 1228839.395 | 2609488.4417 | 1228854.6185 | 2609484.6262 | 1228867.3089
61 | 2609493.3523 | 1228839.395 | 2609499.5484 | 1228825.6745 | 2609504.4898 | 1228814.9204
62 | 2609546.8128 | 1228921.4843 | 2609552.0001 | 1228922.76
63 | 2609556.1675 | 1228908.0801 | 2609552.0001 | 1228922.76
64 | 2609556.1675 | 1228908.0801 | 2609548.0044 | 1228905.8213
65 | 2609504.4898 | 1228814.9204 | 2609515.6042 | 1228790.7015 | 2609513.0998 | 1228779.1017
66 | 2609504.4898 | 1228814.9204 | 2609523.2555 | 1228824.2335 | 2609528.8969 | 1228825.8657 | 2609532.4312 | 1228823.3698 | 2609533.5034 | 1228821.9705
67 | 2609330.9361 | 1228935.0737 | 2609337.9541 | 1228913.0107
68 | 2609339.1639 | 1228909.2073 | 2609337.9541 | 1228913.0107
69 | 2609323.803 | 1228957.4988 | 2609330.9361 | 1228935.0737
70 | 2609343.3685 | 1228895.9888 | 2609339.1639 | 1228909.2073
71 | 2609290.2011 | 1228935.5002 | 2609323.803 | 1228957.4988
72 | 2609322.7979 | 1228960.7992 | 2609323.803 | 1228957.4988
73 | 2609343.3685 | 1228895.9888 | 2609349.1051 | 1228877.9542
74 | 2609290.2011 | 1228935.5002 | 2609281.0201 | 1228950.7591
75 | 2609290.2011 | 1228935.5002 | 2609278.8929 | 1228927.3373
76 | 2609322.7979 | 1228960.7992 | 2609317.0937 | 1228974.3108
77 | 2609349.1051 | 1228877.9542 | 2609349.2342 | 1228877.5485
78 | 2609281.0201 | 1228950.7591 | 2609279.8158 | 1228952.7608
79 | 2609261.8012 | 1228914.9996 | 2609278.8929 | 1228927.3373
80 | 2609309.7902 | 1228991.6107 | 2609317.0937 | 1228974.3108
81 | 2609353.0981 | 1228865.4009 | 2609349.2342 | 1228877.5485
82 | 2609463.0933 | 1228744.2685 | 2609448.983 | 1228735.7359
83 | 2609435.2403 | 1228727.4257 | 2609448.983 | 1228735.7359
84 | 2609463.0933 | 1228744.2685 | 2609477.562 | 1228753.015
85 | 2609434.7284 | 1228727.1163 | 2609435.2403 | 1228727.4257
86 | 2609491.7484 | 1228761.5908 | 2609477.562 | 1228753.015
87 | 2609409.4156 | 1228711.8202 | 2609434.7284 | 1228727.1163
88 | 2609491.7484 | 1228761.5908 | 2609499.8146 | 1228751.1133
89 | 2609491.7484 | 1228761.5908 | 2609501.2017 | 1228767.2981 | 2609507.4147 | 1228773.4617
90 | 2609409.4156 | 1228711.8202 | 2609400.6705 | 1228729.4609
91 | 2609513.0998 | 1228779.1017 | 2609507.4147 | 1228773.4617
92 | 2609388.2905 | 1228747.6861 | 2609392.4371 | 1228746.0695 | 2609400.6705 | 1228729.4609
93 | 2609261.8012 | 1228914.9996 | 2609287.5758 | 1228878.9389
94 | 2609258.1007 | 1228912.4034 | 2609261.8012 | 1228914.9996
95 | 2609258.1007 | 1228912.4034 | 2609251.4109 | 1228921.727
96 | 2609238.8017 | 1228939.3007 | 2609251.4109 | 1228921.727
97 | 2609385.268 | 1228776.5096 | 2609361.351 | 1228762.1353
98 | 2609385.268 | 1228776.5096 | 2609419.3549 | 1228796.379
99 | 2609385.268 | 1228776.5096 | 2609377.6123 | 1228798.253
100 | 2609320.9571 | 1228843.9603 | 2609319.5227 | 1228843.0037
101 | 2609320.9571 | 1228843.9603 | 2609337.8505 | 1228855.2296
102 | 2609428.8898 | 1228801.9369 | 2609419.3549 | 1228796.379
103 | 2609369.7019 | 1228813.7184 | 2609372.6586 | 1228812.3222 | 2609377.6123 | 1228798.253
104 | 2609428.8898 | 1228801.9369 | 2609438.9697 | 1228807.8126 | 2609448.9184 | 1228813.616
105 | 2609369.7019 | 1228813.7184 | 2609376.1584 | 1228789.2003
106 | 2609369.7019 | 1228813.7184 | 2609369.1296 | 1228815.4998
107 | 2609383.7566 | 1228762.8213 | 2609378.3672 | 1228780.8125 | 2609376.1584 | 1228789.2003
108 | 2609366.5882 | 1228823.4104 | 2609369.1296 | 1228815.4998
109 | 2609388.2905 | 1228747.6861 | 2609383.7566 | 1228762.8213
110 | 2609513.0998 | 1228779.1017 | 2609522.976 | 1228776.1379 | 2609526.8379 | 1228770.8161
111 | 2609366.5882 | 1228823.4104 | 2609361.7002 | 1228838.6252
112 | 2609361.7002 | 1228838.6252 | 2609356.7732 | 1228853.9615
113 | 2609353.0981 | 1228865.4009 | 2609356.7732 | 1228853.9615
114 | 2609353.0981 | 1228865.4009 | 2609337.8505 | 1228855.2296
115 | 2609371.4263 | 1228900.051 | 2609360.2367 | 1228946.4212
116 | 2609360.2367 | 1228946.4212 | 2609357.5044 | 1228957.7436
117 | 2609537.3305 | 1228756.3572 | 2609526.8379 | 1228770.8161
118 | 2609545.9512 | 1228744.4779 | 2609537.3305 | 1228756.3572
119 | 2609572.7894 | 1228765.5555 | 2609545.9512 | 1228744.4779
120 | 2609572.7894 | 1228765.5555 | 2609560.6131 | 1228781.4635
121 | 2609572.7894 | 1228765.5555 | 2609598.8102 | 1228785.987 | 2609584.9322 | 1228803.5732
122 | 2609572.7894 | 1228765.5555 | 2609631.6571 | 1228764.7602
123 | 2609276.9018 | 1228957.6038 | 2609279.8158 | 1228952.7608
124 | 2609301.9989 | 1229010.0658 | 2609309.7902 | 1228991.6107
125 | 2609301.9989 | 1229010.0658 | 2609298.9848 | 1229017.2055
126 | 2609298.9848 | 1229017.2055 | 2609289.6632 | 1229039.2856
127 | 2609286.0572 | 1229047.8271 | 2609289.6632 | 1229039.2856
128 | 2609286.0572 | 1229047.8271 | 2609281.7044 | 1229056.4716
129 | 2609286.0572 | 1229047.8271 | 2609271.7872 | 1229036.5125
130 | 2609271.0265 | 1229077.6771 | 2609281.7044 | 1229056.4716
131 | 2609253.5654 | 1229022.0646 | 2609271.7872 | 1229036.5125
132 | 2609217.2727 | 1228991.8975 | 2609233.0896 | 1229005.245
133 | 2609244.5561 | 1229014.9212 | 2609233.0896 | 1229005.245
134 | 2609244.5561 | 1229014.9212 | 2609253.5654 | 1229022.0646
135 | 2609244.5561 | 1229014.9212 | 2609261.5755 | 1228988.0403
136 | 2609263.112 | 1228985.6136 | 2609261.5755 | 1228988.0403
137 | 2609264.7034 | 1228983.1001 | 2609263.112 | 1228985.6136
138 | 2609229.1002 | 1229045.4265 | 2609247.7735 | 1229060.442 | 2609268.2874 | 1229075.5716 | 2609271.0265 | 1229077.6771
139 | 2609229.1002 | 1229045.4265 | 2609216.4933 | 1229035.2013

## bus_geodata
| x | y | coords
0 | 2609371.3571 | 1229062.547
1 | 2609338.7224 | 1229047.909
2 | 2609419.4361 | 1229084.1125
3 | 2609433.083 | 1229043.5099
4 | 2609405.3323 | 1229121.5459
5 | 2609466.881 | 1229065.3539
6 | 2609381.8694 | 1229022.0236
7 | 2609442.7902 | 1229142.5506
8 | 2609354.4548 | 1229099.7887
9 | 2609493.6423 | 1229105.509
10 | 2609485.5606 | 1229099.9151
11 | 2609502.3237 | 1229091.2588
12 | 2609464.6292 | 1229080.9374
13 | 2609460.2142 | 1229079.9409
14 | 2609355.2792 | 1228972.5679
15 | 2609342.9881 | 1228968.1146
16 | 2609358.41 | 1228961.5329
17 | 2609486.499 | 1229000.1018
18 | 2609482.7884 | 1228999.1843
19 | 2609479.9675 | 1229015.2893
20 | 2609499.8863 | 1228946.9137
21 | 2609461.4669 | 1229063.8
22 | 2609523.4973 | 1229019.8055
23 | 2609518.9828 | 1229019.4648
24 | 2609524.7657 | 1229003.509
25 | 2609512.1108 | 1229058.1769
26 | 2609475.9917 | 1229014.3936
27 | 2609507.7276 | 1229056.2688
28 | 2609518.1301 | 1229003.1093
29 | 2609533.7324 | 1228972.0157
30 | 2609527.2521 | 1228969.1815
31 | 2609541.4288 | 1228958.0085
32 | 2609496.3879 | 1228945.8964
33 | 2609501.4092 | 1228932.463
34 | 2609350.147 | 1229008.7147
35 | 2609432.5852 | 1229138.2765
36 | 2609449.3136 | 1229127.5742
37 | 2609477.0551 | 1229170.5436
38 | 2609478.4123 | 1229145.8644
39 | 2609469.6264 | 1229163.9835
40 | 2609497.2923 | 1229087.3262
41 | 2609440.1388 | 1229123.335
42 | 2609437.1223 | 1228917.6193
43 | 2609423.8827 | 1228920.6669
44 | 2609471.5895 | 1228914.3606
45 | 2609409.0493 | 1228949.7164
46 | 2609512.8927 | 1228904.6759
47 | 2609387.9258 | 1228954.6881
48 | 2609412.6785 | 1228963.8527
49 | 2609425.0901 | 1228875.5976
50 | 2609413.2756 | 1228868.3859
51 | 2609446.9465 | 1228870.6291
52 | 2609497.2442 | 1228931.4003
53 | 2609509.8275 | 1228902.8033
54 | 2609520.6807 | 1228890.2908
55 | 2609484.6262 | 1228867.3089
56 | 2609493.3523 | 1228839.395
57 | 2609552.0001 | 1228922.76
58 | 2609546.8128 | 1228921.4843
59 | 2609556.1675 | 1228908.0801
60 | 2609536.6069 | 1228955.6216
61 | 2609429.0838 | 1228966.7293
62 | 2609411.9883 | 1228863.1807
63 | 2609504.4898 | 1228814.9204
64 | 2609548.0044 | 1228905.8213
65 | 2609337.9541 | 1228913.0107
66 | 2609330.9361 | 1228935.0737
67 | 2609339.1639 | 1228909.2073
68 | 2609323.803 | 1228957.4988
69 | 2609343.3685 | 1228895.9888
70 | 2609290.2011 | 1228935.5002
71 | 2609322.7979 | 1228960.7992
72 | 2609349.1051 | 1228877.9542
73 | 2609281.0201 | 1228950.7591
74 | 2609278.8929 | 1228927.3373
75 | 2609317.0937 | 1228974.3108
76 | 2609349.2342 | 1228877.5485
77 | 2609448.983 | 1228735.7359
78 | 2609463.0933 | 1228744.2685
79 | 2609435.2403 | 1228727.4257
80 | 2609477.562 | 1228753.015
81 | 2609434.7284 | 1228727.1163
82 | 2609491.7484 | 1228761.5908
83 | 2609409.4156 | 1228711.8202
84 | 2609499.8146 | 1228751.1133
85 | 2609507.4147 | 1228773.4617
86 | 2609400.6705 | 1228729.4609
87 | 2609287.5758 | 1228878.9389
88 | 2609261.8012 | 1228914.9996
89 | 2609258.1007 | 1228912.4034
90 | 2609251.4109 | 1228921.727
91 | 2609238.8017 | 1228939.3007
92 | 2609361.351 | 1228762.1353
93 | 2609385.268 | 1228776.5096
94 | 2609319.5227 | 1228843.0037
95 | 2609320.9571 | 1228843.9603
96 | 2609419.3549 | 1228796.379
97 | 2609377.6123 | 1228798.253
98 | 2609428.8898 | 1228801.9369
99 | 2609369.7019 | 1228813.7184
100 | 2609448.9184 | 1228813.616
101 | 2609376.1584 | 1228789.2003
102 | 2609369.1296 | 1228815.4998
103 | 2609388.2905 | 1228747.6861
104 | 2609383.7566 | 1228762.8213
105 | 2609513.0998 | 1228779.1017
106 | 2609533.5034 | 1228821.9705
107 | 2609366.5882 | 1228823.4104
108 | 2609361.7002 | 1228838.6252
109 | 2609356.7732 | 1228853.9615
110 | 2609353.0981 | 1228865.4009
111 | 2609337.8505 | 1228855.2296
112 | 2609371.4263 | 1228900.051
113 | 2609360.2367 | 1228946.4212
114 | 2609357.5044 | 1228957.7436
115 | 2609526.8379 | 1228770.8161
116 | 2609537.3305 | 1228756.3572
117 | 2609545.9512 | 1228744.4779
118 | 2609560.6131 | 1228781.4635
119 | 2609572.7894 | 1228765.5555
120 | 2609584.9322 | 1228803.5732
121 | 2609279.8158 | 1228952.7608
122 | 2609276.9018 | 1228957.6038
123 | 2609301.9989 | 1229010.0658
124 | 2609309.7902 | 1228991.6107
125 | 2609298.9848 | 1229017.2055
126 | 2609289.6632 | 1229039.2856
127 | 2609286.0572 | 1229047.8271
128 | 2609281.7044 | 1229056.4716
129 | 2609271.7872 | 1229036.5125
130 | 2609217.2727 | 1228991.8975
131 | 2609233.0896 | 1229005.245
132 | 2609244.5561 | 1229014.9212
133 | 2609253.5654 | 1229022.0646
134 | 2609261.5755 | 1228988.0403
135 | 2609263.112 | 1228985.6136
136 | 2609264.7034 | 1228983.1001
137 | 2609271.0265 | 1229077.6771
138 | 2609216.4933 | 1229035.2013
139 | 2609229.1002 | 1229045.4265
140 | 2609631.6571 | 1228764.7602
141 | 2609409.0493 | 1228949.7164

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97275 | -0.52445 | 0.026253 | 0.0065796
1 | 0.97263 | -0.52679 | 0.0035568 | 0.00089141
2 | 0.97421 | -0.49556 | 0 | 0
3 | 0.97597 | -0.46093 | 0 | 0
4 | 0.97312 | -0.51703 | 0 | 0
5 | 0.9796 | -0.38992 | 0 | 0
6 | 0.97437 | -0.49255 | 0.026894 | 0.0067402
7 | 0.97196 | -0.5399 | 0 | 0
8 | 0.97175 | -0.54416 | 0.0266 | 0.0066667
9 | 0.97783 | -0.42463 | 0 | 0
10 | 0.97773 | -0.42653 | 0.010587 | 0.0026535
11 | 0.97679 | -0.44496 | 0 | 0
12 | 0.97928 | -0.39632 | 0 | 0
13 | 0.97923 | -0.39719 | 0.010553 | 0.0026449
14 | 0.99484 | -0.097925 | 0 | 0
15 | 0.99419 | -0.11049 | 0.0070989 | 0.0017792
16 | 0.99542 | -0.086918 | 0 | 0
17 | 0.98311 | -0.32192 | 0 | 0
18 | 0.98308 | -0.32252 | 0.0086418 | 0.0021658
19 | 0.98222 | -0.33902 | 0 | 0
20 | 0.98613 | -0.26361 | 0 | 0
21 | 0.97955 | -0.39094 | 0.0099534 | 0.0024946
22 | 0.97314 | -0.51669 | 0 | 0
23 | 0.97311 | -0.51724 | 0.0067073 | 0.001681
24 | 0.9725 | -0.52918 | 0 | 0
25 | 0.97496 | -0.48081 | 0 | 0
26 | 0.98218 | -0.3398 | 0.010494 | 0.00263
27 | 0.97492 | -0.48156 | 0.0085957 | 0.0021543
28 | 0.97247 | -0.52995 | 0.0062765 | 0.001573
29 | 0.97141 | -0.55073 | 0 | 0
30 | 0.97135 | -0.55191 | 0.0090854 | 0.002277
31 | 0.97102 | -0.55844 | 0 | 0
32 | 0.9861 | -0.26421 | 0.0091903 | 0.0023033
33 | 0.98696 | -0.24764 | 0 | 0
34 | 0.97423 | -0.49518 | 0.0041665 | 0.0010442
35 | 0.97187 | -0.54172 | 0.0089472 | 0.0022424
36 | 0.97182 | -0.54264 | 0 | 0
37 | 0.97091 | -0.56073 | 0 | 0
38 | 0.97074 | -0.56417 | 0.0068782 | 0.0017238
39 | 0.97085 | -0.56199 | 0.0068749 | 0.001723
40 | 0.97673 | -0.44612 | 0.0099986 | 0.0025059
41 | 0.97174 | -0.54433 | 0.0090892 | 0.002278
42 | 0.99444 | -0.10494 | 0.016681 | 0.0041807
43 | 0.9953 | -0.088659 | 0 | 0
44 | 0.99212 | -0.14885 | 0 | 0
45 | 0.99825 | -0.033064 | 0 | 0
46 | 0.98876 | -0.21301 | 0 | 0
47 | 0.99702 | -0.056515 | 0.018279 | 0.0045811
48 | 1 | 0 | -0.54639 | -0.14005
49 | 0.9706 | -0.56821 | 0 | 0
50 | 0.97036 | -0.57296 | 0 | 0
51 | 0.97087 | -0.56289 | 0.020534 | 0.0051464
52 | 0.98692 | -0.24829 | 0.0085477 | 0.0021422
53 | 0.98876 | -0.21306 | 0.00072413 | 0.00018148
54 | 0.98875 | -0.21325 | 0.00068255 | 0.00017106
55 | 0.97219 | -0.53665 | 0 | 0
56 | 0.97311 | -0.51866 | 0 | 0
57 | 0.97042 | -0.57042 | 0 | 0
58 | 0.97037 | -0.57132 | 0.0090836 | 0.0022766
59 | 0.9703 | -0.57282 | 0 | 0
60 | 0.97098 | -0.55928 | 0.0085462 | 0.0021419
61 | 0.99975 | -0.0048467 | 0.016691 | 0.0041832
62 | 0.97029 | -0.57423 | 0.012837 | 0.0032172
63 | 0.97394 | -0.50217 | 0 | 0
64 | 0.97023 | -0.57414 | 0.0084863 | 0.0021269
65 | 0.99147 | -0.16257 | 0.0053707 | 0.001346
66 | 0.99222 | -0.14825 | 0.0061354 | 0.0015377
67 | 0.99134 | -0.16495 | 0.0042818 | 0.0010731
68 | 0.99301 | -0.13308 | 0 | 0
69 | 0.99093 | -0.17295 | 0.0031677 | 0.00079389
70 | 0.99211 | -0.15043 | 0 | 0
71 | 0.99314 | -0.13048 | 0 | 0
72 | 0.99037 | -0.1836 | 0.0015872 | 0.00039778
73 | 0.99198 | -0.15303 | 0.0022801 | 0.00057144
74 | 0.99191 | -0.15444 | 0.0054037 | 0.0013543
75 | 0.9926 | -0.14104 | 0.0049931 | 0.0012514
76 | 0.99036 | -0.18384 | 0.0033753 | 0.00084594
77 | 0.97919 | -0.39933 | 0.0011925 | 0.00029887
78 | 0.97831 | -0.41664 | 0.0011909 | 0.00029847
79 | 0.98008 | -0.38215 | 0 | 0
80 | 0.97742 | -0.43406 | 0.0011913 | 0.00029858
81 | 0.98011 | -0.38151 | 0.0011892 | 0.00029803
82 | 0.97656 | -0.4508 | 0 | 0
83 | 0.98177 | -0.34933 | 0 | 0
84 | 0.97654 | -0.45127 | 0.0019266 | 0.00048285
85 | 0.97557 | -0.47013 | 0.0036942 | 0.00092584
86 | 0.98287 | -0.32796 | 0.0011829 | 0.00029647
87 | 0.99149 | -0.16255 | 0.0051727 | 0.0012964
88 | 0.9917 | -0.15848 | 0 | 0
89 | 0.99167 | -0.15893 | 0 | 0
90 | 0.99161 | -0.16008 | 0.0025127 | 0.00062974
91 | 0.99155 | -0.16128 | 0.0031304 | 0.00078455
92 | 0.98682 | -0.25224 | 0.0020467 | 0.00051296
93 | 0.98687 | -0.25122 | 0 | 0
94 | 0.98977 | -0.19519 | 0.0051616 | 0.0012936
95 | 0.98978 | -0.19504 | 0 | 0
96 | 0.98566 | -0.27483 | 0.0044063 | 0.0011043
97 | 0.98762 | -0.23661 | 0.0023867 | 0.00059817
98 | 0.98536 | -0.28058 | 0.024629 | 0.0061727
99 | 0.98825 | -0.22432 | 0 | 0
100 | 0.98527 | -0.28239 | 0.0043635 | 0.0010936
101 | 0.98671 | -0.25395 | 0.0019613 | 0.00049155
102 | 0.98843 | -0.22087 | 0.0051974 | 0.0013026
103 | 0.98418 | -0.30258 | 0 | 0
104 | 0.98508 | -0.28518 | 0.0021576 | 0.00054074
105 | 0.9752 | -0.47743 | 0 | 0
106 | 0.97389 | -0.50315 | 0.0016276 | 0.00040793
107 | 0.98885 | -0.21284 | 0.0023843 | 0.00059755
108 | 0.98926 | -0.20495 | 0.0020672 | 0.00051809
109 | 0.98968 | -0.19686 | 0.0015494 | 0.00038831
110 | 0.99 | -0.19075 | 0 | 0
111 | 0.98988 | -0.19317 | 0.0022754 | 0.00057026
112 | 0.99522 | -0.090781 | 0.0021577 | 0.00054078
113 | 0.99531 | -0.088969 | 0.0042481 | 0.0010647
114 | 0.99538 | -0.087656 | 0.0040367 | 0.0010117
115 | 0.97497 | -0.48197 | 0.0019266 | 0.00048284
116 | 0.97476 | -0.48615 | 0.0046677 | 0.0011698
117 | 0.97465 | -0.48833 | 0 | 0
118 | 0.97436 | -0.49399 | 0.0016127 | 0.00040419
119 | 0.97439 | -0.49339 | 0 | 0
120 | 0.97431 | -0.49503 | 0.0016039 | 0.00040197
121 | 0.99197 | -0.15328 | 0.0024936 | 0.00062495
122 | 0.99195 | -0.15363 | 0.0034758 | 0.00087113
123 | 0.9914 | -0.16417 | 0.0027635 | 0.00069259
124 | 0.99198 | -0.15291 | 0.0040337 | 0.0010109
125 | 0.9912 | -0.16814 | 0.0032346 | 0.00081066
126 | 0.99063 | -0.17907 | 0.0032841 | 0.00082307
127 | 0.99044 | -0.18276 | 0 | 0
128 | 0.99037 | -0.18422 | 0.0055147 | 0.0013821
129 | 0.99021 | -0.18727 | 0.0014872 | 0.00037273
130 | 0.98973 | -0.19654 | 0.0019284 | 0.00048331
131 | 0.98977 | -0.19583 | 0.0029766 | 0.00074602
132 | 0.98984 | -0.19452 | 0 | 0
133 | 0.98995 | -0.19241 | 0.0021391 | 0.00053611
134 | 0.98968 | -0.19757 | 0.0018781 | 0.00047069
135 | 0.98967 | -0.19775 | 0.0016362 | 0.00041006
136 | 0.98967 | -0.19785 | 0.0018792 | 0.00047098
137 | 0.9903 | -0.18547 | 0 | 0
138 | 0.99012 | -0.18911 | 0.0029587 | 0.00074152
139 | 0.99016 | -0.18825 | 0 | 0
140 | 0.97413 | -0.49866 | 0.0048714 | 0.0012209
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0035572 | 0.00089122 | -0.0035568 | -0.00089141 | 3.9713e-07 | -1.8979e-07 | 0.0054413 | 0.0054415 | 0.0054415 | 0.97275 | -0.52445 | 0.97263 | -0.52679 | 1.4949
1 | -0.02981 | -0.0074708 | 0.029851 | 0.0074965 | 4.109e-05 | 2.5642e-05 | 0.045601 | 0.0456 | 0.045601 | 0.97275 | -0.52445 | 0.97421 | -0.49556 | 12.5276
2 | -0.088388 | -0.022219 | 0.088534 | 0.022311 | 0.00014641 | 9.2636e-05 | 0.13503 | 0.13503 | 0.13503 | 0.97421 | -0.49556 | 0.97597 | -0.46093 | 18.5479
3 | 0.058537 | 0.014722 | -0.058477 | -0.014685 | 5.9984e-05 | 3.7395e-05 | 0.089428 | 0.089428 | 0.089428 | 0.97421 | -0.49556 | 0.97312 | -0.51703 | 12.2841
4 | -0.11964 | -0.030125 | 0.12005 | 0.030384 | 0.00040767 | 0.00025927 | 0.18246 | 0.18246 | 0.18246 | 0.97597 | -0.46093 | 0.9796 | -0.38992 | 25.0635
5 | 0.031108 | 0.0078137 | -0.031061 | -0.0077844 | 4.6861e-05 | 2.9298e-05 | 0.047435 | 0.047435 | 0.047435 | 0.97597 | -0.46093 | 0.97437 | -0.49255 | 13.0315
6 | 0.031842 | 0.007997 | -0.031807 | -0.0079767 | 3.4704e-05 | 2.0274e-05 | 0.048696 | 0.048697 | 0.048697 | 0.97312 | -0.51703 | 0.97196 | -0.5399 | 6.6891
7 | 0.026635 | 0.006688 | -0.0266 | -0.0066667 | 3.4427e-05 | 2.1347e-05 | 0.040732 | 0.040732 | 0.040732 | 0.97312 | -0.51703 | 0.97175 | -0.54416 | 11.1902
8 | 0.0099539 | 0.0024948 | -0.0099534 | -0.0024946 | 4.8155e-07 | 2.3748e-07 | 0.01512 | 0.01512 | 0.01512 | 0.9796 | -0.38992 | 0.97955 | -0.39094 | 4.1538
9 | -0.21839 | -0.055205 | 0.21892 | 0.055544 | 0.00053443 | 0.00033943 | 0.3319 | 0.3319 | 0.3319 | 0.9796 | -0.38992 | 0.98222 | -0.33902 | 22.7954
10 | 0.088385 | 0.022326 | -0.088358 | -0.022309 | 2.7108e-05 | 1.6542e-05 | 0.13432 | 0.13432 | 0.13432 | 0.9796 | -0.38992 | 0.97928 | -0.39632 | 9.2252
11 | 0.0041671 | 0.0010441 | -0.0041665 | -0.0010442 | 5.2243e-07 | -9.4062e-08 | 0.0063637 | 0.0063638 | 0.0063638 | 0.97437 | -0.49255 | 0.97423 | -0.49518 | 1.7483
12 | 0.008948 | 0.0022427 | -0.0089472 | -0.0022424 | 7.7664e-07 | 3.6028e-07 | 0.013699 | 0.013699 | 0.013699 | 0.97196 | -0.5399 | 0.97187 | -0.54172 | 3.7635
13 | 0.0090911 | 0.0022789 | -0.0090899 | -0.0022783 | 1.1862e-06 | 5.5683e-07 | 0.013918 | 0.013918 | 0.013918 | 0.97196 | -0.5399 | 0.97182 | -0.54264 | 3.8237
14 | 0.013768 | 0.0034551 | -0.013755 | -0.0034474 | 1.3664e-05 | 7.73e-06 | 0.02108 | 0.02108 | 0.02108 | 0.97196 | -0.5399 | 0.97091 | -0.56073 | 5.7913
15 | 0.010588 | 0.002654 | -0.010587 | -0.0026535 | 9.5512e-07 | 4.8823e-07 | 0.016113 | 0.016113 | 0.016113 | 0.97783 | -0.42463 | 0.97773 | -0.42653 | 4.4267
16 | 0.06711 | 0.016945 | -0.067045 | -0.016903 | 6.5283e-05 | 4.1572e-05 | 0.10217 | 0.10217 | 0.10217 | 0.97783 | -0.42463 | 0.97679 | -0.44496 | 28.0689
17 | -0.077699 | -0.019599 | 0.077804 | 0.019664 | 0.00010546 | 6.5224e-05 | 0.11828 | 0.11828 | 0.11828 | 0.97783 | -0.42463 | 0.97928 | -0.39632 | 10.8318
18 | 0.0099991 | 0.0025061 | -0.0099986 | -0.0025059 | 5.5469e-07 | 2.7521e-07 | 0.015232 | 0.015232 | 0.015232 | 0.97679 | -0.44496 | 0.97673 | -0.44612 | 4.1847
19 | 0.057046 | 0.014397 | -0.056948 | -0.014335 | 9.7774e-05 | 6.2144e-05 | 0.086938 | 0.086938 | 0.086938 | 0.97679 | -0.44496 | 0.97496 | -0.48081 | 23.8842
20 | 0.010554 | 0.0026451 | -0.010553 | -0.0026449 | 4.3521e-07 | 2.2176e-07 | 0.016036 | 0.016036 | 0.016036 | 0.97928 | -0.39632 | 0.97923 | -0.39719 | 4.4056
21 | 0.22005 | 0.055909 | -0.21992 | -0.055824 | 0.00013298 | 8.4431e-05 | 0.3294 | 0.3294 | 0.3294 | 0.99484 | -0.097925 | 0.99419 | -0.11049 | 22.6238
22 | -0.22005 | -0.055909 | 0.22016 | 0.055983 | 0.00011668 | 7.4077e-05 | 0.3294 | 0.3294 | 0.3294 | 0.99484 | -0.097925 | 0.99542 | -0.086918 | 22.6238
23 | 0.21282 | 0.054045 | -0.21261 | -0.053915 | 0.00020458 | 0.00012982 | 0.31878 | 0.31878 | 0.31878 | 0.99419 | -0.11049 | 0.99314 | -0.13048 | 21.8941
24 | -0.23061 | -0.0586 | 0.23095 | 0.058815 | 0.00033812 | 0.00021482 | 0.34501 | 0.34501 | 0.34501 | 0.99542 | -0.086918 | 0.99702 | -0.056515 | 23.6959
25 | 0.010443 | 0.0026169 | -0.010443 | -0.0026167 | 3.6749e-07 | 1.8292e-07 | 0.015611 | 0.015611 | 0.015611 | 0.99542 | -0.086918 | 0.99538 | -0.087656 | 4.2888
26 | 0.008642 | 0.0021659 | -0.0086418 | -0.0021658 | 2.4458e-07 | 1.082e-07 | 0.01308 | 0.01308 | 0.01308 | 0.98311 | -0.32192 | 0.98308 | -0.32252 | 3.5935
27 | 0.22961 | 0.058294 | -0.22942 | -0.058174 | 0.00018879 | 0.00011998 | 0.3478 | 0.3478 | 0.3478 | 0.98311 | -0.32192 | 0.98222 | -0.33902 | 23.8872
28 | -0.23825 | -0.06046 | 0.23892 | 0.060887 | 0.00067021 | 0.00042614 | 0.36088 | 0.36088 | 0.36088 | 0.98311 | -0.32192 | 0.98613 | -0.26361 | 24.7856
29 | 0.010494 | 0.0026302 | -0.010494 | -0.00263 | 3.8519e-07 | 1.9508e-07 | 0.015898 | 0.015898 | 0.015898 | 0.98222 | -0.33902 | 0.98218 | -0.3398 | 4.3676
30 | 0.0091906 | 0.0023034 | -0.0091903 | -0.0023033 | 2.6202e-07 | 1.2135e-07 | 0.013868 | 0.013868 | 0.013868 | 0.98613 | -0.26361 | 0.9861 | -0.26421 | 3.8099
31 | -0.24811 | -0.06319 | 0.2483 | 0.063312 | 0.00019138 | 0.00012174 | 0.37474 | 0.37474 | 0.37474 | 0.98613 | -0.26361 | 0.98696 | -0.24764 | 25.738
32 | 0.0067075 | 0.0016811 | -0.0067073 | -0.001681 | 1.7807e-07 | 5.7883e-08 | 0.010256 | 0.010256 | 0.010256 | 0.97314 | -0.51669 | 0.97311 | -0.51724 | 2.8177
33 | 0.041562 | 0.010447 | -0.041537 | -0.010431 | 2.4782e-05 | 1.5658e-05 | 0.063563 | 0.063563 | 0.063563 | 0.97314 | -0.51669 | 0.9725 | -0.52918 | 17.4623
34 | -0.048269 | -0.012128 | 0.048352 | 0.012181 | 8.2807e-05 | 5.2492e-05 | 0.073819 | 0.073819 | 0.073819 | 0.97314 | -0.51669 | 0.97496 | -0.48081 | 20.28
35 | 0.0062768 | 0.0015731 | -0.0062765 | -0.001573 | 2.2926e-07 | 6.4488e-08 | 0.009604 | 0.009604 | 0.009604 | 0.9725 | -0.52918 | 0.97247 | -0.52995 | 2.6385
36 | 0.03526 | 0.0088583 | -0.035224 | -0.0088355 | 3.6215e-05 | 2.2766e-05 | 0.053959 | 0.053959 | 0.053959 | 0.9725 | -0.52918 | 0.97141 | -0.55073 | 14.8239
37 | 0.008596 | 0.0021544 | -0.0085957 | -0.0021543 | 3.0782e-07 | 1.3754e-07 | 0.01312 | 0.01312 | 0.01312 | 0.97496 | -0.48081 | 0.97492 | -0.48156 | 3.6043
38 | 0.009086 | 0.0022773 | -0.0090854 | -0.002277 | 5.1256e-07 | 2.4069e-07 | 0.013918 | 0.013918 | 0.013918 | 0.97141 | -0.55073 | 0.97135 | -0.55191 | 3.8236
39 | 0.026138 | 0.0065582 | -0.026128 | -0.0065523 | 9.6034e-06 | 5.9485e-06 | 0.040041 | 0.040041 | 0.040041 | 0.97141 | -0.55073 | 0.97102 | -0.55844 | 11.0003
40 | 0.0085465 | 0.002142 | -0.0085462 | -0.0021419 | 3.4529e-07 | 1.5458e-07 | 0.013097 | 0.013097 | 0.013097 | 0.97102 | -0.55844 | 0.97098 | -0.55928 | 3.5981
41 | 0.017582 | 0.0044103 | -0.017572 | -0.0044043 | 1.0038e-05 | 5.9687e-06 | 0.026944 | 0.026944 | 0.026944 | 0.97102 | -0.55844 | 0.97042 | -0.57042 | 7.4023
42 | 0.0085479 | 0.0021424 | -0.0085477 | -0.0021422 | 2.6701e-07 | 1.161e-07 | 0.012888 | 0.012888 | 0.012888 | 0.98696 | -0.24764 | 0.98692 | -0.24829 | 3.5405
43 | -0.25685 | -0.065454 | 0.25728 | 0.065728 | 0.00042995 | 0.00027361 | 0.38763 | 0.38763 | 0.38763 | 0.98696 | -0.24764 | 0.98876 | -0.21301 | 26.6231
44 | 0.0090899 | 0.0022783 | -0.0090892 | -0.002278 | 7.3246e-07 | 3.4385e-07 | 0.013918 | 0.013918 | 0.013918 | 0.97182 | -0.54264 | 0.97174 | -0.54433 | 3.8237
45 | 0.0068793 | 0.0017242 | -0.0068782 | -0.0017238 | 1.1259e-06 | 3.866e-07 | 0.010543 | 0.010543 | 0.010543 | 0.97091 | -0.56073 | 0.97074 | -0.56417 | 2.8965
46 | 0.0068753 | 0.0017232 | -0.0068749 | -0.001723 | 4.1199e-07 | 1.4131e-07 | 0.010537 | 0.010537 | 0.010537 | 0.97091 | -0.56073 | 0.97085 | -0.56199 | 2.8948
47 | -0.27672 | -0.071126 | 0.27694 | 0.071265 | 0.00021905 | 0.00013949 | 0.41471 | 0.41471 | 0.41471 | 0.99444 | -0.10494 | 0.9953 | -0.088659 | 28.4826
48 | 0.26004 | 0.066945 | -0.25949 | -0.066592 | 0.00055417 | 0.00035265 | 0.38975 | 0.38975 | 0.38975 | 0.99444 | -0.10494 | 0.99212 | -0.14885 | 26.7684
49 | -0.27694 | -0.071265 | 0.27769 | 0.071743 | 0.00075093 | 0.00047817 | 0.41471 | 0.41471 | 0.41471 | 0.9953 | -0.088659 | 0.99825 | -0.033064 | 28.4826
50 | 0.25949 | 0.066592 | -0.25868 | -0.06608 | 0.00080518 | 0.0005124 | 0.38975 | 0.38975 | 0.38975 | 0.99212 | -0.14885 | 0.98876 | -0.21301 | 26.7684
51 | 0.24951 | 0.063575 | -0.24923 | -0.063396 | 0.00028198 | 0.00017933 | 0.37229 | 0.37229 | 0.37229 | 0.99825 | -0.033064 | 0.99702 | -0.056515 | 25.5695
52 | -0.5272 | -0.13532 | 0.52805 | 0.13586 | 0.00084745 | 0.0005416 | 0.787 | 0.787 | 0.787 | 0.99825 | -0.033064 | 1 | 0 | 54.052
53 | 0.00072413 | 0.00018144 | -0.00072413 | -0.00018148 | 1.5961e-09 | -4.4947e-08 | 0.0010898 | 0.0010898 | 0.0010898 | 0.98876 | -0.21301 | 0.98876 | -0.21306 | 0.29939
54 | 0.00068256 | 0.00017081 | -0.00068255 | -0.00017106 | 7.8287e-09 | -2.4878e-07 | 0.0010271 | 0.0010272 | 0.0010272 | 0.98876 | -0.21301 | 0.98875 | -0.21325 | 0.2822
55 | 0.016695 | 0.0041854 | -0.016691 | -0.0041832 | 3.8547e-06 | 2.2486e-06 | 0.024843 | 0.024843 | 0.024843 | 1 | 0 | 0.99975 | -0.0048467 | 6.825
56 | 0.01284 | 0.0032192 | -0.012837 | -0.0032176 | 2.9052e-06 | 1.6123e-06 | 0.019686 | 0.019686 | 0.019686 | 0.9706 | -0.56821 | 0.97036 | -0.57296 | 5.4082
57 | -0.01284 | -0.0032192 | 0.012844 | 0.003221 | 3.2573e-06 | 1.8076e-06 | 0.019686 | 0.019686 | 0.019686 | 0.9706 | -0.56821 | 0.97087 | -0.56289 | 5.4082
58 | 0.012837 | 0.0032176 | -0.012837 | -0.0032172 | 7.7924e-07 | 4.3248e-07 | 0.019686 | 0.019686 | 0.019686 | 0.97036 | -0.57296 | 0.97029 | -0.57423 | 5.4082
59 | -0.033378 | -0.0083674 | 0.03342 | 0.0083936 | 4.1789e-05 | 2.6218e-05 | 0.051158 | 0.051158 | 0.051158 | 0.97087 | -0.56289 | 0.97219 | -0.53665 | 14.0544
60 | -0.03342 | -0.0083936 | 0.033448 | 0.0084117 | 2.8701e-05 | 1.8006e-05 | 0.051158 | 0.051158 | 0.051158 | 0.97219 | -0.53665 | 0.97311 | -0.51866 | 14.0544
61 | -0.033448 | -0.0084117 | 0.033475 | 0.0084282 | 2.6381e-05 | 1.6549e-05 | 0.051158 | 0.051158 | 0.051158 | 0.97311 | -0.51866 | 0.97394 | -0.50217 | 14.0543
62 | 0.009084 | 0.0022768 | -0.0090836 | -0.0022766 | 3.8759e-07 | 1.8225e-07 | 0.013929 | 0.013929 | 0.013929 | 0.97042 | -0.57042 | 0.97037 | -0.57132 | 3.8267
63 | 0.0084878 | 0.0021275 | -0.0084868 | -0.0021271 | 9.6929e-07 | 4.3185e-07 | 0.013015 | 0.013015 | 0.013015 | 0.97042 | -0.57042 | 0.9703 | -0.57282 | 3.5756
64 | 0.0084868 | 0.0021271 | -0.0084863 | -0.0021269 | 5.3658e-07 | 2.3908e-07 | 0.013015 | 0.013015 | 0.013015 | 0.9703 | -0.57282 | 0.97023 | -0.57414 | 3.5756
65 | -0.035103 | -0.0088358 | 0.035144 | 0.0088619 | 4.1563e-05 | 2.612e-05 | 0.053644 | 0.053644 | 0.053644 | 0.97394 | -0.50217 | 0.9752 | -0.47743 | 14.7375
66 | 0.0016277 | 0.00040756 | -0.0016276 | -0.00040793 | 7.6325e-08 | -3.607e-07 | 0.0024867 | 0.0024869 | 0.0024869 | 0.97394 | -0.50217 | 0.97389 | -0.50315 | 0.68321
67 | -0.14096 | -0.035831 | 0.14105 | 0.035893 | 9.7302e-05 | 6.1078e-05 | 0.21173 | 0.21173 | 0.21173 | 0.99147 | -0.16257 | 0.99222 | -0.14825 | 14.5418
68 | 0.13558 | 0.034485 | -0.13557 | -0.034476 | 1.5521e-05 | 9.7277e-06 | 0.20367 | 0.20367 | 0.20367 | 0.99147 | -0.16257 | 0.99134 | -0.16495 | 13.9882
69 | -0.14719 | -0.03743 | 0.1473 | 0.037498 | 0.00010768 | 6.7699e-05 | 0.22093 | 0.22093 | 0.22093 | 0.99222 | -0.14825 | 0.99301 | -0.13308 | 15.1737
70 | 0.13129 | 0.033403 | -0.13124 | -0.033371 | 5.0591e-05 | 3.1663e-05 | 0.19724 | 0.19724 | 0.19724 | 0.99134 | -0.16495 | 0.99093 | -0.17295 | 13.5468
71 | 0.024497 | 0.0061482 | -0.024477 | -0.0061358 | 2.0258e-05 | 1.2447e-05 | 0.036712 | 0.036712 | 0.036712 | 0.99301 | -0.13308 | 0.99211 | -0.15043 | 10.0858
72 | -0.17179 | -0.043646 | 0.17181 | 0.04366 | 2.1469e-05 | 1.3562e-05 | 0.25764 | 0.25764 | 0.25764 | 0.99301 | -0.13308 | 0.99314 | -0.13048 | 17.6951
73 | 0.12807 | 0.032577 | -0.128 | -0.032536 | 6.5735e-05 | 4.1096e-05 | 0.19248 | 0.19248 | 0.19248 | 0.99093 | -0.17295 | 0.99037 | -0.1836 | 13.2201
74 | 0.0082506 | 0.0020679 | -0.0082496 | -0.0020675 | 1.0226e-06 | 4.2456e-07 | 0.012375 | 0.012375 | 0.012375 | 0.99211 | -0.15043 | 0.99198 | -0.15303 | 3.3997
75 | 0.016226 | 0.0040678 | -0.016223 | -0.004066 | 3.0978e-06 | 1.8025e-06 | 0.024337 | 0.024338 | 0.024338 | 0.99211 | -0.15043 | 0.99191 | -0.15444 | 6.6861
76 | 0.040797 | 0.010256 | -0.040777 | -0.010243 | 2.0557e-05 | 1.2967e-05 | 0.061137 | 0.061137 | 0.061137 | 0.99314 | -0.13048 | 0.9926 | -0.14104 | 16.796
77 | 0.12642 | 0.032138 | -0.12641 | -0.032137 | 1.4424e-06 | 9.0123e-07 | 0.1901 | 0.1901 | 0.1901 | 0.99037 | -0.1836 | 0.99036 | -0.18384 | 13.0563
78 | 0.0059696 | 0.0014961 | -0.0059695 | -0.001496 | 7.0245e-08 | 1.4799e-08 | 0.0089546 | 0.0089546 | 0.0089546 | 0.99198 | -0.15303 | 0.99197 | -0.15328 | 2.4601
79 | 0.01082 | 0.0027117 | -0.010817 | -0.0027107 | 2.0825e-06 | 1.0608e-06 | 0.016231 | 0.016231 | 0.016231 | 0.99191 | -0.15444 | 0.9917 | -0.15848 | 4.4591
80 | 0.035784 | 0.0089914 | -0.035763 | -0.0089787 | 2.027e-05 | 1.273e-05 | 0.053652 | 0.053652 | 0.053652 | 0.9926 | -0.14104 | 0.99198 | -0.15291 | 14.7396
81 | 0.12304 | 0.031291 | -0.123 | -0.031266 | 4.0914e-05 | 2.5529e-05 | 0.18503 | 0.18503 | 0.18503 | 0.99036 | -0.18384 | 0.99 | -0.19075 | 12.708
82 | 0.058046 | 0.014682 | -0.057998 | -0.014652 | 4.8167e-05 | 3.0619e-05 | 0.088258 | 0.088258 | 0.088258 | 0.97919 | -0.39933 | 0.97831 | -0.41664 | 24.2466
83 | -0.059239 | -0.014981 | 0.059288 | 0.015012 | 4.8858e-05 | 3.1067e-05 | 0.09007 | 0.09007 | 0.09007 | 0.97919 | -0.39933 | 0.98008 | -0.38215 | 24.7444
84 | 0.056807 | 0.014353 | -0.05676 | -0.014323 | 4.7379e-05 | 3.0111e-05 | 0.086446 | 0.086446 | 0.086446 | 0.97831 | -0.41664 | 0.97742 | -0.43406 | 23.749
85 | -0.059288 | -0.015012 | 0.05929 | 0.015013 | 1.8197e-06 | 1.1571e-06 | 0.09007 | 0.09007 | 0.09007 | 0.98008 | -0.38215 | 0.98011 | -0.38151 | 24.7444
86 | 0.055569 | 0.014025 | -0.055524 | -0.013996 | 4.4526e-05 | 2.8289e-05 | 0.084633 | 0.084633 | 0.084633 | 0.97742 | -0.43406 | 0.97656 | -0.4508 | 23.2508
87 | -0.060479 | -0.015311 | 0.060572 | 0.015371 | 9.3618e-05 | 5.9542e-05 | 0.091875 | 0.091875 | 0.091875 | 0.98011 | -0.38151 | 0.98177 | -0.34933 | 25.2404
88 | 0.0019266 | 0.00048271 | -0.0019266 | -0.00048285 | 4.2732e-08 | -1.3808e-07 | 0.0029356 | 0.0029357 | 0.0029357 | 0.97656 | -0.4508 | 0.97654 | -0.45127 | 0.8065
89 | 0.053597 | 0.013514 | -0.053548 | -0.013482 | 4.9543e-05 | 3.146e-05 | 0.081697 | 0.081697 | 0.081697 | 0.97656 | -0.4508 | 0.97557 | -0.47013 | 22.4443
90 | -0.060572 | -0.015371 | 0.060635 | 0.015411 | 6.2324e-05 | 3.9638e-05 | 0.091875 | 0.091875 | 0.091875 | 0.98177 | -0.34933 | 0.98287 | -0.32796 | 25.2404
91 | 0.049854 | 0.012556 | -0.049836 | -0.012545 | 1.7374e-05 | 1.102e-05 | 0.076063 | 0.076063 | 0.076063 | 0.97557 | -0.47013 | 0.9752 | -0.47743 | 20.8964
92 | -0.061818 | -0.015707 | 0.061893 | 0.015755 | 7.563e-05 | 4.8111e-05 | 0.093666 | 0.093666 | 0.093666 | 0.98287 | -0.32796 | 0.98418 | -0.30258 | 25.7324
93 | -0.0051727 | -0.0012964 | 0.0051737 | 0.0012965 | 1.0017e-06 | 6.9331e-08 | 0.0077632 | 0.007763 | 0.0077632 | 0.99149 | -0.16255 | 0.9917 | -0.15848 | 2.1327
94 | 0.0056437 | 0.0014142 | -0.0056436 | -0.0014142 | 1.2133e-07 | 1.944e-08 | 0.0084682 | 0.0084682 | 0.0084682 | 0.9917 | -0.15848 | 0.99167 | -0.15893 | 2.3264
95 | 0.0056436 | 0.0014142 | -0.0056433 | -0.0014141 | 3.0859e-07 | 4.9455e-08 | 0.0084682 | 0.0084683 | 0.0084683 | 0.99167 | -0.15893 | 0.99161 | -0.16008 | 2.3264
96 | 0.0031306 | 0.00078439 | -0.0031304 | -0.00078455 | 1.79e-07 | -1.6445e-07 | 0.0046977 | 0.0046978 | 0.0046978 | 0.99161 | -0.16008 | 0.99155 | -0.16128 | 1.2906
97 | -0.0020467 | -0.00051296 | 0.0020468 | 0.00051266 | 9.9665e-08 | -2.9273e-07 | 0.0030862 | 0.0030861 | 0.0030862 | 0.98682 | -0.25224 | 0.98687 | -0.25122 | 0.84787
98 | 0.033445 | 0.0083991 | -0.033407 | -0.0083755 | 3.7636e-05 | 2.3583e-05 | 0.050435 | 0.050435 | 0.050435 | 0.98687 | -0.25122 | 0.98566 | -0.27483 | 13.8558
99 | -0.035492 | -0.0089117 | 0.035517 | 0.0089273 | 2.4762e-05 | 1.5553e-05 | 0.053521 | 0.053521 | 0.053521 | 0.98687 | -0.25122 | 0.98762 | -0.23661 | 14.7036
100 | -0.0051616 | -0.0012936 | 0.0051617 | 0.0012936 | 3.8933e-08 | 2.758e-09 | 0.00776 | 0.0077599 | 0.00776 | 0.98977 | -0.19519 | 0.98978 | -0.19504 | 2.1319
101 | -0.0051617 | -0.0012936 | 0.0051621 | 0.0012937 | 4.5856e-07 | 3.2453e-08 | 0.0077599 | 0.0077598 | 0.0077599 | 0.98978 | -0.19504 | 0.98988 | -0.19317 | 2.1319
102 | 0.029001 | 0.0072712 | -0.028993 | -0.0072662 | 7.9337e-06 | 4.937e-06 | 0.043783 | 0.043783 | 0.043783 | 0.98566 | -0.27483 | 0.98536 | -0.28058 | 12.0283
103 | -0.037903 | -0.0095254 | 0.037926 | 0.0095395 | 2.2248e-05 | 1.4006e-05 | 0.057117 | 0.057117 | 0.057117 | 0.98762 | -0.23661 | 0.98825 | -0.22432 | 15.6915
104 | 0.0043639 | 0.0010935 | -0.0043635 | -0.0010936 | 3.7758e-07 | -5.3652e-08 | 0.0065899 | 0.00659 | 0.00659 | 0.98536 | -0.28058 | 0.98527 | -0.28239 | 1.8105
105 | 0.066256 | 0.016942 | -0.066161 | -0.016882 | 9.4854e-05 | 6.0382e-05 | 0.099882 | 0.099882 | 0.099882 | 0.98825 | -0.22432 | 0.98671 | -0.25395 | 27.4402
106 | -0.10418 | -0.026482 | 0.1042 | 0.026493 | 1.7295e-05 | 1.1045e-05 | 0.157 | 0.157 | 0.157 | 0.98825 | -0.22432 | 0.98843 | -0.22087 | 43.1315
107 | 0.064199 | 0.016391 | -0.064103 | -0.016329 | 9.6721e-05 | 6.1551e-05 | 0.096925 | 0.096925 | 0.096925 | 0.98671 | -0.25395 | 0.98508 | -0.28518 | 26.6277
108 | -0.1094 | -0.027796 | 0.10944 | 0.027822 | 4.2323e-05 | 2.6873e-05 | 0.16482 | 0.16482 | 0.16482 | 0.98843 | -0.22087 | 0.98885 | -0.21284 | 22.6405
109 | -0.061893 | -0.015755 | 0.061945 | 0.015788 | 5.198e-05 | 3.3066e-05 | 0.093666 | 0.093666 | 0.093666 | 0.98418 | -0.30258 | 0.98508 | -0.28518 | 25.7323
110 | 0.014692 | 0.0036833 | -0.014689 | -0.0036815 | 3.1827e-06 | 1.8263e-06 | 0.022418 | 0.022419 | 0.022419 | 0.9752 | -0.47743 | 0.97497 | -0.48197 | 6.1589
111 | -0.11182 | -0.02842 | 0.11186 | 0.028446 | 4.2492e-05 | 2.6375e-05 | 0.16841 | 0.16841 | 0.16841 | 0.98885 | -0.21284 | 0.98926 | -0.20495 | 11.5667
112 | -0.11393 | -0.028964 | 0.11398 | 0.028992 | 4.4427e-05 | 2.7606e-05 | 0.17152 | 0.17152 | 0.17152 | 0.98926 | -0.20495 | 0.98968 | -0.19686 | 11.7802
113 | -0.11553 | -0.02938 | 0.11556 | 0.029402 | 3.4045e-05 | 2.1171e-05 | 0.17385 | 0.17385 | 0.17385 | 0.98968 | -0.19686 | 0.99 | -0.19075 | 11.9402
114 | 0.0074384 | 0.0018642 | -0.0074375 | -0.0018639 | 8.5915e-07 | 3.1421e-07 | 0.01118 | 0.01118 | 0.01118 | 0.99 | -0.19075 | 0.98988 | -0.19317 | 3.0715
115 | -0.0021577 | -0.00054078 | 0.0021579 | 0.00054028 | 1.8617e-07 | -5.0075e-07 | 0.0032262 | 0.0032259 | 0.0032262 | 0.99522 | -0.090781 | 0.99531 | -0.088969 | 0.88631
116 | -0.006406 | -0.0016049 | 0.0064064 | 0.001605 | 4.006e-07 | 1.0499e-07 | 0.0095769 | 0.0095768 | 0.0095769 | 0.99531 | -0.088969 | 0.99538 | -0.087656 | 2.631
117 | 0.012762 | 0.0031987 | -0.01276 | -0.0031973 | 2.5417e-06 | 1.404e-06 | 0.019478 | 0.019478 | 0.019478 | 0.97497 | -0.48197 | 0.97476 | -0.48615 | 5.3512
118 | 0.0080922 | 0.0020274 | -0.0080913 | -0.0020271 | 8.3989e-07 | 3.5459e-07 | 0.012353 | 0.012353 | 0.012353 | 0.97476 | -0.48615 | 0.97465 | -0.48833 | 3.3936
119 | 0.0080913 | 0.0020271 | -0.0080894 | -0.0020263 | 1.9494e-06 | 8.2316e-07 | 0.012353 | 0.012353 | 0.012353 | 0.97465 | -0.48833 | 0.97439 | -0.49339 | 3.3937
120 | -0.0016127 | -0.00040419 | 0.0016128 | 0.00040397 | 4.5568e-08 | -2.2036e-07 | 0.0024629 | 0.0024628 | 0.0024629 | 0.97436 | -0.49399 | 0.97439 | -0.49339 | 0.67662
121 | 0.001604 | 0.00040136 | -0.0016039 | -0.00040197 | 1.2484e-07 | -6.1118e-07 | 0.0024493 | 0.0024495 | 0.0024495 | 0.97439 | -0.49339 | 0.97431 | -0.49503 | 0.67295
122 | 0.0048726 | 0.0012209 | -0.0048714 | -0.0012209 | 1.2224e-06 | 4.9223e-08 | 0.0074409 | 0.0074412 | 0.0074412 | 0.97439 | -0.49339 | 0.97413 | -0.49866 | 2.0443
123 | 0.0034759 | 0.00087109 | -0.0034758 | -0.00087113 | 5.7622e-08 | -3.6085e-08 | 0.0052141 | 0.0052141 | 0.0052141 | 0.99197 | -0.15328 | 0.99195 | -0.15363 | 1.4324
124 | -0.031713 | -0.0079571 | 0.03173 | 0.0079677 | 1.7022e-05 | 1.0635e-05 | 0.047602 | 0.047601 | 0.047602 | 0.9914 | -0.16417 | 0.99198 | -0.15291 | 13.0773
125 | 0.028949 | 0.0072645 | -0.028944 | -0.0072611 | 5.4875e-06 | 3.4121e-06 | 0.043454 | 0.043454 | 0.043454 | 0.9914 | -0.16417 | 0.9912 | -0.16814 | 11.9379
126 | 0.025709 | 0.0064504 | -0.025696 | -0.0064422 | 1.339e-05 | 8.2608e-06 | 0.038598 | 0.038598 | 0.038598 | 0.9912 | -0.16814 | 0.99063 | -0.17907 | 10.6039
127 | 0.022412 | 0.0056191 | -0.022408 | -0.0056167 | 3.9404e-06 | 2.4025e-06 | 0.033665 | 0.033665 | 0.033665 | 0.99063 | -0.17907 | 0.99044 | -0.18276 | 9.2487
128 | 0.0084747 | 0.0021231 | -0.0084741 | -0.0021229 | 5.8834e-07 | 2.5198e-07 | 0.012732 | 0.012732 | 0.012732 | 0.99044 | -0.18276 | 0.99037 | -0.18422 | 3.4978
129 | 0.013933 | 0.0034936 | -0.01393 | -0.0034919 | 2.9926e-06 | 1.681e-06 | 0.020933 | 0.020933 | 0.020933 | 0.99044 | -0.18276 | 0.99021 | -0.18727 | 5.7509
130 | 0.0029594 | 0.00074076 | -0.0029592 | -0.00074096 | 1.76e-07 | -1.9285e-07 | 0.0044461 | 0.0044462 | 0.0044462 | 0.99037 | -0.18422 | 0.9903 | -0.18547 | 1.2215
131 | 0.012443 | 0.0031192 | -0.01244 | -0.0031175 | 3.049e-06 | 1.6523e-06 | 0.018699 | 0.018699 | 0.018699 | 0.99021 | -0.18727 | 0.98995 | -0.19241 | 5.137
132 | -0.0019284 | -0.00048331 | 0.0019285 | 0.00048309 | 6.5237e-08 | -2.2423e-07 | 0.0028993 | 0.0028992 | 0.0028993 | 0.98973 | -0.19654 | 0.98977 | -0.19583 | 0.79651
133 | -0.0049051 | -0.0012291 | 0.0049054 | 0.0012291 | 3.0596e-07 | 2.9695e-09 | 0.0073743 | 0.0073742 | 0.0073743 | 0.98977 | -0.19583 | 0.98984 | -0.19452 | 2.0259
134 | -0.0103 | -0.0025809 | 0.010301 | 0.0025814 | 1.0337e-06 | 5.1373e-07 | 0.015483 | 0.015483 | 0.015483 | 0.98984 | -0.19452 | 0.98995 | -0.19241 | 4.2537
135 | 0.0053943 | 0.0013518 | -0.0053935 | -0.0013517 | 7.8457e-07 | 9.3231e-08 | 0.0081092 | 0.0081093 | 0.0081093 | 0.98984 | -0.19452 | 0.98968 | -0.19757 | 2.2278
136 | 0.0035154 | 0.00088099 | -0.0035154 | -0.00088101 | 3.0091e-08 | -1.765e-08 | 0.0052856 | 0.0052856 | 0.0052856 | 0.98968 | -0.19757 | 0.98967 | -0.19775 | 1.4521
137 | 0.0018792 | 0.00047095 | -0.0018792 | -0.00047098 | 8.9066e-09 | -3.2527e-08 | 0.0028255 | 0.0028255 | 0.0028255 | 0.98967 | -0.19775 | 0.98967 | -0.19785 | 0.77625
138 | 0.0029592 | 0.00074096 | -0.0029588 | -0.00074139 | 3.9223e-07 | -4.2957e-07 | 0.0044462 | 0.0044464 | 0.0044464 | 0.9903 | -0.18547 | 0.99016 | -0.18825 | 1.2216
139 | -0.0029587 | -0.00074152 | 0.0029588 | 0.00074139 | 1.2035e-07 | -1.3175e-07 | 0.0044465 | 0.0044464 | 0.0044465 | 0.99012 | -0.18911 | 0.99016 | -0.18825 | 1.2216

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58091 | 0.1487

## res_load
| p_mw | q_mvar
0 | 0.026253 | 0.0065796
1 | 0.0035568 | 0.00089141
2 | 0.026894 | 0.0067402
3 | 0.0266 | 0.0066667
4 | 0.010587 | 0.0026535
5 | 0.010553 | 0.0026449
6 | 0.0070989 | 0.0017792
7 | 0.0086418 | 0.0021658
8 | 0.0099534 | 0.0024946
9 | 0.0067073 | 0.001681
10 | 0.010494 | 0.00263
11 | 0.0085957 | 0.0021543
12 | 0.0062765 | 0.001573
13 | 0.0090854 | 0.002277
14 | 0.0091903 | 0.0023033
15 | 0.0041665 | 0.0010442
16 | 0.0089472 | 0.0022424
17 | 0.0068782 | 0.0017238
18 | 0.0068749 | 0.001723
19 | 0.0099986 | 0.0025059
20 | 0.0090892 | 0.002278
21 | 0.016681 | 0.0041807
22 | 0.018279 | 0.0045811
23 | 0.034515 | 0.0086503
24 | 0.020534 | 0.0051464
25 | 0.0085477 | 0.0021422
26 | 0.00072413 | 0.00018148
27 | 0.00068255 | 0.00017106
28 | 0.0090836 | 0.0022766
29 | 0.0085462 | 0.0021419
30 | 0.016691 | 0.0041832
31 | 0.012837 | 0.0032172
32 | 0.0084863 | 0.0021269
33 | 0.0053707 | 0.001346
34 | 0.0061354 | 0.0015377
35 | 0.0042818 | 0.0010731
36 | 0.0031677 | 0.00079389
37 | 0.0015872 | 0.00039778
38 | 0.0022801 | 0.00057144
39 | 0.0054037 | 0.0013543
40 | 0.0049931 | 0.0012514
41 | 0.0033753 | 0.00084594
42 | 0.0011925 | 0.00029887
43 | 0.0011909 | 0.00029847
44 | 0.0011913 | 0.00029858
45 | 0.0011892 | 0.00029803
46 | 0.0019266 | 0.00048285
47 | 0.0036942 | 0.00092584
48 | 0.0011829 | 0.00029647
49 | 0.0051727 | 0.0012964
50 | 0.0025127 | 0.00062974
51 | 0.0031304 | 0.00078455
52 | 0.0020467 | 0.00051296
53 | 0.0051616 | 0.0012936
54 | 0.0044063 | 0.0011043
55 | 0.0023867 | 0.00059817
56 | 0.024629 | 0.0061727
57 | 0.0043635 | 0.0010936
58 | 0.0019613 | 0.00049155
59 | 0.0051974 | 0.0013026
60 | 0.0021576 | 0.00054074
61 | 0.0016276 | 0.00040793
62 | 0.0023843 | 0.00059755
63 | 0.0020672 | 0.00051809
64 | 0.0015494 | 0.00038831
65 | 0.0022754 | 0.00057026
66 | 0.0021577 | 0.00054078
67 | 0.0042481 | 0.0010647
68 | 0.0040367 | 0.0010117
69 | 0.0019266 | 0.00048284
70 | 0.0046677 | 0.0011698
71 | 0.0016127 | 0.00040419
72 | 0.0016039 | 0.00040197
73 | 0.0024936 | 0.00062495
74 | 0.0034758 | 0.00087113
75 | 0.0027635 | 0.00069259
76 | 0.0040337 | 0.0010109
77 | 0.0032346 | 0.00081066
78 | 0.0032841 | 0.00082307
79 | 0.0055147 | 0.0013821
80 | 0.0014872 | 0.00037273
81 | 0.0019284 | 0.00048331
82 | 0.0029766 | 0.00074602
83 | 0.0021391 | 0.00053611
84 | 0.0018781 | 0.00047069
85 | 0.0016362 | 0.00041006
86 | 0.0018792 | 0.00047098
87 | 0.0029587 | 0.00074152
88 | 0.0048714 | 0.0012209

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1