## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2542-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2542-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2542-1_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2542-1_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2542-1_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2542-1_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2542-1_0_5_node_112 | 0.4 | n |  | TRUE
7 | bus_LV_2542-1_0_5_node_105 | 0.4 | n |  | TRUE
8 | bus_LV_2542-1_0_5_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_2542-1_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2542-1_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2542-1_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2542-1_0_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2542-1_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2542-1_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2542-1_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2542-1_0_5_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_2542-1_0_5_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_2542-1_0_5_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_2542-1_0_5_node_113 | 0.4 | n |  | TRUE
20 | bus_LV_2542-1_0_5_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2542-1_0_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2542-1_0_5_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_2542-1_0_5_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_2542-1_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2542-1_0_5_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_2542-1_0_5_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_2542-1_0_5_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_2542-1_0_5_node_107 | 0.4 | n |  | TRUE
29 | bus_LV_2542-1_0_5_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_2542-1_0_5_node_111 | 0.4 | n |  | TRUE
31 | bus_LV_2542-1_0_5_node_102 | 0.4 | n |  | TRUE
32 | bus_LV_2542-1_0_5_node_103 | 0.4 | n |  | TRUE
33 | bus_LV_2542-1_0_5_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_2542-1_0_5_node_106 | 0.4 | n |  | TRUE
35 | bus_LV_2542-1_0_5_node_109 | 0.4 | n |  | TRUE
36 | bus_LV_2542-1_0_5_node_115 | 0.4 | n |  | TRUE
37 | bus_LV_2542-1_0_5_node_114 | 0.4 | n |  | TRUE
38 | bus_MV_292_0_node_154 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2542-1_0_5_load_0 | 0 | 0.0019662 | 0.00049278 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2542-1_0_5_load_1 | 1 | 0.0019699 | 0.0004937 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2542-1_0_5_load_5 | 5 | 0.0030099 | 0.00075435 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2542-1_0_5_load_112 | 6 | 0.0016448 | 0.00041222 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2542-1_0_5_load_31 | 8 | 0.00093225 | 0.00023364 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2542-1_0_5_load_6 | 9 | 0.065189 | 0.016338 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2542-1_0_5_load_7 | 10 | 0.0014107 | 0.00035356 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2542-1_0_5_load_10 | 13 | 0.029577 | 0.0074127 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2542-1_0_5_load_11 | 14 | 0.028448 | 0.0071297 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2542-1_0_5_load_12 | 15 | 0.0019089 | 0.00047842 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2542-1_0_5_load_18 | 17 | 0.032923 | 0.0082512 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2542-1_0_5_load_25 | 18 | 0.03456 | 0.0086615 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2542-1_0_5_load_113 | 19 | 0.00076127 | 0.00019079 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2542-1_0_5_load_19 | 20 | 0.02441 | 0.0061178 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2542-1_0_5_load_20 | 21 | 0.025541 | 0.0064011 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2542-1_0_5_load_22 | 24 | 0.01955 | 0.0048997 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2542-1_0_5_load_24 | 25 | 0.020026 | 0.005019 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2542-1_0_5_load_26 | 26 | 0.0084182 | 0.0021098 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2542-1_0_5_load_28 | 27 | 0.0037525 | 0.00094047 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2542-1_0_5_load_107 | 28 | 0.016054 | 0.0040235 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2542-1_0_5_load_37 | 29 | 9.9253e-05 | 2.4875e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2542-1_0_5_load_111 | 30 | 0.00022662 | 5.6797e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2542-1_0_5_load_102 | 31 | 0.002956 | 0.00074085 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2542-1_0_5_load_103 | 32 | 0.00079478 | 0.00019919 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2542-1_0_5_load_104 | 33 | 0.0072199 | 0.0018095 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2542-1_0_5_load_106 | 34 | 0.0060544 | 0.0015174 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2542-1_0_5_load_109 | 35 | 0.001002 | 0.00025114 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2542-1_0_5_load_115 | 36 | 0.00064345 | 0.00016126 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2542-1_0_5_load_114 | 37 | 0.0022006 | 0.00055153 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2542-1_0_5_line_0 |  | 0 | 1 | 0.023793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2542-1_0_5_line_1 |  | 0 | 2 | 0.027738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2542-1_0_5_line_2 |  | 1 | 3 | 0.066409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2542-1_0_5_line_3 |  | 2 | 4 | 0.048561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2542-1_0_5_line_4 |  | 2 | 5 | 0.047387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2542-1_0_5_line_5 |  | 3 | 6 | 0.0372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2542-1_0_5_line_6 |  | 3 | 7 | 0.04388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2542-1_0_5_line_7 |  | 4 | 8 | 0.024495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2542-1_0_5_line_8 |  | 6 | 37 | 0.021169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2542-1_0_5_line_9 |  | 7 | 35 | 0.0031903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2542-1_0_5_line_10 |  | 7 | 32 | 0.026213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2542-1_0_5_line_11 |  | 9 | 10 | 0.030166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2542-1_0_5_line_12 |  | 9 | 11 | 0.060369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2542-1_0_5_line_13 |  | 10 | 12 | 0.10449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2542-1_0_5_line_14 |  | 11 | 13 | 0.041289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2542-1_0_5_line_15 |  | 11 | 14 | 0.022216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2542-1_0_5_line_16 |  | 11 | 15 | 0.091882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2542-1_0_5_line_17 |  | 12 | 16 | 0.071779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2542-1_0_5_line_18 |  | 13 | 17 | 0.024797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2542-1_0_5_line_19 |  | 14 | 18 | 0.025445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2542-1_0_5_line_20 |  | 15 | 19 | 0.0047345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2542-1_0_5_line_21 |  | 16 | 30 | 0.021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2542-1_0_5_line_22 |  | 17 | 20 | 0.027711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2542-1_0_5_line_23 |  | 18 | 26 | 0.029474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2542-1_0_5_line_24 |  | 19 | 37 | 0.025228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2542-1_0_5_line_25 |  | 20 | 21 | 0.03564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2542-1_0_5_line_26 |  | 21 | 22 | 0.010199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2542-1_0_5_line_27 |  | 22 | 23 | 0.021549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2542-1_0_5_line_28 |  | 22 | 24 | 0.025205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2542-1_0_5_line_29 |  | 23 | 25 | 0.024647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2542-1_0_5_line_30 |  | 27 | 28 | 0.027449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2542-1_0_5_line_31 |  | 28 | 34 | 0.082258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2542-1_0_5_line_32 |  | 29 | 30 | 0.039496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2542-1_0_5_line_33 |  | 31 | 32 | 0.025543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2542-1_0_5_line_34 |  | 31 | 33 | 0.025596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2542-1_0_5_line_35 |  | 33 | 34 | 0.063833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2542-1_0_5_line_36 |  | 35 | 36 | 0.011449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2542-1_0_5_trafo_8 | 0.63 MVA 20/0.4 kV | 38 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2604337.6437 | 1228585.9025 | 2604341.5107 | 1228562.4258
1 | 2604319.0804 | 1228594.2226 | 2604322.7996 | 1228595.1036 | 2604330.8146 | 1228595.9654 | 2604335.8977 | 1228596.5027 | 2604337.6437 | 1228585.9025
2 | 2604352.3036 | 1228496.9 | 2604341.5107 | 1228562.4258
3 | 2604319.0804 | 1228594.2226 | 2604315.0483 | 1228607.0718 | 2604310.3761 | 1228625.1125 | 2604305.4783 | 1228640.8294
4 | 2604319.0804 | 1228594.2226 | 2604273.5993 | 1228580.9168
5 | 2604352.3036 | 1228496.9 | 2604388.6128 | 1228504.991
6 | 2604352.3036 | 1228496.9 | 2604359.4035 | 1228453.6017
7 | 2604305.4783 | 1228640.8294 | 2604321.0582 | 1228646.5773 | 2604322.4897 | 1228647.1008 | 2604325.5237 | 1228652.6952
8 | 2604409.2748 | 1228509.5953 | 2604388.6128 | 1228504.991
9 | 2604359.4035 | 1228453.6017 | 2604359.9298 | 1228450.4551
10 | 2604359.4035 | 1228453.6017 | 2604333.9185 | 1228447.4688
11 | 2604518.5892 | 1228595.6956 | 2604513.7855 | 1228625.4767
12 | 2604528.2025 | 1228536.0969 | 2604518.5892 | 1228595.6956
13 | 2604496.6254 | 1228728.5428 | 2604506.5106 | 1228669.6819 | 2604509.4326 | 1228652.4628 | 2604513.7855 | 1228625.4767
14 | 2604528.2025 | 1228536.0969 | 2604568.697 | 1228544.1588
15 | 2604528.2025 | 1228536.0969 | 2604526.2776 | 1228526.6121 | 2604526.0024 | 1228514.077
16 | 2604528.2025 | 1228536.0969 | 2604438.5197 | 1228516.1122
17 | 2604426.8487 | 1228710.8808 | 2604496.6254 | 1228728.5428
18 | 2604568.697 | 1228544.1588 | 2604593.0166 | 1228549.0006
19 | 2604525.2813 | 1228488.6486 | 2604525.4864 | 1228490.579 | 2604526.0024 | 1228514.077
20 | 2604438.5197 | 1228516.1122 | 2604433.8985 | 1228515.0824
21 | 2604426.8487 | 1228710.8808 | 2604406.1241 | 1228705.6339
22 | 2604620.1943 | 1228554.4113 | 2604593.0166 | 1228549.0006
23 | 2604525.2813 | 1228488.6486 | 2604522.1673 | 1228459.3393
24 | 2604433.8985 | 1228515.0824 | 2604409.2748 | 1228509.5953
25 | 2604620.1943 | 1228554.4113 | 2604655.1485 | 1228561.3702
26 | 2604665.1516 | 1228563.3617 | 2604655.1485 | 1228561.3702
27 | 2604686.3997 | 1228567.3027 | 2604665.1516 | 1228563.3617
28 | 2604665.1516 | 1228563.3617 | 2604669.0766 | 1228538.4646
29 | 2604686.3997 | 1228567.3027 | 2604710.5005 | 1228572.4625
30 | 2604208.1673 | 1228485.5345 | 2604201.6234 | 1228512.1923
31 | 2604227.7776 | 1228405.6482 | 2604208.1673 | 1228485.5345
32 | 2604367.8363 | 1228695.9404 | 2604406.1241 | 1228705.6339
33 | 2604309.084 | 1228441.4925 | 2604333.9185 | 1228447.4688
34 | 2604284.1988 | 1228435.5039 | 2604309.084 | 1228441.4925
35 | 2604284.1988 | 1228435.5039 | 2604227.7776 | 1228405.6482
36 | 2604361.8186 | 1228439.1626 | 2604359.9298 | 1228450.4551

## bus_geodata
| x | y | coords
0 | 2604337.6437 | 1228585.9025
1 | 2604341.5107 | 1228562.4258
2 | 2604319.0804 | 1228594.2226
3 | 2604352.3036 | 1228496.9
4 | 2604305.4783 | 1228640.8294
5 | 2604273.5993 | 1228580.9168
6 | 2604388.6128 | 1228504.991
7 | 2604359.4035 | 1228453.6017
8 | 2604325.5237 | 1228652.6952
9 | 2604518.5892 | 1228595.6956
10 | 2604513.7855 | 1228625.4767
11 | 2604528.2025 | 1228536.0969
12 | 2604496.6254 | 1228728.5428
13 | 2604568.697 | 1228544.1588
14 | 2604526.0024 | 1228514.077
15 | 2604438.5197 | 1228516.1122
16 | 2604426.8487 | 1228710.8808
17 | 2604593.0166 | 1228549.0006
18 | 2604525.2813 | 1228488.6486
19 | 2604433.8985 | 1228515.0824
20 | 2604620.1943 | 1228554.4113
21 | 2604655.1485 | 1228561.3702
22 | 2604665.1516 | 1228563.3617
23 | 2604686.3997 | 1228567.3027
24 | 2604669.0766 | 1228538.4646
25 | 2604710.5005 | 1228572.4625
26 | 2604522.1673 | 1228459.3393
27 | 2604201.6234 | 1228512.1923
28 | 2604208.1673 | 1228485.5345
29 | 2604367.8363 | 1228695.9404
30 | 2604406.1241 | 1228705.6339
31 | 2604309.084 | 1228441.4925
32 | 2604333.9185 | 1228447.4688
33 | 2604284.1988 | 1228435.5039
34 | 2604227.7776 | 1228405.6482
35 | 2604359.9298 | 1228450.4551
36 | 2604361.8186 | 1228439.1626
37 | 2604409.2748 | 1228509.5953
38 | 2604352.3036 | 1228496.9

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99103 | -0.1719 | 0.0019662 | 0.00049278
1 | 0.99115 | -0.16941 | 0.0019699 | 0.0004937
2 | 0.99093 | -0.17385 | 0 | 0
3 | 0.99163 | -0.16012 | 0 | 0
4 | 0.99088 | -0.17465 | 0 | 0
5 | 0.99079 | -0.17638 | 0.0030099 | 0.00075435
6 | 0.99322 | -0.12959 | 0.0016448 | 0.00041222
7 | 0.99008 | -0.1901 | 0 | 0
8 | 0.99086 | -0.17506 | 0.00093225 | 0.00023364
9 | 0.99632 | -0.070689 | 0.065189 | 0.016338
10 | 0.99628 | -0.071613 | 0.0014107 | 0.00035356
11 | 1 | 0 | -0.34693 | -0.08731
12 | 0.99624 | -0.072222 | 0 | 0
13 | 0.99713 | -0.054863 | 0.029577 | 0.0074127
14 | 0.99856 | -0.027698 | 0.028448 | 0.0071297
15 | 0.99554 | -0.085086 | 0.0019089 | 0.00047842
16 | 0.99622 | -0.072637 | 0 | 0
17 | 0.99435 | -0.10824 | 0.032923 | 0.0082512
18 | 0.99756 | -0.046833 | 0.03456 | 0.0086615
19 | 0.99532 | -0.089332 | 0.00076127 | 0.00019079
20 | 0.99208 | -0.15208 | 0.02441 | 0.0061178
21 | 0.98995 | -0.19327 | 0.025541 | 0.0064011
22 | 0.98958 | -0.20045 | 0 | 0
23 | 0.98919 | -0.20813 | 0 | 0
24 | 0.98913 | -0.20922 | 0.01955 | 0.0048997
25 | 0.98873 | -0.21693 | 0.020026 | 0.005019
26 | 0.99734 | -0.05118 | 0.0084182 | 0.0021098
27 | 0.98445 | -0.29948 | 0.0037525 | 0.00094047
28 | 0.98454 | -0.29763 | 0.016054 | 0.0040235
29 | 0.99621 | -0.07283 | 9.9253e-05 | 2.4875e-05
30 | 0.99622 | -0.07276 | 0.00022662 | 5.6797e-05
31 | 0.98834 | -0.2237 | 0.002956 | 0.00074085
32 | 0.98919 | -0.20729 | 0.00079478 | 0.00019919
33 | 0.98757 | -0.23882 | 0.0072199 | 0.0018095
34 | 0.98605 | -0.26837 | 0.0060544 | 0.0015174
35 | 0.99007 | -0.19019 | 0.001002 | 0.00025114
36 | 0.99007 | -0.19032 | 0.00064345 | 0.00016126
37 | 0.99415 | -0.11165 | 0.0022006 | 0.00055153
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0059092 | -0.0014794 | 0.0059099 | 0.0014795 | 7.0229e-07 | 1.4286e-07 | 0.008872 | 0.0088719 | 0.008872 | 0.99103 | -0.1719 | 0.99115 | -0.16941 | 2.4374
1 | 0.0039429 | 0.00098659 | -0.0039426 | -0.00098671 | 3.6452e-07 | -1.2407e-07 | 0.0059197 | 0.0059198 | 0.0059198 | 0.99103 | -0.1719 | 0.99093 | -0.17385 | 1.6263
2 | -0.0078797 | -0.0019732 | 0.0078832 | 0.0019746 | 3.4846e-06 | 1.3739e-06 | 0.011829 | 0.011829 | 0.011829 | 0.99115 | -0.16941 | 0.99163 | -0.16012 | 3.2498
3 | 0.0009323 | 0.00023274 | -0.00093227 | -0.00023334 | 3.5681e-08 | -6.0271e-07 | 0.0013997 | 0.0013999 | 0.0013999 | 0.99093 | -0.17385 | 0.99088 | -0.17465 | 0.38458
4 | 0.0030103 | 0.00075398 | -0.0030099 | -0.00075435 | 3.631e-07 | -3.7799e-07 | 0.0045202 | 0.0045204 | 0.0045204 | 0.99093 | -0.17385 | 0.99079 | -0.17638 | 1.2419
5 | -0.046563 | -0.011744 | 0.046631 | 0.011787 | 6.8154e-05 | 4.3138e-05 | 0.069897 | 0.069897 | 0.069897 | 0.99163 | -0.16012 | 0.99322 | -0.12959 | 19.2025
6 | 0.03868 | 0.009769 | -0.038624 | -0.0097341 | 5.5485e-05 | 3.4945e-05 | 0.058068 | 0.058068 | 0.058068 | 0.99163 | -0.16012 | 0.99008 | -0.1901 | 15.9529
7 | 0.00093227 | 0.00023334 | -0.00093225 | -0.00023364 | 1.8002e-08 | -3.0399e-07 | 0.0013999 | 0.0014 | 0.0014 | 0.99088 | -0.17465 | 0.99086 | -0.17506 | 0.38461
8 | -0.048276 | -0.012199 | 0.048317 | 0.012225 | 4.1566e-05 | 2.6328e-05 | 0.072361 | 0.072361 | 0.072361 | 0.99322 | -0.12959 | 0.99415 | -0.11165 | 19.8794
9 | 0.0016455 | 0.00041222 | -0.0016455 | -0.00041226 | 7.3169e-09 | -3.6346e-08 | 0.002473 | 0.002473 | 0.002473 | 0.99008 | -0.1901 | 0.99007 | -0.19019 | 0.6794
10 | 0.036979 | 0.0093218 | -0.036948 | -0.0093027 | 3.0382e-05 | 1.9108e-05 | 0.055595 | 0.055596 | 0.055596 | 0.99008 | -0.1901 | 0.98919 | -0.20729 | 15.2735
11 | 0.0017367 | 0.00043181 | -0.0017366 | -0.00043216 | 7.6037e-08 | -3.4417e-07 | 0.0025925 | 0.0025927 | 0.0025927 | 0.99632 | -0.070689 | 0.99628 | -0.071613 | 0.71228
12 | -0.066925 | -0.01677 | 0.067151 | 0.016914 | 0.00022617 | 0.00014396 | 0.099952 | 0.099952 | 0.099952 | 0.99632 | -0.070689 | 1 | 0 | 27.4594
13 | 0.00032589 | 7.8596e-05 | -0.00032588 | -7.995e-05 | 9.2513e-09 | -1.3546e-06 | 0.00048568 | 0.00048615 | 0.00048615 | 0.99628 | -0.071613 | 0.99624 | -0.072222 | 0.13356
14 | 0.1531 | 0.038783 | -0.1527 | -0.038527 | 0.0004023 | 0.00025639 | 0.22796 | 0.22796 | 0.22796 | 1 | 0 | 0.99713 | -0.054863 | 31.3129
15 | 0.071562 | 0.017987 | -0.071467 | -0.017927 | 9.4499e-05 | 6.0188e-05 | 0.1065 | 0.1065 | 0.1065 | 1 | 0 | 0.99856 | -0.027698 | 29.2591
16 | 0.053471 | 0.013626 | -0.053253 | -0.013487 | 0.00021857 | 0.00013868 | 0.079646 | 0.079646 | 0.079646 | 1 | 0 | 0.99554 | -0.085086 | 21.8808
17 | 0.00032588 | 7.995e-05 | -0.00032588 | -8.0881e-05 | 6.3658e-09 | -9.3054e-07 | 0.00048615 | 0.00048647 | 0.00048647 | 0.99624 | -0.072222 | 0.99622 | -0.072637 | 0.13365
18 | 0.12312 | 0.031114 | -0.1228 | -0.030913 | 0.00031421 | 0.00020077 | 0.18382 | 0.18382 | 0.18382 | 0.99713 | -0.054863 | 0.99435 | -0.10824 | 50.5001
19 | 0.043019 | 0.010797 | -0.04298 | -0.010772 | 3.9219e-05 | 2.4768e-05 | 0.064111 | 0.064111 | 0.064111 | 0.99856 | -0.027698 | 0.99756 | -0.046833 | 17.6129
20 | 0.051344 | 0.013009 | -0.051333 | -0.013002 | 1.047e-05 | 6.6392e-06 | 0.076793 | 0.076793 | 0.076793 | 0.99554 | -0.085086 | 0.99532 | -0.089332 | 21.0969
21 | 0.00032588 | 8.0881e-05 | -0.00032588 | -8.1158e-05 | 1.8976e-09 | -2.7714e-07 | 0.00048647 | 0.00048657 | 0.00048657 | 0.99622 | -0.072637 | 0.99622 | -0.07276 | 0.13367
22 | 0.089881 | 0.022662 | -0.089693 | -0.022542 | 0.00018813 | 0.00012005 | 0.13455 | 0.13455 | 0.13455 | 0.99435 | -0.10824 | 0.99208 | -0.15208 | 36.965
23 | 0.00842 | 0.0021105 | -0.0084182 | -0.0021098 | 1.7436e-06 | 7.3118e-07 | 0.01256 | 0.01256 | 0.01256 | 0.99756 | -0.046833 | 0.99734 | -0.05118 | 3.4505
24 | 0.050572 | 0.012811 | -0.050518 | -0.012777 | 5.4148e-05 | 3.4327e-05 | 0.075655 | 0.075655 | 0.075655 | 0.99532 | -0.089332 | 0.99415 | -0.11165 | 20.7843
25 | 0.065283 | 0.016424 | -0.065155 | -0.016343 | 0.0001282 | 8.1589e-05 | 0.09794 | 0.09794 | 0.09794 | 0.99208 | -0.15208 | 0.98995 | -0.19327 | 26.9066
26 | 0.039614 | 0.0099417 | -0.0396 | -0.0099331 | 1.3563e-05 | 8.5492e-06 | 0.059549 | 0.059549 | 0.059549 | 0.98995 | -0.19327 | 0.98958 | -0.20045 | 16.3596
27 | 0.020042 | 0.0050285 | -0.020035 | -0.0050241 | 7.3402e-06 | 4.421e-06 | 0.030139 | 0.030139 | 0.030139 | 0.98958 | -0.20045 | 0.98919 | -0.20813 | 8.2799
28 | 0.019558 | 0.0049046 | -0.01955 | -0.0048997 | 8.1754e-06 | 4.9086e-06 | 0.02941 | 0.02941 | 0.02941 | 0.98958 | -0.20045 | 0.98913 | -0.20922 | 8.0798
29 | 0.020035 | 0.0050241 | -0.020026 | -0.005019 | 8.3955e-06 | 5.0569e-06 | 0.030139 | 0.030139 | 0.030139 | 0.98919 | -0.20813 | 0.98873 | -0.21693 | 8.2799
30 | -0.0037525 | -0.00094047 | 0.0037528 | 0.00094033 | 3.3115e-07 | -1.371e-07 | 0.005672 | 0.0056719 | 0.005672 | 0.98445 | -0.29948 | 0.98454 | -0.29763 | 1.5582
31 | -0.019807 | -0.0049638 | 0.019834 | 0.0049805 | 2.7642e-05 | 1.6643e-05 | 0.029935 | 0.029935 | 0.029935 | 0.98454 | -0.29763 | 0.98605 | -0.26837 | 8.224
32 | -9.9253e-05 | -2.4875e-05 | 9.9254e-05 | 2.4361e-05 | 3.2513e-10 | -5.1403e-07 | 0.00014825 | 0.00014807 | 0.00014825 | 0.99621 | -0.07283 | 0.99622 | -0.07276 | 0.040729
33 | -0.036125 | -0.0090857 | 0.036153 | 0.0091035 | 2.8347e-05 | 1.7815e-05 | 0.0544 | 0.0544 | 0.0544 | 0.98834 | -0.2237 | 0.98919 | -0.20729 | 14.9451
34 | 0.033169 | 0.0083449 | -0.033145 | -0.0083299 | 2.3948e-05 | 1.4999e-05 | 0.04995 | 0.04995 | 0.04995 | 0.98834 | -0.2237 | 0.98757 | -0.23882 | 13.7224
35 | 0.025925 | 0.0065204 | -0.025889 | -0.0064978 | 3.6542e-05 | 2.2572e-05 | 0.039071 | 0.039071 | 0.039071 | 0.98757 | -0.23882 | 0.98605 | -0.26837 | 10.7339
36 | 0.00064346 | 0.00016112 | -0.00064345 | -0.00016126 | 4.0152e-09 | -1.4467e-07 | 0.00096702 | 0.00096708 | 0.00096708 | 0.99007 | -0.19019 | 0.99007 | -0.19032 | 0.26568

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34693 | 0.08731

## res_load
| p_mw | q_mvar
0 | 0.0019662 | 0.00049278
1 | 0.0019699 | 0.0004937
2 | 0.0030099 | 0.00075435
3 | 0.0016448 | 0.00041222
4 | 0.00093225 | 0.00023364
5 | 0.065189 | 0.016338
6 | 0.0014107 | 0.00035356
7 | 0.029577 | 0.0074127
8 | 0.028448 | 0.0071297
9 | 0.0019089 | 0.00047842
10 | 0.032923 | 0.0082512
11 | 0.03456 | 0.0086615
12 | 0.00076127 | 0.00019079
13 | 0.02441 | 0.0061178
14 | 0.025541 | 0.0064011
15 | 0.01955 | 0.0048997
16 | 0.020026 | 0.005019
17 | 0.0084182 | 0.0021098
18 | 0.0037525 | 0.00094047
19 | 0.016054 | 0.0040235
20 | 9.9253e-05 | 2.4875e-05
21 | 0.00022662 | 5.6797e-05
22 | 0.002956 | 0.00074085
23 | 0.00079478 | 0.00019919
24 | 0.0072199 | 0.0018095
25 | 0.0060544 | 0.0015174
26 | 0.001002 | 0.00025114
27 | 0.00064345 | 0.00016126
28 | 0.0022006 | 0.00055153

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1