## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2542-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2542-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2542-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2542-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2542-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2542-8_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2542-8_0_4_node_96 | 0.4 | n |  | TRUE
7 | bus_LV_2542-8_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2542-8_0_4_node_108 | 0.4 | n |  | TRUE
9 | bus_LV_2542-8_0_4_node_121 | 0.4 | n |  | TRUE
10 | bus_LV_2542-8_0_4_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2542-8_0_4_node_109 | 0.4 | n |  | TRUE
12 | bus_LV_2542-8_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2542-8_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2542-8_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2542-8_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2542-8_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_2542-8_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_2542-8_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2542-8_0_4_node_107 | 0.4 | n |  | TRUE
20 | bus_LV_2542-8_0_4_node_133 | 0.4 | n |  | TRUE
21 | bus_LV_2542-8_0_4_node_105 | 0.4 | n |  | TRUE
22 | bus_LV_2542-8_0_4_node_116 | 0.4 | n |  | TRUE
23 | bus_LV_2542-8_0_4_node_115 | 0.4 | n |  | TRUE
24 | bus_LV_2542-8_0_4_node_117 | 0.4 | n |  | TRUE
25 | bus_LV_2542-8_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2542-8_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2542-8_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2542-8_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2542-8_0_4_node_118 | 0.4 | n |  | TRUE
30 | bus_LV_2542-8_0_4_node_119 | 0.4 | n |  | TRUE
31 | bus_LV_2542-8_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2542-8_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2542-8_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2542-8_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2542-8_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2542-8_0_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_2542-8_0_4_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_2542-8_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_2542-8_0_4_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_2542-8_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2542-8_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2542-8_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2542-8_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2542-8_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2542-8_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2542-8_0_4_node_129 | 0.4 | n |  | TRUE
47 | bus_LV_2542-8_0_4_node_93 | 0.4 | n |  | TRUE
48 | bus_LV_2542-8_0_4_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_2542-8_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_2542-8_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2542-8_0_4_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_2542-8_0_4_node_85 | 0.4 | n |  | TRUE
53 | bus_LV_2542-8_0_4_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_2542-8_0_4_node_113 | 0.4 | n |  | TRUE
55 | bus_LV_2542-8_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_2542-8_0_4_node_94 | 0.4 | n |  | TRUE
57 | bus_LV_2542-8_0_4_node_131 | 0.4 | n |  | TRUE
58 | bus_LV_2542-8_0_4_node_128 | 0.4 | n |  | TRUE
59 | bus_LV_2542-8_0_4_node_130 | 0.4 | n |  | TRUE
60 | bus_LV_2542-8_0_4_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_2542-8_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_2542-8_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2542-8_0_4_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2542-8_0_4_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_2542-8_0_4_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_2542-8_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_2542-8_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_2542-8_0_4_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_2542-8_0_4_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_2542-8_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_2542-8_0_4_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_2542-8_0_4_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_2542-8_0_4_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_2542-8_0_4_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_2542-8_0_4_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_2542-8_0_4_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_2542-8_0_4_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_2542-8_0_4_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_2542-8_0_4_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_2542-8_0_4_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_2542-8_0_4_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_2542-8_0_4_node_57 | 0.4 | n |  | TRUE
83 | bus_LV_2542-8_0_4_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_2542-8_0_4_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_2542-8_0_4_node_125 | 0.4 | n |  | TRUE
86 | bus_LV_2542-8_0_4_node_126 | 0.4 | n |  | TRUE
87 | bus_LV_2542-8_0_4_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_2542-8_0_4_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2542-8_0_4_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_2542-8_0_4_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_2542-8_0_4_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_2542-8_0_4_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_2542-8_0_4_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_2542-8_0_4_node_99 | 0.4 | n |  | TRUE
95 | bus_LV_2542-8_0_4_node_120 | 0.4 | n |  | TRUE
96 | bus_LV_2542-8_0_4_node_66 | 0.4 | n |  | TRUE
97 | bus_LV_2542-8_0_4_node_67 | 0.4 | n |  | TRUE
98 | bus_LV_2542-8_0_4_node_68 | 0.4 | n |  | TRUE
99 | bus_LV_2542-8_0_4_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_2542-8_0_4_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_2542-8_0_4_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_2542-8_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_2542-8_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2542-8_0_4_node_78 | 0.4 | n |  | TRUE
105 | bus_LV_2542-8_0_4_node_79 | 0.4 | n |  | TRUE
106 | bus_LV_2542-8_0_4_node_80 | 0.4 | n |  | TRUE
107 | bus_LV_2542-8_0_4_node_81 | 0.4 | n |  | TRUE
108 | bus_LV_2542-8_0_4_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_2542-8_0_4_node_92 | 0.4 | n |  | TRUE
110 | bus_LV_2542-8_0_4_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_2542-8_0_4_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_2542-8_0_4_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_2542-8_0_4_node_87 | 0.4 | n |  | TRUE
114 | bus_LV_2542-8_0_4_node_123 | 0.4 | n |  | TRUE
115 | bus_LV_2542-8_0_4_node_122 | 0.4 | n |  | TRUE
116 | bus_LV_2542-8_0_4_node_132 | 0.4 | n |  | TRUE
117 | bus_LV_2542-8_0_4_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_2542-8_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_2542-8_0_4_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_2542-8_0_4_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2542-8_0_4_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_2542-8_0_4_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_2542-8_0_4_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_2542-8_0_4_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_2542-8_0_4_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_2542-8_0_4_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_2542-8_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_MV_292_0_node_122 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2542-8_0_4_load_0 | 0 | 0.0019454 | 0.00048757 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2542-8_0_4_load_1 | 1 | 0.00074638 | 0.00018706 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2542-8_0_4_load_3 | 3 | 0.0016734 | 0.0004194 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2542-8_0_4_load_4 | 4 | 0.0011328 | 0.00028391 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2542-8_0_4_load_5 | 5 | 0.0076483 | 0.0019169 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2542-8_0_4_load_96 | 6 | 0.0013831 | 0.00034663 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2542-8_0_4_load_12 | 7 | 0.0032405 | 0.00081214 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2542-8_0_4_load_108 | 8 | 0.0028018 | 0.00070221 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2542-8_0_4_load_121 | 9 | 0.0018256 | 0.00045754 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2542-8_0_4_load_13 | 10 | 0.0038189 | 0.00095712 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2542-8_0_4_load_6 | 12 | 0.0025277 | 0.00063351 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2542-8_0_4_load_7 | 13 | 0.0023146 | 0.0005801 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2542-8_0_4_load_17 | 16 | 0.00095251 | 0.00023872 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2542-8_0_4_load_18 | 17 | 0.001281 | 0.00032105 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2542-8_0_4_load_14 | 18 | 0.0012733 | 0.00031911 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2542-8_0_4_load_133 | 20 | 0.0017998 | 0.00045108 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2542-8_0_4_load_116 | 22 | 0.0021926 | 0.00054951 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2542-8_0_4_load_117 | 24 | 0.0017944 | 0.00044973 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2542-8_0_4_load_15 | 25 | 0.0011252 | 0.00028201 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2542-8_0_4_load_19 | 27 | 0.0015134 | 0.0003793 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2542-8_0_4_load_20 | 28 | 0.0018195 | 0.00045601 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2542-8_0_4_load_118 | 29 | 0.0020455 | 0.00051266 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2542-8_0_4_load_119 | 30 | 0.0014508 | 0.0003636 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2542-8_0_4_load_21 | 31 | 0.0011917 | 0.00029866 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2542-8_0_4_load_22 | 32 | 0.0038038 | 0.00095331 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2542-8_0_4_load_23 | 33 | 0.0032841 | 0.00082307 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2542-8_0_4_load_24 | 34 | 0.0021879 | 0.00054834 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2542-8_0_4_load_25 | 35 | 0.001311 | 0.00032856 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2542-8_0_4_load_45 | 36 | 0.0023088 | 0.00057863 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2542-8_0_4_load_83 | 37 | 0.0021612 | 0.00054164 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2542-8_0_4_load_36 | 38 | 0.0047572 | 0.0011923 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2542-8_0_4_load_84 | 39 | 0.0028954 | 0.00072566 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2542-8_0_4_load_26 | 40 | 0.032414 | 0.0081238 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2542-8_0_4_load_129 | 46 | 0.042877 | 0.010746 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2542-8_0_4_load_44 | 49 | 0.0013461 | 0.00033737 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2542-8_0_4_load_42 | 50 | 0.00054633 | 0.00013692 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2542-8_0_4_load_82 | 51 | 0.0015895 | 0.00039837 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2542-8_0_4_load_85 | 52 | 0.0015382 | 0.00038551 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2542-8_0_4_load_113 | 54 | 0.0031749 | 0.00079571 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2542-8_0_4_load_54 | 55 | 0.0045166 | 0.001132 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2542-8_0_4_load_131 | 57 | 0.0068035 | 0.0017051 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2542-8_0_4_load_128 | 58 | 0.007195 | 0.0018032 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2542-8_0_4_load_130 | 59 | 0.029895 | 0.0074925 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2542-8_0_4_load_43 | 60 | 0.00082748 | 0.00020739 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2542-8_0_4_load_49 | 61 | 0.0016797 | 0.00042097 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2542-8_0_4_load_34 | 62 | 0.0078321 | 0.0019629 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2542-8_0_4_load_37 | 64 | 0.0010037 | 0.00025155 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2542-8_0_4_load_38 | 65 | 0.0015514 | 0.00038881 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2542-8_0_4_load_39 | 66 | 0.00062166 | 0.0001558 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2542-8_0_4_load_40 | 67 | 0.0014009 | 0.0003511 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2542-8_0_4_load_41 | 68 | 0.0012657 | 0.00031722 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2542-8_0_4_load_46 | 69 | 0.002053 | 0.00051452 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2542-8_0_4_load_47 | 70 | 0.0017067 | 0.00042773 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2542-8_0_4_load_76 | 72 | 0.0042201 | 0.0010577 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2542-8_0_4_load_73 | 73 | 0.0026391 | 0.00066141 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2542-8_0_4_load_77 | 74 | 0.0010622 | 0.0002662 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2542-8_0_4_load_51 | 75 | 0.0010802 | 0.00027072 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2542-8_0_4_load_52 | 76 | 0.00598 | 0.0014987 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2542-8_0_4_load_53 | 77 | 0.0034245 | 0.00085825 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2542-8_0_4_load_55 | 78 | 0.00064634 | 0.00016199 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2542-8_0_4_load_60 | 79 | 0.0013439 | 0.00033681 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2542-8_0_4_load_56 | 80 | 0.0017636 | 0.00044199 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2542-8_0_4_load_127 | 81 | 0.00098353 | 0.00024649 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2542-8_0_4_load_58 | 83 | 0.0023665 | 0.0005931 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2542-8_0_4_load_59 | 84 | 0.003245 | 0.00081326 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2542-8_0_4_load_125 | 85 | 0.0018489 | 0.00046339 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2542-8_0_4_load_126 | 86 | 0.0026038 | 0.00065258 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2542-8_0_4_load_61 | 88 | 0.0011864 | 0.00029734 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2542-8_0_4_load_62 | 89 | 0.0022378 | 0.00056085 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2542-8_0_4_load_63 | 90 | 0.0023736 | 0.00059487 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2542-8_0_4_load_64 | 91 | 0.0032672 | 0.00081884 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2542-8_0_4_load_72 | 92 | 0.0022478 | 0.00056334 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2542-8_0_4_load_69 | 93 | 0.002234 | 0.00055989 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2542-8_0_4_load_120 | 95 | 0.0015752 | 0.00039477 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2542-8_0_4_load_66 | 96 | 0.0012608 | 0.00031599 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2542-8_0_4_load_67 | 97 | 0.0034027 | 0.00085279 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2542-8_0_4_load_70 | 99 | 0.0028229 | 0.0007075 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2542-8_0_4_load_71 | 100 | 0.002606 | 0.00065311 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2542-8_0_4_load_75 | 101 | 0.0027625 | 0.00069236 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2542-8_0_4_load_97 | 102 | 0.0047023 | 0.0011785 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2542-8_0_4_load_98 | 103 | 0.0030475 | 0.00076377 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2542-8_0_4_load_78 | 104 | 0.0037 | 0.00092731 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2542-8_0_4_load_79 | 105 | 0.0026255 | 0.00065802 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2542-8_0_4_load_80 | 106 | 0.0030536 | 0.00076531 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2542-8_0_4_load_89 | 108 | 0.0017475 | 0.00043797 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2542-8_0_4_load_92 | 109 | 0.0026512 | 0.00066447 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2542-8_0_4_load_91 | 110 | 0.0022607 | 0.00056659 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2542-8_0_4_load_86 | 112 | 0.0026161 | 0.00065565 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2542-8_0_4_load_87 | 113 | 0.0020046 | 0.00050241 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2542-8_0_4_load_123 | 114 | 0.0021605 | 0.00054148 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2542-8_0_4_load_122 | 115 | 0.0026951 | 0.00067546 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2542-8_0_4_load_132 | 116 | 0.0018323 | 0.00045923 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2542-8_0_4_load_102 | 118 | 0.0024747 | 0.00062021 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2542-8_0_4_load_100 | 119 | 0.0025465 | 0.00063822 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2542-8_0_4_load_101 | 120 | 0.0032863 | 0.00082362 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2542-8_0_4_load_124 | 121 | 0.0060743 | 0.0015224 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2542-8_0_4_load_103 | 122 | 0.0023311 | 0.00058424 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2542-8_0_4_load_104 | 123 | 0.0044839 | 0.0011238 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2542-8_0_4_load_106 | 124 | 0.0026367 | 0.00066082 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2542-8_0_4_load_110 | 125 | 0.0071324 | 0.0017875 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2542-8_0_4_load_111 | 126 | 0.0012063 | 0.00030233 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2542-8_0_4_load_114 | 127 | 0.0035677 | 0.00089414 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2542-8_0_4_line_0 |  | 0 | 1 | 0.020672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2542-8_0_4_line_1 |  | 0 | 2 | 0.014889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2542-8_0_4_line_2 |  | 1 | 3 | 0.026748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2542-8_0_4_line_3 |  | 2 | 4 | 0.046073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2542-8_0_4_line_4 |  | 2 | 5 | 0.010777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2542-8_0_4_line_5 |  | 3 | 6 | 0.0097587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2542-8_0_4_line_6 |  | 4 | 7 | 0.012766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2542-8_0_4_line_7 |  | 5 | 8 | 0.016659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2542-8_0_4_line_8 |  | 6 | 9 | 0.03337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2542-8_0_4_line_9 |  | 7 | 10 | 0.003957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2542-8_0_4_line_10 |  | 8 | 11 | 0.0060819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2542-8_0_4_line_11 |  | 9 | 118 | 0.0062569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2542-8_0_4_line_12 |  | 10 | 16 | 0.025034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2542-8_0_4_line_13 |  | 11 | 126 | 0.010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2542-8_0_4_line_14 |  | 11 | 125 | 0.028331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2542-8_0_4_line_15 |  | 12 | 13 | 0.00012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2542-8_0_4_line_16 |  | 13 | 14 | 0.027549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2542-8_0_4_line_17 |  | 14 | 15 | 0.10532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2542-8_0_4_line_18 |  | 15 | 16 | 0.020251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2542-8_0_4_line_19 |  | 15 | 17 | 0.040083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2542-8_0_4_line_20 |  | 15 | 18 | 0.033583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2542-8_0_4_line_21 |  | 17 | 24 | 0.010088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2542-8_0_4_line_22 |  | 18 | 25 | 0.020544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2542-8_0_4_line_23 |  | 19 | 20 | 0.036636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2542-8_0_4_line_24 |  | 19 | 21 | 0.051888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2542-8_0_4_line_25 |  | 21 | 122 | 0.039643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2542-8_0_4_line_26 |  | 22 | 23 | 0.018575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2542-8_0_4_line_27 |  | 23 | 24 | 0.014029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2542-8_0_4_line_28 |  | 23 | 127 | 0.03748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2542-8_0_4_line_29 |  | 25 | 26 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2542-8_0_4_line_30 |  | 26 | 27 | 0.03178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2542-8_0_4_line_31 |  | 26 | 28 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2542-8_0_4_line_32 |  | 28 | 29 | 0.023378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2542-8_0_4_line_33 |  | 29 | 30 | 0.020576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2542-8_0_4_line_34 |  | 30 | 94 | 0.015444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2542-8_0_4_line_35 |  | 31 | 32 | 0.020248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2542-8_0_4_line_36 |  | 31 | 33 | 0.014142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2542-8_0_4_line_37 |  | 33 | 34 | 0.025943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2542-8_0_4_line_38 |  | 33 | 35 | 0.028529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2542-8_0_4_line_39 |  | 34 | 36 | 0.005167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2542-8_0_4_line_40 |  | 35 | 37 | 0.00067916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2542-8_0_4_line_41 |  | 36 | 38 | 0.0062027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2542-8_0_4_line_42 |  | 37 | 39 | 0.020415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2542-8_0_4_line_43 |  | 38 | 63 | 0.01874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2542-8_0_4_line_44 |  | 39 | 52 | 0.0016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2542-8_0_4_line_45 |  | 40 | 41 | 0.039659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2542-8_0_4_line_46 |  | 40 | 42 | 0.017064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2542-8_0_4_line_47 |  | 41 | 43 | 0.02524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2542-8_0_4_line_48 |  | 42 | 44 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2542-8_0_4_line_49 |  | 42 | 45 | 0.048492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2542-8_0_4_line_50 |  | 43 | 46 | 0.034064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2542-8_0_4_line_51 |  | 44 | 47 | 0.042923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2542-8_0_4_line_52 |  | 45 | 51 | 0.052107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2542-8_0_4_line_53 |  | 45 | 52 | 0.018877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2542-8_0_4_line_54 |  | 45 | 48 | 0.045396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2542-8_0_4_line_55 |  | 46 | 56 | 0.0021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2542-8_0_4_line_56 |  | 47 | 57 | 0.010003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2542-8_0_4_line_57 |  | 47 | 58 | 0.01222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2542-8_0_4_line_58 |  | 48 | 49 | 0.026913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2542-8_0_4_line_59 |  | 48 | 50 | 0.0093911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2542-8_0_4_line_60 |  | 50 | 60 | 0.0053989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2542-8_0_4_line_61 |  | 51 | 61 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2542-8_0_4_line_62 |  | 53 | 54 | 0.014083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2542-8_0_4_line_63 |  | 53 | 55 | 0.0065646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2542-8_0_4_line_64 |  | 54 | 117 | 0.017814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2542-8_0_4_line_65 |  | 55 | 76 | 0.028291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2542-8_0_4_line_66 |  | 56 | 59 | 0.003383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2542-8_0_4_line_67 |  | 57 | 116 | 0.013523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2542-8_0_4_line_68 |  | 58 | 81 | 0.026352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2542-8_0_4_line_69 |  | 60 | 68 | 0.01289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2542-8_0_4_line_70 |  | 61 | 70 | 0.018609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2542-8_0_4_line_71 |  | 62 | 63 | 0.019574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2542-8_0_4_line_72 |  | 63 | 64 | 0.035954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2542-8_0_4_line_73 |  | 65 | 66 | 0.0076792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2542-8_0_4_line_74 |  | 65 | 67 | 0.015299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2542-8_0_4_line_75 |  | 66 | 68 | 0.013544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2542-8_0_4_line_76 |  | 69 | 70 | 0.018078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2542-8_0_4_line_77 |  | 71 | 72 | 0.022375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2542-8_0_4_line_78 |  | 71 | 73 | 0.017761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2542-8_0_4_line_79 |  | 72 | 74 | 0.0025094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2542-8_0_4_line_80 |  | 74 | 104 | 0.014845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2542-8_0_4_line_81 |  | 75 | 76 | 0.00054675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2542-8_0_4_line_82 |  | 75 | 77 | 0.029962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2542-8_0_4_line_83 |  | 77 | 78 | 0.013386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_2542-8_0_4_line_84 |  | 78 | 79 | 0.012991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2542-8_0_4_line_85 |  | 78 | 80 | 0.012614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2542-8_0_4_line_86 |  | 79 | 81 | 0.0041607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2542-8_0_4_line_87 |  | 80 | 82 | 0.018637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2542-8_0_4_line_88 |  | 82 | 83 | 0.0094384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2542-8_0_4_line_89 |  | 82 | 84 | 0.0021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2542-8_0_4_line_90 |  | 83 | 85 | 0.020225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2542-8_0_4_line_91 |  | 84 | 86 | 0.019109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2542-8_0_4_line_92 |  | 86 | 87 | 0.0068422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2542-8_0_4_line_93 |  | 87 | 114 | 0.017448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2542-8_0_4_line_94 |  | 87 | 111 | 0.024501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2542-8_0_4_line_95 |  | 88 | 89 | 6.7535e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2542-8_0_4_line_96 |  | 88 | 90 | 0.028828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2542-8_0_4_line_97 |  | 89 | 91 | 0.023204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2542-8_0_4_line_98 |  | 91 | 92 | 0.0056128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2542-8_0_4_line_99 |  | 92 | 93 | 0.0017927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2542-8_0_4_line_100 |  | 93 | 97 | 0.015697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2542-8_0_4_line_101 |  | 94 | 95 | 0.013677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2542-8_0_4_line_102 |  | 95 | 121 | 0.0069548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2542-8_0_4_line_103 |  | 96 | 97 | 0.01226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2542-8_0_4_line_104 |  | 96 | 98 | 0.019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2542-8_0_4_line_105 |  | 98 | 99 | 0.0015086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2542-8_0_4_line_106 |  | 98 | 100 | 0.018075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2542-8_0_4_line_107 |  | 99 | 101 | 0.021556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2542-8_0_4_line_108 |  | 100 | 102 | 0.02681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2542-8_0_4_line_109 |  | 102 | 103 | 0.0031208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2542-8_0_4_line_110 |  | 103 | 119 | 0.024753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2542-8_0_4_line_111 |  | 104 | 105 | 0.0050895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2542-8_0_4_line_112 |  | 105 | 106 | 0.021502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2542-8_0_4_line_113 |  | 106 | 107 | 0.0006069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2542-8_0_4_line_114 |  | 107 | 108 | 0.016276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2542-8_0_4_line_115 |  | 107 | 109 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2542-8_0_4_line_116 |  | 108 | 110 | 0.023395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2542-8_0_4_line_117 |  | 108 | 111 | 0.025962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2542-8_0_4_line_118 |  | 111 | 113 | 0.0086296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2542-8_0_4_line_119 |  | 112 | 113 | 0.019953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2542-8_0_4_line_120 |  | 114 | 115 | 0.022492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2542-8_0_4_line_121 |  | 117 | 126 | 0.030478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2542-8_0_4_line_122 |  | 118 | 120 | 0.021296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2542-8_0_4_line_123 |  | 119 | 120 | 0.00053724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2542-8_0_4_line_124 |  | 122 | 123 | 0.011171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2542-8_0_4_line_125 |  | 123 | 124 | 0.016859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2542-8_0_4_line_126 |  | 124 | 125 | 0.033769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2542-8_0_4_trafo_56 | 0.63 MVA 20/0.4 kV | 128 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2604082.1485 | 1229098.8411 | 2604065.2286 | 1229087.7501 | 2604064.7993 | 1229087.649
1 | 2604094.6009 | 1229107.0036 | 2604082.1485 | 1229098.8411
2 | 2604064.7993 | 1229087.649 | 2604058.033 | 1229086.0554 | 2604050.6319 | 1229085.8392 | 2604038.3638 | 1229087.5893
3 | 2604094.6009 | 1229107.0036 | 2604088.3604 | 1229115.7045 | 2604086.899 | 1229125.9985 | 2604087.4791 | 1229141.9083 | 2604090.3044 | 1229150.5035
4 | 2604094.6009 | 1229107.0036 | 2604102.2859 | 1229099.4483
5 | 2604028.7029 | 1229088.9674 | 2604038.3638 | 1229087.5893
6 | 2604090.3044 | 1229150.5035 | 2604092.8012 | 1229158.0993 | 2604092.2574 | 1229162.8388
7 | 2604102.2859 | 1229099.4483 | 2604114.1653 | 1229087.7696
8 | 2603995.6676 | 1229093.68 | 2604028.7029 | 1229088.9674
9 | 2604092.2574 | 1229162.8388 | 2604091.8063 | 1229166.7701
10 | 2604118.5024 | 1229083.5058 | 2604114.1653 | 1229087.7696
11 | 2603995.6676 | 1229093.68 | 2603989.4735 | 1229094.5636
12 | 2604088.9526 | 1229191.641 | 2604091.8063 | 1229166.7701
13 | 2604118.5024 | 1229083.5058 | 2604122.4137 | 1229074.2707
14 | 2604118.5024 | 1229083.5058 | 2604125.4149 | 1229089.2251 | 2604142.2063 | 1229098.8606
15 | 2604111.3939 | 1229311.6579 | 2604111.269 | 1229311.6792
16 | 2604084.1114 | 1229316.3095 | 2604111.269 | 1229311.6792
17 | 2604084.1114 | 1229316.3095 | 2604079.9993 | 1229258.4057 | 2604079.9074 | 1229248.6888 | 2604086.644 | 1229211.7603
18 | 2604086.644 | 1229211.7603 | 2604088.9526 | 1229191.641
19 | 2604086.644 | 1229211.7603 | 2604126.6678 | 1229209.5802
20 | 2604086.644 | 1229211.7603 | 2604053.098 | 1229213.3299
21 | 2604136.7411 | 1229209.0315 | 2604126.6678 | 1229209.5802
22 | 2604053.098 | 1229213.3299 | 2604032.5763 | 1229214.2902
23 | 2604197.2117 | 1229171.0674 | 2604233.7374 | 1229175.0508
24 | 2604233.7374 | 1229175.0508 | 2604236.0008 | 1229155.8966 | 2604240.1293 | 1229123.5581
25 | 2604240.1293 | 1229123.5581 | 2604218.6931 | 1229120.2967 | 2604201.1768 | 1229116.3295
26 | 2604150.749 | 1229208.2685 | 2604169.2725 | 1229206.8807
27 | 2604150.749 | 1229208.2685 | 2604136.7411 | 1229209.0315
28 | 2604150.749 | 1229208.2685 | 2604149.7636 | 1229170.8016
29 | 2604014.7291 | 1229215.1253 | 2604032.5763 | 1229214.2902
30 | 2604014.7291 | 1229215.1253 | 2604015.2608 | 1229183.35
31 | 2604014.7291 | 1229215.1253 | 2604000.9125 | 1229215.3113
32 | 2604000.9125 | 1229215.3113 | 2603977.537 | 1229215.6261
33 | 2603956.9629 | 1229215.9031 | 2603977.537 | 1229215.6261
34 | 2603941.5204 | 1229216.1111 | 2603956.9629 | 1229215.9031
35 | 2603929.3784 | 1228875.7014 | 2603923.1927 | 1228894.9816
36 | 2603918.8724 | 1228908.4473 | 2603923.1927 | 1228894.9816
37 | 2603918.8724 | 1228908.4473 | 2603894.2635 | 1228900.2345
38 | 2603918.8724 | 1228908.4473 | 2603926.8024 | 1228911.0985 | 2603945.8817 | 1228917.6324
39 | 2603889.3623 | 1228898.5988 | 2603894.2635 | 1228900.2345
40 | 2603945.8817 | 1228917.6324 | 2603946.5242 | 1228917.8525
41 | 2603883.4786 | 1228896.6352 | 2603889.3623 | 1228898.5988
42 | 2603965.8258 | 1228924.5036 | 2603956.3033 | 1228921.2014 | 2603946.5242 | 1228917.8525
43 | 2603865.7021 | 1228890.7026 | 2603883.4786 | 1228896.6352
44 | 2603967.3546 | 1228925.0337 | 2603965.8258 | 1228924.5036
45 | 2604081.9482 | 1228918.7167 | 2604042.3749 | 1228921.3253
46 | 2604025.3475 | 1228922.4477 | 2604042.3749 | 1228921.3253
47 | 2604081.9482 | 1228918.7167 | 2604085.5146 | 1228943.7006
48 | 2604025.3475 | 1228922.4477 | 2604021.3591 | 1228927.8705 | 2604012.8077 | 1228936.8701
49 | 2604025.3475 | 1228922.4477 | 2604009.312 | 1228918.9461 | 2604000.6614 | 1228917.773 | 2603993.6229 | 1228918.7356 | 2603986.5326 | 1228929.3817 | 2603984.7276 | 1228932.3267
50 | 2604085.5146 | 1228943.7006 | 2604053.1517 | 1228954.3296
51 | 2604012.8077 | 1228936.8701 | 2604016.942 | 1228939.9525 | 2604023.6384 | 1228963.5487 | 2604024.7645 | 1228967.5407 | 2604021.0513 | 1228969.1392 | 2604017.6171 | 1228972.8391
52 | 2603984.7276 | 1228932.3267 | 2603967.4021 | 1228955.2066 | 2603960.2007 | 1228962.106 | 2603952.9033 | 1228965.3031 | 2603947.7111 | 1228967.0171
53 | 2603984.7276 | 1228932.3267 | 2603975.8972 | 1228927.9961 | 2603967.3546 | 1228925.0337
54 | 2604010.4037 | 1228894.8992 | 2603993.6229 | 1228918.7356 | 2603986.5326 | 1228929.3817 | 2603984.7276 | 1228932.3267
55 | 2604053.8397 | 1228956.4091 | 2604053.1517 | 1228954.3296
56 | 2604017.6171 | 1228972.8391 | 2604015.8007 | 1228970.1919 | 2604012.9302 | 1228969.1338 | 2604010.8239 | 1228969.6216 | 2604009.6161 | 1228970.6257
57 | 2604017.6171 | 1228972.8391 | 2604022.9317 | 1228983.8425
58 | 2604010.4037 | 1228894.8992 | 2604025.8009 | 1228872.8259
59 | 2604010.4037 | 1228894.8992 | 2604001.3074 | 1228892.5645
60 | 2604001.3074 | 1228892.5645 | 2603996.078 | 1228891.2222
61 | 2603947.7111 | 1228967.0171 | 2603940.8024 | 1228969.2976 | 2603927.8755 | 1228972.8958
62 | 2604103.3972 | 1229038.3021 | 2604117.0413 | 1229041.7916
63 | 2604103.3972 | 1229038.3021 | 2604096.9526 | 1229037.0527
64 | 2604134.3001 | 1229046.2056 | 2604117.0413 | 1229041.7916
65 | 2604096.9526 | 1229037.0527 | 2604087.3997 | 1229035.2006 | 2604069.1927 | 1229031.5961
66 | 2604053.8397 | 1228956.4091 | 2604054.8982 | 1228959.6228
67 | 2603999.5583 | 1228979.6553 | 2604005.3588 | 1228974.1651 | 2604009.6161 | 1228970.6257
68 | 2604026.6082 | 1229009.2782 | 2604027.3375 | 1228994.3583 | 2604025.1748 | 1228988.4867 | 2604022.9317 | 1228983.8425
69 | 2603983.5925 | 1228888.0176 | 2603996.078 | 1228891.2222
70 | 2603909.9482 | 1228977.8866 | 2603916.9726 | 1228975.9305 | 2603927.8755 | 1228972.8958
71 | 2603865.7021 | 1228890.7026 | 2603847.1358 | 1228884.5045
72 | 2603865.7021 | 1228890.7026 | 2603867.6014 | 1228882.2989 | 2603875.2347 | 1228856.0478
73 | 2603970.4739 | 1228884.6504 | 2603963.0358 | 1228882.7413
74 | 2603948.2173 | 1228878.9378 | 2603963.0358 | 1228882.7413
75 | 2603983.5925 | 1228888.0176 | 2603970.4739 | 1228884.6504
76 | 2603892.5328 | 1228982.7363 | 2603909.9482 | 1228977.8866
77 | 2603832.8138 | 1229025.3615 | 2603855.1382 | 1229026.87
78 | 2603832.8138 | 1229025.3615 | 2603834.638 | 1229039.7935 | 2603834.3729 | 1229042.9969
79 | 2603855.1382 | 1229026.87 | 2603857.642 | 1229027.0391
80 | 2603872.4528 | 1229028.0399 | 2603857.642 | 1229027.0391
81 | 2604068.6564 | 1229031.4899 | 2604069.1927 | 1229031.5961
82 | 2604068.6564 | 1229031.4899 | 2604046.997 | 1229027.202 | 2604039.139 | 1229026.5795
83 | 2604025.7707 | 1229026.4096 | 2604034.3995 | 1229026.2041 | 2604039.139 | 1229026.5795
84 | 2604025.7707 | 1229026.4096 | 2604026.405 | 1229013.434
85 | 2604025.7707 | 1229026.4096 | 2604013.1604 | 1229026.7019
86 | 2604026.6082 | 1229009.2782 | 2604026.405 | 1229013.434
87 | 2603994.5286 | 1229027.1338 | 2604013.1604 | 1229026.7019
88 | 2603994.5286 | 1229027.1338 | 2603997.4203 | 1229018.1493
89 | 2603994.5286 | 1229027.1338 | 2603992.3897 | 1229027.2587
90 | 2604003.6168 | 1228998.897 | 2603997.4203 | 1229018.1493
91 | 2603973.3133 | 1229028.3729 | 2603992.3897 | 1229027.2587
92 | 2603966.4827 | 1229028.7719 | 2603973.3133 | 1229028.3729
93 | 2603966.4827 | 1229028.7719 | 2603971.8625 | 1229012.1741
94 | 2603966.4827 | 1229028.7719 | 2603941.9446 | 1229030.0788
95 | 2603894.1742 | 1229166.8778 | 2603894.1727 | 1229166.9453
96 | 2603894.1727 | 1229166.9453 | 2603893.5355 | 1229195.7662
97 | 2603894.6871 | 1229143.6796 | 2603894.1742 | 1229166.8778
98 | 2603894.8112 | 1229138.0682 | 2603894.6871 | 1229143.6796
99 | 2603894.8112 | 1229138.0682 | 2603894.8508 | 1229136.276
100 | 2603895.1978 | 1229120.5825 | 2603894.8508 | 1229136.276
101 | 2603941.5204 | 1229216.1111 | 2603940.4496 | 1229202.4758
102 | 2603939.9051 | 1229195.5423 | 2603940.4496 | 1229202.4758
103 | 2603895.4687 | 1229108.3255 | 2603895.1978 | 1229120.5825
104 | 2603895.9003 | 1229088.8061 | 2603895.4687 | 1229108.3255
105 | 2603895.9003 | 1229088.8061 | 2603894.4177 | 1229088.5274
106 | 2603895.9003 | 1229088.8061 | 2603913.6749 | 1229092.0852
107 | 2603873.2324 | 1229084.546 | 2603894.4177 | 1229088.5274
108 | 2603913.6749 | 1229092.0852 | 2603926.1987 | 1229094.3956 | 2603940.184 | 1229095.9803
109 | 2603943.2849 | 1229096.3317 | 2603940.184 | 1229095.9803
110 | 2603943.2849 | 1229096.3317 | 2603962.119 | 1229098.4659 | 2603967.8595 | 1229097.647
111 | 2603877.5307 | 1229028.383 | 2603872.4528 | 1229028.0399
112 | 2603877.5307 | 1229028.383 | 2603898.9841 | 1229029.8326
113 | 2603899.5897 | 1229029.8735 | 2603898.9841 | 1229029.8326
114 | 2603915.9072 | 1229030.3287 | 2603899.5897 | 1229029.8735
115 | 2603899.5897 | 1229029.8735 | 2603900.4432 | 1229015.0211
116 | 2603915.9072 | 1229030.3287 | 2603923.2853 | 1229008.1272
117 | 2603941.9446 | 1229030.0788 | 2603915.9072 | 1229030.3287
118 | 2603941.9446 | 1229030.0788 | 2603944.7377 | 1229021.9138
119 | 2603951.1962 | 1229003.0345 | 2603944.7377 | 1229021.9138
120 | 2603978.7975 | 1228990.7784 | 2603971.8625 | 1229012.1741
121 | 2604134.3001 | 1229046.2056 | 2604122.4137 | 1229074.2707
122 | 2603968.3913 | 1229097.5711 | 2603989.4735 | 1229094.5636
123 | 2603967.8595 | 1229097.647 | 2603968.3913 | 1229097.5711
124 | 2604201.1768 | 1229116.3295 | 2604190.282 | 1229113.862
125 | 2604173.7857 | 1229110.3819 | 2604190.282 | 1229113.862 | 2604190.282 | 1229113.862
126 | 2604173.7857 | 1229110.3819 | 2604171.2476 | 1229109.8465 | 2604148.7307 | 1229102.6045 | 2604142.2063 | 1229098.8606

## bus_geodata
| x | y | coords
0 | 2604082.1485 | 1229098.8411
1 | 2604064.7993 | 1229087.649
2 | 2604094.6009 | 1229107.0036
3 | 2604038.3638 | 1229087.5893
4 | 2604090.3044 | 1229150.5035
5 | 2604102.2859 | 1229099.4483
6 | 2604028.7029 | 1229088.9674
7 | 2604092.2574 | 1229162.8388
8 | 2604114.1653 | 1229087.7696
9 | 2603995.6676 | 1229093.68
10 | 2604091.8063 | 1229166.7701
11 | 2604118.5024 | 1229083.5058
12 | 2604111.3939 | 1229311.6579
13 | 2604111.269 | 1229311.6792
14 | 2604084.1114 | 1229316.3095
15 | 2604086.644 | 1229211.7603
16 | 2604088.9526 | 1229191.641
17 | 2604126.6678 | 1229209.5802
18 | 2604053.098 | 1229213.3299
19 | 2604233.7374 | 1229175.0508
20 | 2604197.2117 | 1229171.0674
21 | 2604240.1293 | 1229123.5581
22 | 2604169.2725 | 1229206.8807
23 | 2604150.749 | 1229208.2685
24 | 2604136.7411 | 1229209.0315
25 | 2604032.5763 | 1229214.2902
26 | 2604014.7291 | 1229215.1253
27 | 2604015.2608 | 1229183.35
28 | 2604000.9125 | 1229215.3113
29 | 2603977.537 | 1229215.6261
30 | 2603956.9629 | 1229215.9031
31 | 2603923.1927 | 1228894.9816
32 | 2603929.3784 | 1228875.7014
33 | 2603918.8724 | 1228908.4473
34 | 2603894.2635 | 1228900.2345
35 | 2603945.8817 | 1228917.6324
36 | 2603889.3623 | 1228898.5988
37 | 2603946.5242 | 1228917.8525
38 | 2603883.4786 | 1228896.6352
39 | 2603965.8258 | 1228924.5036
40 | 2604042.3749 | 1228921.3253
41 | 2604081.9482 | 1228918.7167
42 | 2604025.3475 | 1228922.4477
43 | 2604085.5146 | 1228943.7006
44 | 2604012.8077 | 1228936.8701
45 | 2603984.7276 | 1228932.3267
46 | 2604053.1517 | 1228954.3296
47 | 2604017.6171 | 1228972.8391
48 | 2604010.4037 | 1228894.8992
49 | 2604025.8009 | 1228872.8259
50 | 2604001.3074 | 1228892.5645
51 | 2603947.7111 | 1228967.0171
52 | 2603967.3546 | 1228925.0337
53 | 2604103.3972 | 1229038.3021
54 | 2604117.0413 | 1229041.7916
55 | 2604096.9526 | 1229037.0527
56 | 2604053.8397 | 1228956.4091
57 | 2604009.6161 | 1228970.6257
58 | 2604022.9317 | 1228983.8425
59 | 2604054.8982 | 1228959.6228
60 | 2603996.078 | 1228891.2222
61 | 2603927.8755 | 1228972.8958
62 | 2603847.1358 | 1228884.5045
63 | 2603865.7021 | 1228890.7026
64 | 2603875.2347 | 1228856.0478
65 | 2603963.0358 | 1228882.7413
66 | 2603970.4739 | 1228884.6504
67 | 2603948.2173 | 1228878.9378
68 | 2603983.5925 | 1228888.0176
69 | 2603892.5328 | 1228982.7363
70 | 2603909.9482 | 1228977.8866
71 | 2603832.8138 | 1229025.3615
72 | 2603855.1382 | 1229026.87
73 | 2603834.3729 | 1229042.9969
74 | 2603857.642 | 1229027.0391
75 | 2604068.6564 | 1229031.4899
76 | 2604069.1927 | 1229031.5961
77 | 2604039.139 | 1229026.5795
78 | 2604025.7707 | 1229026.4096
79 | 2604026.405 | 1229013.434
80 | 2604013.1604 | 1229026.7019
81 | 2604026.6082 | 1229009.2782
82 | 2603994.5286 | 1229027.1338
83 | 2603997.4203 | 1229018.1493
84 | 2603992.3897 | 1229027.2587
85 | 2604003.6168 | 1228998.897
86 | 2603973.3133 | 1229028.3729
87 | 2603966.4827 | 1229028.7719
88 | 2603894.1727 | 1229166.9453
89 | 2603894.1742 | 1229166.8778
90 | 2603893.5355 | 1229195.7662
91 | 2603894.6871 | 1229143.6796
92 | 2603894.8112 | 1229138.0682
93 | 2603894.8508 | 1229136.276
94 | 2603941.5204 | 1229216.1111
95 | 2603940.4496 | 1229202.4758
96 | 2603895.4687 | 1229108.3255
97 | 2603895.1978 | 1229120.5825
98 | 2603895.9003 | 1229088.8061
99 | 2603894.4177 | 1229088.5274
100 | 2603913.6749 | 1229092.0852
101 | 2603873.2324 | 1229084.546
102 | 2603940.184 | 1229095.9803
103 | 2603943.2849 | 1229096.3317
104 | 2603872.4528 | 1229028.0399
105 | 2603877.5307 | 1229028.383
106 | 2603898.9841 | 1229029.8326
107 | 2603899.5897 | 1229029.8735
108 | 2603915.9072 | 1229030.3287
109 | 2603900.4432 | 1229015.0211
110 | 2603923.2853 | 1229008.1272
111 | 2603941.9446 | 1229030.0788
112 | 2603951.1962 | 1229003.0345
113 | 2603944.7377 | 1229021.9138
114 | 2603971.8625 | 1229012.1741
115 | 2603978.7975 | 1228990.7784
116 | 2603999.5583 | 1228979.6553
117 | 2604134.3001 | 1229046.2056
118 | 2603989.4735 | 1229094.5636
119 | 2603967.8595 | 1229097.647
120 | 2603968.3913 | 1229097.5711
121 | 2603939.9051 | 1229195.5423
122 | 2604201.1768 | 1229116.3295
123 | 2604190.282 | 1229113.862
124 | 2604173.7857 | 1229110.3819
125 | 2604142.2063 | 1229098.8606
126 | 2604122.4137 | 1229074.2707
127 | 2604149.7636 | 1229170.8016
128 | 2604025.7707 | 1229026.4096

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97824 | -0.41696 | 0.0019454 | 0.00048757
1 | 0.97731 | -0.43508 | 0.00074638 | 0.00018706
2 | 0.97893 | -0.4034 | 0 | 0
3 | 0.97613 | -0.45822 | 0.0016734 | 0.0004194
4 | 0.97723 | -0.43673 | 0.0011328 | 0.00028391
5 | 0.97984 | -0.38582 | 0.0076483 | 0.0019169
6 | 0.97571 | -0.46638 | 0.0013831 | 0.00034663
7 | 0.97677 | -0.44573 | 0.0032405 | 0.00081214
8 | 0.98135 | -0.3564 | 0.0028018 | 0.00070221
9 | 0.97433 | -0.49348 | 0.0018256 | 0.00045754
10 | 0.97664 | -0.44828 | 0.0038189 | 0.00095712
11 | 0.98191 | -0.34538 | 0 | 0
12 | 0.97474 | -0.48586 | 0.0025277 | 0.00063351
13 | 0.97474 | -0.48585 | 0.0023146 | 0.0005801
14 | 0.97486 | -0.4834 | 0 | 0
15 | 0.97533 | -0.47405 | 0 | 0
16 | 0.97591 | -0.46271 | 0.00095251 | 0.00023872
17 | 0.97501 | -0.48054 | 0.001281 | 0.00032105
18 | 0.97481 | -0.48444 | 0.0012733 | 0.00031911
19 | 0.98075 | -0.36814 | 0 | 0
20 | 0.98069 | -0.36934 | 0.0017998 | 0.00045108
21 | 0.98084 | -0.36645 | 0 | 0
22 | 0.97482 | -0.48417 | 0.0021926 | 0.00054951
23 | 0.97486 | -0.48342 | 0 | 0
24 | 0.97493 | -0.48194 | 0.0017944 | 0.00044973
25 | 0.97451 | -0.49033 | 0.0011252 | 0.00028201
26 | 0.97427 | -0.49508 | 0 | 0
27 | 0.97422 | -0.49596 | 0.0015134 | 0.0003793
28 | 0.9741 | -0.49837 | 0.0018195 | 0.00045601
29 | 0.97386 | -0.50316 | 0.0020455 | 0.00051266
30 | 0.97368 | -0.5066 | 0.0014508 | 0.0003636
31 | 0.98838 | -0.22298 | 0.0011917 | 0.00029866
32 | 0.98831 | -0.22435 | 0.0038038 | 0.00095331
33 | 0.98845 | -0.22172 | 0.0032841 | 0.00082307
34 | 0.98802 | -0.23009 | 0.0021879 | 0.00054834
35 | 0.98914 | -0.2083 | 0.001311 | 0.00032856
36 | 0.98794 | -0.23156 | 0.0023088 | 0.00057863
37 | 0.98916 | -0.20797 | 0.0021612 | 0.00054164
38 | 0.98787 | -0.23307 | 0.0047572 | 0.0011923
39 | 0.98972 | -0.19712 | 0.0028954 | 0.00072566
40 | 0.99088 | -0.17445 | 0.032414 | 0.0081238
41 | 0.98822 | -0.22583 | 0 | 0
42 | 0.99253 | -0.14264 | 0 | 0
43 | 0.98653 | -0.25867 | 0 | 0
44 | 0.99388 | -0.11661 | 0 | 0
45 | 0.99036 | -0.18467 | 0 | 0
46 | 0.98424 | -0.30316 | 0.042877 | 0.010746
47 | 0.99591 | -0.077797 | 0 | 0
48 | 0.99004 | -0.19078 | 0 | 0
49 | 0.99001 | -0.19142 | 0.0013461 | 0.00033737
50 | 0.98999 | -0.19181 | 0.00054633 | 0.00013692
51 | 0.99002 | -0.19118 | 0.0015895 | 0.00039837
52 | 0.98976 | -0.19618 | 0.0015382 | 0.00038551
53 | 0.99001 | -0.18926 | 0 | 0
54 | 0.9884 | -0.22011 | 0.0031749 | 0.00079571
55 | 0.99076 | -0.17491 | 0.0045166 | 0.001132
56 | 0.98418 | -0.30434 | 0 | 0
57 | 0.99583 | -0.079315 | 0.0068035 | 0.0017051
58 | 0.99652 | -0.066157 | 0.007195 | 0.0018032
59 | 0.98409 | -0.30616 | 0.029895 | 0.0074925
60 | 0.98996 | -0.19236 | 0.00082748 | 0.00020739
61 | 0.98992 | -0.19319 | 0.0016797 | 0.00042097
62 | 0.98757 | -0.23877 | 0.0078321 | 0.0019629
63 | 0.98771 | -0.23603 | 0 | 0
64 | 0.98768 | -0.23667 | 0.0010037 | 0.00025155
65 | 0.98984 | -0.19473 | 0.0015514 | 0.00038881
66 | 0.98986 | -0.19433 | 0.00062166 | 0.0001558
67 | 0.98982 | -0.19511 | 0.0014009 | 0.0003511
68 | 0.98991 | -0.19347 | 0.0012657 | 0.00031722
69 | 0.98982 | -0.19509 | 0.002053 | 0.00051452
70 | 0.98986 | -0.19443 | 0.0017067 | 0.00042773
71 | 0.99634 | -0.070502 | 0 | 0
72 | 0.99639 | -0.069464 | 0.0042201 | 0.0010577
73 | 0.99629 | -0.071325 | 0.0026391 | 0.00066141
74 | 0.99641 | -0.069162 | 0.0010622 | 0.0002662
75 | 0.99419 | -0.10979 | 0.0010802 | 0.00027072
76 | 0.99412 | -0.11108 | 0.00598 | 0.0014987
77 | 0.99794 | -0.038959 | 0.0034245 | 0.00085825
78 | 0.99879 | -0.02281 | 0.00064634 | 0.00016199
79 | 0.99811 | -0.03585 | 0.0013439 | 0.00033681
80 | 1 | 0 | -0.36086 | -0.091902
81 | 0.99789 | -0.039998 | 0.00098353 | 0.00024649
82 | 0.99926 | -0.014144 | 0 | 0
83 | 0.99923 | -0.014839 | 0.0023665 | 0.0005931
84 | 0.99919 | -0.015614 | 0.003245 | 0.00081326
85 | 0.99919 | -0.015492 | 0.0018489 | 0.00046339
86 | 0.99856 | -0.027647 | 0.0026038 | 0.00065258
87 | 0.99835 | -0.031648 | 0 | 0
88 | 0.97041 | -0.5709 | 0.0011864 | 0.00029734
89 | 0.97041 | -0.57089 | 0.0022378 | 0.00056085
90 | 0.97035 | -0.57216 | 0.0023736 | 0.00059487
91 | 0.97054 | -0.5684 | 0.0032672 | 0.00081884
92 | 0.97059 | -0.56746 | 0.0022478 | 0.00056334
93 | 0.97061 | -0.56709 | 0.002234 | 0.00055989
94 | 0.97357 | -0.50877 | 0 | 0
95 | 0.97348 | -0.5107 | 0.0015752 | 0.00039477
96 | 0.971 | -0.55931 | 0.0012608 | 0.00031599
97 | 0.97081 | -0.56315 | 0.0034027 | 0.00085279
98 | 0.97133 | -0.55274 | 0 | 0
99 | 0.97132 | -0.55289 | 0.0028229 | 0.0007075
100 | 0.97173 | -0.54479 | 0.002606 | 0.00065311
101 | 0.97127 | -0.55399 | 0.0027625 | 0.00069236
102 | 0.97239 | -0.53174 | 0.0047023 | 0.0011785
103 | 0.97248 | -0.52995 | 0.0030475 | 0.00076377
104 | 0.99651 | -0.067098 | 0.0037 | 0.00092731
105 | 0.99657 | -0.066059 | 0.0026255 | 0.00065802
106 | 0.99684 | -0.060684 | 0.0030536 | 0.00076531
107 | 0.99685 | -0.0605 | 0 | 0
108 | 0.99715 | -0.054805 | 0.0017475 | 0.00043797
109 | 0.99682 | -0.061191 | 0.0026512 | 0.00066447
110 | 0.9971 | -0.055732 | 0.0022607 | 0.00056659
111 | 0.99772 | -0.043904 | 0 | 0
112 | 0.99763 | -0.045517 | 0.0026161 | 0.00065565
113 | 0.99768 | -0.044603 | 0.0020046 | 0.00050241
114 | 0.99828 | -0.03313 | 0.0021605 | 0.00054148
115 | 0.99822 | -0.034191 | 0.0026951 | 0.00067546
116 | 0.99581 | -0.079751 | 0.0018323 | 0.00045923
117 | 0.98642 | -0.25826 | 0 | 0
118 | 0.97409 | -0.49836 | 0.0024747 | 0.00062021
119 | 0.97327 | -0.51438 | 0.0025465 | 0.00063822
120 | 0.97329 | -0.51401 | 0.0032863 | 0.00082362
121 | 0.97344 | -0.51147 | 0.0060743 | 0.0015224
122 | 0.9809 | -0.36515 | 0.0023311 | 0.00058424
123 | 0.98095 | -0.36432 | 0.0044839 | 0.0011238
124 | 0.98108 | -0.36168 | 0.0026367 | 0.00066082
125 | 0.98143 | -0.3548 | 0.0071324 | 0.0017875
126 | 0.98302 | -0.3239 | 0.0012063 | 0.00030233
127 | 0.97473 | -0.48588 | 0.0035677 | 0.00089414
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.048365 | 0.012225 | -0.048323 | -0.012199 | 4.1999e-05 | 2.662e-05 | 0.073606 | 0.073606 | 0.073606 | 0.97824 | -0.41696 | 0.97731 | -0.43508 | 20.2213
1 | -0.05031 | -0.012713 | 0.050343 | 0.012734 | 3.2731e-05 | 2.0761e-05 | 0.076565 | 0.076565 | 0.076565 | 0.97824 | -0.41696 | 0.97893 | -0.4034 | 21.0343
2 | 0.047576 | 0.012012 | -0.047523 | -0.011978 | 5.2678e-05 | 3.3379e-05 | 0.072469 | 0.072469 | 0.072469 | 0.97731 | -0.43508 | 0.97613 | -0.45822 | 19.9092
3 | 0.039853 | 0.010041 | -0.03979 | -0.010001 | 6.3443e-05 | 4.0026e-05 | 0.060598 | 0.060598 | 0.060598 | 0.97893 | -0.4034 | 0.97723 | -0.43673 | 16.6477
4 | -0.090196 | -0.022775 | 0.090272 | 0.022823 | 7.6032e-05 | 4.8525e-05 | 0.13716 | 0.13716 | 0.13716 | 0.97893 | -0.4034 | 0.97984 | -0.38582 | 37.6819
5 | 0.04585 | 0.011559 | -0.045832 | -0.011547 | 1.789e-05 | 1.1328e-05 | 0.069918 | 0.069918 | 0.069918 | 0.97613 | -0.45822 | 0.97571 | -0.46638 | 19.2084
6 | 0.038657 | 0.009717 | -0.038641 | -0.0097066 | 1.6593e-05 | 1.046e-05 | 0.058873 | 0.058873 | 0.058873 | 0.97723 | -0.43673 | 0.97677 | -0.44573 | 16.1739
7 | -0.09792 | -0.02474 | 0.098059 | 0.024828 | 0.00013828 | 8.8286e-05 | 0.14878 | 0.14878 | 0.14878 | 0.97984 | -0.38582 | 0.98135 | -0.3564 | 40.8729
8 | 0.044449 | 0.011201 | -0.044392 | -0.011164 | 5.7539e-05 | 3.6409e-05 | 0.067809 | 0.067809 | 0.067809 | 0.97571 | -0.46638 | 0.97433 | -0.49348 | 18.6289
9 | 0.0354 | 0.0088944 | -0.035396 | -0.0088917 | 4.3168e-06 | 2.7132e-06 | 0.053936 | 0.053936 | 0.053936 | 0.97677 | -0.44573 | 0.97664 | -0.44828 | 14.8177
10 | -0.10086 | -0.02553 | 0.10091 | 0.025564 | 5.3407e-05 | 3.4104e-05 | 0.15303 | 0.15303 | 0.15303 | 0.98135 | -0.3564 | 0.98191 | -0.34538 | 42.04
11 | 0.042566 | 0.010707 | -0.042556 | -0.010701 | 9.9197e-06 | 6.2707e-06 | 0.065021 | 0.065021 | 0.065021 | 0.97433 | -0.49348 | 0.97409 | -0.49836 | 17.863
12 | 0.031577 | 0.0079346 | -0.031555 | -0.007921 | 2.1736e-05 | 1.3598e-05 | 0.048118 | 0.048118 | 0.048118 | 0.97664 | -0.44828 | 0.97591 | -0.46271 | 13.2192
13 | -0.11931 | -0.030178 | 0.11943 | 0.030256 | 0.00012309 | 7.8648e-05 | 0.18091 | 0.18091 | 0.18091 | 0.98191 | -0.34538 | 0.98302 | -0.3239 | 49.6996
14 | 0.018397 | 0.0046134 | -0.018389 | -0.0046084 | 8.2587e-06 | 4.9274e-06 | 0.027881 | 0.027881 | 0.027881 | 0.98191 | -0.34538 | 0.98143 | -0.3548 | 7.6596
15 | -0.0025277 | -0.00063351 | 0.0025277 | 0.00063351 | 7.076e-10 | -1.1269e-09 | 0.0038588 | 0.0038588 | 0.0038588 | 0.97474 | -0.48586 | 0.97474 | -0.48585 | 1.0601
16 | -0.0048424 | -0.0012136 | 0.004843 | 0.0012136 | 5.6454e-07 | 1.7866e-08 | 0.0073923 | 0.0073922 | 0.0073923 | 0.97474 | -0.48585 | 0.97486 | -0.4834 | 2.0309
17 | -0.004843 | -0.0012136 | 0.0048451 | 0.0012137 | 2.158e-06 | 6.7382e-08 | 0.0073922 | 0.0073917 | 0.0073922 | 0.97486 | -0.4834 | 0.97533 | -0.47405 | 2.0308
18 | -0.030586 | -0.0076719 | 0.030603 | 0.0076823 | 1.6538e-05 | 1.0331e-05 | 0.046666 | 0.046666 | 0.046666 | 0.97533 | -0.47405 | 0.97591 | -0.46271 | 12.8203
19 | 0.0088398 | 0.0022156 | -0.0088371 | -0.0022143 | 2.734e-06 | 1.2497e-06 | 0.013486 | 0.013487 | 0.013487 | 0.97533 | -0.47405 | 0.97501 | -0.48054 | 3.7051
20 | 0.016901 | 0.0042427 | -0.016893 | -0.0042377 | 8.3747e-06 | 4.9409e-06 | 0.025788 | 0.025788 | 0.025788 | 0.97533 | -0.47405 | 0.97481 | -0.48444 | 7.0845
21 | 0.007556 | 0.0018933 | -0.0075555 | -0.0018931 | 5.0307e-07 | 1.9616e-07 | 0.011532 | 0.011532 | 0.011532 | 0.97501 | -0.48054 | 0.97493 | -0.48194 | 3.168
22 | 0.015619 | 0.0039186 | -0.015615 | -0.0039161 | 4.3801e-06 | 2.5472e-06 | 0.023844 | 0.023844 | 0.023844 | 0.97481 | -0.48444 | 0.97451 | -0.49033 | 6.5506
23 | 0.0017999 | 0.00045069 | -0.0017998 | -0.00045108 | 1.0246e-07 | -3.9671e-07 | 0.0027308 | 0.0027309 | 0.0027309 | 0.98075 | -0.36814 | 0.98069 | -0.36934 | 0.75025
24 | -0.0017999 | -0.00045069 | 0.0018001 | 0.00045012 | 1.4509e-07 | -5.6199e-07 | 0.0027308 | 0.0027305 | 0.0027308 | 0.98075 | -0.36814 | 0.98084 | -0.36645 | 0.75021
25 | -0.0018001 | -0.00045012 | 0.0018002 | 0.0004497 | 1.1083e-07 | -4.2945e-07 | 0.0027305 | 0.0027304 | 0.0027305 | 0.98084 | -0.36645 | 0.9809 | -0.36515 | 0.75015
26 | -0.0021926 | -0.00054951 | 0.0021926 | 0.00054933 | 7.8024e-08 | -1.8165e-07 | 0.0033468 | 0.0033468 | 0.0033468 | 0.97482 | -0.48417 | 0.97486 | -0.48342 | 0.91946
27 | -0.0057607 | -0.0014433 | 0.0057611 | 0.0014433 | 4.0673e-07 | 8.5387e-08 | 0.0087929 | 0.0087928 | 0.0087929 | 0.97486 | -0.48342 | 0.97493 | -0.48194 | 2.4156
28 | 0.0035681 | 0.00089394 | -0.0035677 | -0.00089414 | 4.1689e-07 | -2.0043e-07 | 0.0054462 | 0.0054463 | 0.0054463 | 0.97486 | -0.48342 | 0.97473 | -0.48588 | 1.4962
29 | 0.01449 | 0.003634 | -0.014487 | -0.0036322 | 3.2801e-06 | 1.8767e-06 | 0.022126 | 0.022126 | 0.022126 | 0.97451 | -0.49033 | 0.97427 | -0.49508 | 6.0786
30 | 0.0015135 | 0.00037895 | -0.0015134 | -0.0003793 | 6.3677e-08 | -3.5497e-07 | 0.0023115 | 0.0023116 | 0.0023116 | 0.97427 | -0.49508 | 0.97422 | -0.49596 | 0.63506
31 | 0.012973 | 0.0032532 | -0.012971 | -0.0032521 | 2.0344e-06 | 1.13e-06 | 0.019815 | 0.019815 | 0.019815 | 0.97427 | -0.49508 | 0.9741 | -0.49837 | 5.4436
32 | 0.011152 | 0.0027961 | -0.011149 | -0.0027947 | 2.5441e-06 | 1.3373e-06 | 0.017035 | 0.017035 | 0.017035 | 0.9741 | -0.49837 | 0.97386 | -0.50316 | 4.6801
33 | 0.0091035 | 0.0022821 | -0.009102 | -0.0022814 | 1.493e-06 | 6.9952e-07 | 0.01391 | 0.01391 | 0.01391 | 0.97386 | -0.50316 | 0.97368 | -0.5066 | 3.8214
34 | 0.0076512 | 0.0019178 | -0.0076504 | -0.0019175 | 7.9184e-07 | 3.1471e-07 | 0.011693 | 0.011693 | 0.011693 | 0.97368 | -0.5066 | 0.97357 | -0.50877 | 3.2124
35 | 0.003804 | 0.00095321 | -0.0038038 | -0.00095331 | 2.4904e-07 | -1.001e-07 | 0.0057269 | 0.005727 | 0.005727 | 0.98838 | -0.22298 | 0.98831 | -0.22435 | 1.5734
36 | -0.0049957 | -0.0012519 | 0.004996 | 0.0012519 | 2.9997e-07 | 1.0725e-08 | 0.007521 | 0.0075209 | 0.007521 | 0.98838 | -0.22298 | 0.98845 | -0.22172 | 2.0662
37 | 0.018101 | 0.0045397 | -0.018094 | -0.0045354 | 7.2246e-06 | 4.2913e-06 | 0.027251 | 0.027251 | 0.027251 | 0.98845 | -0.22172 | 0.98802 | -0.23009 | 7.4865
38 | -0.026381 | -0.0066146 | 0.026398 | 0.0066251 | 1.6875e-05 | 1.0434e-05 | 0.039716 | 0.039715 | 0.039716 | 0.98845 | -0.22172 | 0.98914 | -0.2083 | 10.9109
39 | 0.015906 | 0.0039871 | -0.015905 | -0.0039864 | 1.112e-06 | 6.4549e-07 | 0.023956 | 0.023956 | 0.023956 | 0.98802 | -0.23009 | 0.98794 | -0.23156 | 6.5813
40 | -0.027709 | -0.0069536 | 0.02771 | 0.0069539 | 4.4261e-07 | 2.7455e-07 | 0.041688 | 0.041688 | 0.041688 | 0.98914 | -0.2083 | 0.98916 | -0.20797 | 11.4526
41 | 0.013596 | 0.0034078 | -0.013595 | -0.0034072 | 9.7546e-07 | 5.4487e-07 | 0.020478 | 0.020478 | 0.020478 | 0.98794 | -0.23156 | 0.98787 | -0.23307 | 5.6259
42 | -0.029871 | -0.0074956 | 0.029886 | 0.0075052 | 1.5461e-05 | 9.6327e-06 | 0.044939 | 0.044939 | 0.044939 | 0.98916 | -0.20797 | 0.98972 | -0.19712 | 12.3458
43 | 0.0088381 | 0.002215 | -0.0088368 | -0.0022144 | 1.2455e-06 | 5.5723e-07 | 0.013313 | 0.013313 | 0.013313 | 0.98787 | -0.23307 | 0.98771 | -0.23603 | 3.6574
44 | -0.032782 | -0.0082308 | 0.032783 | 0.0082318 | 1.4743e-06 | 9.2278e-07 | 0.049292 | 0.049292 | 0.049292 | 0.98972 | -0.19712 | 0.98976 | -0.19618 | 13.5417
45 | 0.073226 | 0.018527 | -0.073046 | -0.018413 | 0.00018004 | 0.00011472 | 0.11003 | 0.11003 | 0.11003 | 0.99088 | -0.17445 | 0.98822 | -0.22583 | 30.2271
46 | -0.10564 | -0.026651 | 0.1058 | 0.026754 | 0.00016117 | 0.00010293 | 0.1587 | 0.1587 | 0.1587 | 0.99088 | -0.17445 | 0.99253 | -0.14264 | 43.5998
47 | 0.073046 | 0.018413 | -0.072931 | -0.01834 | 0.00011458 | 7.301e-05 | 0.11003 | 0.11003 | 0.11003 | 0.98822 | -0.22583 | 0.98653 | -0.25867 | 30.2271
48 | -0.15483 | -0.039102 | 0.15503 | 0.039226 | 0.00019338 | 0.00012327 | 0.23224 | 0.23224 | 0.23224 | 0.99253 | -0.14264 | 0.99388 | -0.11661 | 31.9005
49 | 0.049033 | 0.012348 | -0.048935 | -0.012286 | 9.8324e-05 | 6.2302e-05 | 0.073532 | 0.073532 | 0.073532 | 0.99253 | -0.14264 | 0.99036 | -0.18467 | 20.2012
50 | 0.072931 | 0.01834 | -0.072777 | -0.018241 | 0.00015464 | 9.8535e-05 | 0.11003 | 0.11003 | 0.11003 | 0.98653 | -0.25867 | 0.98424 | -0.30316 | 30.2271
51 | -0.15503 | -0.039226 | 0.15532 | 0.039409 | 0.00028937 | 0.00018353 | 0.23224 | 0.23223 | 0.23224 | 0.99388 | -0.11661 | 0.99591 | -0.077797 | 21.267
52 | 0.0070318 | 0.0017621 | -0.0070296 | -0.0017614 | 2.1812e-06 | 7.2572e-07 | 0.010565 | 0.010565 | 0.010565 | 0.99036 | -0.18467 | 0.99002 | -0.19118 | 2.9026
53 | 0.03434 | 0.0086291 | -0.034321 | -0.0086173 | 1.8851e-05 | 1.1822e-05 | 0.051604 | 0.051604 | 0.051604 | 0.99036 | -0.18467 | 0.98976 | -0.19618 | 14.177
54 | 0.0075628 | 0.0018949 | -0.0075606 | -0.0018941 | 2.198e-06 | 8.2279e-07 | 0.011363 | 0.011363 | 0.011363 | 0.99036 | -0.18467 | 0.99004 | -0.19078 | 3.1217
55 | 0.0299 | 0.0074951 | -0.029898 | -0.0074941 | 1.6784e-06 | 1.0463e-06 | 0.045204 | 0.045204 | 0.045204 | 0.98424 | -0.30316 | 0.98418 | -0.30434 | 12.4186
56 | 0.0086365 | 0.0021645 | -0.0086359 | -0.0021642 | 6.2459e-07 | 2.6959e-07 | 0.012904 | 0.012904 | 0.012904 | 0.99591 | -0.077797 | 0.99583 | -0.079315 | 3.5451
57 | -0.16395 | -0.041574 | 0.16405 | 0.041632 | 9.1789e-05 | 5.8268e-05 | 0.24514 | 0.24514 | 0.24514 | 0.99591 | -0.077797 | 0.99652 | -0.066157 | 22.4486
58 | 0.0013462 | 0.00033705 | -0.0013461 | -0.00033737 | 4.1312e-08 | -3.1963e-07 | 0.0020232 | 0.0020233 | 0.0020233 | 0.99004 | -0.19078 | 0.99001 | -0.19142 | 0.55585
59 | 0.0062144 | 0.001557 | -0.0062141 | -0.0015569 | 3.0721e-07 | 7.5859e-08 | 0.0093399 | 0.00934 | 0.00934 | 0.99004 | -0.19078 | 0.98999 | -0.19181 | 2.5659
60 | 0.0056678 | 0.00142 | -0.0056676 | -0.00142 | 1.4693e-07 | 2.4616e-08 | 0.0085188 | 0.0085188 | 0.0085188 | 0.98999 | -0.19181 | 0.98996 | -0.19236 | 2.3403
61 | 0.0054401 | 0.001363 | -0.0054396 | -0.0013629 | 5.188e-07 | 6.5964e-08 | 0.0081764 | 0.0081765 | 0.0081765 | 0.99002 | -0.19118 | 0.98992 | -0.19319 | 2.2463
62 | 0.12461 | 0.03186 | -0.12442 | -0.031741 | 0.00018569 | 0.00011866 | 0.18751 | 0.18751 | 0.18751 | 0.99001 | -0.18926 | 0.9884 | -0.22011 | 51.5143
63 | -0.12461 | -0.03186 | 0.12469 | 0.031915 | 8.6555e-05 | 5.5311e-05 | 0.18751 | 0.18751 | 0.18751 | 0.99001 | -0.18926 | 0.99076 | -0.17491 | 51.5142
64 | 0.12125 | 0.030945 | -0.12102 | -0.030803 | 0.00022306 | 0.00014253 | 0.18273 | 0.18273 | 0.18273 | 0.9884 | -0.22011 | 0.98642 | -0.25826 | 50.2012
65 | -0.12921 | -0.033047 | 0.12961 | 0.033303 | 0.0004005 | 0.00025596 | 0.1943 | 0.1943 | 0.1943 | 0.99076 | -0.17491 | 0.99412 | -0.11108 | 53.3778
66 | 0.029898 | 0.0074941 | -0.029895 | -0.0074925 | 2.5923e-06 | 1.6161e-06 | 0.045204 | 0.045204 | 0.045204 | 0.98418 | -0.30434 | 0.98409 | -0.30616 | 12.4186
67 | 0.0018324 | 0.00045907 | -0.0018323 | -0.00045923 | 3.8016e-08 | -1.516e-07 | 0.0027379 | 0.002738 | 0.002738 | 0.99583 | -0.079315 | 0.99581 | -0.079751 | 0.7522
68 | -0.17124 | -0.043435 | 0.17146 | 0.043572 | 0.00021568 | 0.000137 | 0.25588 | 0.25588 | 0.25588 | 0.99652 | -0.066157 | 0.99789 | -0.039998 | 23.4324
69 | 0.0048401 | 0.0012126 | -0.0048399 | -0.0012126 | 2.5584e-07 | -1.9856e-09 | 0.0072751 | 0.0072751 | 0.0072751 | 0.98996 | -0.19236 | 0.98991 | -0.19347 | 1.9987
70 | 0.0037599 | 0.00094196 | -0.0037597 | -0.00094206 | 2.229e-07 | -9.6568e-08 | 0.0056517 | 0.0056517 | 0.0056517 | 0.98992 | -0.19319 | 0.98986 | -0.19443 | 1.5527
71 | -0.0078321 | -0.0019629 | 0.0078331 | 0.0019633 | 1.0222e-06 | 4.0372e-07 | 0.011801 | 0.011801 | 0.011801 | 0.98757 | -0.23877 | 0.98771 | -0.23603 | 3.242
72 | 0.0010037 | 0.00025111 | -0.0010037 | -0.00025155 | 3.0826e-08 | -4.4043e-07 | 0.001512 | 0.0015121 | 0.0015121 | 0.98771 | -0.23603 | 0.98768 | -0.23667 | 0.41542
73 | -0.0029523 | -0.00073973 | 0.0029524 | 0.00073967 | 5.672e-08 | -6.241e-08 | 0.0044381 | 0.0044381 | 0.0044381 | 0.98984 | -0.19473 | 0.98986 | -0.19433 | 1.2193
74 | 0.0014009 | 0.00035092 | -0.0014009 | -0.0003511 | 2.5445e-08 | -1.8036e-07 | 0.0021059 | 0.002106 | 0.002106 | 0.98984 | -0.19473 | 0.98982 | -0.19511 | 0.57857
75 | -0.003574 | -0.00089547 | 0.0035742 | 0.00089539 | 1.466e-07 | -8.0284e-08 | 0.0053726 | 0.0053725 | 0.0053726 | 0.98986 | -0.19433 | 0.98991 | -0.19347 | 1.476
76 | -0.002053 | -0.00051452 | 0.002053 | 0.00051433 | 6.457e-08 | -1.9105e-07 | 0.0030862 | 0.0030862 | 0.0030862 | 0.98982 | -0.19509 | 0.98986 | -0.19443 | 0.84787
77 | -0.0026392 | -0.00066125 | 0.0026393 | 0.00066104 | 1.3035e-07 | -2.0799e-07 | 0.0039415 | 0.0039414 | 0.0039415 | 0.99634 | -0.070502 | 0.99639 | -0.069464 | 1.0828
78 | 0.0026392 | 0.00066125 | -0.0026391 | -0.00066141 | 1.0347e-07 | -1.6508e-07 | 0.0039415 | 0.0039416 | 0.0039416 | 0.99634 | -0.070502 | 0.99629 | -0.071325 | 1.0829
79 | -0.0068594 | -0.0017187 | 0.0068595 | 0.0017187 | 9.8747e-08 | 3.0513e-08 | 0.010244 | 0.010244 | 0.010244 | 0.99639 | -0.069464 | 0.99641 | -0.069162 | 2.8142
80 | -0.0079216 | -0.0019849 | 0.0079224 | 0.0019852 | 7.7904e-07 | 3.0521e-07 | 0.01183 | 0.01183 | 0.01183 | 0.99641 | -0.069162 | 0.99651 | -0.067098 | 3.25
81 | 0.1356 | 0.034807 | -0.13559 | -0.034802 | 8.4695e-06 | 5.4134e-06 | 0.20325 | 0.20325 | 0.20325 | 0.99419 | -0.10979 | 0.99412 | -0.11108 | 55.8368
82 | -0.13668 | -0.035078 | 0.13715 | 0.035379 | 0.00047156 | 0.00030141 | 0.20486 | 0.20486 | 0.20486 | 0.99419 | -0.10979 | 0.99794 | -0.038959 | 56.2809
83 | -0.14057 | -0.036237 | 0.14069 | 0.036308 | 0.00011065 | 7.0465e-05 | 0.20997 | 0.20997 | 0.20997 | 0.99794 | -0.038959 | 0.99879 | -0.02281 | 28.8418
84 | 0.17393 | 0.044247 | -0.17382 | -0.044177 | 0.00010923 | 6.9396e-05 | 0.25935 | 0.25935 | 0.25935 | 0.99879 | -0.02281 | 0.99811 | -0.03585 | 23.7502
85 | -0.31526 | -0.080717 | 0.31561 | 0.080939 | 0.00034871 | 0.00022268 | 0.47028 | 0.47028 | 0.47028 | 0.99879 | -0.02281 | 1 | 0 | 43.0661
86 | 0.17247 | 0.043841 | -0.17244 | -0.043819 | 3.4445e-05 | 2.1882e-05 | 0.25735 | 0.25735 | 0.25735 | 0.99811 | -0.03585 | 0.99789 | -0.039998 | 23.5667
87 | 0.043601 | 0.010962 | -0.043572 | -0.010944 | 2.9429e-05 | 1.859e-05 | 0.064891 | 0.064891 | 0.064891 | 1 | 0 | 0.99926 | -0.014144 | 17.8273
88 | 0.0042156 | 0.0010562 | -0.0042155 | -0.0010563 | 1.3948e-07 | -3.4374e-08 | 0.0062774 | 0.0062775 | 0.0062775 | 0.99926 | -0.014144 | 0.99923 | -0.014839 | 1.7246
89 | 0.039356 | 0.0098874 | -0.039353 | -0.0098857 | 2.7603e-06 | 1.7385e-06 | 0.058614 | 0.058614 | 0.058614 | 0.99926 | -0.014144 | 0.99919 | -0.015614 | 16.1027
90 | 0.001849 | 0.00046316 | -0.0018489 | -0.00046339 | 5.7499e-08 | -2.2812e-07 | 0.0027534 | 0.0027535 | 0.0027535 | 0.99923 | -0.014839 | 0.99919 | -0.015492 | 0.75645
91 | 0.036108 | 0.0090724 | -0.036088 | -0.0090594 | 2.0727e-05 | 1.3015e-05 | 0.053781 | 0.053782 | 0.053782 | 0.99919 | -0.015614 | 0.99856 | -0.027647 | 14.7752
92 | 0.033484 | 0.0084068 | -0.033477 | -0.0084028 | 6.3893e-06 | 3.9997e-06 | 0.049901 | 0.049901 | 0.049901 | 0.99856 | -0.027647 | 0.99835 | -0.031648 | 13.7092
93 | 0.0048562 | 0.0012167 | -0.0048558 | -0.0012167 | 3.4276e-07 | -8.7627e-09 | 0.0072378 | 0.0072379 | 0.0072379 | 0.99835 | -0.031648 | 0.99828 | -0.03313 | 1.9884
94 | 0.028621 | 0.0071861 | -0.028604 | -0.0071757 | 1.6724e-05 | 1.0383e-05 | 0.042664 | 0.042664 | 0.042664 | 0.99835 | -0.031648 | 0.99772 | -0.043904 | 11.7208
95 | -0.0035601 | -0.00089195 | 0.0035601 | 0.00089195 | 7.5519e-10 | -3.5373e-10 | 0.0054589 | 0.0054589 | 0.0054589 | 0.97041 | -0.5709 | 0.97041 | -0.57089 | 1.4997
96 | 0.0023737 | 0.00059461 | -0.0023736 | -0.00059487 | 1.4322e-07 | -2.6447e-07 | 0.0036397 | 0.0036398 | 0.0036398 | 0.97041 | -0.5709 | 0.97035 | -0.57216 | 0.99995
97 | -0.0057979 | -0.0014528 | 0.0057986 | 0.0014529 | 6.8773e-07 | 1.5344e-07 | 0.0088903 | 0.0088902 | 0.0088903 | 0.97041 | -0.57089 | 0.97054 | -0.5684 | 2.4424
98 | -0.0090658 | -0.0022718 | 0.0090662 | 0.002272 | 4.0663e-07 | 1.9088e-07 | 0.013899 | 0.013899 | 0.013899 | 0.97054 | -0.5684 | 0.97059 | -0.56746 | 3.8185
99 | -0.011314 | -0.0028353 | 0.011314 | 0.0028354 | 2.0226e-07 | 1.0729e-07 | 0.017346 | 0.017345 | 0.017346 | 0.97059 | -0.56746 | 0.97061 | -0.56709 | 4.7652
100 | -0.013548 | -0.0033953 | 0.013551 | 0.0033968 | 2.5395e-06 | 1.4312e-06 | 0.02077 | 0.02077 | 0.02077 | 0.97061 | -0.56709 | 0.97081 | -0.56315 | 5.7062
101 | 0.0076504 | 0.0019175 | -0.0076497 | -0.0019172 | 7.0127e-07 | 2.7875e-07 | 0.011693 | 0.011693 | 0.011693 | 0.97357 | -0.50877 | 0.97348 | -0.5107 | 3.2124
102 | 0.0060745 | 0.0015224 | -0.0060743 | -0.0015224 | 2.2486e-07 | 5.7447e-08 | 0.0092853 | 0.0092853 | 0.0092853 | 0.97348 | -0.5107 | 0.97344 | -0.51147 | 2.5509
103 | 0.016957 | 0.0042514 | -0.016953 | -0.0042495 | 3.1045e-06 | 1.8353e-06 | 0.025986 | 0.025986 | 0.025986 | 0.971 | -0.55931 | 0.97081 | -0.56315 | 7.139
104 | -0.018217 | -0.0045674 | 0.018223 | 0.0045708 | 5.7065e-06 | 3.4106e-06 | 0.027918 | 0.027918 | 0.027918 | 0.971 | -0.55931 | 0.97133 | -0.55274 | 7.6697
105 | 0.0055857 | 0.0013997 | -0.0055856 | -0.0013997 | 4.1421e-08 | 7.8368e-09 | 0.0085568 | 0.0085568 | 0.0085568 | 0.97133 | -0.55274 | 0.97132 | -0.55289 | 2.3508
106 | -0.023809 | -0.0059705 | 0.023818 | 0.005976 | 9.0173e-06 | 5.5473e-06 | 0.036475 | 0.036475 | 0.036475 | 0.97133 | -0.55274 | 0.97173 | -0.54479 | 10.0205
107 | 0.0027627 | 0.00069219 | -0.0027625 | -0.00069236 | 1.4479e-07 | -1.7413e-07 | 0.0042322 | 0.0042323 | 0.0042323 | 0.97132 | -0.55289 | 0.97127 | -0.55399 | 1.1627
108 | -0.026424 | -0.0066291 | 0.02644 | 0.0066393 | 1.6462e-05 | 1.0203e-05 | 0.040465 | 0.040465 | 0.040465 | 0.97173 | -0.54479 | 0.97239 | -0.53174 | 11.1168
109 | -0.031142 | -0.0078178 | 0.031145 | 0.0078195 | 2.6584e-06 | 1.6626e-06 | 0.047661 | 0.047661 | 0.047661 | 0.97239 | -0.53174 | 0.97248 | -0.52995 | 13.0936
110 | -0.034193 | -0.0085833 | 0.034218 | 0.0085992 | 2.5413e-05 | 1.5957e-05 | 0.052324 | 0.052323 | 0.052324 | 0.97248 | -0.52995 | 0.97327 | -0.51438 | 14.3746
111 | -0.011622 | -0.0029125 | 0.011623 | 0.0029128 | 5.7483e-07 | 3.0158e-07 | 0.017355 | 0.017355 | 0.017355 | 0.99651 | -0.067098 | 0.99657 | -0.066059 | 4.7678
112 | -0.014249 | -0.0035709 | 0.014252 | 0.0035729 | 3.6497e-06 | 2.0556e-06 | 0.021275 | 0.021275 | 0.021275 | 0.99657 | -0.066059 | 0.99684 | -0.060684 | 5.8448
113 | -0.017306 | -0.0043382 | 0.017306 | 0.0043383 | 1.5188e-07 | 8.9292e-08 | 0.025833 | 0.025833 | 0.025833 | 0.99684 | -0.060684 | 0.99685 | -0.0605 | 7.097
114 | -0.019957 | -0.0050026 | 0.019963 | 0.0050059 | 5.4168e-06 | 3.2545e-06 | 0.029791 | 0.029791 | 0.029791 | 0.99685 | -0.0605 | 0.99715 | -0.054805 | 8.1843
115 | 0.0026513 | 0.00066433 | -0.0026512 | -0.00066447 | 8.7382e-08 | -1.3802e-07 | 0.0039576 | 0.0039577 | 0.0039577 | 0.99685 | -0.0605 | 0.99682 | -0.061191 | 1.0873
116 | 0.0022608 | 0.00056635 | -0.0022607 | -0.00056659 | 9.9857e-08 | -2.4126e-07 | 0.0033737 | 0.0033738 | 0.0033738 | 0.99715 | -0.054805 | 0.9971 | -0.055732 | 0.92686
117 | -0.023971 | -0.0060102 | 0.023983 | 0.0060178 | 1.2458e-05 | 7.6344e-06 | 0.035772 | 0.035772 | 0.035772 | 0.99715 | -0.054805 | 0.99772 | -0.043904 | 9.8275
118 | 0.004621 | 0.0011579 | -0.0046208 | -0.0011579 | 1.537e-07 | -1.4324e-08 | 0.0068917 | 0.0068918 | 0.0068918 | 0.99772 | -0.043904 | 0.99768 | -0.044603 | 1.8933
119 | -0.0026161 | -0.00065565 | 0.0026162 | 0.00065546 | 1.1392e-07 | -1.8764e-07 | 0.003902 | 0.0039019 | 0.003902 | 0.99763 | -0.045517 | 0.99768 | -0.044603 | 1.072
120 | 0.0026953 | 0.00067526 | -0.0026951 | -0.00067546 | 1.3613e-07 | -2.0692e-07 | 0.0040174 | 0.0040176 | 0.0040176 | 0.99828 | -0.03313 | 0.99822 | -0.034191 | 1.1037
121 | 0.12102 | 0.030803 | -0.12064 | -0.030559 | 0.00038164 | 0.00024386 | 0.18273 | 0.18273 | 0.18273 | 0.98642 | -0.25826 | 0.98302 | -0.3239 | 50.2012
122 | 0.040081 | 0.01008 | -0.040051 | -0.010061 | 2.9951e-05 | 1.8903e-05 | 0.061241 | 0.061241 | 0.061241 | 0.97409 | -0.49836 | 0.97329 | -0.51401 | 16.8245
123 | -0.036764 | -0.0092374 | 0.036765 | 0.0092378 | 6.3669e-07 | 4.0081e-07 | 0.056217 | 0.056217 | 0.056217 | 0.97327 | -0.51438 | 0.97329 | -0.51401 | 15.4442
124 | -0.0041313 | -0.0010339 | 0.0041315 | 0.0010339 | 1.6451e-07 | -3.5732e-08 | 0.0062666 | 0.0062666 | 0.0062666 | 0.9809 | -0.36515 | 0.98095 | -0.36432 | 1.7216
125 | -0.0086154 | -0.0021577 | 0.0086164 | 0.0021581 | 1.0797e-06 | 4.7814e-07 | 0.013068 | 0.013068 | 0.013068 | 0.98095 | -0.36432 | 0.98108 | -0.36168 | 3.5902
126 | -0.011253 | -0.002819 | 0.011257 | 0.0028209 | 3.6887e-06 | 1.9342e-06 | 0.017067 | 0.017067 | 0.017067 | 0.98108 | -0.36168 | 0.98143 | -0.3548 | 4.6888

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36262 | 0.092344

## res_load
| p_mw | q_mvar
0 | 0.0019454 | 0.00048757
1 | 0.00074638 | 0.00018706
2 | 0.0016734 | 0.0004194
3 | 0.0011328 | 0.00028391
4 | 0.0076483 | 0.0019169
5 | 0.0013831 | 0.00034663
6 | 0.0032405 | 0.00081214
7 | 0.0028018 | 0.00070221
8 | 0.0018256 | 0.00045754
9 | 0.0038189 | 0.00095712
10 | 0.0025277 | 0.00063351
11 | 0.0023146 | 0.0005801
12 | 0.00095251 | 0.00023872
13 | 0.001281 | 0.00032105
14 | 0.0012733 | 0.00031911
15 | 0.0017998 | 0.00045108
16 | 0.0021926 | 0.00054951
17 | 0.0017944 | 0.00044973
18 | 0.0011252 | 0.00028201
19 | 0.0015134 | 0.0003793
20 | 0.0018195 | 0.00045601
21 | 0.0020455 | 0.00051266
22 | 0.0014508 | 0.0003636
23 | 0.0011917 | 0.00029866
24 | 0.0038038 | 0.00095331
25 | 0.0032841 | 0.00082307
26 | 0.0021879 | 0.00054834
27 | 0.001311 | 0.00032856
28 | 0.0023088 | 0.00057863
29 | 0.0021612 | 0.00054164
30 | 0.0047572 | 0.0011923
31 | 0.0028954 | 0.00072566
32 | 0.032414 | 0.0081238
33 | 0.042877 | 0.010746
34 | 0.0013461 | 0.00033737
35 | 0.00054633 | 0.00013692
36 | 0.0015895 | 0.00039837
37 | 0.0015382 | 0.00038551
38 | 0.0031749 | 0.00079571
39 | 0.0045166 | 0.001132
40 | 0.0068035 | 0.0017051
41 | 0.007195 | 0.0018032
42 | 0.029895 | 0.0074925
43 | 0.00082748 | 0.00020739
44 | 0.0016797 | 0.00042097
45 | 0.0078321 | 0.0019629
46 | 0.0010037 | 0.00025155
47 | 0.0015514 | 0.00038881
48 | 0.00062166 | 0.0001558
49 | 0.0014009 | 0.0003511
50 | 0.0012657 | 0.00031722
51 | 0.002053 | 0.00051452
52 | 0.0017067 | 0.00042773
53 | 0.0042201 | 0.0010577
54 | 0.0026391 | 0.00066141
55 | 0.0010622 | 0.0002662
56 | 0.0010802 | 0.00027072
57 | 0.00598 | 0.0014987
58 | 0.0034245 | 0.00085825
59 | 0.00064634 | 0.00016199
60 | 0.0013439 | 0.00033681
61 | 0.0017636 | 0.00044199
62 | 0.00098353 | 0.00024649
63 | 0.0023665 | 0.0005931
64 | 0.003245 | 0.00081326
65 | 0.0018489 | 0.00046339
66 | 0.0026038 | 0.00065258
67 | 0.0011864 | 0.00029734
68 | 0.0022378 | 0.00056085
69 | 0.0023736 | 0.00059487
70 | 0.0032672 | 0.00081884
71 | 0.0022478 | 0.00056334
72 | 0.002234 | 0.00055989
73 | 0.0015752 | 0.00039477
74 | 0.0012608 | 0.00031599
75 | 0.0034027 | 0.00085279
76 | 0.0028229 | 0.0007075
77 | 0.002606 | 0.00065311
78 | 0.0027625 | 0.00069236
79 | 0.0047023 | 0.0011785
80 | 0.0030475 | 0.00076377
81 | 0.0037 | 0.00092731
82 | 0.0026255 | 0.00065802
83 | 0.0030536 | 0.00076531
84 | 0.0017475 | 0.00043797
85 | 0.0026512 | 0.00066447
86 | 0.0022607 | 0.00056659
87 | 0.0026161 | 0.00065565
88 | 0.0020046 | 0.00050241
89 | 0.0021605 | 0.00054148
90 | 0.0026951 | 0.00067546
91 | 0.0018323 | 0.00045923
92 | 0.0024747 | 0.00062021
93 | 0.0025465 | 0.00063822
94 | 0.0032863 | 0.00082362
95 | 0.0060743 | 0.0015224
96 | 0.0023311 | 0.00058424
97 | 0.0044839 | 0.0011238
98 | 0.0026367 | 0.00066082
99 | 0.0071324 | 0.0017875
100 | 0.0012063 | 0.00030233
101 | 0.0035677 | 0.00089414

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1