## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2543-10_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2543-10_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2543-10_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2543-10_0_7_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_2543-10_0_7_node_117 | 0.4 | n |  | TRUE
5 | bus_LV_2543-10_0_7_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_2543-10_0_7_node_118 | 0.4 | n |  | TRUE
7 | bus_LV_2543-10_0_7_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_2543-10_0_7_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2543-10_0_7_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2543-10_0_7_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2543-10_0_7_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2543-10_0_7_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_2543-10_0_7_node_33 | 0.4 | n |  | TRUE
14 | bus_LV_2543-10_0_7_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_2543-10_0_7_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2543-10_0_7_node_67 | 0.4 | n |  | TRUE
17 | bus_LV_2543-10_0_7_node_77 | 0.4 | n |  | TRUE
18 | bus_LV_2543-10_0_7_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_2543-10_0_7_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_2543-10_0_7_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_2543-10_0_7_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_2543-10_0_7_node_79 | 0.4 | n |  | TRUE
23 | bus_LV_2543-10_0_7_node_76 | 0.4 | n |  | TRUE
24 | bus_LV_2543-10_0_7_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_2543-10_0_7_node_80 | 0.4 | n |  | TRUE
26 | bus_LV_2543-10_0_7_node_9 | 0.4 | n |  | TRUE
27 | bus_LV_2543-10_0_7_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_2543-10_0_7_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2543-10_0_7_node_135 | 0.4 | n |  | TRUE
30 | bus_LV_2543-10_0_7_node_134 | 0.4 | n |  | TRUE
31 | bus_LV_2543-10_0_7_node_130 | 0.4 | n |  | TRUE
32 | bus_LV_2543-10_0_7_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_2543-10_0_7_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2543-10_0_7_node_129 | 0.4 | n |  | TRUE
35 | bus_LV_2543-10_0_7_node_14 | 0.4 | n |  | TRUE
36 | bus_LV_2543-10_0_7_node_15 | 0.4 | n |  | TRUE
37 | bus_LV_2543-10_0_7_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2543-10_0_7_node_16 | 0.4 | n |  | TRUE
39 | bus_LV_2543-10_0_7_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_2543-10_0_7_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_2543-10_0_7_node_84 | 0.4 | n |  | TRUE
42 | bus_LV_2543-10_0_7_node_69 | 0.4 | n |  | TRUE
43 | bus_LV_2543-10_0_7_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_2543-10_0_7_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_2543-10_0_7_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_2543-10_0_7_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_2543-10_0_7_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_2543-10_0_7_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_2543-10_0_7_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_2543-10_0_7_node_101 | 0.4 | n |  | TRUE
51 | bus_LV_2543-10_0_7_node_122 | 0.4 | n |  | TRUE
52 | bus_LV_2543-10_0_7_node_132 | 0.4 | n |  | TRUE
53 | bus_LV_2543-10_0_7_node_136 | 0.4 | n |  | TRUE
54 | bus_LV_2543-10_0_7_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_2543-10_0_7_node_123 | 0.4 | n |  | TRUE
56 | bus_LV_2543-10_0_7_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_2543-10_0_7_node_138 | 0.4 | n |  | TRUE
58 | bus_LV_2543-10_0_7_node_93 | 0.4 | n |  | TRUE
59 | bus_LV_2543-10_0_7_node_94 | 0.4 | n |  | TRUE
60 | bus_LV_2543-10_0_7_node_92 | 0.4 | n |  | TRUE
61 | bus_LV_2543-10_0_7_node_27 | 0.4 | n |  | TRUE
62 | bus_LV_2543-10_0_7_node_28 | 0.4 | n |  | TRUE
63 | bus_LV_2543-10_0_7_node_29 | 0.4 | n |  | TRUE
64 | bus_LV_2543-10_0_7_node_30 | 0.4 | n |  | TRUE
65 | bus_LV_2543-10_0_7_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_2543-10_0_7_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_2543-10_0_7_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_2543-10_0_7_node_128 | 0.4 | n |  | TRUE
69 | bus_LV_2543-10_0_7_node_125 | 0.4 | n |  | TRUE
70 | bus_LV_2543-10_0_7_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_2543-10_0_7_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2543-10_0_7_node_36 | 0.4 | n |  | TRUE
73 | bus_LV_2543-10_0_7_node_35 | 0.4 | n |  | TRUE
74 | bus_LV_2543-10_0_7_node_131 | 0.4 | n |  | TRUE
75 | bus_LV_2543-10_0_7_node_146 | 0.4 | n |  | TRUE
76 | bus_LV_2543-10_0_7_node_34 | 0.4 | n |  | TRUE
77 | bus_LV_2543-10_0_7_node_37 | 0.4 | n |  | TRUE
78 | bus_LV_2543-10_0_7_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2543-10_0_7_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_2543-10_0_7_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_2543-10_0_7_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2543-10_0_7_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2543-10_0_7_node_139 | 0.4 | n |  | TRUE
84 | bus_LV_2543-10_0_7_node_44 | 0.4 | n |  | TRUE
85 | bus_LV_2543-10_0_7_node_113 | 0.4 | n |  | TRUE
86 | bus_LV_2543-10_0_7_node_144 | 0.4 | n |  | TRUE
87 | bus_LV_2543-10_0_7_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_2543-10_0_7_node_141 | 0.4 | n |  | TRUE
89 | bus_LV_2543-10_0_7_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_2543-10_0_7_node_142 | 0.4 | n |  | TRUE
91 | bus_LV_2543-10_0_7_node_52 | 0.4 | n |  | TRUE
92 | bus_LV_2543-10_0_7_node_111 | 0.4 | n |  | TRUE
93 | bus_LV_2543-10_0_7_node_121 | 0.4 | n |  | TRUE
94 | bus_LV_2543-10_0_7_node_112 | 0.4 | n |  | TRUE
95 | bus_LV_2543-10_0_7_node_119 | 0.4 | n |  | TRUE
96 | bus_LV_2543-10_0_7_node_124 | 0.4 | n |  | TRUE
97 | bus_LV_2543-10_0_7_node_110 | 0.4 | n |  | TRUE
98 | bus_LV_2543-10_0_7_node_108 | 0.4 | n |  | TRUE
99 | bus_LV_2543-10_0_7_node_109 | 0.4 | n |  | TRUE
100 | bus_LV_2543-10_0_7_node_140 | 0.4 | n |  | TRUE
101 | bus_LV_2543-10_0_7_node_116 | 0.4 | n |  | TRUE
102 | bus_LV_2543-10_0_7_node_51 | 0.4 | n |  | TRUE
103 | bus_LV_2543-10_0_7_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_2543-10_0_7_node_145 | 0.4 | n |  | TRUE
105 | bus_LV_2543-10_0_7_node_45 | 0.4 | n |  | TRUE
106 | bus_LV_2543-10_0_7_node_46 | 0.4 | n |  | TRUE
107 | bus_LV_2543-10_0_7_node_47 | 0.4 | n |  | TRUE
108 | bus_LV_2543-10_0_7_node_55 | 0.4 | n |  | TRUE
109 | bus_LV_2543-10_0_7_node_56 | 0.4 | n |  | TRUE
110 | bus_LV_2543-10_0_7_node_57 | 0.4 | n |  | TRUE
111 | bus_LV_2543-10_0_7_node_58 | 0.4 | n |  | TRUE
112 | bus_LV_2543-10_0_7_node_59 | 0.4 | n |  | TRUE
113 | bus_LV_2543-10_0_7_node_68 | 0.4 | n |  | TRUE
114 | bus_LV_2543-10_0_7_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_2543-10_0_7_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_2543-10_0_7_node_104 | 0.4 | n |  | TRUE
117 | bus_LV_2543-10_0_7_node_71 | 0.4 | n |  | TRUE
118 | bus_LV_2543-10_0_7_node_72 | 0.4 | n |  | TRUE
119 | bus_LV_2543-10_0_7_node_73 | 0.4 | n |  | TRUE
120 | bus_LV_2543-10_0_7_node_75 | 0.4 | n |  | TRUE
121 | bus_LV_2543-10_0_7_node_81 | 0.4 | n |  | TRUE
122 | bus_LV_2543-10_0_7_node_82 | 0.4 | n |  | TRUE
123 | bus_LV_2543-10_0_7_node_133 | 0.4 | n |  | TRUE
124 | bus_LV_2543-10_0_7_node_137 | 0.4 | n |  | TRUE
125 | bus_LV_2543-10_0_7_node_83 | 0.4 | n |  | TRUE
126 | bus_LV_2543-10_0_7_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_2543-10_0_7_node_87 | 0.4 | n |  | TRUE
128 | bus_LV_2543-10_0_7_node_88 | 0.4 | n |  | TRUE
129 | bus_LV_2543-10_0_7_node_89 | 0.4 | n |  | TRUE
130 | bus_LV_2543-10_0_7_node_90 | 0.4 | n |  | TRUE
131 | bus_LV_2543-10_0_7_node_91 | 0.4 | n |  | TRUE
132 | bus_LV_2543-10_0_7_node_97 | 0.4 | n |  | TRUE
133 | bus_LV_2543-10_0_7_node_98 | 0.4 | n |  | TRUE
134 | bus_LV_2543-10_0_7_node_99 | 0.4 | n |  | TRUE
135 | bus_LV_2543-10_0_7_node_100 | 0.4 | n |  | TRUE
136 | bus_LV_2543-10_0_7_node_106 | 0.4 | n |  | TRUE
137 | bus_LV_2543-10_0_7_node_107 | 0.4 | n |  | TRUE
138 | bus_LV_2543-10_0_7_node_102 | 0.4 | n |  | TRUE
139 | bus_LV_2543-10_0_7_node_103 | 0.4 | n |  | TRUE
140 | bus_LV_2543-10_0_7_node_120 | 0.4 | n |  | TRUE
141 | bus_LV_2543-10_0_7_node_143 | 0.4 | n |  | TRUE
142 | bus_LV_2543-10_0_7_node_126 | 0.4 | n |  | TRUE
143 | bus_MV_396_0_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2543-10_0_7_load_0 | 0 | 0.0066452 | 0.0016654 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2543-10_0_7_load_1 | 1 | 0.01135 | 0.0028446 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2543-10_0_7_load_117 | 4 | 0.0024011 | 0.00060177 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2543-10_0_7_load_118 | 6 | 0.0024064 | 0.00060309 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2543-10_0_7_load_3 | 7 | 0.0021 | 0.00052631 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2543-10_0_7_load_4 | 8 | 0.0029521 | 0.00073987 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2543-10_0_7_load_33 | 13 | 0.002106 | 0.00052781 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2543-10_0_7_load_31 | 14 | 0.0013324 | 0.00033393 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2543-10_0_7_load_67 | 16 | 0.01004 | 0.0025164 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2543-10_0_7_load_66 | 18 | 0.002179 | 0.0005461 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2543-10_0_7_load_85 | 19 | 0.005503 | 0.0013792 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2543-10_0_7_load_65 | 21 | 0.0030423 | 0.00076247 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2543-10_0_7_load_76 | 23 | 0.0041076 | 0.0010294 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2543-10_0_7_load_80 | 25 | 0.011658 | 0.0029218 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2543-10_0_7_load_9 | 26 | 0.010419 | 0.0026113 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2543-10_0_7_load_10 | 27 | 0.011353 | 0.0028453 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2543-10_0_7_load_135 | 29 | 0.0090162 | 0.0022597 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2543-10_0_7_load_134 | 30 | 0.0089816 | 0.002251 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2543-10_0_7_load_130 | 31 | 0.0047782 | 0.0011975 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2543-10_0_7_load_129 | 34 | 0.0067929 | 0.0017025 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2543-10_0_7_load_14 | 35 | 0.01173 | 0.0029397 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2543-10_0_7_load_15 | 36 | 0.044886 | 0.011249 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2543-10_0_7_load_17 | 37 | 0.007112 | 0.0017824 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2543-10_0_7_load_16 | 38 | 0.0055346 | 0.0013871 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2543-10_0_7_load_19 | 43 | 0.0050058 | 0.0012546 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2543-10_0_7_load_22 | 46 | 0.0034062 | 0.00085366 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2543-10_0_7_load_24 | 48 | 0.0031599 | 0.00079195 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2543-10_0_7_load_122 | 51 | 0.00092572 | 0.00023201 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2543-10_0_7_load_132 | 52 | 0.0048109 | 0.0012057 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2543-10_0_7_load_136 | 53 | 0.0078477 | 0.0019668 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2543-10_0_7_load_74 | 54 | 0.0009257 | 0.000232 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2543-10_0_7_load_123 | 55 | 0.0012084 | 0.00030285 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2543-10_0_7_load_138 | 57 | 0.01134 | 0.002842 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2543-10_0_7_load_94 | 59 | 0.005858 | 0.0014681 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2543-10_0_7_load_92 | 60 | 0.0010538 | 0.00026411 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2543-10_0_7_load_27 | 61 | 0.0079307 | 0.0019876 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2543-10_0_7_load_28 | 62 | 0.0011935 | 0.00029912 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2543-10_0_7_load_29 | 63 | 0.0064593 | 0.0016189 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2543-10_0_7_load_53 | 67 | 0.013018 | 0.0032627 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2543-10_0_7_load_128 | 68 | 0.0047008 | 0.0011781 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2543-10_0_7_load_125 | 69 | 0.0047574 | 0.0011923 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2543-10_0_7_load_131 | 74 | 0.011645 | 0.0029186 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2543-10_0_7_load_146 | 75 | 0.034707 | 0.0086984 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2543-10_0_7_load_54 | 78 | 0.012787 | 0.0032048 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2543-10_0_7_load_60 | 79 | 0.004823 | 0.0012087 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2543-10_0_7_load_63 | 81 | 0.0019734 | 0.00049457 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2543-10_0_7_load_64 | 82 | 0.0024558 | 0.00061548 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2543-10_0_7_load_139 | 83 | 0.0064187 | 0.0016087 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2543-10_0_7_load_86 | 87 | 0.0016384 | 0.00041061 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2543-10_0_7_load_141 | 88 | 0.0064606 | 0.0016192 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2543-10_0_7_load_142 | 90 | 0.0018635 | 0.00046703 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2543-10_0_7_load_52 | 91 | 0.01232 | 0.0030878 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2543-10_0_7_load_121 | 93 | 0.0076848 | 0.001926 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2543-10_0_7_load_119 | 95 | 0.0064406 | 0.0016142 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2543-10_0_7_load_124 | 96 | 0.0018838 | 0.00047214 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2543-10_0_7_load_108 | 98 | 0.0081048 | 0.0020313 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2543-10_0_7_load_109 | 99 | 0.011784 | 0.0029534 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2543-10_0_7_load_140 | 100 | 0.0048764 | 0.0012221 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2543-10_0_7_load_116 | 101 | 0.0058262 | 0.0014602 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2543-10_0_7_load_51 | 102 | 0.0072415 | 0.0018149 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2543-10_0_7_load_145 | 104 | 0.010528 | 0.0026387 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2543-10_0_7_load_45 | 105 | 0.0020687 | 0.00051846 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2543-10_0_7_load_47 | 107 | 0.022606 | 0.0056656 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2543-10_0_7_load_55 | 108 | 0.00046627 | 0.00011686 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2543-10_0_7_load_56 | 109 | 0.00048307 | 0.00012107 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2543-10_0_7_load_57 | 110 | 0.0015618 | 0.00039143 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2543-10_0_7_load_59 | 112 | 0.0026659 | 0.00066813 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2543-10_0_7_load_68 | 113 | 0.0031285 | 0.00078408 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2543-10_0_7_load_96 | 115 | 0.0022615 | 0.00056679 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2543-10_0_7_load_104 | 116 | 0.0028906 | 0.00072445 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2543-10_0_7_load_71 | 117 | 0.0011939 | 0.00029923 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2543-10_0_7_load_72 | 118 | 0.0040091 | 0.0010048 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2543-10_0_7_load_73 | 119 | 0.0071805 | 0.0017996 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2543-10_0_7_load_81 | 121 | 0.0049227 | 0.0012337 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2543-10_0_7_load_82 | 122 | 0.012763 | 0.0031988 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2543-10_0_7_load_137 | 124 | 0.00027292 | 6.8401e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2543-10_0_7_load_127 | 126 | 0.0056046 | 0.0014046 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2543-10_0_7_load_87 | 127 | 0.0016551 | 0.00041482 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2543-10_0_7_load_88 | 128 | 0.0012156 | 0.00030465 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2543-10_0_7_load_89 | 129 | 0.0015442 | 0.00038701 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2543-10_0_7_load_90 | 130 | 0.0066631 | 0.0016699 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2543-10_0_7_load_91 | 131 | 0.0057825 | 0.0014492 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2543-10_0_7_load_97 | 132 | 0.034055 | 0.0085351 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2543-10_0_7_load_99 | 134 | 0.0058027 | 0.0014543 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2543-10_0_7_load_100 | 135 | 0.012026 | 0.003014 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2543-10_0_7_load_106 | 136 | 0.0063914 | 0.0016018 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2543-10_0_7_load_107 | 137 | 0.0087852 | 0.0022018 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2543-10_0_7_load_102 | 138 | 0.00077282 | 0.00019369 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2543-10_0_7_load_103 | 139 | 0.00057266 | 0.00014352 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2543-10_0_7_load_120 | 140 | 0.0062246 | 0.00156 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2543-10_0_7_load_143 | 141 | 0.0051868 | 0.0012999 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2543-10_0_7_load_126 | 142 | 0.003179 | 0.00079674 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 66 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2543-10_0_7_line_0 |  | 0 | 1 | 0.0039639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2543-10_0_7_line_1 |  | 1 | 2 | 0.03846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2543-10_0_7_line_2 |  | 2 | 3 | 0.003789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2543-10_0_7_line_3 |  | 2 | 4 | 0.015911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2543-10_0_7_line_4 |  | 3 | 5 | 0.003812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2543-10_0_7_line_5 |  | 4 | 6 | 0.0012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2543-10_0_7_line_6 |  | 5 | 31 | 0.00586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2543-10_0_7_line_7 |  | 7 | 8 | 0.016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2543-10_0_7_line_8 |  | 7 | 9 | 0.015065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2543-10_0_7_line_9 |  | 8 | 10 | 0.10496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2543-10_0_7_line_10 |  | 9 | 11 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2543-10_0_7_line_11 |  | 10 | 12 | 0.10293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2543-10_0_7_line_12 |  | 11 | 13 | 0.012845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2543-10_0_7_line_13 |  | 11 | 14 | 0.026335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2543-10_0_7_line_14 |  | 12 | 18 | 0.051411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2543-10_0_7_line_15 |  | 13 | 19 | 0.0052873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2543-10_0_7_line_16 |  | 14 | 20 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2543-10_0_7_line_17 |  | 15 | 16 | 0.024097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2543-10_0_7_line_18 |  | 15 | 17 | 0.01217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2543-10_0_7_line_19 |  | 16 | 21 | 0.034885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2543-10_0_7_line_20 |  | 17 | 22 | 0.040678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2543-10_0_7_line_21 |  | 17 | 23 | 0.036723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2543-10_0_7_line_22 |  | 18 | 21 | 0.020056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2543-10_0_7_line_23 |  | 19 | 87 | 0.0010978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2543-10_0_7_line_24 |  | 20 | 76 | 0.003953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2543-10_0_7_line_25 |  | 22 | 123 | 0.012707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2543-10_0_7_line_26 |  | 22 | 52 | 0.026935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_2543-10_0_7_line_27 |  | 23 | 24 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2543-10_0_7_line_28 |  | 24 | 25 | 0.014174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2543-10_0_7_line_29 |  | 26 | 27 | 0.020566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2543-10_0_7_line_30 |  | 27 | 28 | 0.043416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2543-10_0_7_line_31 |  | 28 | 29 | 0.017577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2543-10_0_7_line_32 |  | 28 | 30 | 0.030565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2543-10_0_7_line_33 |  | 29 | 32 | 0.014231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2543-10_0_7_line_34 |  | 30 | 33 | 0.004329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2543-10_0_7_line_35 |  | 31 | 34 | 0.023827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2543-10_0_7_line_36 |  | 32 | 106 | 0.027153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2543-10_0_7_line_37 |  | 33 | 53 | 0.038226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2543-10_0_7_line_38 |  | 33 | 45 | 0.02639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2543-10_0_7_line_39 |  | 34 | 48 | 0.004622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2543-10_0_7_line_40 |  | 35 | 36 | 0.0025506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2543-10_0_7_line_41 |  | 36 | 37 | 0.028069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2543-10_0_7_line_42 |  | 37 | 40 | 0.05001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2543-10_0_7_line_43 |  | 37 | 41 | 0.08733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2543-10_0_7_line_44 |  | 38 | 39 | 0.091701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2543-10_0_7_line_45 |  | 39 | 41 | 0.15641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2543-10_0_7_line_46 |  | 40 | 42 | 0.04849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2543-10_0_7_line_47 |  | 42 | 93 | 0.013077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2543-10_0_7_line_48 |  | 42 | 85 | 0.05739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2543-10_0_7_line_49 |  | 42 | 111 | 0.052114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2543-10_0_7_line_50 |  | 43 | 44 | 0.051362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2543-10_0_7_line_51 |  | 43 | 45 | 0.052016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2543-10_0_7_line_52 |  | 44 | 46 | 0.017102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2543-10_0_7_line_53 |  | 44 | 47 | 0.037672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2543-10_0_7_line_54 |  | 44 | 48 | 0.021859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2543-10_0_7_line_55 |  | 45 | 49 | 0.008764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2543-10_0_7_line_56 |  | 46 | 50 | 0.020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2543-10_0_7_line_57 |  | 47 | 51 | 0.045944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2543-10_0_7_line_58 |  | 49 | 52 | 0.020197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2543-10_0_7_line_59 |  | 50 | 54 | 0.0053246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2543-10_0_7_line_60 |  | 51 | 55 | 0.058708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2543-10_0_7_line_61 |  | 54 | 118 | 0.015454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2543-10_0_7_line_62 |  | 56 | 57 | 0.012233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2543-10_0_7_line_63 |  | 56 | 58 | 0.022236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2543-10_0_7_line_64 |  | 57 | 124 | 0.013836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2543-10_0_7_line_65 |  | 58 | 59 | 0.015396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2543-10_0_7_line_66 |  | 58 | 60 | 0.039505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2543-10_0_7_line_67 |  | 59 | 131 | 0.029662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2543-10_0_7_line_68 |  | 60 | 64 | 0.0011725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2543-10_0_7_line_69 |  | 61 | 62 | 0.0039415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2543-10_0_7_line_70 |  | 61 | 63 | 0.064836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2543-10_0_7_line_71 |  | 62 | 64 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2543-10_0_7_line_72 |  | 64 | 65 | 0.076978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2543-10_0_7_line_73 |  | 65 | 69 | 0.0070221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2543-10_0_7_line_74 |  | 65 | 70 | 0.073701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2543-10_0_7_line_75 |  | 65 | 66 | 0.046773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2543-10_0_7_line_76 |  | 66 | 67 | 0.025987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2543-10_0_7_line_77 |  | 66 | 68 | 0.01497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2543-10_0_7_line_78 |  | 67 | 102 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2543-10_0_7_line_79 |  | 68 | 103 | 0.01418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2543-10_0_7_line_80 |  | 70 | 74 | 0.023657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2543-10_0_7_line_81 |  | 70 | 71 | 0.12551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2543-10_0_7_line_82 |  | 71 | 72 | 0.073574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2543-10_0_7_line_83 |  | 72 | 73 | 0.04871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2543-10_0_7_line_84 |  | 73 | 75 | 0.052818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2543-10_0_7_line_85 |  | 76 | 83 | 0.015695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2543-10_0_7_line_86 |  | 77 | 78 | 0.03056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2543-10_0_7_line_87 |  | 77 | 79 | 0.079687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2543-10_0_7_line_88 |  | 78 | 91 | 0.04894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2543-10_0_7_line_89 |  | 79 | 80 | 0.015953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2543-10_0_7_line_90 |  | 80 | 81 | 0.033549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2543-10_0_7_line_91 |  | 80 | 82 | 0.014406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2543-10_0_7_line_92 |  | 84 | 85 | 0.17171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2543-10_0_7_line_93 |  | 84 | 86 | 0.009607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2543-10_0_7_line_94 |  | 85 | 88 | 0.016298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2543-10_0_7_line_95 |  | 86 | 104 | 0.027435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2543-10_0_7_line_96 |  | 86 | 89 | 0.006946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2543-10_0_7_line_97 |  | 87 | 127 | 0.017507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2543-10_0_7_line_98 |  | 89 | 90 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2543-10_0_7_line_99 |  | 90 | 141 | 0.022018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2543-10_0_7_line_100 |  | 91 | 102 | 0.0035773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2543-10_0_7_line_101 |  | 92 | 93 | 0.071856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2543-10_0_7_line_102 |  | 92 | 94 | 0.057195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2543-10_0_7_line_103 |  | 92 | 95 | 0.047683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2543-10_0_7_line_104 |  | 94 | 96 | 0.01687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2543-10_0_7_line_105 |  | 94 | 97 | 0.016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2543-10_0_7_line_106 |  | 95 | 140 | 0.03187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2543-10_0_7_line_107 |  | 96 | 135 | 0.023083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2543-10_0_7_line_108 |  | 97 | 99 | 0.027138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2543-10_0_7_line_109 |  | 97 | 125 | 0.051488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_2543-10_0_7_line_110 |  | 98 | 99 | 0.080897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2543-10_0_7_line_111 |  | 100 | 101 | 0.021026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2543-10_0_7_line_112 |  | 101 | 125 | 0.025718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2543-10_0_7_line_113 |  | 103 | 126 | 0.021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2543-10_0_7_line_114 |  | 103 | 125 | 0.023346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_2543-10_0_7_line_115 |  | 105 | 106 | 0.022312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2543-10_0_7_line_116 |  | 105 | 107 | 0.0039146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2543-10_0_7_line_117 |  | 108 | 109 | 0.052139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2543-10_0_7_line_118 |  | 108 | 110 | 0.0003449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2543-10_0_7_line_119 |  | 109 | 111 | 0.036987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2543-10_0_7_line_120 |  | 110 | 112 | 0.036478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2543-10_0_7_line_121 |  | 111 | 113 | 0.026086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2543-10_0_7_line_122 |  | 112 | 114 | 0.048036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2543-10_0_7_line_123 |  | 113 | 115 | 0.0153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2543-10_0_7_line_124 |  | 114 | 116 | 0.052349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2543-10_0_7_line_125 |  | 116 | 138 | 0.0043102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2543-10_0_7_line_126 |  | 117 | 118 | 0.025877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2543-10_0_7_line_127 |  | 119 | 120 | 0.043524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2543-10_0_7_line_128 |  | 120 | 121 | 0.0073101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2543-10_0_7_line_129 |  | 121 | 122 | 0.041348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2543-10_0_7_line_130 |  | 122 | 125 | 0.031154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2543-10_0_7_line_131 |  | 123 | 124 | 0.018637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_2543-10_0_7_line_132 |  | 126 | 142 | 0.028005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2543-10_0_7_line_133 |  | 128 | 129 | 0.011593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2543-10_0_7_line_134 |  | 128 | 130 | 0.0086908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2543-10_0_7_line_135 |  | 129 | 131 | 0.0055376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2543-10_0_7_line_136 |  | 132 | 133 | 0.030174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2543-10_0_7_line_137 |  | 133 | 134 | 0.0063324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2543-10_0_7_line_138 |  | 133 | 135 | 0.013999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2543-10_0_7_line_139 |  | 134 | 136 | 0.021659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2543-10_0_7_line_140 |  | 136 | 137 | 0.011038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2543-10_0_7_line_141 |  | 138 | 139 | 0.027501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2543-10_0_7_trafo_42 | 0.63 MVA 20/0.4 kV | 143 | 66 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2598955.4067 | 1227609.4806 | 2598956.7574 | 1227605.7539
1 | 2598934.6923 | 1227585.7748 | 2598958.396 | 1227593.7083 | 2598959.5478 | 1227594.2751 | 2598960.1239 | 1227595.4312 | 2598959.8742 | 1227597.1545 | 2598956.7574 | 1227605.7539
2 | 2598935.9343 | 1227582.1946 | 2598934.6923 | 1227585.7748
3 | 2598934.6923 | 1227585.7748 | 2598930.8981 | 1227596.7042 | 2598928.9225 | 1227600.5709
4 | 2598937.1839 | 1227578.5923 | 2598935.9343 | 1227582.1946
5 | 2598928.9225 | 1227600.5709 | 2598928.3419 | 1227601.7073
6 | 2598937.1839 | 1227578.5923 | 2598937.6004 | 1227577.4026 | 2598938.9711 | 1227573.0109
7 | 2599245.7685 | 1227625.9533 | 2599238.6531 | 1227641.2524
8 | 2599252.1214 | 1227612.2937 | 2599245.7685 | 1227625.9533
9 | 2599189.3987 | 1227733.7298 | 2599214.5644 | 1227693.0466 | 2599238.6531 | 1227641.2524
10 | 2599252.1214 | 1227612.2937 | 2599276.9543 | 1227625.6982
11 | 2599096.2906 | 1227692.2866 | 2599105.4974 | 1227694.6976 | 2599115.2043 | 1227697.1975 | 2599126.798 | 1227700.4976 | 2599138.9981 | 1227704.6982 | 2599147.4017 | 1227707.8987 | 2599158.2001 | 1227713.1001 | 2599168.4985 | 1227718.8019 | 2599186.2008 | 1227731.3066 | 2599189.3987 | 1227733.7298
12 | 2599276.9543 | 1227625.6982 | 2599271.5518 | 1227637.3522
13 | 2599276.9543 | 1227625.6982 | 2599298.9984 | 1227638.3027 | 2599299.8348 | 1227638.7352
14 | 2599096.2906 | 1227692.2866 | 2599118.2814 | 1227645.8158
15 | 2599269.3281 | 1227642.1492 | 2599271.5518 | 1227637.3522
16 | 2599315.5485 | 1227646.8612 | 2599299.8348 | 1227638.7352
17 | 2599151.1999 | 1227573.997 | 2599147.2007 | 1227584.7039 | 2599141.782 | 1227596.1546
18 | 2599151.1999 | 1227573.997 | 2599139.5831 | 1227570.2633
19 | 2599126.8603 | 1227627.687 | 2599141.782 | 1227596.1546
20 | 2599139.5831 | 1227570.2633 | 2599100.7392 | 1227557.8288
21 | 2599139.5831 | 1227570.2633 | 2599151.0424 | 1227535.3743
22 | 2599126.8603 | 1227627.687 | 2599118.2814 | 1227645.8158
23 | 2599269.3281 | 1227642.1492 | 2599268.8665 | 1227643.1451
24 | 2599319.0949 | 1227648.6284 | 2599315.5485 | 1227646.8612
25 | 2599100.7392 | 1227557.8288 | 2599103.9879 | 1227545.5433
26 | 2599100.7392 | 1227557.8288 | 2599074.8854 | 1227550.2724
27 | 2599163.4926 | 1227538.4186 | 2599151.0424 | 1227535.3743
28 | 2599168.128 | 1227525.0211 | 2599163.4926 | 1227538.4186
29 | 2598985.2787 | 1227593.8689 | 2599004.7998 | 1227600.3413
30 | 2599046.0094 | 1227614.0045 | 2599004.7998 | 1227600.3413
31 | 2599046.0094 | 1227614.0045 | 2599043.6043 | 1227631.416
32 | 2599046.0094 | 1227614.0045 | 2599050.1923 | 1227583.7271
33 | 2599040.7865 | 1227645.3572 | 2599043.179 | 1227634.4948 | 2599043.6043 | 1227631.416
34 | 2599050.7848 | 1227579.4388 | 2599050.1923 | 1227583.7271
35 | 2598938.9711 | 1227573.0109 | 2598944.9991 | 1227553.6984 | 2598946.1336 | 1227550.2864
36 | 2599040.7865 | 1227645.3572 | 2599066.6645 | 1227653.8133
37 | 2599050.7848 | 1227579.4388 | 2599087.4235 | 1227590.6948
38 | 2599054.4023 | 1227553.3006 | 2599050.7848 | 1227579.4388
39 | 2598947.5919 | 1227545.9006 | 2598946.1336 | 1227550.2864
40 | 2599043.246 | 1227110.5072 | 2599045.6872 | 1227111.2459
41 | 2599072.553 | 1227119.3754 | 2599045.6872 | 1227111.2459
42 | 2599109.1796 | 1227085.3382 | 2599104.1938 | 1227088.6854 | 2599072.553 | 1227119.3754
43 | 2599012.4025 | 1227182.7009 | 2599014.7968 | 1227180.5992 | 2599028.3205 | 1227164.176 | 2599036.3515 | 1227155.0359 | 2599072.553 | 1227119.3754
44 | 2598862.0326 | 1227139.7932 | 2598863.6061 | 1227126.574 | 2598849.7823 | 1227119.4282 | 2598864.723 | 1227066.5941 | 2598872.3032 | 1227068.894
45 | 2599012.4025 | 1227182.7009 | 2599006.3403 | 1227183.2133 | 2599001.9147 | 1227182.5916 | 2598862.0326 | 1227139.7932
46 | 2599109.1796 | 1227085.3382 | 2599111.7787 | 1227084.3261 | 2599115.8025 | 1227083.0358 | 2599126.6244 | 1227086.1248 | 2599135.5972 | 1227088.5025 | 2599134.3425 | 1227109.4039
47 | 2599134.3425 | 1227109.4039 | 2599133.6009 | 1227122.4602
48 | 2599134.3425 | 1227109.4039 | 2599144.0274 | 1227110.6253 | 2599182.7528 | 1227122.0039 | 2599189.7249 | 1227124.0485
49 | 2599134.3425 | 1227109.4039 | 2599135.5972 | 1227088.5025 | 2599139.1872 | 1227075.7945 | 2599140.649 | 1227071.1693 | 2599141.3375 | 1227063.6314 | 2599141.2078 | 1227058.0837
50 | 2598954.8975 | 1227525.302 | 2598981.6018 | 1227532.2011 | 2599004.442 | 1227538.8217
51 | 2599054.4023 | 1227553.3006 | 2599044.1571 | 1227550.3339 | 2599004.442 | 1227538.8217
52 | 2598954.8975 | 1227525.302 | 2598958.4041 | 1227515.7957 | 2598960.3747 | 1227509.1103
53 | 2598954.8975 | 1227525.302 | 2598939.0294 | 1227521.0803 | 2598918.3948 | 1227515.581
54 | 2598954.8975 | 1227525.302 | 2598950.7774 | 1227536.3204 | 2598947.5919 | 1227545.9006
55 | 2599054.4023 | 1227553.3006 | 2599055.4995 | 1227544.6064
56 | 2598966.3024 | 1227489.0007 | 2598960.3747 | 1227509.1103
57 | 2598918.3948 | 1227515.581 | 2598934.4503 | 1227472.5342
58 | 2599055.4995 | 1227544.6064 | 2599074.8854 | 1227550.2724
59 | 2598966.3024 | 1227489.0007 | 2598967.9129 | 1227483.9255
60 | 2598957.6741 | 1227421.6849 | 2598953.9612 | 1227422.2192 | 2598951.9381 | 1227422.9422 | 2598950.6199 | 1227424.3989 | 2598949.2034 | 1227427.0785 | 2598943.6443 | 1227442.233 | 2598935.3143 | 1227470.2177 | 2598934.4503 | 1227472.5342
61 | 2598967.9129 | 1227483.9255 | 2598972.587 | 1227469.1954
62 | 2599077.6299 | 1227524.3907 | 2599089.4689 | 1227527.4724
63 | 2599058.7986 | 1227517.0007 | 2599058.4656 | 1227519.4133 | 2599077.6299 | 1227524.3907
64 | 2599102.8584 | 1227530.9576 | 2599089.4689 | 1227527.4724
65 | 2599058.7986 | 1227517.0007 | 2599043.9843 | 1227512.8086
66 | 2599058.7986 | 1227517.0007 | 2599064.0684 | 1227477.8491
67 | 2599043.9843 | 1227512.8086 | 2599015.443 | 1227504.732
68 | 2599064.2248 | 1227476.6871 | 2599064.0684 | 1227477.8491
69 | 2599044.3299 | 1227471.4293 | 2599040.5192 | 1227470.4223
70 | 2599022.7651 | 1227425.4879 | 2599015.1719 | 1227457.1953 | 2599014.7104 | 1227461.3645 | 2599016.7189 | 1227464.1324 | 2599040.5192 | 1227470.4223
71 | 2599064.2248 | 1227476.6871 | 2599044.3299 | 1227471.4293
72 | 2599064.2248 | 1227476.6871 | 2599066.9498 | 1227459.3765 | 2599069.4023 | 1227443.8002 | 2599071.2949 | 1227432.8935 | 2599079.9997 | 1227421.6298 | 2599082.5455 | 1227419.9951 | 2599084.5911 | 1227417.7712 | 2599086.3257 | 1227414.0465 | 2599086.6585 | 1227409.9441 | 2599085.5515 | 1227405.9863
73 | 2599085.5515 | 1227405.9863 | 2599092.4848 | 1227404.8734
74 | 2599085.5515 | 1227405.9863 | 2599112.7496 | 1227418.0001 | 2599155.3981 | 1227428.6885
75 | 2599083.8095 | 1227365.8852 | 2599083.3627 | 1227367.653 | 2599077.4788 | 1227391.1901 | 2599075.7904 | 1227399.4174 | 2599079.2535 | 1227400.184 | 2599082.3227 | 1227401.9512 | 2599084.1644 | 1227403.7853 | 2599085.5515 | 1227405.9863
76 | 2599083.8095 | 1227365.8852 | 2599060.3101 | 1227359.8634 | 2599058.5831 | 1227359.7948
77 | 2599083.8095 | 1227365.8852 | 2599086.0586 | 1227356.9018 | 2599087.65 | 1227351.4188
78 | 2599041.0257 | 1227358.0099 | 2599046.3897 | 1227359.3099 | 2599058.5831 | 1227359.7948
79 | 2599091.6023 | 1227337.8008 | 2599087.65 | 1227351.4188
80 | 2599155.3981 | 1227428.6885 | 2599161.9764 | 1227434.6799 | 2599168.2132 | 1227437.3361 | 2599175.9412 | 1227439.3255
81 | 2599155.3981 | 1227428.6885 | 2599271.0288 | 1227457.6667 | 2599271.9079 | 1227457.8889 | 2599274.3017 | 1227453.0524
82 | 2599274.3017 | 1227453.0524 | 2599271.9079 | 1227457.8889 | 2599285.0933 | 1227461.1891 | 2599299.9155 | 1227464.9338 | 2599331.9545 | 1227473.0345 | 2599330.2957 | 1227479.0604
83 | 2599317.3668 | 1227526.0231 | 2599322.3732 | 1227507.8339 | 2599324.0244 | 1227501.8413 | 2599330.2957 | 1227479.0604
84 | 2599285.453 | 1227545.6165 | 2599310.1185 | 1227552.3617 | 2599315.0492 | 1227534.4506 | 2599317.3668 | 1227526.0231
85 | 2599319.0949 | 1227648.6284 | 2599313.5666 | 1227663.3171
86 | 2599011.075 | 1227386.8768 | 2599012.3541 | 1227378.2493 | 2599002.9498 | 1227375.9051 | 2599003.5443 | 1227363.7735
87 | 2599011.075 | 1227386.8768 | 2598999.5336 | 1227383.6992 | 2598987.386 | 1227380.4217 | 2598968.8046 | 1227375.022 | 2598934.0438 | 1227366.5239
88 | 2599037.5491 | 1227357.1673 | 2599004.2634 | 1227349.1002 | 2599003.5443 | 1227363.7735
89 | 2598918.547 | 1227362.7354 | 2598934.0438 | 1227366.5239
90 | 2598918.547 | 1227362.7354 | 2598925.9835 | 1227337.7081 | 2598930.1934 | 1227331.5731
91 | 2598918.547 | 1227362.7354 | 2598904.5901 | 1227359.1659
92 | 2599189.7249 | 1227124.0485 | 2599203.1764 | 1227128.0266 | 2599211.8005 | 1227130.4824 | 2599271.9041 | 1227148.8959 | 2599268.6927 | 1227161.3481 | 2599205.8006 | 1227143.3464 | 2599204.1486 | 1227142.8908 | 2599198.5028 | 1227141.324
93 | 2599198.5028 | 1227141.324 | 2599196.2989 | 1227150.6743
94 | 2599189.7249 | 1227124.0485 | 2599193.2195 | 1227108.1299
95 | 2599196.2989 | 1227150.6743 | 2599169.8206 | 1227144.3523 | 2599169.8698 | 1227144.1453
96 | 2599200.8842 | 1227154.7871 | 2599197.3527 | 1227153.7871 | 2599196.2989 | 1227150.6743
97 | 2599261.5033 | 1227659.0289 | 2599268.8665 | 1227643.1451
98 | 2599200.8842 | 1227154.7871 | 2599198.9983 | 1227161.6359 | 2599193.6784 | 1227160.2803 | 2599191.5561 | 1227168.8422
99 | 2599191.5561 | 1227168.8422 | 2599189.619 | 1227176.6572 | 2599190.506 | 1227178.9362 | 2599187.7417 | 1227190.121
100 | 2599041.0257 | 1227358.0099 | 2599037.5491 | 1227357.1673
101 | 2599129.3242 | 1227194.1879 | 2599130.5414 | 1227176.3216 | 2599133.6009 | 1227122.4602
102 | 2599117.0039 | 1227250.0005 | 2599120.4573 | 1227236.781 | 2599124.0016 | 1227223.2058 | 2599129.3242 | 1227194.1879
103 | 2599129.3242 | 1227194.1879 | 2599083.135 | 1227182.3458
104 | 2599117.0039 | 1227250.0005 | 2599113.5027 | 1227248.5002 | 2599100.9801 | 1227244.7898
105 | 2599117.0039 | 1227250.0005 | 2599112.3537 | 1227265.8995
106 | 2599083.135 | 1227182.3458 | 2599052.2636 | 1227174.4309
107 | 2599078.8484 | 1227238.2322 | 2599100.9801 | 1227244.7898
108 | 2599112.3537 | 1227265.8995 | 2599120.4169 | 1227268.2996 | 2599122.6677 | 1227269.5222 | 2599138.4378 | 1227273.067
109 | 2599097.7821 | 1227315.2865 | 2599112.3537 | 1227265.8995
110 | 2599208.3224 | 1227270.0187 | 2599207.396 | 1227274.5678 | 2599198.0922 | 1227286.4761 | 2599138.4378 | 1227273.067
111 | 2599123.021 | 1227315.968 | 2599125.7745 | 1227316.3715 | 2599143.942 | 1227318.0289
112 | 2599097.7821 | 1227315.2865 | 2599104.7078 | 1227313.2842 | 2599123.021 | 1227315.968
113 | 2599091.6023 | 1227337.8008 | 2599102.7041 | 1227340.0002 | 2599112.3335 | 1227341.8897
114 | 2599097.7821 | 1227315.2865 | 2599091.6023 | 1227337.8008
115 | 2599066.6645 | 1227653.8133 | 2599073.7712 | 1227632.6635
116 | 2599075.0181 | 1227628.9528 | 2599073.7712 | 1227632.6635
117 | 2599146.6951 | 1226969.1639 | 2599145.5758 | 1226980.8599 | 2599144.2078 | 1227004.2294 | 2599143.6715 | 1227021.2013
118 | 2599146.7279 | 1226968.8206 | 2599146.6951 | 1226969.1639
119 | 2599141.2078 | 1227058.0837 | 2599143.0993 | 1227039.3057 | 2599143.6715 | 1227021.2013
120 | 2599146.7279 | 1226968.8206 | 2599148.0877 | 1226954.6107 | 2599150.6372 | 1226932.5543
121 | 2599141.2078 | 1227058.0837 | 2599158.1224 | 1227060.2046 | 2599166.6152 | 1227063.2973
122 | 2599162.9609 | 1226886.5462 | 2599157.476 | 1226898.0983 | 2599154.9005 | 1226905.3029 | 2599151.8415 | 1226922.1355 | 2599150.6372 | 1226932.5543
123 | 2599180.6167 | 1227069.4357 | 2599170.6345 | 1227064.7609 | 2599166.6152 | 1227063.2973
124 | 2599162.9609 | 1226886.5462 | 2599182.4158 | 1226895.6153 | 2599210.3306 | 1226908.8279
125 | 2599214.2264 | 1226910.6719 | 2599210.3306 | 1226908.8279
126 | 2598980.4135 | 1227444.5307 | 2598972.587 | 1227469.1954
127 | 2599020.5763 | 1227295.3546 | 2599014.9084 | 1227296.5452 | 2599011.5138 | 1227298.1578 | 2599008.074 | 1227301.1046 | 2599004.8998 | 1227306.0526 | 2599001.7262 | 1227313.9689 | 2598998.8867 | 1227326.2767 | 2598998.5864 | 1227328.6638
128 | 2599020.5763 | 1227295.3546 | 2599025.9339 | 1227295.8873 | 2599027.7905 | 1227296.4001
129 | 2599027.7905 | 1227296.4001 | 2599067.6459 | 1227307.4085
130 | 2599097.7821 | 1227315.2865 | 2599087.1576 | 1227312.7979 | 2599067.6459 | 1227307.4085
131 | 2599103.9879 | 1227545.5433 | 2599107.5092 | 1227532.1682 | 2599102.8584 | 1227530.9576
132 | 2599139.8436 | 1227347.1188 | 2599134.8043 | 1227346.2988 | 2599112.3335 | 1227341.8897
133 | 2598998.96 | 1227500.0677 | 2599010.1146 | 1227503.2242
134 | 2598990.5976 | 1227497.7013 | 2598998.96 | 1227500.0677
135 | 2599015.443 | 1227504.732 | 2599010.1146 | 1227503.2242
136 | 2599065.4265 | 1227234.2553 | 2599061.7533 | 1227246.5409 | 2599078.3753 | 1227251.518
137 | 2599065.4265 | 1227234.2553 | 2599059.377 | 1227232.3836
138 | 2599065.4265 | 1227234.2553 | 2599078.8484 | 1227238.2322
139 | 2599038.6092 | 1227226.2377 | 2599050.7019 | 1227229.6996 | 2599059.377 | 1227232.3836
140 | 2599027.9974 | 1227223.1997 | 2599038.6092 | 1227226.2377
141 | 2599214.2264 | 1226910.6719 | 2599239.0832 | 1226922.437

## bus_geodata
| x | y | coords
0 | 2598955.4067 | 1227609.4806
1 | 2598956.7574 | 1227605.7539
2 | 2598934.6923 | 1227585.7748
3 | 2598935.9343 | 1227582.1947
4 | 2598928.9225 | 1227600.5709
5 | 2598937.1839 | 1227578.5923
6 | 2598928.3419 | 1227601.7073
7 | 2599245.7685 | 1227625.9533
8 | 2599238.6531 | 1227641.2524
9 | 2599252.1214 | 1227612.2937
10 | 2599189.3987 | 1227733.7298
11 | 2599276.9543 | 1227625.6982
12 | 2599096.2906 | 1227692.2866
13 | 2599271.5518 | 1227637.3522
14 | 2599299.8348 | 1227638.7352
15 | 2599151.1999 | 1227573.997
16 | 2599141.782 | 1227596.1546
17 | 2599139.5831 | 1227570.2633
18 | 2599118.2814 | 1227645.8158
19 | 2599269.3281 | 1227642.1492
20 | 2599315.5485 | 1227646.8612
21 | 2599126.8603 | 1227627.687
22 | 2599100.7392 | 1227557.8288
23 | 2599151.0424 | 1227535.3743
24 | 2599163.4926 | 1227538.4186
25 | 2599168.128 | 1227525.0211
26 | 2598985.2787 | 1227593.8689
27 | 2599004.7998 | 1227600.3413
28 | 2599046.0094 | 1227614.0045
29 | 2599043.6043 | 1227631.416
30 | 2599050.1923 | 1227583.7271
31 | 2598938.9711 | 1227573.0109
32 | 2599040.7864 | 1227645.3572
33 | 2599050.7848 | 1227579.4388
34 | 2598946.1336 | 1227550.2864
35 | 2599043.246 | 1227110.5072
36 | 2599045.6872 | 1227111.2459
37 | 2599072.553 | 1227119.3754
38 | 2598872.3032 | 1227068.894
39 | 2598862.0326 | 1227139.7932
40 | 2599109.1796 | 1227085.3382
41 | 2599012.4025 | 1227182.7009
42 | 2599134.3425 | 1227109.4039
43 | 2599004.442 | 1227538.8217
44 | 2598954.8975 | 1227525.302
45 | 2599054.4023 | 1227553.3006
46 | 2598960.3747 | 1227509.1103
47 | 2598918.3948 | 1227515.581
48 | 2598947.5919 | 1227545.9006
49 | 2599055.4995 | 1227544.6064
50 | 2598966.3024 | 1227489.0007
51 | 2598934.4503 | 1227472.5342
52 | 2599074.8854 | 1227550.2724
53 | 2599087.4235 | 1227590.6948
54 | 2598967.9129 | 1227483.9255
55 | 2598957.6741 | 1227421.6849
56 | 2599077.6299 | 1227524.3907
57 | 2599089.4689 | 1227527.4724
58 | 2599058.7986 | 1227517.0007
59 | 2599043.9843 | 1227512.8086
60 | 2599064.0684 | 1227477.8491
61 | 2599040.5192 | 1227470.4223
62 | 2599044.3299 | 1227471.4293
63 | 2599022.7651 | 1227425.4879
64 | 2599064.2248 | 1227476.6871
65 | 2599085.5515 | 1227405.9863
66 | 2599083.8095 | 1227365.8852
67 | 2599058.5831 | 1227359.7948
68 | 2599087.65 | 1227351.4188
69 | 2599092.4848 | 1227404.8734
70 | 2599155.3981 | 1227428.6885
71 | 2599274.3017 | 1227453.0524
72 | 2599330.2957 | 1227479.0604
73 | 2599317.3668 | 1227526.0231
74 | 2599175.9412 | 1227439.3255
75 | 2599285.453 | 1227545.6165
76 | 2599319.0949 | 1227648.6284
77 | 2599011.075 | 1227386.8768
78 | 2599003.5443 | 1227363.7735
79 | 2598934.0438 | 1227366.5239
80 | 2598918.547 | 1227362.7354
81 | 2598930.1934 | 1227331.5731
82 | 2598904.5901 | 1227359.1659
83 | 2599313.5666 | 1227663.3171
84 | 2599198.5028 | 1227141.324
85 | 2599189.7249 | 1227124.0485
86 | 2599196.2989 | 1227150.6743
87 | 2599268.8665 | 1227643.1451
88 | 2599193.2195 | 1227108.1299
89 | 2599200.8842 | 1227154.7871
90 | 2599191.5561 | 1227168.8422
91 | 2599037.5491 | 1227357.1673
92 | 2599129.3242 | 1227194.1879
93 | 2599133.6009 | 1227122.4602
94 | 2599117.0039 | 1227250.0005
95 | 2599083.135 | 1227182.3458
96 | 2599100.9801 | 1227244.7898
97 | 2599112.3537 | 1227265.8995
98 | 2599208.3224 | 1227270.0187
99 | 2599138.4378 | 1227273.067
100 | 2599143.942 | 1227318.0289
101 | 2599123.021 | 1227315.968
102 | 2599041.0257 | 1227358.0099
103 | 2599091.6023 | 1227337.8008
104 | 2599169.8698 | 1227144.1453
105 | 2599073.7712 | 1227632.6635
106 | 2599066.6645 | 1227653.8133
107 | 2599075.0181 | 1227628.9528
108 | 2599146.6951 | 1226969.1639
109 | 2599143.6715 | 1227021.2013
110 | 2599146.7279 | 1226968.8206
111 | 2599141.2078 | 1227058.0838
112 | 2599150.6372 | 1226932.5543
113 | 2599166.6152 | 1227063.2973
114 | 2599162.9609 | 1226886.5462
115 | 2599180.6167 | 1227069.4357
116 | 2599210.3306 | 1226908.8279
117 | 2598980.4135 | 1227444.5307
118 | 2598972.587 | 1227469.1954
119 | 2598998.5864 | 1227328.6638
120 | 2599020.5763 | 1227295.3546
121 | 2599027.7905 | 1227296.4001
122 | 2599067.6459 | 1227307.4085
123 | 2599103.9879 | 1227545.5433
124 | 2599102.8584 | 1227530.9576
125 | 2599097.7821 | 1227315.2865
126 | 2599112.3335 | 1227341.8897
127 | 2599261.5033 | 1227659.0289
128 | 2598998.96 | 1227500.0677
129 | 2599010.1146 | 1227503.2242
130 | 2598990.5976 | 1227497.7013
131 | 2599015.443 | 1227504.732
132 | 2599078.3753 | 1227251.518
133 | 2599065.4264 | 1227234.2553
134 | 2599059.377 | 1227232.3836
135 | 2599078.8484 | 1227238.2322
136 | 2599038.6092 | 1227226.2377
137 | 2599027.9974 | 1227223.1997
138 | 2599214.2264 | 1226910.6719
139 | 2599239.0832 | 1226922.437
140 | 2599052.2636 | 1227174.4309
141 | 2599187.7417 | 1227190.121
142 | 2599139.8436 | 1227347.1188
143 | 2599083.3627 | 1227367.653

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9702 | -0.57474 | 0.0066452 | 0.0016654
1 | 0.97023 | -0.57425 | 0.01135 | 0.0028446
2 | 0.97087 | -0.56145 | 0 | 0
3 | 0.97095 | -0.55985 | 0 | 0
4 | 0.9708 | -0.56286 | 0.0024011 | 0.00060177
5 | 0.97104 | -0.55824 | 0 | 0
6 | 0.9708 | -0.56292 | 0.0024064 | 0.00060309
7 | 0.97187 | -0.54195 | 0.0021 | 0.00052631
8 | 0.9722 | -0.53549 | 0.0029521 | 0.00073987
9 | 0.97161 | -0.54714 | 0 | 0
10 | 0.97452 | -0.48971 | 0 | 0
11 | 0.97112 | -0.55685 | 0 | 0
12 | 0.9768 | -0.44501 | 0 | 0
13 | 0.97099 | -0.55944 | 0.002106 | 0.00052781
14 | 0.97093 | -0.56062 | 0.0013324 | 0.00033393
15 | 0.98024 | -0.37788 | 0 | 0
16 | 0.97936 | -0.39493 | 0.01004 | 0.0025164
17 | 0.98068 | -0.36928 | 0 | 0
18 | 0.97794 | -0.42276 | 0.002179 | 0.0005461
19 | 0.97094 | -0.56029 | 0.005503 | 0.0013792
20 | 0.97082 | -0.56272 | 0 | 0
21 | 0.97842 | -0.4133 | 0.0030423 | 0.00076247
22 | 0.98275 | -0.329 | 0 | 0
23 | 0.98014 | -0.37978 | 0.0041076 | 0.0010294
24 | 0.98 | -0.38249 | 0 | 0
25 | 0.97985 | -0.38549 | 0.011658 | 0.0029218
26 | 0.97298 | -0.51994 | 0.010419 | 0.0026113
27 | 0.97318 | -0.51599 | 0.011353 | 0.0028453
28 | 0.97406 | -0.49861 | 0 | 0
29 | 0.97351 | -0.5095 | 0.0090162 | 0.0022597
30 | 0.97564 | -0.46752 | 0.0089816 | 0.002251
31 | 0.97116 | -0.55577 | 0.0047782 | 0.0011975
32 | 0.97318 | -0.51596 | 0 | 0
33 | 0.9759 | -0.46241 | 0 | 0
34 | 0.97177 | -0.54364 | 0.0067929 | 0.0017025
35 | 0.97097 | -0.5602 | 0.01173 | 0.0029397
36 | 0.97099 | -0.55964 | 0.044886 | 0.011249
37 | 0.97248 | -0.53031 | 0.007112 | 0.0017824
38 | 0.97074 | -0.56462 | 0.0055346 | 0.0013871
39 | 0.97122 | -0.55524 | 0 | 0
40 | 0.97571 | -0.46667 | 0 | 0
41 | 0.97203 | -0.53924 | 0 | 0
42 | 0.97885 | -0.40537 | 0 | 0
43 | 0.97505 | -0.47912 | 0.0050058 | 0.0012546
44 | 0.97269 | -0.52558 | 0 | 0
45 | 0.97768 | -0.42756 | 0 | 0
46 | 0.97254 | -0.52858 | 0.0034062 | 0.00085366
47 | 0.97261 | -0.52706 | 0 | 0
48 | 0.97192 | -0.5407 | 0.0031599 | 0.00079195
49 | 0.97872 | -0.40736 | 0 | 0
50 | 0.97242 | -0.53095 | 0 | 0
51 | 0.97252 | -0.52887 | 0.00092572 | 0.00023201
52 | 0.9811 | -0.36097 | 0.0048109 | 0.0012057
53 | 0.97562 | -0.4679 | 0.0078477 | 0.0019668
54 | 0.97239 | -0.53155 | 0.0009257 | 0.000232
55 | 0.97246 | -0.53018 | 0.0012084 | 0.00030285
56 | 0.98611 | -0.26407 | 0 | 0
57 | 0.98536 | -0.27853 | 0.01134 | 0.002842
58 | 0.98748 | -0.23784 | 0 | 0
59 | 0.98718 | -0.24364 | 0.005858 | 0.0014681
60 | 0.99016 | -0.18649 | 0.0010538 | 0.00026411
61 | 0.98989 | -0.19167 | 0.0079307 | 0.0019876
62 | 0.98994 | -0.19066 | 0.0011935 | 0.00029912
63 | 0.98951 | -0.19913 | 0.0064593 | 0.0016189
64 | 0.99024 | -0.18496 | 0 | 0
65 | 0.99585 | -0.078193 | 0 | 0
66 | 1 | 0 | -0.61918 | -0.15863
67 | 0.99871 | -0.024775 | 0.013018 | 0.0032627
68 | 0.99877 | -0.023199 | 0.0047008 | 0.0011781
69 | 0.99582 | -0.07878 | 0.0047574 | 0.0011923
70 | 0.99271 | -0.13844 | 0 | 0
71 | 0.98869 | -0.21581 | 0 | 0
72 | 0.98633 | -0.26146 | 0 | 0
73 | 0.98477 | -0.2918 | 0 | 0
74 | 0.99246 | -0.14331 | 0.011645 | 0.0029186
75 | 0.98308 | -0.3248 | 0.034707 | 0.0086984
76 | 0.9708 | -0.56319 | 0 | 0
77 | 0.99669 | -0.063686 | 0 | 0
78 | 0.99695 | -0.058723 | 0.012787 | 0.0032048
79 | 0.99602 | -0.076635 | 0.004823 | 0.0012087
80 | 0.99595 | -0.077877 | 0 | 0
81 | 0.99589 | -0.079041 | 0.0019734 | 0.00049457
82 | 0.99592 | -0.078499 | 0.0024558 | 0.00061548
83 | 0.9707 | -0.56505 | 0.0064187 | 0.0016087
84 | 0.97476 | -0.48574 | 0 | 0
85 | 0.97757 | -0.43051 | 0 | 0
86 | 0.9746 | -0.48884 | 0 | 0
87 | 0.97094 | -0.56036 | 0.0016384 | 0.00041061
88 | 0.97747 | -0.43243 | 0.0064606 | 0.0016192
89 | 0.97455 | -0.48973 | 0 | 0
90 | 0.97441 | -0.49251 | 0.0018635 | 0.00046703
91 | 0.99793 | -0.039821 | 0.01232 | 0.0030878
92 | 0.98792 | -0.22987 | 0 | 0
93 | 0.98017 | -0.37968 | 0.0076848 | 0.001926
94 | 0.99135 | -0.16448 | 0 | 0
95 | 0.98737 | -0.24067 | 0.0064406 | 0.0016142
96 | 0.99028 | -0.18513 | 0.0018838 | 0.00047214
97 | 0.99236 | -0.14516 | 0 | 0
98 | 0.99126 | -0.16635 | 0.0081048 | 0.0020313
99 | 0.99186 | -0.15472 | 0.011784 | 0.0029534
100 | 0.99547 | -0.086012 | 0.0048764 | 0.0012221
101 | 0.99556 | -0.084209 | 0.0058262 | 0.0014602
102 | 0.99804 | -0.03767 | 0.0072415 | 0.0018149
103 | 0.99763 | -0.044837 | 0 | 0
104 | 0.97433 | -0.49414 | 0.010528 | 0.0026387
105 | 0.97205 | -0.53845 | 0.0020687 | 0.00051846
106 | 0.97256 | -0.5283 | 0 | 0
107 | 0.97196 | -0.54008 | 0.022606 | 0.0056656
108 | 0.97738 | -0.43427 | 0.00046627 | 0.00011686
109 | 0.97781 | -0.42577 | 0.00048307 | 0.00012107
110 | 0.97738 | -0.43432 | 0.0015618 | 0.00039143
111 | 0.97813 | -0.41942 | 0 | 0
112 | 0.97714 | -0.43892 | 0.0026659 | 0.00066813
113 | 0.978 | -0.42199 | 0.0031285 | 0.00078408
114 | 0.97695 | -0.44264 | 0 | 0
115 | 0.97797 | -0.42262 | 0.0022615 | 0.00056679
116 | 0.97675 | -0.44669 | 0.0028906 | 0.00072445
117 | 0.97228 | -0.5336 | 0.0011939 | 0.00029923
118 | 0.97231 | -0.53303 | 0.0040091 | 0.0010048
119 | 0.99432 | -0.10824 | 0.0071805 | 0.0017996
120 | 0.9946 | -0.10274 | 0 | 0
121 | 0.99465 | -0.10181 | 0.0049227 | 0.0012337
122 | 0.99511 | -0.092997 | 0.012763 | 0.0031988
123 | 0.98348 | -0.31478 | 0 | 0
124 | 0.98456 | -0.29398 | 0.00027292 | 6.8401e-05
125 | 0.99581 | -0.079369 | 0 | 0
126 | 0.99746 | -0.048089 | 0.0056046 | 0.0014046
127 | 0.97091 | -0.5609 | 0.0016551 | 0.00041482
128 | 0.98663 | -0.25428 | 0.0012156 | 0.00030465
129 | 0.98672 | -0.25265 | 0.0015442 | 0.00038701
130 | 0.98658 | -0.25532 | 0.0066631 | 0.0016699
131 | 0.98676 | -0.25171 | 0.0057825 | 0.0014492
132 | 0.98721 | -0.24478 | 0.034055 | 0.0085351
133 | 0.98815 | -0.22642 | 0 | 0
134 | 0.98803 | -0.22879 | 0.0058027 | 0.0014543
135 | 0.98886 | -0.21268 | 0.012026 | 0.003014
136 | 0.98773 | -0.23466 | 0.0063914 | 0.0016018
137 | 0.98764 | -0.2364 | 0.0087852 | 0.0022018
138 | 0.97674 | -0.4468 | 0.00077282 | 0.00019369
139 | 0.97673 | -0.44709 | 0.00057266 | 0.00014352
140 | 0.98719 | -0.24421 | 0.0062246 | 0.00156
141 | 0.97431 | -0.4946 | 0.0051868 | 0.0012999
142 | 0.99738 | -0.049649 | 0.003179 | 0.00079674
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0066452 | -0.0016654 | 0.0066454 | 0.0016655 | 1.544e-07 | 4.9867e-08 | 0.010192 | 0.010192 | 0.010192 | 0.9702 | -0.57474 | 0.97023 | -0.57425 | 2.8
1 | -0.017995 | -0.0045101 | 0.018006 | 0.0045166 | 1.0986e-05 | 6.5555e-06 | 0.027599 | 0.027599 | 0.027599 | 0.97023 | -0.57425 | 0.97087 | -0.56145 | 7.5822
2 | -0.022814 | -0.0057215 | 0.022816 | 0.0057226 | 1.7373e-06 | 1.065e-06 | 0.034968 | 0.034968 | 0.034968 | 0.97087 | -0.56145 | 0.97095 | -0.55985 | 9.6065
3 | 0.0048078 | 0.0012049 | -0.0048075 | -0.0012049 | 3.2398e-07 | 1.0601e-08 | 0.0073687 | 0.0073688 | 0.0073688 | 0.97087 | -0.56145 | 0.9708 | -0.56286 | 2.0244
4 | -0.022816 | -0.0057226 | 0.022818 | 0.0057236 | 1.7479e-06 | 1.0715e-06 | 0.034968 | 0.034968 | 0.034968 | 0.97095 | -0.55985 | 0.97104 | -0.55824 | 9.6065
5 | 0.0024064 | 0.00060308 | -0.0024064 | -0.00060309 | 6.5103e-09 | -1.1612e-08 | 0.0036884 | 0.0036884 | 0.0036884 | 0.9708 | -0.56286 | 0.9708 | -0.56292 | 1.0133
6 | -0.022818 | -0.0057236 | 0.02282 | 0.0057253 | 2.6869e-06 | 1.6471e-06 | 0.034968 | 0.034967 | 0.034968 | 0.97104 | -0.55824 | 0.97116 | -0.55577 | 9.6065
7 | -0.020771 | -0.0052109 | 0.020778 | 0.0052148 | 6.4003e-06 | 3.887e-06 | 0.031805 | 0.031805 | 0.031805 | 0.97187 | -0.54195 | 0.9722 | -0.53549 | 8.7375
8 | 0.018671 | 0.0046846 | -0.018667 | -0.0046818 | 4.6174e-06 | 2.7685e-06 | 0.028589 | 0.028589 | 0.028589 | 0.97187 | -0.54195 | 0.97161 | -0.54714 | 7.8542
9 | -0.02373 | -0.0059547 | 0.023782 | 0.0059866 | 5.1929e-05 | 3.193e-05 | 0.036323 | 0.036322 | 0.036323 | 0.9722 | -0.53549 | 0.97452 | -0.48971 | 9.9788
10 | 0.018667 | 0.0046818 | -0.018658 | -0.0046767 | 8.6304e-06 | 5.1749e-06 | 0.028589 | 0.02859 | 0.02859 | 0.97161 | -0.54714 | 0.97112 | -0.55685 | 7.8543
11 | -0.023782 | -0.0059866 | 0.023833 | 0.0060179 | 5.0925e-05 | 3.1307e-05 | 0.036322 | 0.036322 | 0.036322 | 0.97452 | -0.48971 | 0.9768 | -0.44501 | 9.9787
12 | 0.010904 | 0.0027331 | -0.010903 | -0.0027324 | 1.3448e-06 | 7.0175e-07 | 0.016708 | 0.016708 | 0.016708 | 0.97112 | -0.55685 | 0.97099 | -0.55944 | 4.5902
13 | 0.0077538 | 0.0019436 | -0.0077524 | -0.001943 | 1.3941e-06 | 5.6644e-07 | 0.011881 | 0.011881 | 0.011881 | 0.97112 | -0.55685 | 0.97093 | -0.56062 | 3.2641
14 | -0.023833 | -0.0060179 | 0.023858 | 0.0060336 | 2.5435e-05 | 1.5634e-05 | 0.036322 | 0.036322 | 0.036322 | 0.9768 | -0.44501 | 0.97794 | -0.42276 | 9.9786
15 | 0.0087969 | 0.0022046 | -0.0087966 | -0.0022044 | 3.6034e-07 | 1.6522e-07 | 0.013481 | 0.013481 | 0.013481 | 0.97099 | -0.55944 | 0.97094 | -0.56029 | 3.7036
16 | 0.00642 | 0.0016091 | -0.0064194 | -0.0016089 | 6.4223e-07 | 1.9227e-07 | 0.0098392 | 0.0098393 | 0.0098393 | 0.97093 | -0.56062 | 0.97082 | -0.56272 | 2.7031
17 | 0.039189 | 0.0099019 | -0.039157 | -0.0098818 | 3.2012e-05 | 2.0184e-05 | 0.059519 | 0.059519 | 0.059519 | 0.98024 | -0.37788 | 0.97936 | -0.39493 | 16.3513
18 | -0.039189 | -0.0099019 | 0.039205 | 0.0099121 | 1.6167e-05 | 1.0193e-05 | 0.059519 | 0.059519 | 0.059519 | 0.98024 | -0.37788 | 0.98068 | -0.36928 | 16.3513
19 | 0.029117 | 0.0073654 | -0.029091 | -0.0073494 | 2.5631e-05 | 1.5965e-05 | 0.044264 | 0.044264 | 0.044264 | 0.97936 | -0.39493 | 0.97842 | -0.4133 | 12.1604
20 | -0.054982 | -0.01387 | 0.055088 | 0.013937 | 0.00010625 | 6.7485e-05 | 0.083458 | 0.083458 | 0.083458 | 0.98068 | -0.36928 | 0.98275 | -0.329 | 22.9281
21 | 0.015777 | 0.0039575 | -0.015769 | -0.0039529 | 7.8922e-06 | 4.5879e-06 | 0.02394 | 0.02394 | 0.02394 | 0.98068 | -0.36928 | 0.98014 | -0.37978 | 6.5768
22 | -0.026037 | -0.0065797 | 0.026049 | 0.006587 | 1.1816e-05 | 7.3108e-06 | 0.039637 | 0.039637 | 0.039637 | 0.97794 | -0.42276 | 0.97842 | -0.4133 | 10.8894
23 | 0.0032936 | 0.00082523 | -0.0032935 | -0.00082524 | 1.0488e-08 | -6.8648e-09 | 0.0050475 | 0.0050475 | 0.0050475 | 0.97094 | -0.56029 | 0.97094 | -0.56036 | 1.3867
24 | 0.0064194 | 0.0016089 | -0.0064192 | -0.0016088 | 1.4351e-07 | 4.297e-08 | 0.0098393 | 0.0098393 | 0.0098393 | 0.97082 | -0.56272 | 0.9708 | -0.56319 | 2.7031
25 | -0.18762 | -0.047616 | 0.18775 | 0.047698 | 0.00012838 | 8.1677e-05 | 0.28429 | 0.28429 | 0.28429 | 0.98275 | -0.329 | 0.98348 | -0.31478 | 26.0341
26 | 0.13253 | 0.033679 | -0.13233 | -0.03355 | 0.00020371 | 0.00012969 | 0.20083 | 0.20083 | 0.20083 | 0.98275 | -0.329 | 0.9811 | -0.36097 | 27.5872
27 | 0.011661 | 0.0029234 | -0.01166 | -0.0029226 | 1.5064e-06 | 8.0261e-07 | 0.017704 | 0.017704 | 0.017704 | 0.98014 | -0.37978 | 0.98 | -0.38249 | 4.8637
28 | 0.01166 | 0.0029226 | -0.011658 | -0.0029218 | 1.6659e-06 | 8.8764e-07 | 0.017704 | 0.017704 | 0.017704 | 0.98 | -0.38249 | 0.97985 | -0.38549 | 4.8637
29 | -0.010419 | -0.0026113 | 0.010421 | 0.0026123 | 1.9581e-06 | 9.9773e-07 | 0.015934 | 0.015934 | 0.015934 | 0.97298 | -0.51994 | 0.97318 | -0.51599 | 4.3775
30 | -0.021774 | -0.0054576 | 0.021792 | 0.0054686 | 1.8046e-05 | 1.1009e-05 | 0.033293 | 0.033293 | 0.033293 | 0.97318 | -0.51599 | 0.97406 | -0.49861 | 9.1464
31 | 0.033744 | 0.0084769 | -0.033727 | -0.0084659 | 1.752e-05 | 1.0994e-05 | 0.051556 | 0.051556 | 0.051556 | 0.97406 | -0.49861 | 0.97351 | -0.5095 | 14.1639
32 | -0.055536 | -0.013945 | 0.055619 | 0.013998 | 8.2518e-05 | 5.243e-05 | 0.084849 | 0.084849 | 0.084849 | 0.97406 | -0.49861 | 0.97564 | -0.46752 | 23.3102
33 | 0.024711 | 0.0062062 | -0.024703 | -0.0062015 | 7.615e-06 | 4.6967e-06 | 0.037775 | 0.037775 | 0.037775 | 0.97351 | -0.5095 | 0.97318 | -0.51596 | 10.3778
34 | -0.0646 | -0.016249 | 0.064616 | 0.016259 | 1.5766e-05 | 1.0036e-05 | 0.098547 | 0.098547 | 0.098547 | 0.97564 | -0.46752 | 0.9759 | -0.46241 | 27.0734
35 | -0.027599 | -0.0069228 | 0.027614 | 0.0069327 | 1.5979e-05 | 9.9315e-06 | 0.042289 | 0.042289 | 0.042289 | 0.97116 | -0.55577 | 0.97177 | -0.54364 | 11.6178
36 | 0.024703 | 0.0062015 | -0.024689 | -0.0061925 | 1.453e-05 | 8.962e-06 | 0.037775 | 0.037775 | 0.037775 | 0.97318 | -0.51596 | 0.97256 | -0.5283 | 10.3778
37 | 0.0078498 | 0.0019677 | -0.0078477 | -0.0019668 | 2.0536e-06 | 8.3683e-07 | 0.011969 | 0.011969 | 0.011969 | 0.9759 | -0.46241 | 0.97562 | -0.4679 | 3.2883
38 | -0.072466 | -0.018227 | 0.072587 | 0.018304 | 0.00012087 | 7.7027e-05 | 0.11052 | 0.11052 | 0.11052 | 0.9759 | -0.46241 | 0.97768 | -0.42756 | 30.3617
39 | -0.034407 | -0.0086352 | 0.034412 | 0.0086382 | 4.8119e-06 | 3.0224e-06 | 0.05269 | 0.05269 | 0.05269 | 0.97177 | -0.54364 | 0.97192 | -0.5407 | 14.4753
40 | -0.01173 | -0.0029397 | 0.01173 | 0.0029399 | 3.0906e-07 | 1.6625e-07 | 0.017976 | 0.017976 | 0.017976 | 0.97097 | -0.5602 | 0.97099 | -0.55964 | 4.9384
41 | -0.056615 | -0.014189 | 0.056695 | 0.01424 | 7.9233e-05 | 5.0362e-05 | 0.086761 | 0.086761 | 0.086761 | 0.97099 | -0.55964 | 0.97248 | -0.53031 | 23.8355
42 | -0.06935 | -0.017411 | 0.069562 | 0.017545 | 0.00021122 | 0.00013456 | 0.10613 | 0.10613 | 0.10613 | 0.97248 | -0.53031 | 0.97571 | -0.46667 | 29.1555
43 | 0.0055437 | 0.0013887 | -0.0055413 | -0.0013883 | 2.3564e-06 | 4.2506e-07 | 0.0084823 | 0.0084827 | 0.0084827 | 0.97248 | -0.53031 | 0.97203 | -0.53924 | 2.3304
44 | -0.0055346 | -0.0013871 | 0.0055371 | 0.0013876 | 2.4749e-06 | 4.4972e-07 | 0.0084838 | 0.0084834 | 0.0084838 | 0.97074 | -0.56462 | 0.97122 | -0.55524 | 2.3307
45 | -0.0055371 | -0.0013876 | 0.0055413 | 0.0013883 | 4.2209e-06 | 7.6417e-07 | 0.0084834 | 0.0084827 | 0.0084834 | 0.97122 | -0.55524 | 0.97203 | -0.53924 | 2.3306
46 | -0.069562 | -0.017545 | 0.069766 | 0.017676 | 0.0002048 | 0.00013046 | 0.10613 | 0.10613 | 0.10613 | 0.97571 | -0.46667 | 0.97885 | -0.40537 | 29.1554
47 | -0.10871 | -0.027468 | 0.10885 | 0.027554 | 0.00013406 | 8.5636e-05 | 0.16534 | 0.16534 | 0.16534 | 0.97885 | -0.40537 | 0.98017 | -0.37968 | 45.4232
48 | 0.024122 | 0.0060737 | -0.024093 | -0.0060559 | 2.8955e-05 | 1.7811e-05 | 0.03668 | 0.03668 | 0.03668 | 0.97885 | -0.40537 | 0.97757 | -0.43051 | 10.077
49 | 0.014823 | 0.0037186 | -0.014813 | -0.0037129 | 9.9246e-06 | 5.6971e-06 | 0.022535 | 0.022536 | 0.022536 | 0.97885 | -0.40537 | 0.97813 | -0.41942 | 6.1911
50 | 0.049381 | 0.01244 | -0.049271 | -0.012371 | 0.00010945 | 6.9409e-05 | 0.075383 | 0.075383 | 0.075383 | 0.97505 | -0.47912 | 0.97269 | -0.52558 | 20.7096
51 | -0.054387 | -0.013695 | 0.054521 | 0.01378 | 0.00013445 | 8.5397e-05 | 0.083022 | 0.083022 | 0.083022 | 0.97505 | -0.47912 | 0.97768 | -0.42756 | 22.8083
52 | 0.0095375 | 0.0023903 | -0.0095361 | -0.0023896 | 1.3653e-06 | 6.6153e-07 | 0.01459 | 0.01459 | 0.01459 | 0.97269 | -0.52558 | 0.97254 | -0.52858 | 4.0084
53 | 0.0021345 | 0.00053335 | -0.0021344 | -0.00053373 | 1.5059e-07 | -3.7119e-07 | 0.0032648 | 0.003265 | 0.003265 | 0.97269 | -0.52558 | 0.97261 | -0.52706 | 0.89697
54 | 0.037599 | 0.0094473 | -0.037572 | -0.0094302 | 2.7129e-05 | 1.7091e-05 | 0.057528 | 0.057528 | 0.057528 | 0.97269 | -0.52558 | 0.97192 | -0.5407 | 15.8044
55 | -0.12711 | -0.032084 | 0.12723 | 0.032163 | 0.0001231 | 7.8676e-05 | 0.19354 | 0.19354 | 0.19354 | 0.97768 | -0.42756 | 0.97872 | -0.40736 | 53.1699
56 | 0.00613 | 0.001536 | -0.0061293 | -0.0015358 | 6.9158e-07 | 1.8249e-07 | 0.009379 | 0.009379 | 0.009379 | 0.97254 | -0.52858 | 0.97242 | -0.53095 | 2.5767
57 | 0.0021344 | 0.00053373 | -0.0021342 | -0.00053418 | 1.8367e-07 | -4.5258e-07 | 0.003265 | 0.0032652 | 0.0032652 | 0.97261 | -0.52706 | 0.97252 | -0.52887 | 0.89703
58 | -0.12723 | -0.032163 | 0.12751 | 0.032344 | 0.00028369 | 0.00018131 | 0.19354 | 0.19354 | 0.19354 | 0.97872 | -0.40736 | 0.9811 | -0.36097 | 53.1699
59 | 0.0061293 | 0.0015358 | -0.0061291 | -0.0015357 | 1.7564e-07 | 4.636e-08 | 0.009379 | 0.0093791 | 0.0093791 | 0.97242 | -0.53095 | 0.97239 | -0.53155 | 2.5767
60 | 0.0012085 | 0.00030217 | -0.0012084 | -0.00030285 | 7.5258e-08 | -6.8024e-07 | 0.0018488 | 0.001849 | 0.001849 | 0.97252 | -0.52887 | 0.97246 | -0.53018 | 0.50798
61 | 0.0052034 | 0.0013037 | -0.005203 | -0.0013037 | 3.6743e-07 | 4.3467e-08 | 0.0079625 | 0.0079626 | 0.0079626 | 0.97239 | -0.53155 | 0.97231 | -0.53303 | 2.1875
62 | 0.19983 | 0.050906 | -0.19969 | -0.050817 | 0.00013931 | 8.869e-05 | 0.30183 | 0.30183 | 0.30183 | 0.98611 | -0.26407 | 0.98536 | -0.27853 | 27.64
63 | -0.19983 | -0.050906 | 0.20008 | 0.051067 | 0.00025321 | 0.0001612 | 0.30183 | 0.30183 | 0.30183 | 0.98611 | -0.26407 | 0.98748 | -0.23784 | 27.64
64 | 0.18835 | 0.047975 | -0.18821 | -0.047886 | 0.00014018 | 8.919e-05 | 0.2847 | 0.2847 | 0.2847 | 0.98536 | -0.27853 | 0.98456 | -0.29398 | 26.0718
65 | 0.021076 | 0.0052864 | -0.021071 | -0.0052829 | 5.8242e-06 | 3.5306e-06 | 0.031761 | 0.031761 | 0.031761 | 0.98748 | -0.23784 | 0.98718 | -0.24364 | 8.7256
66 | -0.22116 | -0.056354 | 0.22171 | 0.056704 | 0.00054952 | 0.00035017 | 0.33359 | 0.33359 | 0.33359 | 0.98748 | -0.23784 | 0.99016 | -0.18649 | 30.5484
67 | 0.015213 | 0.0038147 | -0.015207 | -0.0038114 | 5.8491e-06 | 3.3644e-06 | 0.022931 | 0.022931 | 0.022931 | 0.98718 | -0.24364 | 0.98676 | -0.25171 | 6.2998
68 | -0.22276 | -0.056968 | 0.22278 | 0.056979 | 1.6464e-05 | 1.0492e-05 | 0.33517 | 0.33517 | 0.33517 | 0.99016 | -0.18649 | 0.99024 | -0.18496 | 30.6934
69 | -0.014392 | -0.0036071 | 0.014393 | 0.0036075 | 6.9182e-07 | 3.9209e-07 | 0.021635 | 0.021635 | 0.021635 | 0.98989 | -0.19167 | 0.98994 | -0.19066 | 5.9436
70 | 0.0064616 | 0.0016195 | -0.0064593 | -0.0016189 | 2.2939e-06 | 6.3496e-07 | 0.0097132 | 0.0097135 | 0.0097135 | 0.98989 | -0.19167 | 0.98951 | -0.19913 | 2.6685
71 | -0.015587 | -0.0039066 | 0.015591 | 0.0039091 | 4.2358e-06 | 2.4462e-06 | 0.023429 | 0.023429 | 0.023429 | 0.98994 | -0.19066 | 0.99024 | -0.18496 | 6.4365
72 | -0.23837 | -0.060888 | 0.2396 | 0.061677 | 0.0012374 | 0.00078893 | 0.3586 | 0.3586 | 0.3586 | 0.99024 | -0.18496 | 0.99585 | -0.078193 | 32.8389
73 | 0.0047576 | 0.0011923 | -0.0047574 | -0.0011923 | 1.3307e-07 | -6.1921e-09 | 0.0071088 | 0.0071088 | 0.0071088 | 0.99585 | -0.078193 | 0.99582 | -0.07878 | 1.953
74 | 0.046802 | 0.011899 | -0.046666 | -0.011814 | 0.00013539 | 8.5696e-05 | 0.069992 | 0.069992 | 0.069992 | 0.99585 | -0.078193 | 0.99271 | -0.13844 | 19.2286
75 | -0.29116 | -0.074768 | 0.29227 | 0.075477 | 0.0011099 | 0.00070849 | 0.4357 | 0.4357 | 0.4357 | 0.99585 | -0.078193 | 1 | 0 | 39.8992
76 | 0.054742 | 0.013764 | -0.054677 | -0.013723 | 6.4686e-05 | 4.1058e-05 | 0.081472 | 0.081472 | 0.081472 | 1 | 0 | 0.99871 | -0.024775 | 22.3825
77 | 0.27051 | 0.069394 | -0.27021 | -0.0692 | 0.00030405 | 0.00019401 | 0.4031 | 0.4031 | 0.4031 | 1 | 0 | 0.99877 | -0.023199 | 36.9137
78 | 0.041659 | 0.01046 | -0.041633 | -0.010444 | 2.5609e-05 | 1.6158e-05 | 0.062076 | 0.062076 | 0.062076 | 0.99871 | -0.024775 | 0.99804 | -0.03767 | 17.0538
79 | 0.26551 | 0.068022 | -0.26523 | -0.067845 | 0.00027809 | 0.00017742 | 0.39609 | 0.39609 | 0.39609 | 0.99877 | -0.023199 | 0.99763 | -0.044837 | 36.2724
80 | 0.011648 | 0.00292 | -0.011645 | -0.0029186 | 2.7044e-06 | 1.4251e-06 | 0.01746 | 0.01746 | 0.01746 | 0.99271 | -0.13844 | 0.99246 | -0.14331 | 4.7967
81 | 0.035018 | 0.0088937 | -0.034888 | -0.0088122 | 0.00012989 | 8.1511e-05 | 0.052532 | 0.052533 | 0.052533 | 0.99271 | -0.13844 | 0.98869 | -0.21581 | 14.4321
82 | 0.034888 | 0.0088122 | -0.034812 | -0.0087644 | 7.6141e-05 | 4.7789e-05 | 0.052533 | 0.052533 | 0.052533 | 0.98869 | -0.21581 | 0.98633 | -0.26146 | 14.4322
83 | 0.034812 | 0.0087644 | -0.034762 | -0.0087327 | 5.041e-05 | 3.1642e-05 | 0.052533 | 0.052533 | 0.052533 | 0.98633 | -0.26146 | 0.98477 | -0.2918 | 14.4322
84 | 0.034762 | 0.0087327 | -0.034707 | -0.0086984 | 5.4662e-05 | 3.4313e-05 | 0.052533 | 0.052534 | 0.052534 | 0.98477 | -0.2918 | 0.98308 | -0.3248 | 14.4323
85 | 0.0064192 | 0.0016088 | -0.0064187 | -0.0016087 | 5.6979e-07 | 1.7063e-07 | 0.0098393 | 0.0098394 | 0.0098394 | 0.9708 | -0.56319 | 0.9707 | -0.56505 | 2.7031
86 | -0.0092583 | -0.0023209 | 0.0092605 | 0.0023219 | 2.1895e-06 | 1.0029e-06 | 0.013822 | 0.013822 | 0.013822 | 0.99669 | -0.063686 | 0.99695 | -0.058723 | 3.7974
87 | 0.0092583 | 0.0023209 | -0.0092526 | -0.0023183 | 5.7095e-06 | 2.6163e-06 | 0.013822 | 0.013823 | 0.013823 | 0.99669 | -0.063686 | 0.99602 | -0.076635 | 3.7975
88 | -0.022048 | -0.0055267 | 0.022068 | 0.0055388 | 1.9875e-05 | 1.2081e-05 | 0.032908 | 0.032908 | 0.032908 | 0.99695 | -0.058723 | 0.99793 | -0.039821 | 9.0407
89 | 0.0044296 | 0.0011095 | -0.0044293 | -0.0011095 | 2.6198e-07 | -3.9952e-08 | 0.0066174 | 0.0066175 | 0.0066175 | 0.99602 | -0.076635 | 0.99595 | -0.077877 | 1.818
90 | 0.0019735 | 0.00049421 | -0.0019734 | -0.00049457 | 1.0937e-07 | -3.6657e-07 | 0.0029484 | 0.0029485 | 0.0029485 | 0.99595 | -0.077877 | 0.99589 | -0.079041 | 0.81003
91 | 0.0024559 | 0.00061534 | -0.0024558 | -0.00061548 | 7.2731e-08 | -1.4092e-07 | 0.0036692 | 0.0036692 | 0.0036692 | 0.99595 | -0.077877 | 0.99592 | -0.078499 | 1.008
92 | -0.017586 | -0.004409 | 0.017632 | 0.0044366 | 4.6405e-05 | 2.7553e-05 | 0.026846 | 0.026845 | 0.026846 | 0.97476 | -0.48574 | 0.97757 | -0.43051 | 7.3753
93 | 0.017586 | 0.004409 | -0.017583 | -0.0044075 | 2.5965e-06 | 1.542e-06 | 0.026846 | 0.026846 | 0.026846 | 0.97476 | -0.48574 | 0.9746 | -0.48884 | 7.3753
94 | 0.0064612 | 0.0016193 | -0.0064606 | -0.0016192 | 5.9116e-07 | 1.7403e-07 | 0.009835 | 0.009835 | 0.009835 | 0.97757 | -0.43051 | 0.97747 | -0.43243 | 2.7019
95 | 0.010531 | 0.00264 | -0.010528 | -0.0026387 | 2.6599e-06 | 1.3606e-06 | 0.016079 | 0.016079 | 0.016079 | 0.9746 | -0.48884 | 0.97433 | -0.49414 | 4.4174
96 | 0.007052 | 0.0017674 | -0.0070517 | -0.0017673 | 3.0196e-07 | 1.067e-07 | 0.010767 | 0.010767 | 0.010767 | 0.9746 | -0.48884 | 0.97455 | -0.48973 | 2.958
97 | 0.0016552 | 0.00041463 | -0.0016551 | -0.00041482 | 4.2244e-08 | -1.8949e-07 | 0.0025366 | 0.0025367 | 0.0025367 | 0.97094 | -0.56036 | 0.97091 | -0.5609 | 0.69688
98 | 0.0070517 | 0.0017673 | -0.0070508 | -0.001767 | 9.3097e-07 | 3.2903e-07 | 0.010767 | 0.010767 | 0.010767 | 0.97455 | -0.48973 | 0.97441 | -0.49251 | 2.958
99 | 0.0051873 | 0.0013 | -0.0051868 | -0.0012999 | 5.1812e-07 | 5.7353e-08 | 0.0079214 | 0.0079215 | 0.0079215 | 0.97441 | -0.49251 | 0.97431 | -0.4946 | 2.1762
100 | -0.034388 | -0.0086265 | 0.034392 | 0.0086287 | 3.5275e-06 | 2.2108e-06 | 0.051279 | 0.051279 | 0.051279 | 0.99793 | -0.039821 | 0.99804 | -0.03767 | 14.0877
101 | 0.11738 | 0.030019 | -0.11653 | -0.02948 | 0.00084426 | 0.00053941 | 0.17701 | 0.17701 | 0.17701 | 0.98792 | -0.22987 | 0.98017 | -0.37968 | 48.6283
102 | -0.13005 | -0.033197 | 0.13046 | 0.03346 | 0.00041238 | 0.00026245 | 0.19609 | 0.19609 | 0.19609 | 0.98792 | -0.22987 | 0.99135 | -0.16448 | 26.9361
103 | 0.012673 | 0.003178 | -0.012666 | -0.0031745 | 6.5155e-06 | 3.5597e-06 | 0.019089 | 0.019089 | 0.019089 | 0.98792 | -0.22987 | 0.98737 | -0.24067 | 5.2442
104 | 0.069174 | 0.017425 | -0.069106 | -0.017381 | 6.8243e-05 | 4.3458e-05 | 0.10386 | 0.10386 | 0.10386 | 0.99135 | -0.16448 | 0.99028 | -0.18513 | 28.5335
105 | -0.19963 | -0.050884 | 0.19982 | 0.051003 | 0.00018629 | 0.00011858 | 0.29996 | 0.29996 | 0.29996 | 0.99135 | -0.16448 | 0.99236 | -0.14516 | 27.4685
106 | 0.0062257 | 0.0015603 | -0.0062246 | -0.00156 | 1.0521e-06 | 2.6579e-07 | 0.0093824 | 0.0093826 | 0.0093826 | 0.98737 | -0.24067 | 0.98719 | -0.24421 | 2.5776
107 | 0.067222 | 0.016909 | -0.067134 | -0.016853 | 8.8355e-05 | 5.6251e-05 | 0.10103 | 0.10103 | 0.10103 | 0.99028 | -0.18513 | 0.98886 | -0.21268 | 27.7559
108 | 0.019903 | 0.004992 | -0.019894 | -0.0049865 | 9.0647e-06 | 5.451e-06 | 0.029845 | 0.029845 | 0.029845 | 0.99236 | -0.14516 | 0.99186 | -0.15472 | 8.1992
109 | -0.21972 | -0.055995 | 0.22042 | 0.056441 | 0.00070003 | 0.00044602 | 0.3298 | 0.3298 | 0.3298 | 0.99236 | -0.14516 | 0.99581 | -0.079369 | 30.2015
110 | -0.0081048 | -0.0020313 | 0.0081093 | 0.0020331 | 4.4903e-06 | 1.8303e-06 | 0.012166 | 0.012166 | 0.012166 | 0.99126 | -0.16635 | 0.99186 | -0.15472 | 3.3424
111 | -0.0048764 | -0.0012221 | 0.0048768 | 0.0012221 | 4.1892e-07 | -5.2633e-09 | 0.0072892 | 0.0072891 | 0.0072892 | 0.99547 | -0.086012 | 0.99556 | -0.084209 | 2.0025
112 | -0.010703 | -0.0026823 | 0.010705 | 0.0026836 | 2.4681e-06 | 1.2451e-06 | 0.015997 | 0.015997 | 0.015997 | 0.99556 | -0.084209 | 0.99581 | -0.079369 | 4.3949
113 | 0.0087852 | 0.0022018 | -0.0087838 | -0.0022012 | 1.3606e-06 | 5.9492e-07 | 0.013104 | 0.013104 | 0.013104 | 0.99763 | -0.044837 | 0.99746 | -0.048089 | 3.5999
114 | 0.25645 | 0.065643 | -0.25602 | -0.06537 | 0.00042805 | 0.00027304 | 0.38299 | 0.38299 | 0.38299 | 0.99763 | -0.044837 | 0.99581 | -0.079369 | 35.0724
115 | -0.024677 | -0.0061852 | 0.024689 | 0.0061925 | 1.1939e-05 | 7.3645e-06 | 0.037775 | 0.037775 | 0.037775 | 0.97205 | -0.53845 | 0.97256 | -0.5283 | 10.3779
116 | 0.022608 | 0.0056667 | -0.022606 | -0.0056656 | 1.7583e-06 | 1.0768e-06 | 0.034609 | 0.034609 | 0.034609 | 0.97205 | -0.53845 | 0.97196 | -0.54008 | 9.5079
117 | -0.0089332 | -0.002238 | 0.0089368 | 0.0022396 | 3.6163e-06 | 1.6607e-06 | 0.0136 | 0.0136 | 0.0136 | 0.97738 | -0.43427 | 0.97781 | -0.42577 | 3.7363
118 | 0.0084669 | 0.0021211 | -0.0084669 | -0.0021211 | 2.149e-08 | 9.4315e-09 | 0.01289 | 0.01289 | 0.01289 | 0.97738 | -0.43427 | 0.97738 | -0.43432 | 3.5412
119 | -0.0094198 | -0.0023607 | 0.0094227 | 0.002362 | 2.8501e-06 | 1.36e-06 | 0.014335 | 0.014335 | 0.014335 | 0.97781 | -0.42577 | 0.97813 | -0.41942 | 3.9382
120 | 0.0069051 | 0.0017297 | -0.0069035 | -0.0017292 | 1.5117e-06 | 5.1045e-07 | 0.010512 | 0.010513 | 0.010513 | 0.97738 | -0.43432 | 0.97714 | -0.43892 | 2.8881
121 | 0.0053907 | 0.0013508 | -0.0053901 | -0.0013507 | 6.5788e-07 | 9.3664e-08 | 0.0082008 | 0.0082009 | 0.0082009 | 0.97813 | -0.41942 | 0.978 | -0.42199 | 2.253
122 | 0.0042377 | 0.001061 | -0.0042369 | -0.0010611 | 7.5009e-07 | -1.2154e-07 | 0.0064528 | 0.0064531 | 0.0064531 | 0.97714 | -0.43892 | 0.97695 | -0.44264 | 1.7728
123 | 0.0022616 | 0.00056664 | -0.0022615 | -0.00056679 | 6.7932e-08 | -1.4851e-07 | 0.0034409 | 0.003441 | 0.003441 | 0.978 | -0.42199 | 0.97797 | -0.42262 | 0.94532
124 | 0.0042369 | 0.0010611 | -0.0042361 | -0.0010613 | 8.1749e-07 | -1.3215e-07 | 0.0064531 | 0.0064533 | 0.0064533 | 0.97695 | -0.44264 | 0.97675 | -0.44669 | 1.7729
125 | 0.0013455 | 0.00033682 | -0.0013455 | -0.00033687 | 6.7903e-09 | -4.9601e-08 | 0.0020496 | 0.0020497 | 0.0020497 | 0.97675 | -0.44669 | 0.97674 | -0.4468 | 0.56309
126 | -0.0011939 | -0.00029923 | 0.001194 | 0.00029893 | 3.2397e-08 | -3.002e-07 | 0.0018272 | 0.0018271 | 0.0018272 | 0.97228 | -0.5336 | 0.97231 | -0.53303 | 0.50199
127 | -0.0071805 | -0.0017996 | 0.0071823 | 0.0018002 | 1.8846e-06 | 6.4145e-07 | 0.010746 | 0.010746 | 0.010746 | 0.99432 | -0.10824 | 0.9946 | -0.10274 | 2.9521
128 | -0.0071823 | -0.0018002 | 0.0071827 | 0.0018003 | 3.1652e-07 | 1.077e-07 | 0.010746 | 0.010745 | 0.010746 | 0.9946 | -0.10274 | 0.99465 | -0.10181 | 2.9521
129 | -0.012105 | -0.0030341 | 0.01211 | 0.0030368 | 5.0852e-06 | 2.7176e-06 | 0.01811 | 0.01811 | 0.01811 | 0.99465 | -0.10181 | 0.99511 | -0.092997 | 4.9752
130 | -0.024874 | -0.0062356 | 0.02489 | 0.0062455 | 1.6163e-05 | 9.9392e-06 | 0.037195 | 0.037195 | 0.037195 | 0.99511 | -0.092997 | 0.99581 | -0.079369 | 10.2184
131 | -0.18775 | -0.047698 | 0.18793 | 0.047818 | 0.00018828 | 0.00011979 | 0.28429 | 0.28429 | 0.28429 | 0.98348 | -0.31478 | 0.98456 | -0.29398 | 26.0341
132 | 0.0031793 | 0.00079652 | -0.003179 | -0.00079674 | 2.3623e-07 | -2.1432e-07 | 0.0047427 | 0.0047429 | 0.0047429 | 0.99746 | -0.048089 | 0.99738 | -0.049649 | 1.303
133 | -0.007879 | -0.0019747 | 0.0078796 | 0.0019749 | 6.1384e-07 | 2.448e-07 | 0.011883 | 0.011883 | 0.011883 | 0.98663 | -0.25428 | 0.98672 | -0.25265 | 3.2645
134 | 0.0066634 | 0.00167 | -0.0066631 | -0.0016699 | 3.2915e-07 | 9.9671e-08 | 0.01005 | 0.01005 | 0.01005 | 0.98663 | -0.25428 | 0.98658 | -0.25532 | 2.7609
135 | -0.0094238 | -0.0023619 | 0.0094242 | 0.0023621 | 4.1941e-07 | 1.9769e-07 | 0.014212 | 0.014212 | 0.014212 | 0.98672 | -0.25265 | 0.98676 | -0.25171 | 3.9043
136 | -0.034055 | -0.0085351 | 0.034085 | 0.0085538 | 2.9815e-05 | 1.8695e-05 | 0.051332 | 0.051331 | 0.051332 | 0.98721 | -0.24478 | 0.98815 | -0.22642 | 14.1021
137 | 0.020987 | 0.0052621 | -0.020984 | -0.0052607 | 2.3718e-06 | 1.4368e-06 | 0.031604 | 0.031604 | 0.031604 | 0.98815 | -0.22642 | 0.98803 | -0.22879 | 8.6823
138 | -0.055072 | -0.013816 | 0.055108 | 0.013839 | 3.6108e-05 | 2.2929e-05 | 0.082935 | 0.082935 | 0.082935 | 0.98815 | -0.22642 | 0.98886 | -0.21268 | 22.7844
139 | 0.015182 | 0.0038064 | -0.015177 | -0.0038039 | 4.2463e-06 | 2.4403e-06 | 0.022865 | 0.022865 | 0.022865 | 0.98803 | -0.22879 | 0.98773 | -0.23466 | 6.2815
140 | 0.0087859 | 0.0022021 | -0.0087852 | -0.0022018 | 7.2518e-07 | 3.2285e-07 | 0.013236 | 0.013236 | 0.013236 | 0.98773 | -0.23466 | 0.98764 | -0.2364 | 3.6363
141 | 0.00057267 | 0.00014318 | -0.00057266 | -0.00014352 | 7.8483e-09 | -3.3917e-07 | 0.00087231 | 0.00087244 | 0.00087244 | 0.97674 | -0.4468 | 0.97673 | -0.44709 | 0.23968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61918 | 0.15863

## res_load
| p_mw | q_mvar
0 | 0.0066452 | 0.0016654
1 | 0.01135 | 0.0028446
2 | 0.0024011 | 0.00060177
3 | 0.0024064 | 0.00060309
4 | 0.0021 | 0.00052631
5 | 0.0029521 | 0.00073987
6 | 0.002106 | 0.00052781
7 | 0.0013324 | 0.00033393
8 | 0.01004 | 0.0025164
9 | 0.002179 | 0.0005461
10 | 0.005503 | 0.0013792
11 | 0.0030423 | 0.00076247
12 | 0.0041076 | 0.0010294
13 | 0.011658 | 0.0029218
14 | 0.010419 | 0.0026113
15 | 0.011353 | 0.0028453
16 | 0.0090162 | 0.0022597
17 | 0.0089816 | 0.002251
18 | 0.0047782 | 0.0011975
19 | 0.0067929 | 0.0017025
20 | 0.01173 | 0.0029397
21 | 0.044886 | 0.011249
22 | 0.007112 | 0.0017824
23 | 0.0055346 | 0.0013871
24 | 0.0050058 | 0.0012546
25 | 0.0034062 | 0.00085366
26 | 0.0031599 | 0.00079195
27 | 0.00092572 | 0.00023201
28 | 0.0048109 | 0.0012057
29 | 0.0078477 | 0.0019668
30 | 0.0009257 | 0.000232
31 | 0.0012084 | 0.00030285
32 | 0.01134 | 0.002842
33 | 0.005858 | 0.0014681
34 | 0.0010538 | 0.00026411
35 | 0.0079307 | 0.0019876
36 | 0.0011935 | 0.00029912
37 | 0.0064593 | 0.0016189
38 | 0.013018 | 0.0032627
39 | 0.0047008 | 0.0011781
40 | 0.0047574 | 0.0011923
41 | 0.011645 | 0.0029186
42 | 0.034707 | 0.0086984
43 | 0.012787 | 0.0032048
44 | 0.004823 | 0.0012087
45 | 0.0019734 | 0.00049457
46 | 0.0024558 | 0.00061548
47 | 0.0064187 | 0.0016087
48 | 0.0016384 | 0.00041061
49 | 0.0064606 | 0.0016192
50 | 0.0018635 | 0.00046703
51 | 0.01232 | 0.0030878
52 | 0.0076848 | 0.001926
53 | 0.0064406 | 0.0016142
54 | 0.0018838 | 0.00047214
55 | 0.0081048 | 0.0020313
56 | 0.011784 | 0.0029534
57 | 0.0048764 | 0.0012221
58 | 0.0058262 | 0.0014602
59 | 0.0072415 | 0.0018149
60 | 0.010528 | 0.0026387
61 | 0.0020687 | 0.00051846
62 | 0.022606 | 0.0056656
63 | 0.00046627 | 0.00011686
64 | 0.00048307 | 0.00012107
65 | 0.0015618 | 0.00039143
66 | 0.0026659 | 0.00066813
67 | 0.0031285 | 0.00078408
68 | 0.0022615 | 0.00056679
69 | 0.0028906 | 0.00072445
70 | 0.0011939 | 0.00029923
71 | 0.0040091 | 0.0010048
72 | 0.0071805 | 0.0017996
73 | 0.0049227 | 0.0012337
74 | 0.012763 | 0.0031988
75 | 0.00027292 | 6.8401e-05
76 | 0.0056046 | 0.0014046
77 | 0.0016551 | 0.00041482
78 | 0.0012156 | 0.00030465
79 | 0.0015442 | 0.00038701
80 | 0.0066631 | 0.0016699
81 | 0.0057825 | 0.0014492
82 | 0.034055 | 0.0085351
83 | 0.0058027 | 0.0014543
84 | 0.012026 | 0.003014
85 | 0.0063914 | 0.0016018
86 | 0.0087852 | 0.0022018
87 | 0.00077282 | 0.00019369
88 | 0.00057266 | 0.00014352
89 | 0.0062246 | 0.00156
90 | 0.0051868 | 0.0012999
91 | 0.003179 | 0.00079674

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1