## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2543-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2543-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2543-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2543-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2543-4_0_3_node_91 | 0.4 | n |  | TRUE
5 | bus_LV_2543-4_0_3_node_114 | 0.4 | n |  | TRUE
6 | bus_LV_2543-4_0_3_node_93 | 0.4 | n |  | TRUE
7 | bus_LV_2543-4_0_3_node_89 | 0.4 | n |  | TRUE
8 | bus_LV_2543-4_0_3_node_112 | 0.4 | n |  | TRUE
9 | bus_LV_2543-4_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2543-4_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2543-4_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2543-4_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2543-4_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2543-4_0_3_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_2543-4_0_3_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_2543-4_0_3_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_2543-4_0_3_node_69 | 0.4 | n |  | TRUE
18 | bus_LV_2543-4_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_2543-4_0_3_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_2543-4_0_3_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2543-4_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2543-4_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2543-4_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2543-4_0_3_node_84 | 0.4 | n |  | TRUE
25 | bus_LV_2543-4_0_3_node_103 | 0.4 | n |  | TRUE
26 | bus_LV_2543-4_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2543-4_0_3_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2543-4_0_3_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2543-4_0_3_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2543-4_0_3_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2543-4_0_3_node_121 | 0.4 | n |  | TRUE
32 | bus_LV_2543-4_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2543-4_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2543-4_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_2543-4_0_3_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2543-4_0_3_node_81 | 0.4 | n |  | TRUE
37 | bus_LV_2543-4_0_3_node_111 | 0.4 | n |  | TRUE
38 | bus_LV_2543-4_0_3_node_80 | 0.4 | n |  | TRUE
39 | bus_LV_2543-4_0_3_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_2543-4_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2543-4_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2543-4_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2543-4_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2543-4_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2543-4_0_3_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_2543-4_0_3_node_86 | 0.4 | n |  | TRUE
47 | bus_LV_2543-4_0_3_node_88 | 0.4 | n |  | TRUE
48 | bus_LV_2543-4_0_3_node_95 | 0.4 | n |  | TRUE
49 | bus_LV_2543-4_0_3_node_135 | 0.4 | n |  | TRUE
50 | bus_LV_2543-4_0_3_node_134 | 0.4 | n |  | TRUE
51 | bus_LV_2543-4_0_3_node_87 | 0.4 | n |  | TRUE
52 | bus_LV_2543-4_0_3_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_2543-4_0_3_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_2543-4_0_3_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2543-4_0_3_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_2543-4_0_3_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_2543-4_0_3_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_2543-4_0_3_node_68 | 0.4 | n |  | TRUE
59 | bus_LV_2543-4_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_2543-4_0_3_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_2543-4_0_3_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_2543-4_0_3_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_2543-4_0_3_node_38 | 0.4 | n |  | TRUE
64 | bus_LV_2543-4_0_3_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_2543-4_0_3_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_2543-4_0_3_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_2543-4_0_3_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_2543-4_0_3_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_2543-4_0_3_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_2543-4_0_3_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_2543-4_0_3_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_2543-4_0_3_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_2543-4_0_3_node_47 | 0.4 | n |  | TRUE
74 | bus_LV_2543-4_0_3_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_2543-4_0_3_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_2543-4_0_3_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_2543-4_0_3_node_147 | 0.4 | n |  | TRUE
78 | bus_LV_2543-4_0_3_node_146 | 0.4 | n |  | TRUE
79 | bus_LV_2543-4_0_3_node_148 | 0.4 | n |  | TRUE
80 | bus_LV_2543-4_0_3_node_110 | 0.4 | n |  | TRUE
81 | bus_LV_2543-4_0_3_node_54 | 0.4 | n |  | TRUE
82 | bus_LV_2543-4_0_3_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_2543-4_0_3_node_83 | 0.4 | n |  | TRUE
84 | bus_LV_2543-4_0_3_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_2543-4_0_3_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_2543-4_0_3_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_2543-4_0_3_node_61 | 0.4 | n |  | TRUE
88 | bus_LV_2543-4_0_3_node_62 | 0.4 | n |  | TRUE
89 | bus_LV_2543-4_0_3_node_94 | 0.4 | n |  | TRUE
90 | bus_LV_2543-4_0_3_node_96 | 0.4 | n |  | TRUE
91 | bus_LV_2543-4_0_3_node_63 | 0.4 | n |  | TRUE
92 | bus_LV_2543-4_0_3_node_64 | 0.4 | n |  | TRUE
93 | bus_LV_2543-4_0_3_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_2543-4_0_3_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_2543-4_0_3_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_2543-4_0_3_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_2543-4_0_3_node_104 | 0.4 | n |  | TRUE
98 | bus_LV_2543-4_0_3_node_129 | 0.4 | n |  | TRUE
99 | bus_LV_2543-4_0_3_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_2543-4_0_3_node_130 | 0.4 | n |  | TRUE
101 | bus_LV_2543-4_0_3_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_2543-4_0_3_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_2543-4_0_3_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_2543-4_0_3_node_75 | 0.4 | n |  | TRUE
105 | bus_LV_2543-4_0_3_node_76 | 0.4 | n |  | TRUE
106 | bus_LV_2543-4_0_3_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_2543-4_0_3_node_78 | 0.4 | n |  | TRUE
108 | bus_LV_2543-4_0_3_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_2543-4_0_3_node_115 | 0.4 | n |  | TRUE
110 | bus_LV_2543-4_0_3_node_116 | 0.4 | n |  | TRUE
111 | bus_LV_2543-4_0_3_node_133 | 0.4 | n |  | TRUE
112 | bus_LV_2543-4_0_3_node_141 | 0.4 | n |  | TRUE
113 | bus_LV_2543-4_0_3_node_90 | 0.4 | n |  | TRUE
114 | bus_LV_2543-4_0_3_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_2543-4_0_3_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_2543-4_0_3_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_2543-4_0_3_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_2543-4_0_3_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_2543-4_0_3_node_143 | 0.4 | n |  | TRUE
120 | bus_LV_2543-4_0_3_node_142 | 0.4 | n |  | TRUE
121 | bus_LV_2543-4_0_3_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_2543-4_0_3_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_2543-4_0_3_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_2543-4_0_3_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_2543-4_0_3_node_125 | 0.4 | n |  | TRUE
126 | bus_LV_2543-4_0_3_node_132 | 0.4 | n |  | TRUE
127 | bus_LV_2543-4_0_3_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_2543-4_0_3_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_2543-4_0_3_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_2543-4_0_3_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_2543-4_0_3_node_144 | 0.4 | n |  | TRUE
132 | bus_LV_2543-4_0_3_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_2543-4_0_3_node_117 | 0.4 | n |  | TRUE
134 | bus_LV_2543-4_0_3_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_2543-4_0_3_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_2543-4_0_3_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_2543-4_0_3_node_140 | 0.4 | n |  | TRUE
138 | bus_LV_2543-4_0_3_node_136 | 0.4 | n |  | TRUE
139 | bus_LV_2543-4_0_3_node_137 | 0.4 | n |  | TRUE
140 | bus_LV_2543-4_0_3_node_138 | 0.4 | n |  | TRUE
141 | bus_LV_2543-4_0_3_node_145 | 0.4 | n |  | TRUE
142 | bus_LV_2543-4_0_3_node_149 | 0.4 | n |  | TRUE
143 | bus_MV_396_0_node_145 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2543-4_0_3_load_0 | 0 | 0.0015805 | 0.00039611 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2543-4_0_3_load_1 | 1 | 0.00162 | 0.00040602 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2543-4_0_3_load_2 | 2 | 0.0027101 | 0.00067921 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2543-4_0_3_load_114 | 5 | 0.0019922 | 0.00049928 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2543-4_0_3_load_93 | 6 | 0.0042757 | 0.0010716 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2543-4_0_3_load_89 | 7 | 0.0039391 | 0.00098723 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2543-4_0_3_load_4 | 9 | 0.0065267 | 0.0016357 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2543-4_0_3_load_5 | 10 | 0.0018039 | 0.00045211 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2543-4_0_3_load_6 | 11 | 0.0022762 | 0.00057047 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2543-4_0_3_load_7 | 12 | 0.0011519 | 0.00028869 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2543-4_0_3_load_36 | 14 | 0.0018841 | 0.00047221 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2543-4_0_3_load_70 | 15 | 0.0036266 | 0.00090892 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2543-4_0_3_load_71 | 16 | 0.0027554 | 0.00069058 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2543-4_0_3_load_69 | 17 | 0.0048814 | 0.0012234 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2543-4_0_3_load_34 | 18 | 0.0015879 | 0.00039797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2543-4_0_3_load_59 | 19 | 0.00094149 | 0.00023596 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2543-4_0_3_load_30 | 20 | 0.0013165 | 0.00032996 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2543-4_0_3_load_9 | 21 | 0.0022977 | 0.00057585 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2543-4_0_3_load_10 | 22 | 0.0080767 | 0.0020242 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2543-4_0_3_load_11 | 23 | 0.0051575 | 0.0012926 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2543-4_0_3_load_103 | 25 | 0.0077732 | 0.0019482 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2543-4_0_3_load_17 | 26 | 0.005008 | 0.0012551 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2543-4_0_3_load_13 | 27 | 0.0011634 | 0.00029157 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2543-4_0_3_load_14 | 28 | 0.00152 | 0.00038094 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2543-4_0_3_load_15 | 29 | 0.0058783 | 0.0014732 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2543-4_0_3_load_121 | 31 | 0.0065746 | 0.0016477 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2543-4_0_3_load_18 | 32 | 0.0021974 | 0.00055072 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2543-4_0_3_load_111 | 37 | 0.0035385 | 0.00088684 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2543-4_0_3_load_80 | 38 | 0.0038539 | 0.00096589 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2543-4_0_3_load_22 | 40 | 0.00031777 | 7.964e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2543-4_0_3_load_23 | 41 | 0.0021806 | 0.00054651 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2543-4_0_3_load_24 | 42 | 0.00031824 | 7.9759e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2543-4_0_3_load_26 | 44 | 0.0014252 | 0.00035719 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2543-4_0_3_load_85 | 45 | 0.00081465 | 0.00020417 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2543-4_0_3_load_88 | 47 | 0.00028227 | 7.0744e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2543-4_0_3_load_95 | 48 | 0.00037911 | 9.5013e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2543-4_0_3_load_135 | 49 | 0.0021781 | 0.00054587 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2543-4_0_3_load_134 | 50 | 0.0035868 | 0.00089895 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2543-4_0_3_load_87 | 51 | 0.0014231 | 0.00035667 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2543-4_0_3_load_27 | 52 | 0.0015829 | 0.00039671 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2543-4_0_3_load_28 | 53 | 0.0023194 | 0.00058131 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2543-4_0_3_load_31 | 55 | 0.0017739 | 0.00044457 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2543-4_0_3_load_32 | 56 | 0.0017855 | 0.0004475 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2543-4_0_3_load_55 | 57 | 0.0029655 | 0.00074323 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2543-4_0_3_load_68 | 58 | 0.0030171 | 0.00075615 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2543-4_0_3_load_42 | 59 | 0.0025408 | 0.00063677 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2543-4_0_3_load_33 | 60 | 0.004676 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2543-4_0_3_load_35 | 61 | 0.0063498 | 0.0015914 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2543-4_0_3_load_37 | 62 | 0.0022224 | 0.00055699 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2543-4_0_3_load_38 | 63 | 0.0019698 | 0.00049369 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2543-4_0_3_load_39 | 64 | 0.0054397 | 0.0013633 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2543-4_0_3_load_40 | 65 | 0.0017294 | 0.00043343 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2543-4_0_3_load_41 | 66 | 0.0018051 | 0.0004524 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2543-4_0_3_load_44 | 67 | 0.0022768 | 0.00057061 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2543-4_0_3_load_43 | 68 | 0.0027591 | 0.00069149 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2543-4_0_3_load_45 | 69 | 0.0035456 | 0.00088862 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2543-4_0_3_load_46 | 70 | 0.0025509 | 0.00063933 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2543-4_0_3_load_52 | 71 | 0.002716 | 0.00068069 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2543-4_0_3_load_53 | 72 | 0.0039724 | 0.00099557 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2543-4_0_3_load_47 | 73 | 0.0038544 | 0.000966 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2543-4_0_3_load_48 | 74 | 0.0059471 | 0.0014905 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2543-4_0_3_load_49 | 75 | 0.0066476 | 0.0016661 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2543-4_0_3_load_50 | 76 | 0.0084631 | 0.0021211 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2543-4_0_3_load_147 | 77 | 0.0056682 | 0.0014206 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2543-4_0_3_load_146 | 78 | 0.004164 | 0.0010436 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2543-4_0_3_load_148 | 79 | 0.0019283 | 0.00048329 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2543-4_0_3_load_110 | 80 | 0.003982 | 0.00099799 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2543-4_0_3_load_54 | 81 | 0.002709 | 0.00067893 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2543-4_0_3_load_82 | 82 | 0.0031657 | 0.0007934 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2543-4_0_3_load_83 | 83 | 0.0020861 | 0.00052282 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2543-4_0_3_load_56 | 84 | 0.0027292 | 0.000684 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2543-4_0_3_load_60 | 86 | 0.0017235 | 0.00043196 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2543-4_0_3_load_61 | 87 | 0.0013697 | 0.00034327 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2543-4_0_3_load_62 | 88 | 0.0012451 | 0.00031204 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2543-4_0_3_load_96 | 90 | 0.00036042 | 9.033e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2543-4_0_3_load_63 | 91 | 0.005104 | 0.0012792 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2543-4_0_3_load_64 | 92 | 0.0057809 | 0.0014488 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2543-4_0_3_load_66 | 94 | 0.0014107 | 0.00035355 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2543-4_0_3_load_72 | 96 | 0.0016609 | 0.00041627 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2543-4_0_3_load_104 | 97 | 0.0019833 | 0.00049706 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2543-4_0_3_load_129 | 98 | 0.0016841 | 0.00042208 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2543-4_0_3_load_73 | 99 | 0.0042657 | 0.0010691 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2543-4_0_3_load_130 | 100 | 0.0031304 | 0.00078456 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2543-4_0_3_load_74 | 101 | 0.0010464 | 0.00026225 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2543-4_0_3_load_109 | 102 | 0.0028523 | 0.00071484 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2543-4_0_3_load_75 | 104 | 0.0016513 | 0.00041386 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2543-4_0_3_load_76 | 105 | 0.0016578 | 0.00041548 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2543-4_0_3_load_77 | 106 | 0.0013243 | 0.00033189 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2543-4_0_3_load_78 | 107 | 0.0016586 | 0.00041567 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2543-4_0_3_load_79 | 108 | 0.0016356 | 0.00040993 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2543-4_0_3_load_115 | 109 | 0.0017248 | 0.00043227 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2543-4_0_3_load_116 | 110 | 0.0017248 | 0.00043227 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2543-4_0_3_load_133 | 111 | 0.0030588 | 0.0007666 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2543-4_0_3_load_141 | 112 | 0.0040707 | 0.0010202 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2543-4_0_3_load_90 | 113 | 0.0041059 | 0.001029 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2543-4_0_3_load_92 | 114 | 0.0023742 | 0.00059503 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2543-4_0_3_load_97 | 115 | 0.0015922 | 0.00039903 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2543-4_0_3_load_98 | 116 | 0.0015781 | 0.00039552 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2543-4_0_3_load_101 | 117 | 0.00037062 | 9.2887e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2543-4_0_3_load_99 | 118 | 0.0012328 | 0.00030898 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2543-4_0_3_load_143 | 119 | 0.0021036 | 0.0005272 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2543-4_0_3_load_142 | 120 | 0.0016103 | 0.00040358 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2543-4_0_3_load_100 | 121 | 0.00043096 | 0.00010801 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2543-4_0_3_load_105 | 122 | 0.0020795 | 0.00052117 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2543-4_0_3_load_106 | 123 | 0.0011807 | 0.00029592 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2543-4_0_3_load_125 | 125 | 0.0027816 | 0.00069714 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2543-4_0_3_load_132 | 126 | 0.010548 | 0.0026435 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2543-4_0_3_load_123 | 127 | 0.0030961 | 0.00077595 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2543-4_0_3_load_113 | 128 | 0.0039072 | 0.00097923 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2543-4_0_3_load_120 | 129 | 0.0022758 | 0.00057037 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2543-4_0_3_load_118 | 130 | 0.0022362 | 0.00056044 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2543-4_0_3_load_117 | 133 | 0.002573 | 0.00064484 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2543-4_0_3_load_119 | 134 | 0.0028182 | 0.00070631 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2543-4_0_3_load_122 | 135 | 0.0041848 | 0.0010488 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2543-4_0_3_load_131 | 136 | 0.0052159 | 0.0013072 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2543-4_0_3_load_140 | 137 | 0.0053205 | 0.0013334 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2543-4_0_3_load_136 | 138 | 0.0055462 | 0.00139 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2543-4_0_3_load_137 | 139 | 0.0016489 | 0.00041326 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2543-4_0_3_load_138 | 140 | 0.0076675 | 0.0019216 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2543-4_0_3_load_149 | 142 | 0.0076233 | 0.0019106 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 134 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2543-4_0_3_line_0 |  | 0 | 1 | 0.0010899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2543-4_0_3_line_1 |  | 0 | 2 | 0.021493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2543-4_0_3_line_2 |  | 2 | 3 | 0.025614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2543-4_0_3_line_3 |  | 3 | 4 | 0.009491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2543-4_0_3_line_4 |  | 3 | 5 | 0.01223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2543-4_0_3_line_5 |  | 4 | 6 | 0.025088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2543-4_0_3_line_6 |  | 4 | 7 | 0.010529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2543-4_0_3_line_7 |  | 5 | 8 | 0.0066101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2543-4_0_3_line_8 |  | 6 | 111 | 0.0019705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2543-4_0_3_line_9 |  | 7 | 113 | 0.0048743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2543-4_0_3_line_10 |  | 8 | 128 | 0.020967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2543-4_0_3_line_11 |  | 8 | 37 | 0.0057856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2543-4_0_3_line_12 |  | 9 | 10 | 0.018839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2543-4_0_3_line_13 |  | 9 | 11 | 0.0016192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2543-4_0_3_line_14 |  | 10 | 12 | 0.0064172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2543-4_0_3_line_15 |  | 11 | 13 | 0.032991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2543-4_0_3_line_16 |  | 12 | 14 | 0.0095509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2543-4_0_3_line_17 |  | 13 | 15 | 0.018789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2543-4_0_3_line_18 |  | 13 | 16 | 0.021537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2543-4_0_3_line_19 |  | 13 | 17 | 0.034373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2543-4_0_3_line_20 |  | 14 | 18 | 0.0075657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2543-4_0_3_line_21 |  | 15 | 19 | 0.019772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2543-4_0_3_line_22 |  | 17 | 20 | 0.00017812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2543-4_0_3_line_23 |  | 18 | 60 | 0.01529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2543-4_0_3_line_24 |  | 20 | 53 | 0.013543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2543-4_0_3_line_25 |  | 21 | 22 | 0.0045087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2543-4_0_3_line_26 |  | 21 | 23 | 0.011557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2543-4_0_3_line_27 |  | 22 | 24 | 0.053259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2543-4_0_3_line_28 |  | 24 | 25 | 0.0041211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2543-4_0_3_line_29 |  | 24 | 26 | 0.038833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2543-4_0_3_line_30 |  | 25 | 97 | 0.026279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2543-4_0_3_line_31 |  | 26 | 29 | 0.019735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2543-4_0_3_line_32 |  | 27 | 28 | 0.017292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2543-4_0_3_line_33 |  | 27 | 29 | 0.024328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2543-4_0_3_line_34 |  | 28 | 30 | 0.02553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2543-4_0_3_line_35 |  | 30 | 31 | 0.022719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2543-4_0_3_line_36 |  | 32 | 33 | 0.00075425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2543-4_0_3_line_37 |  | 33 | 34 | 0.027153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2543-4_0_3_line_38 |  | 34 | 38 | 0.01819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2543-4_0_3_line_39 |  | 35 | 36 | 0.026571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2543-4_0_3_line_40 |  | 35 | 37 | 0.014687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2543-4_0_3_line_41 |  | 36 | 38 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2543-4_0_3_line_42 |  | 36 | 39 | 0.007534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2543-4_0_3_line_43 |  | 39 | 78 | 0.021592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2543-4_0_3_line_44 |  | 39 | 75 | 0.019579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2543-4_0_3_line_45 |  | 40 | 41 | 0.0053901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2543-4_0_3_line_46 |  | 40 | 42 | 0.0066673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2543-4_0_3_line_47 |  | 41 | 43 | 0.015544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2543-4_0_3_line_48 |  | 42 | 44 | 0.017452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2543-4_0_3_line_49 |  | 43 | 45 | 0.051536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2543-4_0_3_line_50 |  | 43 | 46 | 0.004005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2543-4_0_3_line_51 |  | 44 | 47 | 0.00037204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2543-4_0_3_line_52 |  | 45 | 48 | 0.022666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2543-4_0_3_line_53 |  | 46 | 49 | 0.011693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2543-4_0_3_line_54 |  | 46 | 50 | 0.020056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2543-4_0_3_line_55 |  | 47 | 51 | 0.00036688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2543-4_0_3_line_56 |  | 48 | 89 | 0.010366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2543-4_0_3_line_57 |  | 49 | 112 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2543-4_0_3_line_58 |  | 50 | 62 | 0.024445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2543-4_0_3_line_59 |  | 51 | 107 | 0.0032915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2543-4_0_3_line_60 |  | 52 | 53 | 0.010456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2543-4_0_3_line_61 |  | 52 | 54 | 0.0029098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2543-4_0_3_line_62 |  | 54 | 55 | 0.031993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2543-4_0_3_line_63 |  | 54 | 56 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2543-4_0_3_line_64 |  | 55 | 57 | 0.00094395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2543-4_0_3_line_65 |  | 56 | 58 | 0.010416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2543-4_0_3_line_66 |  | 57 | 59 | 0.0018005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2543-4_0_3_line_67 |  | 59 | 65 | 0.018752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2543-4_0_3_line_68 |  | 60 | 61 | 0.023923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2543-4_0_3_line_69 |  | 63 | 64 | 0.01729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2543-4_0_3_line_70 |  | 63 | 65 | 0.0023977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2543-4_0_3_line_71 |  | 64 | 66 | 0.0022408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2543-4_0_3_line_72 |  | 66 | 67 | 0.0046586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2543-4_0_3_line_73 |  | 67 | 68 | 0.020003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2543-4_0_3_line_74 |  | 68 | 69 | 0.0048688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2543-4_0_3_line_75 |  | 69 | 70 | 0.022659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2543-4_0_3_line_76 |  | 70 | 71 | 0.0030197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2543-4_0_3_line_77 |  | 71 | 72 | 0.017798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2543-4_0_3_line_78 |  | 72 | 81 | 0.0070843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2543-4_0_3_line_79 |  | 73 | 74 | 0.024766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2543-4_0_3_line_80 |  | 73 | 75 | 0.0086642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2543-4_0_3_line_81 |  | 74 | 76 | 0.019434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2543-4_0_3_line_82 |  | 76 | 77 | 0.019404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2543-4_0_3_line_83 |  | 77 | 79 | 0.018947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2543-4_0_3_line_84 |  | 78 | 80 | 0.029126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2543-4_0_3_line_85 |  | 80 | 103 | 0.017487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2543-4_0_3_line_86 |  | 81 | 82 | 0.00082515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2543-4_0_3_line_87 |  | 82 | 83 | 0.023402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2543-4_0_3_line_88 |  | 83 | 111 | 0.00052685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2543-4_0_3_line_89 |  | 84 | 85 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2543-4_0_3_line_90 |  | 85 | 86 | 0.013062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2543-4_0_3_line_91 |  | 86 | 87 | 0.015921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2543-4_0_3_line_92 |  | 87 | 88 | 0.034972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2543-4_0_3_line_93 |  | 88 | 89 | 0.021507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2543-4_0_3_line_94 |  | 89 | 90 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2543-4_0_3_line_95 |  | 90 | 117 | 0.018829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2543-4_0_3_line_96 |  | 91 | 92 | 0.0098552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2543-4_0_3_line_97 |  | 91 | 93 | 0.020086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2543-4_0_3_line_98 |  | 92 | 94 | 0.018378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2543-4_0_3_line_99 |  | 93 | 95 | 0.002776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2543-4_0_3_line_100 |  | 94 | 96 | 0.0062189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2543-4_0_3_line_101 |  | 95 | 97 | 0.017785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2543-4_0_3_line_102 |  | 95 | 98 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2543-4_0_3_line_103 |  | 96 | 99 | 0.014346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2543-4_0_3_line_104 |  | 98 | 100 | 0.008912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2543-4_0_3_line_105 |  | 99 | 101 | 0.0072377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2543-4_0_3_line_106 |  | 100 | 136 | 0.029251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2543-4_0_3_line_107 |  | 101 | 102 | 0.019816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2543-4_0_3_line_108 |  | 102 | 103 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2543-4_0_3_line_109 |  | 103 | 122 | 0.017151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2543-4_0_3_line_110 |  | 104 | 105 | 0.00062171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2543-4_0_3_line_111 |  | 104 | 106 | 0.016775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2543-4_0_3_line_112 |  | 105 | 107 | 1.5515e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2543-4_0_3_line_113 |  | 106 | 108 | 0.001316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2543-4_0_3_line_114 |  | 108 | 109 | 0.0066387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2543-4_0_3_line_115 |  | 109 | 110 | 0.006657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2543-4_0_3_line_116 |  | 110 | 131 | 0.055789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2543-4_0_3_line_117 |  | 112 | 137 | 0.013069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2543-4_0_3_line_118 |  | 113 | 114 | 0.021387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2543-4_0_3_line_119 |  | 114 | 115 | 0.0030656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2543-4_0_3_line_120 |  | 115 | 116 | 0.004118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2543-4_0_3_line_121 |  | 116 | 119 | 0.0028168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2543-4_0_3_line_122 |  | 117 | 118 | 0.0097995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2543-4_0_3_line_123 |  | 118 | 121 | 0.0035005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2543-4_0_3_line_124 |  | 119 | 120 | 0.002801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2543-4_0_3_line_125 |  | 120 | 137 | 0.001996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2543-4_0_3_line_126 |  | 122 | 123 | 0.0073844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2543-4_0_3_line_127 |  | 123 | 124 | 0.017184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2543-4_0_3_line_128 |  | 124 | 125 | 0.043362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2543-4_0_3_line_129 |  | 124 | 126 | 0.035232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2543-4_0_3_line_130 |  | 125 | 127 | 0.025223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2543-4_0_3_line_131 |  | 127 | 135 | 0.025935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2543-4_0_3_line_132 |  | 128 | 129 | 0.024281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_2543-4_0_3_line_133 |  | 129 | 130 | 0.002108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
134 | LV_2543-4_0_3_line_134 |  | 130 | 133 | 0.023714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_2543-4_0_3_line_135 |  | 131 | 132 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2543-4_0_3_line_136 |  | 132 | 141 | 0.047988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2543-4_0_3_line_137 |  | 132 | 139 | 0.043097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2543-4_0_3_line_138 |  | 133 | 134 | 0.0019896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_2543-4_0_3_line_139 |  | 138 | 139 | 0.0031974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2543-4_0_3_line_140 |  | 138 | 140 | 0.0054707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2543-4_0_3_line_141 |  | 141 | 142 | 0.042626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2543-4_0_3_trafo_119 | 0.63 MVA 20/0.4 kV | 143 | 134 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2599116.4402 | 1227649.7066 | 2599116.9064 | 1227648.7215
1 | 2599116.4402 | 1227649.7066 | 2599107.2469 | 1227669.1338
2 | 2599096.2906 | 1227692.2866 | 2599107.2469 | 1227669.1338
3 | 2599105.4974 | 1227694.6976 | 2599096.2906 | 1227692.2866
4 | 2599096.2906 | 1227692.2866 | 2599084.3425 | 1227689.676
5 | 2599105.4974 | 1227694.6976 | 2599096.1206 | 1227717.9674
6 | 2599105.4974 | 1227694.6976 | 2599115.2043 | 1227697.1975 | 2599115.6898 | 1227697.3357
7 | 2599077.8847 | 1227688.265 | 2599084.3425 | 1227689.676
8 | 2599095.3841 | 1227719.7952 | 2599096.1206 | 1227717.9674
9 | 2599115.6898 | 1227697.3357 | 2599120.378 | 1227698.6702
10 | 2599077.8847 | 1227688.265 | 2599069.5898 | 1227707.5219
11 | 2599077.8847 | 1227688.265 | 2599072.2227 | 1227687.0752
12 | 2599088.2811 | 1227875.7516 | 2599096.5027 | 1227858.8009
13 | 2599088.2811 | 1227875.7516 | 2599087.5745 | 1227877.2085
14 | 2599096.5027 | 1227858.8009 | 2599099.3033 | 1227853.027
15 | 2599073.0038 | 1227906.8059 | 2599077.1016 | 1227898.8004 | 2599087.5745 | 1227877.2085
16 | 2599099.3033 | 1227853.027 | 2599101.499 | 1227848.5001 | 2599103.6664 | 1227844.5341
17 | 2599073.0038 | 1227906.8059 | 2599090.4629 | 1227913.7494
18 | 2599073.0038 | 1227906.8059 | 2599063.8021 | 1227926.2784
19 | 2599073.0038 | 1227906.8059 | 2599041.579 | 1227892.877
20 | 2599107.2947 | 1227837.8952 | 2599103.6664 | 1227844.5341
21 | 2599090.4629 | 1227913.7494 | 2599108.8355 | 1227921.0563
22 | 2599041.4162 | 1227892.8048 | 2599041.579 | 1227892.877
23 | 2599107.2947 | 1227837.8952 | 2599110.8993 | 1227831.2995 | 2599115.5754 | 1227825.0901
24 | 2599041.4162 | 1227892.8048 | 2599029.0347 | 1227887.3168
25 | 2598962.5537 | 1227946.6712 | 2598963.1293 | 1227945.526 | 2598964.2809 | 1227944.8698 | 2598966.1751 | 1227944.7027
26 | 2598977.5334 | 1227946.8352 | 2598966.1751 | 1227944.7027
27 | 2598938.7984 | 1227899.0031 | 2598962.5537 | 1227946.6712
28 | 2598938.7984 | 1227899.0031 | 2598940.469 | 1227895.2358
29 | 2598938.7984 | 1227899.0031 | 2598930.9858 | 1227895.3024 | 2598923.1732 | 1227891.6129 | 2598904.1082 | 1227881.5713
30 | 2598940.469 | 1227895.2358 | 2598951.1214 | 1227871.2126
31 | 2598886.4539 | 1227872.7665 | 2598894.0971 | 1227876.2984 | 2598904.1082 | 1227881.5713
32 | 2598863.3649 | 1227866.011 | 2598852.7471 | 1227865.8562 | 2598846.0744 | 1227865.8184
33 | 2598886.4539 | 1227872.7665 | 2598883.1549 | 1227871.2421 | 2598876.9032 | 1227868.4417 | 2598871.7505 | 1227866.7639 | 2598864.7795 | 1227866.0316 | 2598863.3649 | 1227866.011
34 | 2598820.5445 | 1227865.6739 | 2598846.0744 | 1227865.8184
35 | 2598820.5445 | 1227865.6739 | 2598803.3294 | 1227865.155 | 2598797.8428 | 1227864.8316
36 | 2599066.9047 | 1227653.0983 | 2599066.6645 | 1227653.8133
37 | 2599040.7865 | 1227645.3572 | 2599066.6645 | 1227653.8133
38 | 2599040.7865 | 1227645.3572 | 2599037.1598 | 1227661.8564 | 2599036.762 | 1227663.091
39 | 2599031.7752 | 1227678.5672 | 2599057.8496 | 1227684.0548
40 | 2599057.8496 | 1227684.0548 | 2599072.2227 | 1227687.0752
41 | 2599031.7752 | 1227678.5672 | 2599036.762 | 1227663.091
42 | 2599028.5334 | 1227685.3718 | 2599031.7752 | 1227678.5672
43 | 2599028.5334 | 1227685.3718 | 2599021.8683 | 1227701.8827 | 2599020.3876 | 1227705.3677
44 | 2599028.5334 | 1227685.3718 | 2599019.6371 | 1227682.5606 | 2599009.8619 | 1227679.4792
45 | 2599197.5757 | 1227720.5107 | 2599200.4113 | 1227715.9268
46 | 2599203.9187 | 1227710.2566 | 2599200.4113 | 1227715.9268
47 | 2599189.3987 | 1227733.7298 | 2599197.5757 | 1227720.5107
48 | 2599203.9187 | 1227710.2566 | 2599213.0996 | 1227695.4146
49 | 2599189.3987 | 1227733.7298 | 2599223.5002 | 1227760.9965 | 2599229.4567 | 1227766.1463
50 | 2599186.2008 | 1227731.3066 | 2599189.3987 | 1227733.7298
51 | 2599213.2953 | 1227695.0982 | 2599213.0996 | 1227695.4146
52 | 2599229.4567 | 1227766.1463 | 2599244.0974 | 1227778.804 | 2599246.5933 | 1227780.9818
53 | 2599186.2008 | 1227731.3066 | 2599176.6502 | 1227724.5602
54 | 2599186.2008 | 1227731.3066 | 2599174.136 | 1227747.3275
55 | 2599213.4883 | 1227694.7862 | 2599213.2953 | 1227695.0982
56 | 2599254.4036 | 1227787.7968 | 2599246.5933 | 1227780.9818
57 | 2599165.8086 | 1227717.3126 | 2599168.4985 | 1227718.8019 | 2599176.6502 | 1227724.5602
58 | 2599159.4304 | 1227766.855 | 2599174.136 | 1227747.3275
59 | 2599213.4883 | 1227694.7862 | 2599214.5644 | 1227693.0466 | 2599215.0898 | 1227691.9168
60 | 2599019.4761 | 1227883.08 | 2599029.0347 | 1227887.3168
61 | 2599016.8159 | 1227881.9009 | 2599019.4761 | 1227883.08
62 | 2599016.8159 | 1227881.9009 | 2599024.1785 | 1227868.803 | 2599032.2088 | 1227853.8561
63 | 2599016.8159 | 1227881.9009 | 2599006.0671 | 1227876.4146
64 | 2599032.2088 | 1227853.8561 | 2599032.6555 | 1227853.0245
65 | 2599006.0671 | 1227876.4146 | 2598996.7895 | 1227871.6792
66 | 2599032.6555 | 1227853.0245 | 2599033.5077 | 1227851.4384
67 | 2599042.1845 | 1227834.8179 | 2599039.5246 | 1227840.239 | 2599033.5077 | 1227851.4384
68 | 2599129.9667 | 1227805.9799 | 2599115.5754 | 1227825.0901
69 | 2599043.2407 | 1227832.6653 | 2599050.857 | 1227817.1428
70 | 2599042.1845 | 1227834.8179 | 2599043.2407 | 1227832.6653
71 | 2599051.844 | 1227815.1311 | 2599050.857 | 1227817.1428
72 | 2599051.844 | 1227815.1311 | 2599053.8961 | 1227810.9488
73 | 2599053.8961 | 1227810.9488 | 2599062.7074 | 1227792.9908
74 | 2599064.852 | 1227788.6199 | 2599062.7074 | 1227792.9908
75 | 2599064.852 | 1227788.6199 | 2599073.2993 | 1227771.4037 | 2599074.6804 | 1227768.2075
76 | 2599075.8782 | 1227765.4356 | 2599074.6804 | 1227768.2075
77 | 2599075.8782 | 1227765.4356 | 2599082.9378 | 1227749.0981
78 | 2599082.9378 | 1227749.0981 | 2599085.7478 | 1227742.595
79 | 2599001.5985 | 1227676.8744 | 2598977.9778 | 1227669.4286
80 | 2599001.5985 | 1227676.8744 | 2599009.8619 | 1227679.4792
81 | 2598959.4431 | 1227663.5859 | 2598977.9778 | 1227669.4286
82 | 2598959.4431 | 1227663.5859 | 2598940.9363 | 1227657.7521
83 | 2598922.8655 | 1227652.0558 | 2598940.9363 | 1227657.7521
84 | 2599008.9985 | 1227732.1746 | 2599020.3876 | 1227705.3677
85 | 2599002.1606 | 1227748.2691 | 2599008.9985 | 1227732.1746
86 | 2599085.7478 | 1227742.595 | 2599086.0751 | 1227741.8375
87 | 2599095.1872 | 1227720.2838 | 2599092.4016 | 1227727.1967 | 2599086.0751 | 1227741.8375
88 | 2599095.1872 | 1227720.2838 | 2599095.3841 | 1227719.7952
89 | 2599204.0105 | 1227856.7891 | 2599192.406 | 1227873.3159
90 | 2599204.0105 | 1227856.7891 | 2599211.518 | 1227846.1004
91 | 2599211.518 | 1227846.1004 | 2599220.6691 | 1227833.0718
92 | 2599241.273 | 1227804.8147 | 2599221.6993 | 1227831.605 | 2599220.6691 | 1227833.0718
93 | 2599254.4036 | 1227787.7968 | 2599249.1005 | 1227794.1013 | 2599241.273 | 1227804.8147
94 | 2599254.4036 | 1227787.7968 | 2599264.8353 | 1227796.2318
95 | 2599264.8353 | 1227796.2318 | 2599266.8997 | 1227797.9011 | 2599280.2726 | 1227806.9996
96 | 2598966.8683 | 1227833.7392 | 2598970.6297 | 1227824.63
97 | 2598959.2022 | 1227852.305 | 2598966.8683 | 1227833.7392
98 | 2598977.6438 | 1227807.6435 | 2598970.6297 | 1227824.63
99 | 2598959.2022 | 1227852.305 | 2598958.1191 | 1227854.8623
100 | 2598980.0173 | 1227801.8954 | 2598977.6438 | 1227807.6435
101 | 2598958.1191 | 1227854.8623 | 2598952.613 | 1227867.8488 | 2598951.1214 | 1227871.2126
102 | 2598958.1191 | 1227854.8623 | 2598942.7694 | 1227845.8333
103 | 2598985.4924 | 1227788.6358 | 2598980.0173 | 1227801.8954
104 | 2598935.0878 | 1227841.3149 | 2598942.7694 | 1227845.8333
105 | 2598985.4924 | 1227788.6358 | 2598988.2548 | 1227781.946
106 | 2598935.0878 | 1227841.3149 | 2598926.8677 | 1227836.4796 | 2598909.1676 | 1227827.7989
107 | 2598988.2548 | 1227781.946 | 2598995.8179 | 1227763.6297
108 | 2599002.1606 | 1227748.2691 | 2598995.8179 | 1227763.6297
109 | 2599002.1606 | 1227748.2691 | 2598986.3441 | 1227741.6355
110 | 2599215.3586 | 1227691.339 | 2599215.0964 | 1227691.9028
111 | 2599222.4328 | 1227676.1284 | 2599215.3586 | 1227691.339
112 | 2599215.0964 | 1227691.9028 | 2599215.0898 | 1227691.9168
113 | 2599222.4328 | 1227676.1284 | 2599222.9877 | 1227674.9352
114 | 2599225.7873 | 1227668.9157 | 2599222.9877 | 1227674.9352
115 | 2599228.5946 | 1227662.8796 | 2599225.7873 | 1227668.9157
116 | 2599252.1214 | 1227612.2937 | 2599228.5946 | 1227662.8796
117 | 2599154.2613 | 1227711.2028 | 2599158.2001 | 1227713.1001 | 2599165.8086 | 1227717.3126
118 | 2599140.6885 | 1227705.342 | 2599138.9981 | 1227704.6982 | 2599126.798 | 1227700.4976 | 2599120.378 | 1227698.6702
119 | 2599143.5534 | 1227706.4331 | 2599140.6885 | 1227705.342
120 | 2599143.5534 | 1227706.4331 | 2599147.4017 | 1227707.8987
121 | 2599147.4017 | 1227707.8987 | 2599147.4017 | 1227707.8987 | 2599149.9395 | 1227709.1211
122 | 2599288.4521 | 1227812.3947 | 2599284.3969 | 1227809.8057 | 2599280.2726 | 1227806.9996
123 | 2599288.4521 | 1227812.3947 | 2599291.4025 | 1227814.2784
124 | 2599152.463 | 1227710.3366 | 2599149.9395 | 1227709.1211
125 | 2599154.2613 | 1227711.2028 | 2599152.463 | 1227710.3366
126 | 2598986.3441 | 1227741.6355 | 2598979.5344 | 1227738.7794
127 | 2598963.6881 | 1227732.1333 | 2598979.5344 | 1227738.7794
128 | 2598963.6881 | 1227732.1333 | 2598967.4434 | 1227716.1677 | 2598967.0789 | 1227711.9764 | 2598963.6078 | 1227708.1525 | 2598946.7816 | 1227703.0269
129 | 2598963.6881 | 1227732.1333 | 2598961.7877 | 1227740.2162 | 2598958.6815 | 1227742.5849 | 2598956.3022 | 1227742.4074 | 2598936.5154 | 1227736.5477
130 | 2598922.6528 | 1227695.6768 | 2598946.7816 | 1227703.0269
131 | 2598897.8431 | 1227688.1193 | 2598922.6528 | 1227695.6768
132 | 2599069.5898 | 1227707.5219 | 2599059.984 | 1227729.8221
133 | 2599059.984 | 1227729.8221 | 2599059.15 | 1227731.7581
134 | 2599049.7685 | 1227753.5378 | 2599059.15 | 1227731.7581
135 | 2599252.1214 | 1227612.2937 | 2599276.9543 | 1227625.6982
136 | 2599276.9543 | 1227625.6982 | 2599298.9984 | 1227638.3027 | 2599315.5485 | 1227646.8612 | 2599319.0949 | 1227648.6284
137 | 2599276.9543 | 1227625.6982 | 2599258.829 | 1227664.798
138 | 2599048.9814 | 1227755.3651 | 2599049.7685 | 1227753.5378
139 | 2599257.4842 | 1227667.6988 | 2599258.829 | 1227664.798
140 | 2599255.1834 | 1227672.6622 | 2599257.4842 | 1227667.6988
141 | 2599319.0949 | 1227648.6284 | 2599304.0802 | 1227688.5228

## bus_geodata
| x | y | coords
0 | 2599116.4402 | 1227649.7066
1 | 2599116.9064 | 1227648.7215
2 | 2599107.2469 | 1227669.1338
3 | 2599096.2906 | 1227692.2866
4 | 2599105.4974 | 1227694.6976
5 | 2599084.3425 | 1227689.676
6 | 2599096.1206 | 1227717.9674
7 | 2599115.6898 | 1227697.3357
8 | 2599077.8847 | 1227688.265
9 | 2599088.2811 | 1227875.7516
10 | 2599096.5027 | 1227858.8009
11 | 2599087.5745 | 1227877.2085
12 | 2599099.3033 | 1227853.027
13 | 2599073.0038 | 1227906.8059
14 | 2599103.6664 | 1227844.5341
15 | 2599090.4629 | 1227913.7494
16 | 2599063.8021 | 1227926.2784
17 | 2599041.579 | 1227892.877
18 | 2599107.2947 | 1227837.8952
19 | 2599108.8355 | 1227921.0563
20 | 2599041.4162 | 1227892.8048
21 | 2598966.1751 | 1227944.7027
22 | 2598962.5537 | 1227946.6712
23 | 2598977.5334 | 1227946.8352
24 | 2598938.7984 | 1227899.0031
25 | 2598940.469 | 1227895.2358
26 | 2598904.1082 | 1227881.5713
27 | 2598863.3649 | 1227866.011
28 | 2598846.0744 | 1227865.8184
29 | 2598886.4539 | 1227872.7665
30 | 2598820.5445 | 1227865.6739
31 | 2598797.8428 | 1227864.8316
32 | 2599066.9047 | 1227653.0983
33 | 2599066.6645 | 1227653.8133
34 | 2599040.7864 | 1227645.3572
35 | 2599057.8496 | 1227684.0548
36 | 2599031.7752 | 1227678.5672
37 | 2599072.2227 | 1227687.0752
38 | 2599036.762 | 1227663.091
39 | 2599028.5334 | 1227685.3718
40 | 2599200.4113 | 1227715.9268
41 | 2599197.5757 | 1227720.5107
42 | 2599203.9187 | 1227710.2566
43 | 2599189.3987 | 1227733.7298
44 | 2599213.0996 | 1227695.4146
45 | 2599229.4567 | 1227766.1463
46 | 2599186.2008 | 1227731.3066
47 | 2599213.2953 | 1227695.0982
48 | 2599246.5933 | 1227780.9818
49 | 2599176.6502 | 1227724.5602
50 | 2599174.136 | 1227747.3275
51 | 2599213.4883 | 1227694.7862
52 | 2599019.4761 | 1227883.08
53 | 2599029.0347 | 1227887.3168
54 | 2599016.8159 | 1227881.9009
55 | 2599032.2088 | 1227853.8561
56 | 2599006.0671 | 1227876.4146
57 | 2599032.6555 | 1227853.0245
58 | 2598996.7895 | 1227871.6792
59 | 2599033.5077 | 1227851.4384
60 | 2599115.5754 | 1227825.0901
61 | 2599129.9667 | 1227805.9799
62 | 2599159.4304 | 1227766.855
63 | 2599043.2407 | 1227832.6653
64 | 2599050.857 | 1227817.1428
65 | 2599042.1845 | 1227834.8179
66 | 2599051.844 | 1227815.1311
67 | 2599053.8961 | 1227810.9488
68 | 2599062.7074 | 1227792.9908
69 | 2599064.852 | 1227788.6199
70 | 2599074.6804 | 1227768.2075
71 | 2599075.8782 | 1227765.4356
72 | 2599082.9378 | 1227749.0981
73 | 2599001.5985 | 1227676.8744
74 | 2598977.9778 | 1227669.4286
75 | 2599009.8619 | 1227679.4792
76 | 2598959.4431 | 1227663.5859
77 | 2598940.9363 | 1227657.7521
78 | 2599020.3876 | 1227705.3677
79 | 2598922.8655 | 1227652.0558
80 | 2599008.9985 | 1227732.1746
81 | 2599085.7478 | 1227742.595
82 | 2599086.0751 | 1227741.8375
83 | 2599095.1872 | 1227720.2838
84 | 2599192.406 | 1227873.3159
85 | 2599204.0105 | 1227856.7891
86 | 2599211.518 | 1227846.1004
87 | 2599220.6691 | 1227833.0718
88 | 2599241.273 | 1227804.8147
89 | 2599254.4036 | 1227787.7968
90 | 2599264.8353 | 1227796.2318
91 | 2598966.8683 | 1227833.7392
92 | 2598970.6297 | 1227824.63
93 | 2598959.2022 | 1227852.305
94 | 2598977.6438 | 1227807.6435
95 | 2598958.1191 | 1227854.8623
96 | 2598980.0173 | 1227801.8954
97 | 2598951.1214 | 1227871.2126
98 | 2598942.7694 | 1227845.8333
99 | 2598985.4924 | 1227788.6358
100 | 2598935.0878 | 1227841.3149
101 | 2598988.2548 | 1227781.946
102 | 2598995.8179 | 1227763.6297
103 | 2599002.1606 | 1227748.2691
104 | 2599215.3586 | 1227691.339
105 | 2599215.0964 | 1227691.9028
106 | 2599222.4328 | 1227676.1284
107 | 2599215.0898 | 1227691.9168
108 | 2599222.9877 | 1227674.9352
109 | 2599225.7873 | 1227668.9157
110 | 2599228.5946 | 1227662.8796
111 | 2599095.3841 | 1227719.7952
112 | 2599165.8086 | 1227717.3126
113 | 2599120.378 | 1227698.6702
114 | 2599140.6885 | 1227705.342
115 | 2599143.5534 | 1227706.4331
116 | 2599147.4017 | 1227707.8987
117 | 2599280.2726 | 1227806.9996
118 | 2599288.4521 | 1227812.3947
119 | 2599149.9395 | 1227709.1211
120 | 2599152.463 | 1227710.3366
121 | 2599291.4025 | 1227814.2784
122 | 2598986.3441 | 1227741.6355
123 | 2598979.5344 | 1227738.7794
124 | 2598963.6881 | 1227732.1333
125 | 2598946.7816 | 1227703.0269
126 | 2598936.5154 | 1227736.5477
127 | 2598922.6528 | 1227695.6768
128 | 2599069.5898 | 1227707.5219
129 | 2599059.984 | 1227729.8221
130 | 2599059.15 | 1227731.7581
131 | 2599252.1214 | 1227612.2937
132 | 2599276.9543 | 1227625.6982
133 | 2599049.7685 | 1227753.5378
134 | 2599048.9814 | 1227755.3651
135 | 2598897.8431 | 1227688.1193
136 | 2598909.1676 | 1227827.7989
137 | 2599154.2613 | 1227711.2028
138 | 2599257.4842 | 1227667.6988
139 | 2599258.829 | 1227664.798
140 | 2599255.1834 | 1227672.6622
141 | 2599319.0949 | 1227648.6284
142 | 2599304.0802 | 1227688.5228
143 | 2599077.8847 | 1227688.265

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99045 | -0.18154 | 0.0015805 | 0.00039611
1 | 0.99045 | -0.18157 | 0.00162 | 0.00040602
2 | 0.99052 | -0.18031 | 0.0027101 | 0.00067921
3 | 0.99066 | -0.17762 | 0 | 0
4 | 0.98984 | -0.19323 | 0 | 0
5 | 0.99174 | -0.15691 | 0.0019922 | 0.00049928
6 | 0.98752 | -0.23789 | 0.0042757 | 0.0010716
7 | 0.98902 | -0.20919 | 0.0039391 | 0.00098723
8 | 0.99213 | -0.14938 | 0 | 0
9 | 0.97295 | -0.52204 | 0.0065267 | 0.0016357
10 | 0.97264 | -0.5281 | 0.0018039 | 0.00045211
11 | 0.97298 | -0.52133 | 0.0022762 | 0.00057047
12 | 0.97255 | -0.52995 | 0.0011519 | 0.00028869
13 | 0.97379 | -0.50539 | 0 | 0
14 | 0.97242 | -0.5325 | 0.0018841 | 0.00047221
15 | 0.97371 | -0.50697 | 0.0036266 | 0.00090892
16 | 0.97373 | -0.50648 | 0.0027554 | 0.00069058
17 | 0.97486 | -0.4842 | 0.0048814 | 0.0012234
18 | 0.97233 | -0.53426 | 0.0015879 | 0.00039797
19 | 0.97369 | -0.50731 | 0.00094149 | 0.00023596
20 | 0.97487 | -0.48407 | 0.0013165 | 0.00032996
21 | 0.97275 | -0.5258 | 0.0022977 | 0.00057585
22 | 0.97278 | -0.52519 | 0.0080767 | 0.0020242
23 | 0.97269 | -0.5269 | 0.0051575 | 0.0012926
24 | 0.97355 | -0.50996 | 0 | 0
25 | 0.97369 | -0.50726 | 0.0077732 | 0.0019482
26 | 0.97282 | -0.52436 | 0.005008 | 0.0012551
27 | 0.97233 | -0.53402 | 0.0011634 | 0.00029157
28 | 0.9722 | -0.5366 | 0.00152 | 0.00038094
29 | 0.97254 | -0.52986 | 0.0058783 | 0.0014732
30 | 0.97205 | -0.53969 | 0 | 0
31 | 0.97191 | -0.54245 | 0.0065746 | 0.0016477
32 | 0.98979 | -0.19429 | 0.0021974 | 0.00055072
33 | 0.98979 | -0.19426 | 0 | 0
34 | 0.98984 | -0.1932 | 0 | 0
35 | 0.99119 | -0.16743 | 0 | 0
36 | 0.98997 | -0.19074 | 0 | 0
37 | 0.99186 | -0.15456 | 0.0035385 | 0.00088684
38 | 0.98988 | -0.19249 | 0.0038539 | 0.00096589
39 | 0.98947 | -0.20027 | 0 | 0
40 | 0.98313 | -0.32339 | 0.00031777 | 7.964e-05
41 | 0.98332 | -0.31973 | 0.0021806 | 0.00054651
42 | 0.9829 | -0.32788 | 0.00031824 | 7.9759e-05
43 | 0.98389 | -0.30858 | 0 | 0
44 | 0.9823 | -0.33953 | 0.0014252 | 0.00035719
45 | 0.98339 | -0.31848 | 0.00081465 | 0.00020417
46 | 0.98408 | -0.30494 | 0 | 0
47 | 0.98229 | -0.33977 | 0.00028227 | 7.0744e-05
48 | 0.98318 | -0.3225 | 0.00037911 | 9.5013e-05
49 | 0.98469 | -0.2931 | 0.0021781 | 0.00054587
50 | 0.98397 | -0.30704 | 0.0035868 | 0.00089895
51 | 0.98228 | -0.34001 | 0.0014231 | 0.00035667
52 | 0.97578 | -0.46613 | 0.0015829 | 0.00039671
53 | 0.97537 | -0.47419 | 0.0023194 | 0.00058131
54 | 0.9759 | -0.46381 | 0 | 0
55 | 0.97735 | -0.43546 | 0.0017739 | 0.00044457
56 | 0.97585 | -0.46487 | 0.0017855 | 0.0004475
57 | 0.97739 | -0.43459 | 0.0029655 | 0.00074323
58 | 0.97582 | -0.46544 | 0.0030171 | 0.00075615
59 | 0.97748 | -0.43284 | 0.0025408 | 0.00063677
60 | 0.97217 | -0.53737 | 0.004676 | 0.0011719
61 | 0.97203 | -0.54017 | 0.0063498 | 0.0015914
62 | 0.98392 | -0.30802 | 0.0022224 | 0.00055699
63 | 0.97858 | -0.41127 | 0.0019698 | 0.00049369
64 | 0.97954 | -0.39257 | 0.0054397 | 0.0013633
65 | 0.97845 | -0.41378 | 0.0017294 | 0.00043343
66 | 0.97967 | -0.38993 | 0.0018051 | 0.0004524
67 | 0.97996 | -0.38429 | 0.0022768 | 0.00057061
68 | 0.98125 | -0.35927 | 0.0027591 | 0.00069149
69 | 0.98157 | -0.35295 | 0.0035456 | 0.00088862
70 | 0.98316 | -0.32214 | 0.0025509 | 0.00063933
71 | 0.98338 | -0.3179 | 0.002716 | 0.00068069
72 | 0.98471 | -0.29209 | 0.0039724 | 0.00099557
73 | 0.98868 | -0.2156 | 0.0038544 | 0.000966
74 | 0.98818 | -0.22533 | 0.0059471 | 0.0014905
75 | 0.98889 | -0.21161 | 0.0066476 | 0.0016661
76 | 0.9879 | -0.2309 | 0.0084631 | 0.0021211
77 | 0.98776 | -0.23353 | 0.0056682 | 0.0014206
78 | 0.98728 | -0.2425 | 0.004164 | 0.0010436
79 | 0.98773 | -0.23418 | 0.0019283 | 0.00048329
80 | 0.98442 | -0.29758 | 0.003982 | 0.00099799
81 | 0.98527 | -0.28133 | 0.002709 | 0.00067893
82 | 0.98533 | -0.28004 | 0.0031657 | 0.0007934
83 | 0.9873 | -0.24213 | 0.0020861 | 0.00052282
84 | 0.98261 | -0.33361 | 0.0027292 | 0.000684
85 | 0.98266 | -0.33261 | 0 | 0
86 | 0.9827 | -0.33197 | 0.0017235 | 0.00043196
87 | 0.98276 | -0.33069 | 0.0013697 | 0.00034327
88 | 0.98295 | -0.32701 | 0.0012451 | 0.00031204
89 | 0.98309 | -0.32427 | 0 | 0
90 | 0.98306 | -0.32485 | 0.00036042 | 9.033e-05
91 | 0.97669 | -0.44827 | 0.005104 | 0.0012792
92 | 0.97724 | -0.43737 | 0.0057809 | 0.0014488
93 | 0.97565 | -0.46865 | 0 | 0
94 | 0.97838 | -0.41514 | 0.0014107 | 0.00035355
95 | 0.97551 | -0.47147 | 0 | 0
96 | 0.97877 | -0.40747 | 0.0016609 | 0.00041627
97 | 0.97475 | -0.48628 | 0.0019833 | 0.00049706
98 | 0.97534 | -0.47474 | 0.0016841 | 0.00042208
99 | 0.9797 | -0.38936 | 0.0042657 | 0.0010691
100 | 0.97527 | -0.47611 | 0.0031304 | 0.00078456
101 | 0.9802 | -0.37968 | 0.0010464 | 0.00026225
102 | 0.98157 | -0.35285 | 0.0028523 | 0.00071484
103 | 0.98277 | -0.32955 | 0 | 0
104 | 0.98216 | -0.34237 | 0.0016513 | 0.00041386
105 | 0.98218 | -0.34203 | 0.0016578 | 0.00041548
106 | 0.98171 | -0.35114 | 0.0013243 | 0.00033189
107 | 0.98218 | -0.34202 | 0.0016586 | 0.00041567
108 | 0.98168 | -0.35179 | 0.0016356 | 0.00040993
109 | 0.98152 | -0.35491 | 0.0017248 | 0.00043227
110 | 0.98137 | -0.35783 | 0.0017248 | 0.00043227
111 | 0.98734 | -0.24126 | 0.0030588 | 0.0007666
112 | 0.98539 | -0.27939 | 0.0040707 | 0.0010202
113 | 0.98865 | -0.21625 | 0.0041059 | 0.001029
114 | 0.98713 | -0.24571 | 0.0023742 | 0.00059503
115 | 0.98692 | -0.24981 | 0.0015922 | 0.00039903
116 | 0.98664 | -0.2552 | 0.0015781 | 0.00039552
117 | 0.98302 | -0.32554 | 0.00037062 | 9.2887e-05
118 | 0.98301 | -0.32584 | 0.0012328 | 0.00030898
119 | 0.98645 | -0.25881 | 0.0021036 | 0.0005272
120 | 0.98627 | -0.2623 | 0.0016103 | 0.00040358
121 | 0.98301 | -0.32586 | 0.00043096 | 0.00010801
122 | 0.9824 | -0.33694 | 0.0020795 | 0.00052117
123 | 0.98225 | -0.33985 | 0.0011807 | 0.00029592
124 | 0.98192 | -0.34625 | 0 | 0
125 | 0.98152 | -0.35414 | 0.0027816 | 0.00069714
126 | 0.98158 | -0.35297 | 0.010548 | 0.0026435
127 | 0.98135 | -0.35747 | 0.0030961 | 0.00077595
128 | 0.99436 | -0.10683 | 0.0039072 | 0.00097923
129 | 0.99697 | -0.057226 | 0.0022758 | 0.00057037
130 | 0.9972 | -0.052904 | 0.0022362 | 0.00056044
131 | 0.98021 | -0.38056 | 0 | 0
132 | 0.97962 | -0.39206 | 0 | 0
133 | 0.99978 | -0.0041119 | 0.002573 | 0.00064484
134 | 1 | 0 | -0.3635 | -0.093104
135 | 0.98125 | -0.35943 | 0.0041848 | 0.0010488
136 | 0.97513 | -0.4789 | 0.0052159 | 0.0013072
137 | 0.98615 | -0.26473 | 0.0053205 | 0.0013334
138 | 0.97899 | -0.40447 | 0.0055462 | 0.00139
139 | 0.97903 | -0.4037 | 0.0016489 | 0.00041326
140 | 0.97895 | -0.40523 | 0.0076675 | 0.0019216
141 | 0.97928 | -0.39871 | 0 | 0
142 | 0.97898 | -0.40461 | 0.0076233 | 0.0019106
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00162 | 0.000406 | -0.00162 | -0.00040602 | 2.4209e-09 | -1.2477e-08 | 0.0024339 | 0.0024339 | 0.0024339 | 0.99045 | -0.18154 | 0.99045 | -0.18157 | 0.66864
1 | -0.0032005 | -0.00080212 | 0.0032007 | 0.00080196 | 1.8634e-07 | -1.5737e-07 | 0.0048083 | 0.0048082 | 0.0048083 | 0.99045 | -0.18154 | 0.99052 | -0.18031 | 1.321
2 | -0.0059108 | -0.0014812 | 0.0059115 | 0.0014813 | 7.5733e-07 | 1.5495e-07 | 0.0088795 | 0.0088794 | 0.0088795 | 0.99052 | -0.18031 | 0.99066 | -0.17762 | 2.4394
3 | 0.18675 | 0.047481 | -0.18661 | -0.047392 | 0.00014027 | 8.9526e-05 | 0.28075 | 0.28075 | 0.28075 | 0.99066 | -0.17762 | 0.98984 | -0.19323 | 38.5645
4 | -0.19266 | -0.048963 | 0.19285 | 0.049086 | 0.00019236 | 0.00012279 | 0.28963 | 0.28963 | 0.28963 | 0.99066 | -0.17762 | 0.99174 | -0.15691 | 39.7841
5 | 0.10093 | 0.025719 | -0.10071 | -0.02558 | 0.000217 | 0.00013856 | 0.15187 | 0.15187 | 0.15187 | 0.98984 | -0.19323 | 0.98752 | -0.23789 | 41.7235
6 | 0.085682 | 0.021673 | -0.085617 | -0.021632 | 6.5576e-05 | 4.1833e-05 | 0.12888 | 0.12888 | 0.12888 | 0.98984 | -0.19323 | 0.98902 | -0.20919 | 35.4055
7 | -0.19485 | -0.049585 | 0.19492 | 0.04963 | 7.0749e-05 | 4.5023e-05 | 0.29262 | 0.29262 | 0.29262 | 0.99174 | -0.15691 | 0.99213 | -0.14938 | 26.7965
8 | 0.096434 | 0.024508 | -0.096419 | -0.024498 | 1.5629e-05 | 9.9773e-06 | 0.14543 | 0.14543 | 0.14543 | 0.98752 | -0.23789 | 0.98734 | -0.24126 | 39.9536
9 | 0.081678 | 0.020644 | -0.08165 | -0.020627 | 2.7631e-05 | 1.7621e-05 | 0.12295 | 0.12295 | 0.12295 | 0.98902 | -0.20919 | 0.98865 | -0.21625 | 33.7773
10 | -0.3483 | -0.088712 | 0.34901 | 0.08917 | 0.00071659 | 0.0004578 | 0.52289 | 0.52289 | 0.52289 | 0.99213 | -0.14938 | 0.99436 | -0.10683 | 47.8834
11 | 0.15338 | 0.039082 | -0.15334 | -0.039058 | 3.8347e-05 | 2.4318e-05 | 0.23027 | 0.23027 | 0.23027 | 0.99213 | -0.14938 | 0.99186 | -0.15456 | 21.087
12 | 0.017465 | 0.0043808 | -0.01746 | -0.0043778 | 5.0412e-06 | 2.9925e-06 | 0.026713 | 0.026713 | 0.026713 | 0.97295 | -0.52204 | 0.97264 | -0.5281 | 7.3387
13 | -0.023992 | -0.0060165 | 0.023993 | 0.006017 | 8.1759e-07 | 5.0315e-07 | 0.036695 | 0.036695 | 0.036695 | 0.97295 | -0.52204 | 0.97298 | -0.52133 | 10.0809
14 | 0.015656 | 0.0039257 | -0.015655 | -0.0039249 | 1.3807e-06 | 8.0401e-07 | 0.023953 | 0.023953 | 0.023953 | 0.97264 | -0.5281 | 0.97255 | -0.52995 | 6.5805
15 | -0.026269 | -0.0065875 | 0.026289 | 0.0065999 | 1.9969e-05 | 1.237e-05 | 0.040176 | 0.040176 | 0.040176 | 0.97298 | -0.52133 | 0.97379 | -0.50539 | 11.0373
16 | 0.014503 | 0.0036362 | -0.014501 | -0.0036352 | 1.7637e-06 | 1.0102e-06 | 0.022191 | 0.022191 | 0.022191 | 0.97255 | -0.52995 | 0.97242 | -0.5325 | 6.0963
17 | 0.0045685 | 0.0011446 | -0.0045681 | -0.0011446 | 3.4337e-07 | -1.3974e-08 | 0.0069808 | 0.0069809 | 0.0069809 | 0.97379 | -0.50539 | 0.97371 | -0.50697 | 1.9178
18 | 0.0027556 | 0.0006904 | -0.0027554 | -0.00069058 | 1.4319e-07 | -1.7628e-07 | 0.0042106 | 0.0042107 | 0.0042107 | 0.97379 | -0.50539 | 0.97373 | -0.50648 | 1.1568
19 | -0.033613 | -0.0084349 | 0.033647 | 0.0084563 | 3.4011e-05 | 2.1339e-05 | 0.051367 | 0.051367 | 0.051367 | 0.97379 | -0.50539 | 0.97486 | -0.4842 | 14.1118
20 | 0.012617 | 0.003163 | -0.012616 | -0.0031624 | 1.0576e-06 | 5.8303e-07 | 0.019307 | 0.019308 | 0.019308 | 0.97242 | -0.5325 | 0.97233 | -0.53426 | 5.3043
21 | 0.00094151 | 0.00023572 | -0.00094149 | -0.00023596 | 1.5349e-08 | -2.3611e-07 | 0.0014387 | 0.0014388 | 0.0014388 | 0.97371 | -0.50697 | 0.97369 | -0.50731 | 0.39528
22 | -0.038529 | -0.0096796 | 0.038529 | 0.0096798 | 2.3108e-07 | 1.4567e-07 | 0.058818 | 0.058818 | 0.058818 | 0.97486 | -0.4842 | 0.97487 | -0.48407 | 16.1587
23 | 0.011028 | 0.0027644 | -0.011027 | -0.0027636 | 1.6332e-06 | 8.5564e-07 | 0.016877 | 0.016878 | 0.016878 | 0.97233 | -0.53426 | 0.97217 | -0.53737 | 4.6367
24 | -0.039845 | -0.01001 | 0.039864 | 0.010022 | 1.8791e-05 | 1.1857e-05 | 0.060827 | 0.060827 | 0.060827 | 0.97487 | -0.48407 | 0.97537 | -0.47419 | 16.7108
25 | -0.0074555 | -0.0018685 | 0.0074557 | 0.0018686 | 2.1991e-07 | 8.4769e-08 | 0.011405 | 0.011405 | 0.011405 | 0.97275 | -0.5258 | 0.97278 | -0.52519 | 3.1331
26 | 0.0051578 | 0.0012926 | -0.0051575 | -0.0012926 | 2.6978e-07 | 2.9202e-08 | 0.0078899 | 0.0078899 | 0.0078899 | 0.97275 | -0.5258 | 0.97269 | -0.5269 | 2.1676
27 | -0.015532 | -0.0038928 | 0.015544 | 0.0038993 | 1.1274e-05 | 6.5537e-06 | 0.023759 | 0.023759 | 0.023759 | 0.97278 | -0.52519 | 0.97355 | -0.50996 | 6.5272
28 | -0.03571 | -0.0089605 | 0.035715 | 0.0089634 | 4.6045e-06 | 2.8956e-06 | 0.054585 | 0.054585 | 0.054585 | 0.97355 | -0.50996 | 0.97369 | -0.50726 | 14.9958
29 | 0.020167 | 0.0050611 | -0.020153 | -0.0050528 | 1.3838e-05 | 8.3736e-06 | 0.030826 | 0.030826 | 0.030826 | 0.97355 | -0.50996 | 0.97282 | -0.52436 | 8.4687
30 | -0.043488 | -0.010912 | 0.043532 | 0.010939 | 4.3533e-05 | 2.7534e-05 | 0.066464 | 0.066464 | 0.066464 | 0.97369 | -0.50726 | 0.97475 | -0.48628 | 18.2594
31 | 0.015145 | 0.0037977 | -0.015141 | -0.0037954 | 3.9716e-06 | 2.2969e-06 | 0.023166 | 0.023166 | 0.023166 | 0.97282 | -0.52436 | 0.97254 | -0.52986 | 6.3643
32 | 0.0080974 | 0.0020297 | -0.0080964 | -0.0020293 | 9.9576e-07 | 4.2284e-07 | 0.012392 | 0.012392 | 0.012392 | 0.97233 | -0.53402 | 0.9722 | -0.5366 | 3.4044
33 | -0.0092608 | -0.0023213 | 0.0092626 | 0.0023221 | 1.8324e-06 | 8.7091e-07 | 0.014172 | 0.014172 | 0.014172 | 0.97233 | -0.53402 | 0.97254 | -0.52986 | 3.8935
34 | 0.0065764 | 0.0016483 | -0.0065754 | -0.001648 | 9.7001e-07 | 3.0428e-07 | 0.010066 | 0.010066 | 0.010066 | 0.9722 | -0.5366 | 0.97205 | -0.53969 | 2.7653
35 | 0.0065754 | 0.001648 | -0.0065746 | -0.0016477 | 8.6322e-07 | 2.7087e-07 | 0.010066 | 0.010066 | 0.010066 | 0.97205 | -0.53969 | 0.97191 | -0.54245 | 2.7653
36 | -0.0021974 | -0.00055072 | 0.0021974 | 0.00055071 | 3.0866e-09 | -7.7189e-09 | 0.0033035 | 0.0033035 | 0.0033035 | 0.98979 | -0.19429 | 0.98979 | -0.19426 | 0.90755
37 | -0.0021974 | -0.00055071 | 0.0021975 | 0.00055043 | 1.1112e-07 | -2.779e-07 | 0.0033035 | 0.0033033 | 0.0033035 | 0.98979 | -0.19426 | 0.98984 | -0.1932 | 0.90755
38 | -0.0021975 | -0.00055043 | 0.0021976 | 0.00055024 | 7.4433e-08 | -1.8619e-07 | 0.0033033 | 0.0033033 | 0.0033033 | 0.98984 | -0.1932 | 0.98988 | -0.19249 | 0.90751
39 | 0.14971 | 0.038112 | -0.14954 | -0.038005 | 0.00016809 | 0.00010655 | 0.22496 | 0.22496 | 0.22496 | 0.99119 | -0.16743 | 0.98997 | -0.19074 | 20.6009
40 | -0.14971 | -0.038112 | 0.1498 | 0.038171 | 9.2909e-05 | 5.8894e-05 | 0.22496 | 0.22496 | 0.22496 | 0.99119 | -0.16743 | 0.99186 | -0.15456 | 20.6009
41 | 0.006052 | 0.0015162 | -0.0060515 | -0.0015161 | 5.0455e-07 | 1.1387e-07 | 0.0090965 | 0.0090966 | 0.0090966 | 0.98997 | -0.19074 | 0.98988 | -0.19249 | 2.4991
42 | 0.14349 | 0.036489 | -0.14342 | -0.036447 | 6.5825e-05 | 4.1935e-05 | 0.21587 | 0.21587 | 0.21587 | 0.98997 | -0.19074 | 0.98947 | -0.20027 | 29.6518
43 | 0.11088 | 0.028277 | -0.11065 | -0.028133 | 0.00022559 | 0.0001441 | 0.16692 | 0.16692 | 0.16692 | 0.98947 | -0.20027 | 0.98728 | -0.2425 | 45.8559
44 | 0.032547 | 0.0081704 | -0.032529 | -0.0081594 | 1.7593e-05 | 1.1008e-05 | 0.04895 | 0.04895 | 0.04895 | 0.98947 | -0.20027 | 0.98889 | -0.21161 | 13.4479
45 | -0.037733 | -0.0094937 | 0.03774 | 0.0094979 | 6.5959e-06 | 4.153e-06 | 0.057124 | 0.057124 | 0.057124 | 0.98313 | -0.32339 | 0.98332 | -0.31973 | 15.6935
46 | 0.037416 | 0.0094141 | -0.037408 | -0.009409 | 8.022e-06 | 5.0496e-06 | 0.056644 | 0.056644 | 0.056644 | 0.98313 | -0.32339 | 0.9829 | -0.32788 | 15.5614
47 | -0.039921 | -0.010044 | 0.039942 | 0.010058 | 2.1282e-05 | 1.3423e-05 | 0.060424 | 0.060424 | 0.060424 | 0.98332 | -0.31973 | 0.98389 | -0.30858 | 16.6001
48 | 0.037089 | 0.0093293 | -0.037069 | -0.0093163 | 2.0642e-05 | 1.299e-05 | 0.056162 | 0.056162 | 0.056162 | 0.9829 | -0.32788 | 0.9823 | -0.33953 | 15.4291
49 | 0.010666 | 0.0026743 | -0.010661 | -0.0026717 | 5.0295e-06 | 2.5647e-06 | 0.016132 | 0.016132 | 0.016132 | 0.98389 | -0.30858 | 0.98339 | -0.31848 | 4.4319
50 | -0.050608 | -0.012732 | 0.050617 | 0.012738 | 8.8022e-06 | 5.5826e-06 | 0.076556 | 0.076556 | 0.076556 | 0.98389 | -0.30858 | 0.98408 | -0.30494 | 21.0319
51 | 0.035644 | 0.0089591 | -0.035643 | -0.0089588 | 4.0687e-07 | 2.5569e-07 | 0.054003 | 0.054003 | 0.054003 | 0.9823 | -0.33953 | 0.98229 | -0.33977 | 14.836
52 | 0.0098467 | 0.0024675 | -0.0098448 | -0.0024666 | 1.8869e-06 | 9.2012e-07 | 0.014899 | 0.0149 | 0.0149 | 0.98339 | -0.31848 | 0.98318 | -0.3225 | 4.0933
53 | -0.056427 | -0.014193 | 0.056459 | 0.014214 | 3.1936e-05 | 2.029e-05 | 0.085341 | 0.085341 | 0.085341 | 0.98408 | -0.30494 | 0.98469 | -0.2931 | 23.4454
54 | 0.00581 | 0.0014558 | -0.0058094 | -0.0014557 | 5.8045e-07 | 1.1671e-07 | 0.0087851 | 0.0087852 | 0.0087852 | 0.98408 | -0.30494 | 0.98397 | -0.30704 | 2.4135
55 | 0.035361 | 0.0088881 | -0.03536 | -0.0088878 | 3.949e-07 | 2.4809e-07 | 0.053575 | 0.053575 | 0.053575 | 0.98229 | -0.33977 | 0.98228 | -0.34001 | 14.7185
56 | 0.0094657 | 0.0023716 | -0.0094649 | -0.0023712 | 7.9774e-07 | 3.7911e-07 | 0.014326 | 0.014326 | 0.014326 | 0.98318 | -0.3225 | 0.98309 | -0.32427 | 3.9357
57 | -0.058637 | -0.01476 | 0.058675 | 0.014784 | 3.8459e-05 | 2.4447e-05 | 0.088633 | 0.088632 | 0.088633 | 0.98469 | -0.2931 | 0.98539 | -0.27939 | 24.3496
58 | 0.0022225 | 0.00055675 | -0.0022224 | -0.00055699 | 1.0355e-07 | -2.4422e-07 | 0.0033609 | 0.0033611 | 0.0033611 | 0.98397 | -0.30704 | 0.98392 | -0.30802 | 0.92337
59 | 0.033937 | 0.0085312 | -0.033934 | -0.0085291 | 3.2635e-06 | 2.047e-06 | 0.051419 | 0.05142 | 0.05142 | 0.98228 | -0.34001 | 0.98218 | -0.34202 | 14.1262
60 | 0.0422 | 0.010613 | -0.042184 | -0.010603 | 1.6244e-05 | 1.0265e-05 | 0.064366 | 0.064366 | 0.064366 | 0.97578 | -0.46613 | 0.97537 | -0.47419 | 17.6829
61 | -0.043783 | -0.01101 | 0.043788 | 0.011013 | 4.8661e-06 | 3.0779e-06 | 0.066779 | 0.066779 | 0.066779 | 0.97578 | -0.46613 | 0.9759 | -0.46381 | 18.346
62 | -0.04859 | -0.012217 | 0.048656 | 0.012258 | 6.588e-05 | 4.1763e-05 | 0.074103 | 0.074103 | 0.074103 | 0.9759 | -0.46381 | 0.97735 | -0.43546 | 20.3579
63 | 0.0048029 | 0.0012036 | -0.0048027 | -0.0012036 | 2.4271e-07 | 4.5558e-09 | 0.0073233 | 0.0073233 | 0.0073233 | 0.9759 | -0.46381 | 0.97585 | -0.46487 | 2.0119
64 | -0.05043 | -0.012703 | 0.050432 | 0.012704 | 2.0881e-06 | 1.3245e-06 | 0.076803 | 0.076803 | 0.076803 | 0.97735 | -0.43546 | 0.97739 | -0.43459 | 21.0998
65 | 0.0030172 | 0.00075607 | -0.0030171 | -0.00075615 | 8.2678e-08 | -7.7215e-08 | 0.0046007 | 0.0046007 | 0.0046007 | 0.97585 | -0.46487 | 0.97582 | -0.46544 | 1.2639
66 | -0.053398 | -0.013447 | 0.053402 | 0.01345 | 4.4648e-06 | 2.8349e-06 | 0.081318 | 0.081318 | 0.081318 | 0.97739 | -0.43459 | 0.97748 | -0.43284 | 22.3401
67 | -0.055943 | -0.014087 | 0.055994 | 0.014119 | 5.1028e-05 | 3.2423e-05 | 0.085186 | 0.085186 | 0.085186 | 0.97748 | -0.43284 | 0.97845 | -0.41378 | 23.4027
68 | 0.0063506 | 0.0015916 | -0.0063498 | -0.0015914 | 8.4765e-07 | 2.4591e-07 | 0.0097204 | 0.0097205 | 0.0097205 | 0.97217 | -0.53737 | 0.97203 | -0.54017 | 2.6705
69 | -0.0597 | -0.015051 | 0.059754 | 0.015085 | 5.347e-05 | 3.4004e-05 | 0.090811 | 0.090811 | 0.090811 | 0.97858 | -0.41127 | 0.97954 | -0.39257 | 24.9481
70 | 0.05773 | 0.014557 | -0.057723 | -0.014553 | 6.9339e-06 | 4.4076e-06 | 0.087816 | 0.087816 | 0.087816 | 0.97858 | -0.41127 | 0.97845 | -0.41378 | 24.1252
71 | -0.065193 | -0.016448 | 0.065202 | 0.016454 | 8.2483e-06 | 5.2507e-06 | 0.099074 | 0.099074 | 0.099074 | 0.97954 | -0.39257 | 0.97967 | -0.38993 | 27.2183
72 | -0.067007 | -0.016906 | 0.067025 | 0.016917 | 1.811e-05 | 1.1532e-05 | 0.10182 | 0.10182 | 0.10182 | 0.97967 | -0.38993 | 0.97996 | -0.38429 | 27.9715
73 | -0.069302 | -0.017488 | 0.069385 | 0.017541 | 8.3131e-05 | 5.2952e-05 | 0.10527 | 0.10527 | 0.10527 | 0.97996 | -0.38429 | 0.98125 | -0.35927 | 28.9212
74 | -0.072144 | -0.018233 | 0.072166 | 0.018246 | 2.1874e-05 | 1.3938e-05 | 0.10946 | 0.10946 | 0.10946 | 0.98125 | -0.35927 | 0.98157 | -0.35295 | 30.0707
75 | -0.075711 | -0.019135 | 0.075823 | 0.019207 | 0.00011205 | 7.1422e-05 | 0.11483 | 0.11483 | 0.11483 | 0.98157 | -0.35295 | 0.98316 | -0.32214 | 31.5473
76 | -0.078374 | -0.019846 | 0.07839 | 0.019856 | 1.5953e-05 | 1.0172e-05 | 0.11869 | 0.11869 | 0.11869 | 0.98316 | -0.32214 | 0.98338 | -0.3179 | 32.608
77 | -0.081106 | -0.020537 | 0.081207 | 0.020601 | 0.00010065 | 6.4189e-05 | 0.1228 | 0.1228 | 0.1228 | 0.98338 | -0.3179 | 0.98471 | -0.29209 | 33.737
78 | -0.085179 | -0.021596 | 0.085223 | 0.021625 | 4.4075e-05 | 2.8118e-05 | 0.12881 | 0.12881 | 0.12881 | 0.98471 | -0.29209 | 0.98527 | -0.28133 | 35.3861
79 | 0.022022 | 0.0055243 | -0.022012 | -0.0055181 | 1.0204e-05 | 6.2131e-06 | 0.033146 | 0.033146 | 0.033146 | 0.98868 | -0.2156 | 0.98818 | -0.22533 | 9.1062
80 | -0.025877 | -0.0064903 | 0.025882 | 0.0064933 | 4.9285e-06 | 3.0431e-06 | 0.038947 | 0.038947 | 0.038947 | 0.98868 | -0.2156 | 0.98889 | -0.21161 | 10.6998
81 | 0.016065 | 0.0040276 | -0.016061 | -0.0040251 | 4.2649e-06 | 2.4806e-06 | 0.024191 | 0.024191 | 0.024191 | 0.98818 | -0.22533 | 0.9879 | -0.2309 | 6.646
82 | 0.0075976 | 0.001904 | -0.0075966 | -0.0019037 | 9.5296e-07 | 3.6148e-07 | 0.011444 | 0.011444 | 0.011444 | 0.9879 | -0.2309 | 0.98776 | -0.23353 | 3.1439
83 | 0.0019284 | 0.00048309 | -0.0019283 | -0.00048329 | 5.9962e-08 | -2.0414e-07 | 0.002905 | 0.0029051 | 0.0029051 | 0.98776 | -0.23353 | 0.98773 | -0.23418 | 0.79809
84 | 0.10649 | 0.027089 | -0.1062 | -0.026909 | 0.00028185 | 0.00018001 | 0.16064 | 0.16064 | 0.16064 | 0.98728 | -0.2425 | 0.98442 | -0.29758 | 44.1318
85 | 0.10222 | 0.025911 | -0.10207 | -0.025811 | 0.00015678 | 0.00010011 | 0.15462 | 0.15462 | 0.15462 | 0.98442 | -0.29758 | 0.98277 | -0.32955 | 42.4783
86 | -0.087932 | -0.022304 | 0.087938 | 0.022307 | 5.465e-06 | 3.4871e-06 | 0.1329 | 0.1329 | 0.1329 | 0.98527 | -0.28133 | 0.98533 | -0.28004 | 36.51
87 | -0.091104 | -0.0231 | 0.09127 | 0.023207 | 0.00016635 | 0.00010616 | 0.13768 | 0.13768 | 0.13768 | 0.98533 | -0.28004 | 0.9873 | -0.24213 | 37.8234
88 | -0.093356 | -0.023729 | 0.09336 | 0.023732 | 3.9179e-06 | 2.5007e-06 | 0.14082 | 0.14082 | 0.14082 | 0.9873 | -0.24213 | 0.98734 | -0.24126 | 38.6871
89 | -0.0027292 | -0.000684 | 0.0027293 | 0.00068383 | 1.2935e-07 | -1.7303e-07 | 0.0041329 | 0.0041329 | 0.0041329 | 0.98261 | -0.33361 | 0.98266 | -0.33261 | 1.1354
90 | -0.0027293 | -0.00068383 | 0.0027294 | 0.00068371 | 8.3662e-08 | -1.1193e-07 | 0.0041329 | 0.0041328 | 0.0041329 | 0.98266 | -0.33261 | 0.9827 | -0.33197 | 1.1354
91 | -0.0044529 | -0.0011157 | 0.0044532 | 0.0011156 | 2.7143e-07 | -2.8007e-08 | 0.0067426 | 0.0067425 | 0.0067426 | 0.9827 | -0.33197 | 0.98276 | -0.33069 | 1.8524
92 | -0.0058229 | -0.0014589 | 0.0058239 | 0.0014591 | 1.0193e-06 | 2.0917e-07 | 0.0088164 | 0.0088162 | 0.0088164 | 0.98276 | -0.33069 | 0.98295 | -0.32701 | 2.4221
93 | -0.007069 | -0.0017712 | 0.0070699 | 0.0017715 | 9.2352e-07 | 3.1841e-07 | 0.010701 | 0.010701 | 0.010701 | 0.98295 | -0.32701 | 0.98309 | -0.32427 | 2.9398
94 | 0.002395 | 0.00059973 | -0.0023949 | -0.00059985 | 6.6105e-08 | -1.2778e-07 | 0.0036249 | 0.003625 | 0.003625 | 0.98309 | -0.32427 | 0.98306 | -0.32485 | 0.99587
95 | 0.0020345 | 0.00050952 | -0.0020344 | -0.00050972 | 6.6961e-08 | -1.9587e-07 | 0.0030794 | 0.0030795 | 0.0030795 | 0.98306 | -0.32485 | 0.98302 | -0.32554 | 0.84602
96 | -0.060746 | -0.01529 | 0.060778 | 0.01531 | 3.1671e-05 | 2.0146e-05 | 0.092572 | 0.092572 | 0.092572 | 0.97669 | -0.44827 | 0.97724 | -0.43737 | 25.4319
97 | 0.055642 | 0.014011 | -0.055588 | -0.013976 | 5.4161e-05 | 3.4412e-05 | 0.084796 | 0.084796 | 0.084796 | 0.97669 | -0.44827 | 0.97565 | -0.46865 | 23.2956
98 | -0.066559 | -0.016759 | 0.066629 | 0.016804 | 7.0824e-05 | 4.5097e-05 | 0.10137 | 0.10137 | 0.10137 | 0.97724 | -0.43737 | 0.97838 | -0.41514 | 27.8501
99 | 0.055588 | 0.013976 | -0.05558 | -0.013971 | 7.4852e-06 | 4.7559e-06 | 0.084796 | 0.084796 | 0.084796 | 0.97565 | -0.46865 | 0.97551 | -0.47147 | 23.2956
100 | -0.06804 | -0.017157 | 0.068065 | 0.017173 | 2.4992e-05 | 1.5916e-05 | 0.10352 | 0.10352 | 0.10352 | 0.97838 | -0.41514 | 0.97877 | -0.40747 | 28.4395
101 | 0.045547 | 0.011456 | -0.045515 | -0.011436 | 3.2207e-05 | 2.0391e-05 | 0.069491 | 0.069492 | 0.069492 | 0.97551 | -0.47147 | 0.97475 | -0.48628 | 19.0911
102 | 0.010033 | 0.002515 | -0.010032 | -0.0025142 | 1.5642e-06 | 7.7882e-07 | 0.015305 | 0.015305 | 0.015305 | 0.97551 | -0.47147 | 0.97534 | -0.47474 | 4.2046
103 | -0.069726 | -0.01759 | 0.069787 | 0.017628 | 6.0496e-05 | 3.8537e-05 | 0.10604 | 0.10604 | 0.10604 | 0.97877 | -0.40747 | 0.9797 | -0.38936 | 29.1332
104 | 0.0083476 | 0.0020921 | -0.008347 | -0.0020919 | 5.4204e-07 | 2.3569e-07 | 0.012735 | 0.012735 | 0.012735 | 0.97534 | -0.47474 | 0.97527 | -0.47611 | 3.4987
105 | -0.074052 | -0.018697 | 0.074087 | 0.018719 | 3.4365e-05 | 2.1903e-05 | 0.11252 | 0.11252 | 0.11252 | 0.9797 | -0.38936 | 0.9802 | -0.37968 | 30.9131
106 | 0.0052166 | 0.0013073 | -0.0052159 | -0.0013072 | 6.9489e-07 | 7.9775e-08 | 0.0079592 | 0.0079593 | 0.0079593 | 0.97527 | -0.47611 | 0.97513 | -0.4789 | 2.1866
107 | -0.075133 | -0.018981 | 0.07523 | 0.019043 | 9.6765e-05 | 6.168e-05 | 0.11411 | 0.11411 | 0.11411 | 0.9802 | -0.37968 | 0.98157 | -0.35285 | 31.3495
108 | -0.078082 | -0.019758 | 0.078169 | 0.019814 | 8.7416e-05 | 5.5736e-05 | 0.11844 | 0.11844 | 0.11844 | 0.98157 | -0.35285 | 0.98277 | -0.32955 | 32.5374
109 | 0.023897 | 0.0059972 | -0.023888 | -0.0059921 | 8.4214e-06 | 5.1725e-06 | 0.036185 | 0.036185 | 0.036185 | 0.98277 | -0.32955 | 0.9824 | -0.33694 | 9.941
110 | -0.030617 | -0.0076976 | 0.030618 | 0.0076979 | 5.0184e-07 | 3.1331e-07 | 0.046395 | 0.046395 | 0.046395 | 0.98216 | -0.34237 | 0.98218 | -0.34203 | 12.7459
111 | 0.028966 | 0.0072838 | -0.028954 | -0.0072762 | 1.212e-05 | 7.5445e-06 | 0.043893 | 0.043893 | 0.043893 | 0.98216 | -0.34237 | 0.98171 | -0.35114 | 12.0586
112 | -0.032276 | -0.0081134 | 0.032276 | 0.0081134 | 1.3915e-08 | 8.7136e-09 | 0.048907 | 0.048907 | 0.048907 | 0.98218 | -0.34203 | 0.98218 | -0.34202 | 13.4359
113 | 0.02763 | 0.0069443 | -0.027629 | -0.0069438 | 8.6579e-07 | 5.3747e-07 | 0.041886 | 0.041886 | 0.041886 | 0.98171 | -0.35114 | 0.98168 | -0.35179 | 11.5072
114 | 0.025993 | 0.0065339 | -0.025989 | -0.0065315 | 3.866e-06 | 2.3903e-06 | 0.039407 | 0.039407 | 0.039407 | 0.98168 | -0.35179 | 0.98152 | -0.35491 | 10.8261
115 | 0.024264 | 0.0060992 | -0.024261 | -0.0060971 | 3.3792e-06 | 2.0786e-06 | 0.036792 | 0.036792 | 0.036792 | 0.98152 | -0.35491 | 0.98137 | -0.35783 | 10.1077
116 | 0.022536 | 0.0056649 | -0.022512 | -0.0056499 | 2.4437e-05 | 1.4936e-05 | 0.034177 | 0.034177 | 0.034177 | 0.98137 | -0.35783 | 0.98021 | -0.38056 | 9.3893
117 | -0.062746 | -0.015804 | 0.06279 | 0.015832 | 4.4025e-05 | 2.8009e-05 | 0.09478 | 0.09478 | 0.09478 | 0.98539 | -0.27939 | 0.98615 | -0.26473 | 26.0383
118 | 0.077544 | 0.019598 | -0.077435 | -0.019528 | 0.00010936 | 6.9714e-05 | 0.11677 | 0.11677 | 0.11677 | 0.98865 | -0.21625 | 0.98713 | -0.24571 | 32.0796
119 | 0.075061 | 0.018933 | -0.075046 | -0.018924 | 1.4729e-05 | 9.3872e-06 | 0.11319 | 0.11319 | 0.11319 | 0.98713 | -0.24571 | 0.98692 | -0.24981 | 31.0964
120 | 0.073454 | 0.018524 | -0.073435 | -0.018512 | 1.8955e-05 | 1.2079e-05 | 0.11079 | 0.11079 | 0.11079 | 0.98692 | -0.24981 | 0.98664 | -0.2552 | 30.4369
121 | 0.071857 | 0.018117 | -0.071844 | -0.018109 | 1.2415e-05 | 7.9093e-06 | 0.10841 | 0.10841 | 0.10841 | 0.98664 | -0.2552 | 0.98645 | -0.25881 | 29.7831
122 | 0.0016638 | 0.00041683 | -0.0016638 | -0.00041694 | 2.3309e-08 | -1.0932e-07 | 0.0025185 | 0.0025185 | 0.0025185 | 0.98302 | -0.32554 | 0.98301 | -0.32584 | 0.6919
123 | 0.00043096 | 0.00010796 | -0.00043096 | -0.00010801 | 5.5864e-10 | -4.4019e-08 | 0.00065234 | 0.00065235 | 0.00065235 | 0.98301 | -0.32584 | 0.98301 | -0.32586 | 0.17922
124 | 0.069741 | 0.017582 | -0.069729 | -0.017574 | 1.1633e-05 | 7.4091e-06 | 0.10524 | 0.10524 | 0.10524 | 0.98645 | -0.25881 | 0.98627 | -0.2623 | 28.9113
125 | 0.068119 | 0.017171 | -0.068111 | -0.017166 | 7.9113e-06 | 5.0378e-06 | 0.10281 | 0.10281 | 0.10281 | 0.98627 | -0.2623 | 0.98615 | -0.26473 | 28.2439
126 | 0.021809 | 0.0054709 | -0.021806 | -0.0054691 | 3.0221e-06 | 1.8407e-06 | 0.033035 | 0.033035 | 0.033035 | 0.9824 | -0.33694 | 0.98225 | -0.33985 | 9.0756
127 | 0.020625 | 0.0051731 | -0.020619 | -0.0051693 | 6.2915e-06 | 3.8091e-06 | 0.031247 | 0.031247 | 0.031247 | 0.98225 | -0.33985 | 0.98192 | -0.34625 | 8.5843
128 | 0.010068 | 0.0025241 | -0.010064 | -0.0025222 | 3.7853e-06 | 1.8743e-06 | 0.015257 | 0.015257 | 0.015257 | 0.98192 | -0.34625 | 0.98152 | -0.35414 | 4.1916
129 | 0.010551 | 0.0026452 | -0.010548 | -0.0026435 | 3.3778e-06 | 1.7163e-06 | 0.01599 | 0.01599 | 0.01599 | 0.98192 | -0.34625 | 0.98158 | -0.35297 | 4.3928
130 | 0.0072824 | 0.0018251 | -0.0072812 | -0.0018247 | 1.1529e-06 | 4.1914e-07 | 0.01104 | 0.01104 | 0.01104 | 0.98152 | -0.35414 | 0.98135 | -0.35747 | 3.0331
131 | 0.0041851 | 0.0010487 | -0.0041848 | -0.0010488 | 3.9166e-07 | -7.698e-08 | 0.0063459 | 0.006346 | 0.006346 | 0.98135 | -0.35747 | 0.98125 | -0.35943 | 1.7434
132 | -0.35292 | -0.090149 | 0.35377 | 0.090691 | 0.0008485 | 0.00054209 | 0.52873 | 0.52873 | 0.52873 | 0.99436 | -0.10683 | 0.99697 | -0.057226 | 48.4188
133 | -0.35604 | -0.091261 | 0.35612 | 0.091309 | 7.4613e-05 | 4.767e-05 | 0.53213 | 0.53213 | 0.53213 | 0.99697 | -0.057226 | 0.9972 | -0.052904 | 48.7299
134 | -0.35835 | -0.091869 | 0.3592 | 0.092412 | 0.00084993 | 0.00054303 | 0.53547 | 0.53547 | 0.53547 | 0.9972 | -0.052904 | 0.99978 | -0.0041119 | 49.0354
135 | 0.022512 | 0.0056499 | -0.022499 | -0.0056424 | 1.2334e-05 | 7.5388e-06 | 0.034177 | 0.034177 | 0.034177 | 0.98021 | -0.38056 | 0.97962 | -0.39206 | 9.3894
136 | 0.0076279 | 0.0019124 | -0.0076255 | -0.0019114 | 2.416e-06 | 9.4228e-07 | 0.011587 | 0.011587 | 0.011587 | 0.97962 | -0.39206 | 0.97928 | -0.39871 | 3.1832
137 | 0.014872 | 0.00373 | -0.014863 | -0.0037253 | 8.2477e-06 | 4.7362e-06 | 0.022591 | 0.022591 | 0.022591 | 0.97962 | -0.39206 | 0.97903 | -0.4037 | 6.2062
138 | -0.36178 | -0.093057 | 0.36185 | 0.093103 | 7.2332e-05 | 4.6214e-05 | 0.5393 | 0.5393 | 0.5393 | 0.99978 | -0.0041119 | 1 | 0 | 49.3861
139 | -0.013214 | -0.0033118 | 0.013214 | 0.003312 | 4.8367e-07 | 2.6934e-07 | 0.020085 | 0.020084 | 0.020085 | 0.97899 | -0.40447 | 0.97903 | -0.4037 | 5.5177
140 | 0.0076677 | 0.0019218 | -0.0076675 | -0.0019216 | 2.7866e-07 | 1.0956e-07 | 0.011655 | 0.011655 | 0.011655 | 0.97899 | -0.40447 | 0.97895 | -0.40523 | 3.2018
141 | 0.0076255 | 0.0019114 | -0.0076233 | -0.0019106 | 2.1461e-06 | 8.3741e-07 | 0.011587 | 0.011587 | 0.011587 | 0.97928 | -0.39871 | 0.97898 | -0.40461 | 3.1833

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36632 | 0.09381

## res_load
| p_mw | q_mvar
0 | 0.0015805 | 0.00039611
1 | 0.00162 | 0.00040602
2 | 0.0027101 | 0.00067921
3 | 0.0019922 | 0.00049928
4 | 0.0042757 | 0.0010716
5 | 0.0039391 | 0.00098723
6 | 0.0065267 | 0.0016357
7 | 0.0018039 | 0.00045211
8 | 0.0022762 | 0.00057047
9 | 0.0011519 | 0.00028869
10 | 0.0018841 | 0.00047221
11 | 0.0036266 | 0.00090892
12 | 0.0027554 | 0.00069058
13 | 0.0048814 | 0.0012234
14 | 0.0015879 | 0.00039797
15 | 0.00094149 | 0.00023596
16 | 0.0013165 | 0.00032996
17 | 0.0022977 | 0.00057585
18 | 0.0080767 | 0.0020242
19 | 0.0051575 | 0.0012926
20 | 0.0077732 | 0.0019482
21 | 0.005008 | 0.0012551
22 | 0.0011634 | 0.00029157
23 | 0.00152 | 0.00038094
24 | 0.0058783 | 0.0014732
25 | 0.0065746 | 0.0016477
26 | 0.0021974 | 0.00055072
27 | 0.0035385 | 0.00088684
28 | 0.0038539 | 0.00096589
29 | 0.00031777 | 7.964e-05
30 | 0.0021806 | 0.00054651
31 | 0.00031824 | 7.9759e-05
32 | 0.0014252 | 0.00035719
33 | 0.00081465 | 0.00020417
34 | 0.00028227 | 7.0744e-05
35 | 0.00037911 | 9.5013e-05
36 | 0.0021781 | 0.00054587
37 | 0.0035868 | 0.00089895
38 | 0.0014231 | 0.00035667
39 | 0.0015829 | 0.00039671
40 | 0.0023194 | 0.00058131
41 | 0.0017739 | 0.00044457
42 | 0.0017855 | 0.0004475
43 | 0.0029655 | 0.00074323
44 | 0.0030171 | 0.00075615
45 | 0.0025408 | 0.00063677
46 | 0.004676 | 0.0011719
47 | 0.0063498 | 0.0015914
48 | 0.0022224 | 0.00055699
49 | 0.0019698 | 0.00049369
50 | 0.0054397 | 0.0013633
51 | 0.0017294 | 0.00043343
52 | 0.0018051 | 0.0004524
53 | 0.0022768 | 0.00057061
54 | 0.0027591 | 0.00069149
55 | 0.0035456 | 0.00088862
56 | 0.0025509 | 0.00063933
57 | 0.002716 | 0.00068069
58 | 0.0039724 | 0.00099557
59 | 0.0038544 | 0.000966
60 | 0.0059471 | 0.0014905
61 | 0.0066476 | 0.0016661
62 | 0.0084631 | 0.0021211
63 | 0.0056682 | 0.0014206
64 | 0.004164 | 0.0010436
65 | 0.0019283 | 0.00048329
66 | 0.003982 | 0.00099799
67 | 0.002709 | 0.00067893
68 | 0.0031657 | 0.0007934
69 | 0.0020861 | 0.00052282
70 | 0.0027292 | 0.000684
71 | 0.0017235 | 0.00043196
72 | 0.0013697 | 0.00034327
73 | 0.0012451 | 0.00031204
74 | 0.00036042 | 9.033e-05
75 | 0.005104 | 0.0012792
76 | 0.0057809 | 0.0014488
77 | 0.0014107 | 0.00035355
78 | 0.0016609 | 0.00041627
79 | 0.0019833 | 0.00049706
80 | 0.0016841 | 0.00042208
81 | 0.0042657 | 0.0010691
82 | 0.0031304 | 0.00078456
83 | 0.0010464 | 0.00026225
84 | 0.0028523 | 0.00071484
85 | 0.0016513 | 0.00041386
86 | 0.0016578 | 0.00041548
87 | 0.0013243 | 0.00033189
88 | 0.0016586 | 0.00041567
89 | 0.0016356 | 0.00040993
90 | 0.0017248 | 0.00043227
91 | 0.0017248 | 0.00043227
92 | 0.0030588 | 0.0007666
93 | 0.0040707 | 0.0010202
94 | 0.0041059 | 0.001029
95 | 0.0023742 | 0.00059503
96 | 0.0015922 | 0.00039903
97 | 0.0015781 | 0.00039552
98 | 0.00037062 | 9.2887e-05
99 | 0.0012328 | 0.00030898
100 | 0.0021036 | 0.0005272
101 | 0.0016103 | 0.00040358
102 | 0.00043096 | 0.00010801
103 | 0.0020795 | 0.00052117
104 | 0.0011807 | 0.00029592
105 | 0.0027816 | 0.00069714
106 | 0.010548 | 0.0026435
107 | 0.0030961 | 0.00077595
108 | 0.0039072 | 0.00097923
109 | 0.0022758 | 0.00057037
110 | 0.0022362 | 0.00056044
111 | 0.002573 | 0.00064484
112 | 0.0028182 | 0.00070631
113 | 0.0041848 | 0.0010488
114 | 0.0052159 | 0.0013072
115 | 0.0053205 | 0.0013334
116 | 0.0055462 | 0.00139
117 | 0.0016489 | 0.00041326
118 | 0.0076675 | 0.0019216
119 | 0.0076233 | 0.0019106

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1