## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2543-5_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2543-5_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2543-5_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2543-5_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2543-5_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2543-5_0_8_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_2543-5_0_8_node_59 | 0.4 | n |  | TRUE
7 | bus_LV_2543-5_0_8_node_145 | 0.4 | n |  | TRUE
8 | bus_LV_2543-5_0_8_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2543-5_0_8_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2543-5_0_8_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2543-5_0_8_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2543-5_0_8_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2543-5_0_8_node_166 | 0.4 | n |  | TRUE
14 | bus_LV_2543-5_0_8_node_215 | 0.4 | n |  | TRUE
15 | bus_LV_2543-5_0_8_node_167 | 0.4 | n |  | TRUE
16 | bus_LV_2543-5_0_8_node_164 | 0.4 | n |  | TRUE
17 | bus_LV_2543-5_0_8_node_216 | 0.4 | n |  | TRUE
18 | bus_LV_2543-5_0_8_node_213 | 0.4 | n |  | TRUE
19 | bus_LV_2543-5_0_8_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2543-5_0_8_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2543-5_0_8_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2543-5_0_8_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2543-5_0_8_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2543-5_0_8_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2543-5_0_8_node_110 | 0.4 | n |  | TRUE
26 | bus_LV_2543-5_0_8_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_2543-5_0_8_node_224 | 0.4 | n |  | TRUE
28 | bus_LV_2543-5_0_8_node_221 | 0.4 | n |  | TRUE
29 | bus_LV_2543-5_0_8_node_111 | 0.4 | n |  | TRUE
30 | bus_LV_2543-5_0_8_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_2543-5_0_8_node_131 | 0.4 | n |  | TRUE
32 | bus_LV_2543-5_0_8_node_149 | 0.4 | n |  | TRUE
33 | bus_LV_2543-5_0_8_node_222 | 0.4 | n |  | TRUE
34 | bus_LV_2543-5_0_8_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2543-5_0_8_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2543-5_0_8_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2543-5_0_8_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2543-5_0_8_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2543-5_0_8_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2543-5_0_8_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_2543-5_0_8_node_205 | 0.4 | n |  | TRUE
42 | bus_LV_2543-5_0_8_node_249 | 0.4 | n |  | TRUE
43 | bus_LV_2543-5_0_8_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_2543-5_0_8_node_203 | 0.4 | n |  | TRUE
45 | bus_LV_2543-5_0_8_node_250 | 0.4 | n |  | TRUE
46 | bus_LV_2543-5_0_8_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_2543-5_0_8_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_2543-5_0_8_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_2543-5_0_8_node_25 | 0.4 | n |  | TRUE
50 | bus_LV_2543-5_0_8_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_2543-5_0_8_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_2543-5_0_8_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_2543-5_0_8_node_173 | 0.4 | n |  | TRUE
54 | bus_LV_2543-5_0_8_node_170 | 0.4 | n |  | TRUE
55 | bus_LV_2543-5_0_8_node_262 | 0.4 | n |  | TRUE
56 | bus_LV_2543-5_0_8_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_2543-5_0_8_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_2543-5_0_8_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_2543-5_0_8_node_202 | 0.4 | n |  | TRUE
60 | bus_LV_2543-5_0_8_node_171 | 0.4 | n |  | TRUE
61 | bus_LV_2543-5_0_8_node_263 | 0.4 | n |  | TRUE
62 | bus_LV_2543-5_0_8_node_29 | 0.4 | n |  | TRUE
63 | bus_LV_2543-5_0_8_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_2543-5_0_8_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_2543-5_0_8_node_141 | 0.4 | n |  | TRUE
66 | bus_LV_2543-5_0_8_node_151 | 0.4 | n |  | TRUE
67 | bus_LV_2543-5_0_8_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_2543-5_0_8_node_261 | 0.4 | n |  | TRUE
69 | bus_LV_2543-5_0_8_node_150 | 0.4 | n |  | TRUE
70 | bus_LV_2543-5_0_8_node_34 | 0.4 | n |  | TRUE
71 | bus_LV_2543-5_0_8_node_35 | 0.4 | n |  | TRUE
72 | bus_LV_2543-5_0_8_node_36 | 0.4 | n |  | TRUE
73 | bus_LV_2543-5_0_8_node_37 | 0.4 | n |  | TRUE
74 | bus_LV_2543-5_0_8_node_38 | 0.4 | n |  | TRUE
75 | bus_LV_2543-5_0_8_node_265 | 0.4 | n |  | TRUE
76 | bus_LV_2543-5_0_8_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_2543-5_0_8_node_187 | 0.4 | n |  | TRUE
78 | bus_LV_2543-5_0_8_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_2543-5_0_8_node_188 | 0.4 | n |  | TRUE
80 | bus_LV_2543-5_0_8_node_186 | 0.4 | n |  | TRUE
81 | bus_LV_2543-5_0_8_node_185 | 0.4 | n |  | TRUE
82 | bus_LV_2543-5_0_8_node_245 | 0.4 | n |  | TRUE
83 | bus_LV_2543-5_0_8_node_41 | 0.4 | n |  | TRUE
84 | bus_LV_2543-5_0_8_node_42 | 0.4 | n |  | TRUE
85 | bus_LV_2543-5_0_8_node_43 | 0.4 | n |  | TRUE
86 | bus_LV_2543-5_0_8_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_2543-5_0_8_node_45 | 0.4 | n |  | TRUE
88 | bus_LV_2543-5_0_8_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_2543-5_0_8_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2543-5_0_8_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_2543-5_0_8_node_46 | 0.4 | n |  | TRUE
92 | bus_LV_2543-5_0_8_node_47 | 0.4 | n |  | TRUE
93 | bus_LV_2543-5_0_8_node_48 | 0.4 | n |  | TRUE
94 | bus_LV_2543-5_0_8_node_49 | 0.4 | n |  | TRUE
95 | bus_LV_2543-5_0_8_node_50 | 0.4 | n |  | TRUE
96 | bus_LV_2543-5_0_8_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_2543-5_0_8_node_231 | 0.4 | n |  | TRUE
98 | bus_LV_2543-5_0_8_node_95 | 0.4 | n |  | TRUE
99 | bus_LV_2543-5_0_8_node_252 | 0.4 | n |  | TRUE
100 | bus_LV_2543-5_0_8_node_57 | 0.4 | n |  | TRUE
101 | bus_LV_2543-5_0_8_node_146 | 0.4 | n |  | TRUE
102 | bus_LV_2543-5_0_8_node_144 | 0.4 | n |  | TRUE
103 | bus_LV_2543-5_0_8_node_52 | 0.4 | n |  | TRUE
104 | bus_LV_2543-5_0_8_node_53 | 0.4 | n |  | TRUE
105 | bus_LV_2543-5_0_8_node_54 | 0.4 | n |  | TRUE
106 | bus_LV_2543-5_0_8_node_244 | 0.4 | n |  | TRUE
107 | bus_LV_2543-5_0_8_node_241 | 0.4 | n |  | TRUE
108 | bus_LV_2543-5_0_8_node_256 | 0.4 | n |  | TRUE
109 | bus_LV_2543-5_0_8_node_242 | 0.4 | n |  | TRUE
110 | bus_LV_2543-5_0_8_node_58 | 0.4 | n |  | TRUE
111 | bus_LV_2543-5_0_8_node_72 | 0.4 | n |  | TRUE
112 | bus_LV_2543-5_0_8_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_2543-5_0_8_node_189 | 0.4 | n |  | TRUE
114 | bus_LV_2543-5_0_8_node_62 | 0.4 | n |  | TRUE
115 | bus_LV_2543-5_0_8_node_63 | 0.4 | n |  | TRUE
116 | bus_LV_2543-5_0_8_node_64 | 0.4 | n |  | TRUE
117 | bus_LV_2543-5_0_8_node_65 | 0.4 | n |  | TRUE
118 | bus_LV_2543-5_0_8_node_182 | 0.4 | n |  | TRUE
119 | bus_LV_2543-5_0_8_node_183 | 0.4 | n |  | TRUE
120 | bus_LV_2543-5_0_8_node_274 | 0.4 | n |  | TRUE
121 | bus_LV_2543-5_0_8_node_272 | 0.4 | n |  | TRUE
122 | bus_LV_2543-5_0_8_node_67 | 0.4 | n |  | TRUE
123 | bus_LV_2543-5_0_8_node_69 | 0.4 | n |  | TRUE
124 | bus_LV_2543-5_0_8_node_71 | 0.4 | n |  | TRUE
125 | bus_LV_2543-5_0_8_node_234 | 0.4 | n |  | TRUE
126 | bus_LV_2543-5_0_8_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_2543-5_0_8_node_73 | 0.4 | n |  | TRUE
128 | bus_LV_2543-5_0_8_node_75 | 0.4 | n |  | TRUE
129 | bus_LV_2543-5_0_8_node_77 | 0.4 | n |  | TRUE
130 | bus_LV_2543-5_0_8_node_139 | 0.4 | n |  | TRUE
131 | bus_LV_2543-5_0_8_node_140 | 0.4 | n |  | TRUE
132 | bus_LV_2543-5_0_8_node_190 | 0.4 | n |  | TRUE
133 | bus_LV_2543-5_0_8_node_79 | 0.4 | n |  | TRUE
134 | bus_LV_2543-5_0_8_node_80 | 0.4 | n |  | TRUE
135 | bus_LV_2543-5_0_8_node_81 | 0.4 | n |  | TRUE
136 | bus_LV_2543-5_0_8_node_82 | 0.4 | n |  | TRUE
137 | bus_LV_2543-5_0_8_node_83 | 0.4 | n |  | TRUE
138 | bus_LV_2543-5_0_8_node_105 | 0.4 | n |  | TRUE
139 | bus_LV_2543-5_0_8_node_116 | 0.4 | n |  | TRUE
140 | bus_LV_2543-5_0_8_node_212 | 0.4 | n |  | TRUE
141 | bus_LV_2543-5_0_8_node_107 | 0.4 | n |  | TRUE
142 | bus_LV_2543-5_0_8_node_108 | 0.4 | n |  | TRUE
143 | bus_LV_2543-5_0_8_node_106 | 0.4 | n |  | TRUE
144 | bus_LV_2543-5_0_8_node_114 | 0.4 | n |  | TRUE
145 | bus_LV_2543-5_0_8_node_210 | 0.4 | n |  | TRUE
146 | bus_LV_2543-5_0_8_node_84 | 0.4 | n |  | TRUE
147 | bus_LV_2543-5_0_8_node_85 | 0.4 | n |  | TRUE
148 | bus_LV_2543-5_0_8_node_86 | 0.4 | n |  | TRUE
149 | bus_LV_2543-5_0_8_node_87 | 0.4 | n |  | TRUE
150 | bus_LV_2543-5_0_8_node_88 | 0.4 | n |  | TRUE
151 | bus_LV_2543-5_0_8_node_89 | 0.4 | n |  | TRUE
152 | bus_LV_2543-5_0_8_node_180 | 0.4 | n |  | TRUE
153 | bus_LV_2543-5_0_8_node_136 | 0.4 | n |  | TRUE
154 | bus_LV_2543-5_0_8_node_147 | 0.4 | n |  | TRUE
155 | bus_LV_2543-5_0_8_node_181 | 0.4 | n |  | TRUE
156 | bus_LV_2543-5_0_8_node_121 | 0.4 | n |  | TRUE
157 | bus_LV_2543-5_0_8_node_137 | 0.4 | n |  | TRUE
158 | bus_LV_2543-5_0_8_node_148 | 0.4 | n |  | TRUE
159 | bus_LV_2543-5_0_8_node_90 | 0.4 | n |  | TRUE
160 | bus_LV_2543-5_0_8_node_91 | 0.4 | n |  | TRUE
161 | bus_LV_2543-5_0_8_node_92 | 0.4 | n |  | TRUE
162 | bus_LV_2543-5_0_8_node_93 | 0.4 | n |  | TRUE
163 | bus_LV_2543-5_0_8_node_94 | 0.4 | n |  | TRUE
164 | bus_LV_2543-5_0_8_node_125 | 0.4 | n |  | TRUE
165 | bus_LV_2543-5_0_8_node_220 | 0.4 | n |  | TRUE
166 | bus_LV_2543-5_0_8_node_135 | 0.4 | n |  | TRUE
167 | bus_LV_2543-5_0_8_node_132 | 0.4 | n |  | TRUE
168 | bus_LV_2543-5_0_8_node_174 | 0.4 | n |  | TRUE
169 | bus_LV_2543-5_0_8_node_96 | 0.4 | n |  | TRUE
170 | bus_LV_2543-5_0_8_node_98 | 0.4 | n |  | TRUE
171 | bus_LV_2543-5_0_8_node_172 | 0.4 | n |  | TRUE
172 | bus_LV_2543-5_0_8_node_99 | 0.4 | n |  | TRUE
173 | bus_LV_2543-5_0_8_node_100 | 0.4 | n |  | TRUE
174 | bus_LV_2543-5_0_8_node_101 | 0.4 | n |  | TRUE
175 | bus_LV_2543-5_0_8_node_102 | 0.4 | n |  | TRUE
176 | bus_LV_2543-5_0_8_node_103 | 0.4 | n |  | TRUE
177 | bus_LV_2543-5_0_8_node_104 | 0.4 | n |  | TRUE
178 | bus_LV_2543-5_0_8_node_165 | 0.4 | n |  | TRUE
179 | bus_LV_2543-5_0_8_node_191 | 0.4 | n |  | TRUE
180 | bus_LV_2543-5_0_8_node_154 | 0.4 | n |  | TRUE
181 | bus_LV_2543-5_0_8_node_152 | 0.4 | n |  | TRUE
182 | bus_LV_2543-5_0_8_node_109 | 0.4 | n |  | TRUE
183 | bus_LV_2543-5_0_8_node_236 | 0.4 | n |  | TRUE
184 | bus_LV_2543-5_0_8_node_259 | 0.4 | n |  | TRUE
185 | bus_LV_2543-5_0_8_node_178 | 0.4 | n |  | TRUE
186 | bus_LV_2543-5_0_8_node_258 | 0.4 | n |  | TRUE
187 | bus_LV_2543-5_0_8_node_112 | 0.4 | n |  | TRUE
188 | bus_LV_2543-5_0_8_node_113 | 0.4 | n |  | TRUE
189 | bus_LV_2543-5_0_8_node_115 | 0.4 | n |  | TRUE
190 | bus_LV_2543-5_0_8_node_254 | 0.4 | n |  | TRUE
191 | bus_LV_2543-5_0_8_node_253 | 0.4 | n |  | TRUE
192 | bus_LV_2543-5_0_8_node_117 | 0.4 | n |  | TRUE
193 | bus_LV_2543-5_0_8_node_118 | 0.4 | n |  | TRUE
194 | bus_LV_2543-5_0_8_node_119 | 0.4 | n |  | TRUE
195 | bus_LV_2543-5_0_8_node_120 | 0.4 | n |  | TRUE
196 | bus_LV_2543-5_0_8_node_270 | 0.4 | n |  | TRUE
197 | bus_LV_2543-5_0_8_node_122 | 0.4 | n |  | TRUE
198 | bus_LV_2543-5_0_8_node_196 | 0.4 | n |  | TRUE
199 | bus_LV_2543-5_0_8_node_123 | 0.4 | n |  | TRUE
200 | bus_LV_2543-5_0_8_node_192 | 0.4 | n |  | TRUE
201 | bus_LV_2543-5_0_8_node_193 | 0.4 | n |  | TRUE
202 | bus_LV_2543-5_0_8_node_194 | 0.4 | n |  | TRUE
203 | bus_LV_2543-5_0_8_node_195 | 0.4 | n |  | TRUE
204 | bus_LV_2543-5_0_8_node_124 | 0.4 | n |  | TRUE
205 | bus_LV_2543-5_0_8_node_260 | 0.4 | n |  | TRUE
206 | bus_LV_2543-5_0_8_node_133 | 0.4 | n |  | TRUE
207 | bus_LV_2543-5_0_8_node_127 | 0.4 | n |  | TRUE
208 | bus_LV_2543-5_0_8_node_128 | 0.4 | n |  | TRUE
209 | bus_LV_2543-5_0_8_node_129 | 0.4 | n |  | TRUE
210 | bus_LV_2543-5_0_8_node_130 | 0.4 | n |  | TRUE
211 | bus_LV_2543-5_0_8_node_158 | 0.4 | n |  | TRUE
212 | bus_LV_2543-5_0_8_node_155 | 0.4 | n |  | TRUE
213 | bus_LV_2543-5_0_8_node_156 | 0.4 | n |  | TRUE
214 | bus_LV_2543-5_0_8_node_134 | 0.4 | n |  | TRUE
215 | bus_LV_2543-5_0_8_node_138 | 0.4 | n |  | TRUE
216 | bus_LV_2543-5_0_8_node_268 | 0.4 | n |  | TRUE
217 | bus_LV_2543-5_0_8_node_153 | 0.4 | n |  | TRUE
218 | bus_LV_2543-5_0_8_node_157 | 0.4 | n |  | TRUE
219 | bus_LV_2543-5_0_8_node_233 | 0.4 | n |  | TRUE
220 | bus_LV_2543-5_0_8_node_232 | 0.4 | n |  | TRUE
221 | bus_LV_2543-5_0_8_node_159 | 0.4 | n |  | TRUE
222 | bus_LV_2543-5_0_8_node_160 | 0.4 | n |  | TRUE
223 | bus_LV_2543-5_0_8_node_161 | 0.4 | n |  | TRUE
224 | bus_LV_2543-5_0_8_node_162 | 0.4 | n |  | TRUE
225 | bus_LV_2543-5_0_8_node_163 | 0.4 | n |  | TRUE
226 | bus_LV_2543-5_0_8_node_168 | 0.4 | n |  | TRUE
227 | bus_LV_2543-5_0_8_node_169 | 0.4 | n |  | TRUE
228 | bus_LV_2543-5_0_8_node_229 | 0.4 | n |  | TRUE
229 | bus_LV_2543-5_0_8_node_227 | 0.4 | n |  | TRUE
230 | bus_LV_2543-5_0_8_node_175 | 0.4 | n |  | TRUE
231 | bus_LV_2543-5_0_8_node_176 | 0.4 | n |  | TRUE
232 | bus_LV_2543-5_0_8_node_179 | 0.4 | n |  | TRUE
233 | bus_LV_2543-5_0_8_node_184 | 0.4 | n |  | TRUE
234 | bus_LV_2543-5_0_8_node_246 | 0.4 | n |  | TRUE
235 | bus_LV_2543-5_0_8_node_217 | 0.4 | n |  | TRUE
236 | bus_LV_2543-5_0_8_node_218 | 0.4 | n |  | TRUE
237 | bus_LV_2543-5_0_8_node_206 | 0.4 | n |  | TRUE
238 | bus_LV_2543-5_0_8_node_197 | 0.4 | n |  | TRUE
239 | bus_LV_2543-5_0_8_node_198 | 0.4 | n |  | TRUE
240 | bus_LV_2543-5_0_8_node_199 | 0.4 | n |  | TRUE
241 | bus_LV_2543-5_0_8_node_200 | 0.4 | n |  | TRUE
242 | bus_LV_2543-5_0_8_node_207 | 0.4 | n |  | TRUE
243 | bus_LV_2543-5_0_8_node_201 | 0.4 | n |  | TRUE
244 | bus_LV_2543-5_0_8_node_214 | 0.4 | n |  | TRUE
245 | bus_LV_2543-5_0_8_node_208 | 0.4 | n |  | TRUE
246 | bus_LV_2543-5_0_8_node_209 | 0.4 | n |  | TRUE
247 | bus_LV_2543-5_0_8_node_237 | 0.4 | n |  | TRUE
248 | bus_LV_2543-5_0_8_node_239 | 0.4 | n |  | TRUE
249 | bus_LV_2543-5_0_8_node_240 | 0.4 | n |  | TRUE
250 | bus_LV_2543-5_0_8_node_247 | 0.4 | n |  | TRUE
251 | bus_LV_2543-5_0_8_node_243 | 0.4 | n |  | TRUE
252 | bus_LV_2543-5_0_8_node_248 | 0.4 | n |  | TRUE
253 | bus_LV_2543-5_0_8_node_204 | 0.4 | n |  | TRUE
254 | bus_LV_2543-5_0_8_node_235 | 0.4 | n |  | TRUE
255 | bus_LV_2543-5_0_8_node_211 | 0.4 | n |  | TRUE
256 | bus_LV_2543-5_0_8_node_264 | 0.4 | n |  | TRUE
257 | bus_LV_2543-5_0_8_node_238 | 0.4 | n |  | TRUE
258 | bus_LV_2543-5_0_8_node_219 | 0.4 | n |  | TRUE
259 | bus_LV_2543-5_0_8_node_255 | 0.4 | n |  | TRUE
260 | bus_LV_2543-5_0_8_node_223 | 0.4 | n |  | TRUE
261 | bus_LV_2543-5_0_8_node_226 | 0.4 | n |  | TRUE
262 | bus_LV_2543-5_0_8_node_225 | 0.4 | n |  | TRUE
263 | bus_LV_2543-5_0_8_node_266 | 0.4 | n |  | TRUE
264 | bus_LV_2543-5_0_8_node_228 | 0.4 | n |  | TRUE
265 | bus_LV_2543-5_0_8_node_271 | 0.4 | n |  | TRUE
266 | bus_LV_2543-5_0_8_node_251 | 0.4 | n |  | TRUE
267 | bus_LV_2543-5_0_8_node_269 | 0.4 | n |  | TRUE
268 | bus_LV_2543-5_0_8_node_273 | 0.4 | n |  | TRUE
269 | bus_MV_396_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2543-5_0_8_load_0 | 0 | 0.001174 | 0.00029423 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2543-5_0_8_load_1 | 1 | 0.0011795 | 0.00029561 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2543-5_0_8_load_2 | 2 | 0.0015499 | 0.00038844 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2543-5_0_8_load_3 | 3 | 0.002315 | 0.0005802 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2543-5_0_8_load_4 | 4 | 0.0015036 | 0.00037684 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2543-5_0_8_load_59 | 6 | 0.0014734 | 0.00036926 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2543-5_0_8_load_5 | 8 | 0.0011217 | 0.00028114 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2543-5_0_8_load_6 | 9 | 0.0021784 | 0.00054595 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2543-5_0_8_load_7 | 10 | 0.0014113 | 0.0003537 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2543-5_0_8_load_8 | 11 | 0.0015463 | 0.00038755 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2543-5_0_8_load_9 | 12 | 0.0009422 | 0.00023614 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2543-5_0_8_load_167 | 15 | 0.0018687 | 0.00046833 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2543-5_0_8_load_164 | 16 | 0.0029967 | 0.00075104 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2543-5_0_8_load_216 | 17 | 0.001017 | 0.00025488 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2543-5_0_8_load_213 | 18 | 0.0013585 | 0.00034048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2543-5_0_8_load_10 | 19 | 0.001352 | 0.00033884 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2543-5_0_8_load_11 | 20 | 0.0011233 | 0.00028151 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2543-5_0_8_load_13 | 22 | 0.0011224 | 0.00028131 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2543-5_0_8_load_14 | 23 | 0.006454 | 0.0016175 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2543-5_0_8_load_110 | 25 | 0.0016586 | 0.00041568 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2543-5_0_8_load_39 | 26 | 0.0023015 | 0.0005768 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2543-5_0_8_load_221 | 28 | 0.0015427 | 0.00038664 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2543-5_0_8_load_111 | 29 | 0.0011256 | 0.0002821 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2543-5_0_8_load_40 | 30 | 0.0028271 | 0.00070853 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2543-5_0_8_load_131 | 31 | 0.0012946 | 0.00032445 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2543-5_0_8_load_149 | 32 | 0.0015964 | 0.00040011 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2543-5_0_8_load_222 | 33 | 0.0016614 | 0.00041639 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2543-5_0_8_load_16 | 34 | 0.0022175 | 0.00055576 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2543-5_0_8_load_17 | 35 | 0.0041104 | 0.0010302 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2543-5_0_8_load_19 | 37 | 0.0015634 | 0.00039184 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2543-5_0_8_load_20 | 38 | 0.0016664 | 0.00041763 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2543-5_0_8_load_56 | 40 | 0.0017297 | 0.00043351 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2543-5_0_8_load_205 | 41 | 0.00088708 | 0.00022232 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2543-5_0_8_load_249 | 42 | 0.0031399 | 0.00078692 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2543-5_0_8_load_55 | 43 | 0.0048463 | 0.0012146 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2543-5_0_8_load_250 | 45 | 0.0014602 | 0.00036596 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2543-5_0_8_load_22 | 46 | 0.0021482 | 0.00053839 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2543-5_0_8_load_23 | 47 | 0.00073787 | 0.00018493 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2543-5_0_8_load_25 | 49 | 0.0008177 | 0.00020493 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2543-5_0_8_load_27 | 51 | 0.0019897 | 0.00049867 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2543-5_0_8_load_173 | 53 | 0.0045575 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2543-5_0_8_load_170 | 54 | 0.0025592 | 0.00064141 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2543-5_0_8_load_262 | 55 | 0.0013003 | 0.0003259 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2543-5_0_8_load_33 | 57 | 0.0013011 | 0.00032609 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2543-5_0_8_load_28 | 58 | 0.0010581 | 0.00026517 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2543-5_0_8_load_202 | 59 | 0.0029585 | 0.00074146 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2543-5_0_8_load_171 | 60 | 0.0012087 | 0.00030294 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2543-5_0_8_load_263 | 61 | 0.0016401 | 0.00041104 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2543-5_0_8_load_29 | 62 | 0.0030442 | 0.00076295 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2543-5_0_8_load_31 | 63 | 0.00070581 | 0.00017689 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2543-5_0_8_load_60 | 64 | 0.0007948 | 0.0001992 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2543-5_0_8_load_141 | 65 | 0.0025082 | 0.00062863 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2543-5_0_8_load_151 | 66 | 0.0012632 | 0.00031659 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2543-5_0_8_load_61 | 67 | 0.00081018 | 0.00020305 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2543-5_0_8_load_261 | 68 | 0.0031886 | 0.00079914 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2543-5_0_8_load_150 | 69 | 0.0024515 | 0.00061441 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2543-5_0_8_load_34 | 70 | 0.0018907 | 0.00047386 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2543-5_0_8_load_35 | 71 | 0.00093511 | 0.00023436 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2543-5_0_8_load_36 | 72 | 0.0021062 | 0.00052786 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2543-5_0_8_load_37 | 73 | 0.0019112 | 0.00047899 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2543-5_0_8_load_265 | 75 | 0.0023776 | 0.00059588 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2543-5_0_8_load_70 | 76 | 0.0031167 | 0.00078113 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2543-5_0_8_load_68 | 78 | 0.0016479 | 0.00041299 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2543-5_0_8_load_188 | 79 | 0.00083584 | 0.00020948 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2543-5_0_8_load_186 | 80 | 0.00086453 | 0.00021667 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2543-5_0_8_load_185 | 81 | 0.0023058 | 0.00057788 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2543-5_0_8_load_245 | 82 | 0.0038748 | 0.00097112 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2543-5_0_8_load_41 | 83 | 0.0011617 | 0.00029114 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2543-5_0_8_load_42 | 84 | 0.0017227 | 0.00043176 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2543-5_0_8_load_43 | 85 | 0.0017286 | 0.00043323 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2543-5_0_8_load_44 | 86 | 0.001158 | 0.00029022 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2543-5_0_8_load_45 | 87 | 0.0011655 | 0.00029211 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2543-5_0_8_load_66 | 88 | 0.0011569 | 0.00028994 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2543-5_0_8_load_76 | 89 | 0.0016598 | 0.00041599 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2543-5_0_8_load_74 | 90 | 0.0016546 | 0.00041468 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2543-5_0_8_load_46 | 91 | 0.0016706 | 0.00041869 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2543-5_0_8_load_47 | 92 | 0.003892 | 0.00097543 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2543-5_0_8_load_49 | 94 | 0.00042505 | 0.00010653 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2543-5_0_8_load_97 | 96 | 0.00058433 | 0.00014645 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2543-5_0_8_load_231 | 97 | 0.0012796 | 0.0003207 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2543-5_0_8_load_95 | 98 | 0.00059647 | 0.00014949 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2543-5_0_8_load_252 | 99 | 0.00040956 | 0.00010264 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2543-5_0_8_load_144 | 102 | 0.0024384 | 0.00061113 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2543-5_0_8_load_52 | 103 | 0.0010775 | 0.00027005 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2543-5_0_8_load_53 | 104 | 0.00088791 | 0.00022253 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2543-5_0_8_load_244 | 106 | 0.00086915 | 0.00021783 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2543-5_0_8_load_241 | 107 | 0.0023023 | 0.00057701 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2543-5_0_8_load_256 | 108 | 0.0014342 | 0.00035943 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2543-5_0_8_load_242 | 109 | 0.0011272 | 0.0002825 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2543-5_0_8_load_58 | 110 | 0.0016795 | 0.00042093 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2543-5_0_8_load_72 | 111 | 0.0036124 | 0.00090535 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2543-5_0_8_load_78 | 112 | 0.00055873 | 0.00014003 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2543-5_0_8_load_189 | 113 | 0.00031215 | 7.8232e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2543-5_0_8_load_62 | 114 | 0.0032989 | 0.00082678 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2543-5_0_8_load_63 | 115 | 0.0036694 | 0.00091964 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2543-5_0_8_load_64 | 116 | 0.0029084 | 0.00072891 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2543-5_0_8_load_65 | 117 | 0.0030342 | 0.00076045 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2543-5_0_8_load_182 | 118 | 0.0049746 | 0.0012468 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2543-5_0_8_load_183 | 119 | 0.0020862 | 0.00052285 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2543-5_0_8_load_274 | 120 | 0.0030676 | 0.00076882 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2543-5_0_8_load_67 | 122 | 0.0063589 | 0.0015937 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2543-5_0_8_load_69 | 123 | 0.00201 | 0.00050374 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2543-5_0_8_load_71 | 124 | 0.0031267 | 0.00078361 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2543-5_0_8_load_234 | 125 | 0.0053486 | 0.0013405 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2543-5_0_8_load_73 | 127 | 0.0016557 | 0.00041497 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2543-5_0_8_load_75 | 128 | 0.0011284 | 0.00028279 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2543-5_0_8_load_77 | 129 | 0.0016553 | 0.00041485 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2543-5_0_8_load_139 | 130 | 0.0011264 | 0.00028231 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2543-5_0_8_load_140 | 131 | 0.0020639 | 0.00051727 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2543-5_0_8_load_190 | 132 | 0.00047784 | 0.00011976 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2543-5_0_8_load_79 | 133 | 0.0016685 | 0.00041816 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2543-5_0_8_load_80 | 134 | 0.00061932 | 0.00015522 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2543-5_0_8_load_81 | 135 | 0.0014514 | 0.00036376 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2543-5_0_8_load_105 | 138 | 0.00042793 | 0.00010725 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2543-5_0_8_load_116 | 139 | 0.00141 | 0.00035337 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2543-5_0_8_load_212 | 140 | 0.0019412 | 0.00048652 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2543-5_0_8_load_107 | 141 | 0.00081098 | 0.00020325 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2543-5_0_8_load_114 | 144 | 0.0019401 | 0.00048624 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2543-5_0_8_load_210 | 145 | 0.0011486 | 0.00028787 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2543-5_0_8_load_84 | 146 | 0.0036077 | 0.00090418 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2543-5_0_8_load_85 | 147 | 0.0046197 | 0.0011578 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2543-5_0_8_load_87 | 149 | 0.0015749 | 0.00039471 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2543-5_0_8_load_88 | 150 | 0.00087325 | 0.00021886 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2543-5_0_8_load_89 | 151 | 0.0012224 | 0.00030636 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2543-5_0_8_load_180 | 152 | 0.0014165 | 0.000355 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2543-5_0_8_load_136 | 153 | 0.0011705 | 0.00029335 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2543-5_0_8_load_147 | 154 | 0.0012201 | 0.00030578 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2543-5_0_8_load_181 | 155 | 0.0041581 | 0.0010421 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2543-5_0_8_load_121 | 156 | 0.0017908 | 0.00044881 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2543-5_0_8_load_137 | 157 | 0.0021136 | 0.00052972 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2543-5_0_8_load_148 | 158 | 0.005002 | 0.0012536 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2543-5_0_8_load_90 | 159 | 0.0023567 | 0.00059065 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2543-5_0_8_load_91 | 160 | 0.0055046 | 0.0013796 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2543-5_0_8_load_92 | 161 | 0.003171 | 0.00079473 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2543-5_0_8_load_94 | 163 | 0.0020704 | 0.00051888 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2543-5_0_8_load_220 | 165 | 0.0020501 | 0.00051381 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2543-5_0_8_load_135 | 166 | 0.0032394 | 0.00081187 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2543-5_0_8_load_132 | 167 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2543-5_0_8_load_174 | 168 | 0.0019984 | 0.00050084 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2543-5_0_8_load_96 | 169 | 0.00061053 | 0.00015301 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2543-5_0_8_load_98 | 170 | 0.00064377 | 0.00016134 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2543-5_0_8_load_172 | 171 | 0.0021567 | 0.00054052 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2543-5_0_8_load_99 | 172 | 0.0031224 | 0.00078256 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2543-5_0_8_load_100 | 173 | 0.0020001 | 0.00050127 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2543-5_0_8_load_102 | 175 | 0.0018784 | 0.00047077 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2543-5_0_8_load_103 | 176 | 0.0031478 | 0.00078891 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2543-5_0_8_load_104 | 177 | 0.0016248 | 0.0004072 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2543-5_0_8_load_165 | 178 | 0.0010311 | 0.00025841 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2543-5_0_8_load_191 | 179 | 0.0055426 | 0.0013891 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2543-5_0_8_load_154 | 180 | 0.0026952 | 0.00067547 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2543-5_0_8_load_236 | 183 | 0.0022422 | 0.00056196 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2543-5_0_8_load_259 | 184 | 0.00045532 | 0.00011411 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2543-5_0_8_load_178 | 185 | 0.0050447 | 0.0012643 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2543-5_0_8_load_258 | 186 | 0.00065134 | 0.00016324 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2543-5_0_8_load_112 | 187 | 0.0021088 | 0.0005285 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2543-5_0_8_load_113 | 188 | 0.0015333 | 0.00038429 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2543-5_0_8_load_115 | 189 | 0.0021002 | 0.00052636 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2543-5_0_8_load_254 | 190 | 0.0023048 | 0.00057763 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2543-5_0_8_load_253 | 191 | 0.0023069 | 0.00057817 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2543-5_0_8_load_117 | 192 | 0.0027341 | 0.00068524 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2543-5_0_8_load_118 | 193 | 0.0038343 | 0.00096097 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2543-5_0_8_load_119 | 194 | 0.0019584 | 0.00049082 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2543-5_0_8_load_120 | 195 | 0.0030099 | 0.00075434 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2543-5_0_8_load_270 | 196 | 0.0034463 | 0.00086373 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2543-5_0_8_load_122 | 197 | 0.0039595 | 0.00099235 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2543-5_0_8_load_196 | 198 | 0.0018332 | 0.00045944 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2543-5_0_8_load_123 | 199 | 0.0015394 | 0.00038581 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2543-5_0_8_load_192 | 200 | 0.0023852 | 0.00059778 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2543-5_0_8_load_193 | 201 | 0.0023536 | 0.00058986 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2543-5_0_8_load_194 | 202 | 0.001901 | 0.00047644 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2543-5_0_8_load_195 | 203 | 0.0012925 | 0.00032394 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2543-5_0_8_load_124 | 204 | 0.001957 | 0.00049047 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2543-5_0_8_load_260 | 205 | 0.0014388 | 0.00036059 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2543-5_0_8_load_133 | 206 | 0.0052598 | 0.0013182 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2543-5_0_8_load_127 | 207 | 0.0010886 | 0.00027282 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2543-5_0_8_load_129 | 209 | 0.0027381 | 0.00068624 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2543-5_0_8_load_158 | 211 | 0.0022622 | 0.00056696 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2543-5_0_8_load_155 | 212 | 0.001798 | 0.00045062 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2543-5_0_8_load_156 | 213 | 0.0042102 | 0.0010552 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2543-5_0_8_load_134 | 214 | 0.0016961 | 0.00042508 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2543-5_0_8_load_138 | 215 | 0.0011779 | 0.0002952 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2543-5_0_8_load_268 | 216 | 0.002768 | 0.00069372 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2543-5_0_8_load_153 | 217 | 0.0059147 | 0.0014824 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2543-5_0_8_load_157 | 218 | 0.0021851 | 0.00054764 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2543-5_0_8_load_233 | 219 | 0.0016038 | 0.00040195 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2543-5_0_8_load_232 | 220 | 0.0024547 | 0.0006152 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2543-5_0_8_load_159 | 221 | 0.0020789 | 0.00052103 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2543-5_0_8_load_160 | 222 | 0.006467 | 0.0016208 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2543-5_0_8_load_161 | 223 | 0.0020442 | 0.00051231 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2543-5_0_8_load_162 | 224 | 0.0020758 | 0.00052025 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2543-5_0_8_load_163 | 225 | 0.0020318 | 0.00050922 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2543-5_0_8_load_168 | 226 | 0.0020655 | 0.00051765 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2543-5_0_8_load_169 | 227 | 0.0058001 | 0.0014536 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2543-5_0_8_load_229 | 228 | 0.0013834 | 0.0003467 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2543-5_0_8_load_227 | 229 | 0.0012198 | 0.00030571 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2543-5_0_8_load_175 | 230 | 0.0011434 | 0.00028656 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2543-5_0_8_load_184 | 233 | 0.0023249 | 0.00058268 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2543-5_0_8_load_246 | 234 | 0.0039642 | 0.00099352 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2543-5_0_8_load_217 | 235 | 0.0010892 | 0.00027298 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2543-5_0_8_load_218 | 236 | 0.002168 | 0.00054335 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2543-5_0_8_load_206 | 237 | 0.00038202 | 9.5744e-05 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2543-5_0_8_load_197 | 238 | 0.0026206 | 0.0006568 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2543-5_0_8_load_198 | 239 | 0.0018006 | 0.00045128 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2543-5_0_8_load_200 | 241 | 0.00050991 | 0.0001278 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2543-5_0_8_load_207 | 242 | 0.0028871 | 0.00072357 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2543-5_0_8_load_214 | 244 | 0.00068129 | 0.00017075 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2543-5_0_8_load_208 | 245 | 0.0038356 | 0.00096129 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_2543-5_0_8_load_209 | 246 | 0.0005022 | 0.00012586 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_2543-5_0_8_load_237 | 247 | 0.00095001 | 0.0002381 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_2543-5_0_8_load_239 | 248 | 0.0011372 | 0.00028501 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_2543-5_0_8_load_240 | 249 | 0.00074866 | 0.00018763 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_2543-5_0_8_load_247 | 250 | 0.00022676 | 5.6832e-05 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_2543-5_0_8_load_204 | 253 | 0.0034024 | 0.00085272 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_2543-5_0_8_load_235 | 254 | 0.0013778 | 0.00034532 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_2543-5_0_8_load_211 | 255 | 0.0027463 | 0.0006883 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_2543-5_0_8_load_264 | 256 | 0.0017707 | 0.00044378 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_2543-5_0_8_load_238 | 257 | 0.00079264 | 0.00019865 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_2543-5_0_8_load_219 | 258 | 0.0014103 | 0.00035346 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_2543-5_0_8_load_255 | 259 | 0.00092078 | 0.00023077 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_2543-5_0_8_load_226 | 261 | 0.002239 | 0.00056115 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_2543-5_0_8_load_225 | 262 | 0.0034594 | 0.00086701 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_2543-5_0_8_load_266 | 263 | 0.0019376 | 0.0004856 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_2543-5_0_8_load_228 | 264 | 0.0013349 | 0.00033457 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_2543-5_0_8_load_271 | 265 | 0.000581 | 0.00014561 | 0 | 0 |  | 1 | TRUE | wye
224 | LV_2543-5_0_8_load_251 | 266 | 0.0018763 | 0.00047024 | 0 | 0 |  | 1 | TRUE | wye
225 | LV_2543-5_0_8_load_269 | 267 | 0.0022567 | 0.00056558 | 0 | 0 |  | 1 | TRUE | wye
226 | LV_2543-5_0_8_load_273 | 268 | 0.0064212 | 0.0016093 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2543-5_0_8_line_0 |  | 0 | 1 | 3.7373e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2543-5_0_8_line_1 |  | 0 | 2 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2543-5_0_8_line_2 |  | 1 | 3 | 0.0086954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2543-5_0_8_line_3 |  | 2 | 4 | 0.0066944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2543-5_0_8_line_4 |  | 3 | 5 | 0.019963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2543-5_0_8_line_5 |  | 5 | 6 | 0.018329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2543-5_0_8_line_6 |  | 5 | 7 | 0.006545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2543-5_0_8_line_7 |  | 6 | 100 | 0.038192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2543-5_0_8_line_8 |  | 7 | 101 | 0.014726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2543-5_0_8_line_9 |  | 7 | 102 | 0.013133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2543-5_0_8_line_10 |  | 8 | 9 | 0.010596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2543-5_0_8_line_11 |  | 8 | 10 | 0.003039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2543-5_0_8_line_12 |  | 9 | 11 | 0.01854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2543-5_0_8_line_13 |  | 10 | 12 | 0.029778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2543-5_0_8_line_14 |  | 11 | 13 | 0.027436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2543-5_0_8_line_15 |  | 12 | 14 | 0.011781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2543-5_0_8_line_16 |  | 13 | 15 | 0.020123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2543-5_0_8_line_17 |  | 13 | 16 | 0.026214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2543-5_0_8_line_18 |  | 14 | 17 | 0.039084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2543-5_0_8_line_19 |  | 14 | 18 | 0.012619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2543-5_0_8_line_20 |  | 15 | 228 | 0.026734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2543-5_0_8_line_21 |  | 16 | 178 | 0.032878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2543-5_0_8_line_22 |  | 17 | 256 | 0.020542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2543-5_0_8_line_23 |  | 18 | 255 | 0.023655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2543-5_0_8_line_24 |  | 19 | 20 | 0.0030824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2543-5_0_8_line_25 |  | 19 | 21 | 0.014936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2543-5_0_8_line_26 |  | 20 | 22 | 0.0087816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2543-5_0_8_line_27 |  | 21 | 23 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2543-5_0_8_line_28 |  | 21 | 24 | 0.044047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2543-5_0_8_line_29 |  | 22 | 25 | 0.0045415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2543-5_0_8_line_30 |  | 23 | 26 | 0.010405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2543-5_0_8_line_31 |  | 24 | 27 | 0.006102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2543-5_0_8_line_32 |  | 24 | 28 | 0.0095891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2543-5_0_8_line_33 |  | 25 | 29 | 0.012169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2543-5_0_8_line_34 |  | 26 | 30 | 0.026786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2543-5_0_8_line_35 |  | 27 | 31 | 0.015392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2543-5_0_8_line_36 |  | 27 | 32 | 0.014998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2543-5_0_8_line_37 |  | 28 | 33 | 0.020843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2543-5_0_8_line_38 |  | 29 | 131 | 0.0028534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2543-5_0_8_line_39 |  | 30 | 81 | 0.0030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2543-5_0_8_line_40 |  | 31 | 208 | 0.025646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2543-5_0_8_line_41 |  | 32 | 158 | 0.02033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2543-5_0_8_line_42 |  | 33 | 260 | 0.0089046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2543-5_0_8_line_43 |  | 34 | 35 | 0.020576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2543-5_0_8_line_44 |  | 34 | 36 | 0.0043701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2543-5_0_8_line_45 |  | 35 | 37 | 0.0013199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2543-5_0_8_line_46 |  | 36 | 38 | 0.034349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2543-5_0_8_line_47 |  | 36 | 39 | 0.023606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2543-5_0_8_line_48 |  | 37 | 40 | 0.01731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2543-5_0_8_line_49 |  | 39 | 41 | 0.010951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2543-5_0_8_line_50 |  | 39 | 42 | 0.01103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2543-5_0_8_line_51 |  | 40 | 43 | 0.025909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2543-5_0_8_line_52 |  | 41 | 44 | 0.049277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2543-5_0_8_line_53 |  | 42 | 45 | 0.0059819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2543-5_0_8_line_54 |  | 43 | 100 | 0.0054613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2543-5_0_8_line_55 |  | 44 | 253 | 0.052987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2543-5_0_8_line_56 |  | 45 | 266 | 0.024945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2543-5_0_8_line_57 |  | 46 | 47 | 0.013232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2543-5_0_8_line_58 |  | 46 | 48 | 0.04604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2543-5_0_8_line_59 |  | 47 | 49 | 0.015587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2543-5_0_8_line_60 |  | 48 | 50 | 0.026783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2543-5_0_8_line_61 |  | 48 | 51 | 0.015793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2543-5_0_8_line_62 |  | 49 | 52 | 0.021484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2543-5_0_8_line_63 |  | 50 | 53 | 0.0087997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2543-5_0_8_line_64 |  | 50 | 54 | 0.023285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2543-5_0_8_line_65 |  | 51 | 55 | 0.0041853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2543-5_0_8_line_66 |  | 52 | 56 | 0.01595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2543-5_0_8_line_67 |  | 52 | 57 | 0.022946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2543-5_0_8_line_68 |  | 52 | 58 | 0.01797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2543-5_0_8_line_69 |  | 53 | 59 | 0.056447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2543-5_0_8_line_70 |  | 54 | 60 | 0.036971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2543-5_0_8_line_71 |  | 55 | 61 | 0.0076635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2543-5_0_8_line_72 |  | 56 | 65 | 0.027011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2543-5_0_8_line_73 |  | 57 | 66 | 0.029997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2543-5_0_8_line_74 |  | 58 | 62 | 0.0050136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2543-5_0_8_line_75 |  | 60 | 171 | 0.016759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2543-5_0_8_line_76 |  | 62 | 63 | 0.00081361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2543-5_0_8_line_77 |  | 63 | 64 | 0.0071042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2543-5_0_8_line_78 |  | 64 | 67 | 0.0067545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2543-5_0_8_line_79 |  | 65 | 68 | 0.12778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2543-5_0_8_line_80 |  | 66 | 69 | 0.019067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2543-5_0_8_line_81 |  | 67 | 112 | 0.0053591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2543-5_0_8_line_82 |  | 68 | 99 | 0.6491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2543-5_0_8_line_83 |  | 69 | 181 | 0.015863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2543-5_0_8_line_84 |  | 70 | 71 | 0.014983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2543-5_0_8_line_85 |  | 70 | 72 | 4.2815e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2543-5_0_8_line_86 |  | 71 | 73 | 0.0081591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2543-5_0_8_line_87 |  | 72 | 74 | 0.021475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2543-5_0_8_line_88 |  | 73 | 75 | 0.0031633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2543-5_0_8_line_89 |  | 74 | 76 | 0.0084872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2543-5_0_8_line_90 |  | 74 | 77 | 0.037255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2543-5_0_8_line_91 |  | 76 | 78 | 0.028556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2543-5_0_8_line_92 |  | 77 | 79 | 0.021805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2543-5_0_8_line_93 |  | 77 | 80 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2543-5_0_8_line_94 |  | 78 | 122 | 0.022084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2543-5_0_8_line_95 |  | 79 | 235 | 0.0071691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2543-5_0_8_line_96 |  | 80 | 233 | 0.0082794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2543-5_0_8_line_97 |  | 81 | 82 | 0.026743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2543-5_0_8_line_98 |  | 82 | 234 | 0.0015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2543-5_0_8_line_99 |  | 83 | 84 | 0.0071642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2543-5_0_8_line_100 |  | 83 | 85 | 0.0030186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2543-5_0_8_line_101 |  | 84 | 86 | 0.0095754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2543-5_0_8_line_102 |  | 85 | 87 | 0.0057734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2543-5_0_8_line_103 |  | 86 | 88 | 0.0088003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2543-5_0_8_line_104 |  | 87 | 89 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2543-5_0_8_line_105 |  | 89 | 90 | 0.0036139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2543-5_0_8_line_106 |  | 90 | 127 | 0.0077745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2543-5_0_8_line_107 |  | 91 | 92 | 0.040523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2543-5_0_8_line_108 |  | 91 | 93 | 0.022736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2543-5_0_8_line_109 |  | 92 | 94 | 0.0032528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2543-5_0_8_line_110 |  | 93 | 95 | 0.010915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2543-5_0_8_line_111 |  | 94 | 96 | 0.027107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2543-5_0_8_line_112 |  | 95 | 97 | 0.019028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2543-5_0_8_line_113 |  | 96 | 98 | 0.00070854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2543-5_0_8_line_114 |  | 98 | 169 | 0.0020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2543-5_0_8_line_115 |  | 100 | 110 | 0.026849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2543-5_0_8_line_116 |  | 101 | 205 | 0.020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2543-5_0_8_line_117 |  | 102 | 215 | 0.023838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2543-5_0_8_line_118 |  | 103 | 104 | 0.035597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2543-5_0_8_line_119 |  | 104 | 105 | 0.026833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2543-5_0_8_line_120 |  | 105 | 106 | 0.022896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2543-5_0_8_line_121 |  | 105 | 107 | 0.018409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2543-5_0_8_line_122 |  | 106 | 108 | 0.0049261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2543-5_0_8_line_123 |  | 107 | 109 | 0.041726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2543-5_0_8_line_124 |  | 108 | 259 | 0.026167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2543-5_0_8_line_125 |  | 109 | 251 | 0.083145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2543-5_0_8_line_126 |  | 110 | 111 | 0.077293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2543-5_0_8_line_127 |  | 112 | 113 | 0.0001225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2543-5_0_8_line_128 |  | 113 | 132 | 0.0059846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2543-5_0_8_line_129 |  | 114 | 115 | 0.021664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2543-5_0_8_line_130 |  | 114 | 116 | 0.0018917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2543-5_0_8_line_131 |  | 115 | 117 | 0.009277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2543-5_0_8_line_132 |  | 117 | 118 | 0.015989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2543-5_0_8_line_133 |  | 118 | 119 | 0.027904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2543-5_0_8_line_134 |  | 119 | 233 | 0.010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2543-5_0_8_line_135 |  | 120 | 121 | 0.080076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2543-5_0_8_line_136 |  | 121 | 268 | 0.031593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2543-5_0_8_line_137 |  | 121 | 265 | 0.11047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2543-5_0_8_line_138 |  | 122 | 123 | 0.02951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_2543-5_0_8_line_139 |  | 123 | 124 | 0.02853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_2543-5_0_8_line_140 |  | 124 | 125 | 0.07825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_2543-5_0_8_line_141 |  | 125 | 126 | 0.022996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_2543-5_0_8_line_142 |  | 126 | 162 | 0.069443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_2543-5_0_8_line_143 |  | 127 | 128 | 0.00068619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2543-5_0_8_line_144 |  | 128 | 129 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2543-5_0_8_line_145 |  | 129 | 130 | 0.0027857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2543-5_0_8_line_146 |  | 130 | 131 | 0.0067703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2543-5_0_8_line_147 |  | 132 | 237 | 0.0067524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2543-5_0_8_line_148 |  | 133 | 134 | 0.041605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2543-5_0_8_line_149 |  | 133 | 135 | 0.0061157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2543-5_0_8_line_150 |  | 134 | 136 | 0.055338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2543-5_0_8_line_151 |  | 135 | 137 | 0.027812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2543-5_0_8_line_152 |  | 136 | 138 | 0.050807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2543-5_0_8_line_153 |  | 137 | 139 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_2543-5_0_8_line_154 |  | 137 | 140 | 0.029078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_2543-5_0_8_line_155 |  | 138 | 143 | 0.041644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2543-5_0_8_line_156 |  | 139 | 144 | 0.0020728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
157 | LV_2543-5_0_8_line_157 |  | 140 | 145 | 0.034809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_2543-5_0_8_line_158 |  | 141 | 142 | 0.014089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2543-5_0_8_line_159 |  | 142 | 183 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2543-5_0_8_line_160 |  | 143 | 182 | 0.015832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2543-5_0_8_line_161 |  | 144 | 187 | 0.020188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
162 | LV_2543-5_0_8_line_162 |  | 145 | 255 | 0.0043287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
163 | LV_2543-5_0_8_line_163 |  | 146 | 147 | 0.022131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
164 | LV_2543-5_0_8_line_164 |  | 146 | 148 | 0.0070891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
165 | LV_2543-5_0_8_line_165 |  | 147 | 149 | 0.027875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
166 | LV_2543-5_0_8_line_166 |  | 148 | 150 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2543-5_0_8_line_167 |  | 148 | 151 | 0.018298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_2543-5_0_8_line_168 |  | 149 | 152 | 0.0034144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
169 | LV_2543-5_0_8_line_169 |  | 150 | 153 | 0.023799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2543-5_0_8_line_170 |  | 151 | 154 | 0.00026189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
171 | LV_2543-5_0_8_line_171 |  | 152 | 155 | 0.042388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
172 | LV_2543-5_0_8_line_172 |  | 152 | 156 | 0.02333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2543-5_0_8_line_173 |  | 153 | 157 | 9.809e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_2543-5_0_8_line_174 |  | 154 | 158 | 0.011009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
175 | LV_2543-5_0_8_line_175 |  | 155 | 166 | 0.022998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
176 | LV_2543-5_0_8_line_176 |  | 156 | 194 | 0.030718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_2543-5_0_8_line_177 |  | 157 | 215 | 0.0045306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_2543-5_0_8_line_178 |  | 159 | 160 | 0.0093101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_2543-5_0_8_line_179 |  | 159 | 161 | 0.023428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_2543-5_0_8_line_180 |  | 160 | 162 | 0.023939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2543-5_0_8_line_181 |  | 161 | 163 | 0.012555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2543-5_0_8_line_182 |  | 162 | 164 | 0.022359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
183 | LV_2543-5_0_8_line_183 |  | 163 | 165 | 0.0070014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2543-5_0_8_line_184 |  | 164 | 166 | 0.0023124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
185 | LV_2543-5_0_8_line_185 |  | 164 | 167 | 0.021035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2543-5_0_8_line_186 |  | 165 | 168 | 0.0068833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2543-5_0_8_line_187 |  | 167 | 206 | 0.028045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_2543-5_0_8_line_188 |  | 168 | 224 | 0.011856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_2543-5_0_8_line_189 |  | 169 | 170 | 0.0020857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_2543-5_0_8_line_190 |  | 170 | 171 | 0.016396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_2543-5_0_8_line_191 |  | 172 | 173 | 0.02225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_2543-5_0_8_line_192 |  | 172 | 174 | 0.0092685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_2543-5_0_8_line_193 |  | 173 | 175 | 0.0028365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_2543-5_0_8_line_194 |  | 174 | 176 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_2543-5_0_8_line_195 |  | 174 | 177 | 0.010423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_2543-5_0_8_line_196 |  | 175 | 178 | 0.006159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_2543-5_0_8_line_197 |  | 176 | 179 | 0.0058272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_2543-5_0_8_line_198 |  | 177 | 180 | 0.026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2543-5_0_8_line_199 |  | 180 | 181 | 0.016609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_2543-5_0_8_line_200 |  | 181 | 217 | 0.022575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_2543-5_0_8_line_201 |  | 182 | 184 | 0.018282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_2543-5_0_8_line_202 |  | 183 | 185 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_2543-5_0_8_line_203 |  | 184 | 186 | 0.012082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_2543-5_0_8_line_204 |  | 185 | 231 | 0.020662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_2543-5_0_8_line_205 |  | 186 | 232 | 0.012693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_2543-5_0_8_line_206 |  | 187 | 188 | 0.0044759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
207 | LV_2543-5_0_8_line_207 |  | 188 | 189 | 0.023832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
208 | LV_2543-5_0_8_line_208 |  | 189 | 190 | 0.019199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
209 | LV_2543-5_0_8_line_209 |  | 190 | 191 | 0.0081454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
210 | LV_2543-5_0_8_line_210 |  | 191 | 234 | 0.032406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
211 | LV_2543-5_0_8_line_211 |  | 192 | 193 | 0.029657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_2543-5_0_8_line_212 |  | 192 | 194 | 0.00053246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_2543-5_0_8_line_213 |  | 193 | 195 | 0.021215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2543-5_0_8_line_214 |  | 193 | 196 | 0.037519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2543-5_0_8_line_215 |  | 195 | 197 | 0.013429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_2543-5_0_8_line_216 |  | 196 | 198 | 0.020976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_2543-5_0_8_line_217 |  | 197 | 199 | 0.018571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2543-5_0_8_line_218 |  | 198 | 202 | 0.013352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_2543-5_0_8_line_219 |  | 199 | 204 | 0.010516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2543-5_0_8_line_220 |  | 200 | 201 | 0.039567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2543-5_0_8_line_221 |  | 200 | 202 | 0.0019785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_2543-5_0_8_line_222 |  | 201 | 203 | 0.00020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_2543-5_0_8_line_223 |  | 205 | 216 | 0.0015491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2543-5_0_8_line_224 |  | 206 | 214 | 0.0014804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2543-5_0_8_line_225 |  | 207 | 208 | 0.018774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_2543-5_0_8_line_226 |  | 207 | 209 | 0.0055779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_2543-5_0_8_line_227 |  | 208 | 210 | 0.030197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2543-5_0_8_line_228 |  | 210 | 211 | 0.017827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_2543-5_0_8_line_229 |  | 210 | 212 | 0.015227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_2543-5_0_8_line_230 |  | 212 | 213 | 0.012455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_2543-5_0_8_line_231 |  | 213 | 218 | 0.013379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_2543-5_0_8_line_232 |  | 216 | 267 | 0.047803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_2543-5_0_8_line_233 |  | 218 | 219 | 0.018821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_2543-5_0_8_line_234 |  | 219 | 220 | 0.013024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_2543-5_0_8_line_235 |  | 221 | 222 | 0.011717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_2543-5_0_8_line_236 |  | 221 | 223 | 0.005773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_2543-5_0_8_line_237 |  | 222 | 224 | 0.00038533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_2543-5_0_8_line_238 |  | 223 | 225 | 0.0056696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_2543-5_0_8_line_239 |  | 225 | 226 | 0.0069832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_2543-5_0_8_line_240 |  | 226 | 227 | 0.0022563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2543-5_0_8_line_241 |  | 228 | 229 | 0.028323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_2543-5_0_8_line_242 |  | 229 | 264 | 0.025106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_2543-5_0_8_line_243 |  | 230 | 231 | 0.016073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_2543-5_0_8_line_244 |  | 231 | 232 | 0.025518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_2543-5_0_8_line_245 |  | 235 | 236 | 0.034518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
246 | LV_2543-5_0_8_line_246 |  | 236 | 258 | 0.049686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
247 | LV_2543-5_0_8_line_247 |  | 238 | 239 | 0.029231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_2543-5_0_8_line_248 |  | 238 | 240 | 0.029469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
249 | LV_2543-5_0_8_line_249 |  | 239 | 241 | 0.0062856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_2543-5_0_8_line_250 |  | 239 | 242 | 0.30443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_2543-5_0_8_line_251 |  | 240 | 243 | 0.007046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
252 | LV_2543-5_0_8_line_252 |  | 241 | 244 | 0.0059714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_2543-5_0_8_line_253 |  | 242 | 245 | 0.030417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_2543-5_0_8_line_254 |  | 243 | 250 | 0.0079643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
255 | LV_2543-5_0_8_line_255 |  | 245 | 246 | 0.015037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_2543-5_0_8_line_256 |  | 246 | 247 | 0.0081077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_2543-5_0_8_line_257 |  | 247 | 248 | 0.00045428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_2543-5_0_8_line_258 |  | 248 | 249 | 0.0016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_2543-5_0_8_line_259 |  | 250 | 251 | 0.0644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
260 | LV_2543-5_0_8_line_260 |  | 251 | 252 | 0.084474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_2543-5_0_8_line_261 |  | 252 | 265 | 0.040835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_2543-5_0_8_line_262 |  | 253 | 254 | 0.0080794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_2543-5_0_8_line_263 |  | 256 | 257 | 0.0082821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_2543-5_0_8_line_264 |  | 258 | 259 | 0.019025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
265 | LV_2543-5_0_8_line_265 |  | 260 | 261 | 0.012696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_2543-5_0_8_line_266 |  | 260 | 262 | 0.021272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_2543-5_0_8_line_267 |  | 261 | 263 | 0.032352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2543-5_0_8_trafo_39 | 0.63 MVA 20/0.4 kV | 269 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2598716.2056 | 1228597.9058 | 2598716.2046 | 1228597.9022
1 | 2598716.2056 | 1228597.9058 | 2598717.8695 | 1228603.8213 | 2598718.6281 | 1228608.2237 | 2598718.7583 | 1228614.0716 | 2598718.3029 | 1228619.3245
2 | 2598716.2046 | 1228597.9022 | 2598713.8501 | 1228589.5317
3 | 2598718.3029 | 1228619.3245 | 2598717.7247 | 1228625.9939
4 | 2598708.4447 | 1228570.3148 | 2598713.8501 | 1228589.5317
5 | 2598708.4447 | 1228570.3148 | 2598705.4447 | 1228571.0159 | 2598700.9449 | 1228572.6401 | 2598694.8089 | 1228575.7211 | 2598691.7688 | 1228577.6454
6 | 2598714.998 | 1228570.102 | 2598710.0281 | 1228570.1254 | 2598708.4447 | 1228570.3148
7 | 2598664.8975 | 1228604.5007 | 2598675.8268 | 1228591.8017 | 2598682.5527 | 1228584.4958 | 2598687.605 | 1228580.281 | 2598691.7688 | 1228577.6454
8 | 2598714.998 | 1228570.102 | 2598713.899 | 1228567.901 | 2598708.6765 | 1228556.7956
9 | 2598714.998 | 1228570.102 | 2598720.0439 | 1228570.7346 | 2598724.2565 | 1228571.9232 | 2598727.742 | 1228573.0751
10 | 2598575.28 | 1228962.7209 | 2598568.3039 | 1228970.6967
11 | 2598575.28 | 1228962.7209 | 2598577.2807 | 1228960.4335
12 | 2598568.3039 | 1228970.6967 | 2598568.3039 | 1228970.6967 | 2598558.8981 | 1228983.1064 | 2598556.9478 | 1228985.345
13 | 2598596.8854 | 1228938.0195 | 2598577.2807 | 1228960.4335
14 | 2598537.7222 | 1229004.7803 | 2598545.4023 | 1228998.5968 | 2598556.9478 | 1228985.345
15 | 2598604.6416 | 1228929.1519 | 2598596.8854 | 1228938.0195
16 | 2598537.7222 | 1229004.7803 | 2598545.4808 | 1229009.4032 | 2598554.7701 | 1229015.4631
17 | 2598537.7222 | 1229004.7803 | 2598532.3503 | 1229001.4686 | 2598515.7771 | 1228990.4479
18 | 2598604.6416 | 1228929.1519 | 2598606.136 | 1228937.3897 | 2598619.4147 | 1228962.3346 | 2598620.7001 | 1228964.424
19 | 2598604.6416 | 1228929.1519 | 2598610.8972 | 1228921.6014 | 2598612.7281 | 1228919.4645
20 | 2598554.7701 | 1229015.4631 | 2598561.665 | 1229019.9609 | 2598575.0074 | 1229027.1173 | 2598577.9108 | 1229028.8103
21 | 2598515.7771 | 1228990.4479 | 2598514.8021 | 1228989.7996 | 2598497.5491 | 1228977.508 | 2598489.3766 | 1228970.8782
22 | 2598620.7001 | 1228964.424 | 2598631.4636 | 1228981.9207
23 | 2598628.1189 | 1228901.5009 | 2598612.7281 | 1228919.4645
24 | 2598828.7574 | 1228689.0156 | 2598825.7181 | 1228689.5295
25 | 2598810.9911 | 1228692.0197 | 2598825.7181 | 1228689.5295
26 | 2598828.7574 | 1228689.0156 | 2598837.4161 | 1228687.5516
27 | 2598810.9911 | 1228692.0197 | 2598809.8935 | 1228696.3669 | 2598808.2884 | 1228701.0478 | 2598805.9254 | 1228705.9984
28 | 2598810.9911 | 1228692.0197 | 2598811.687 | 1228686.5163 | 2598812.0191 | 1228681.0018 | 2598811.7902 | 1228673.264 | 2598810.736 | 1228668.0055 | 2598809.2426 | 1228663.3586 | 2598802.8455 | 1228649.7964
29 | 2598841.894 | 1228686.7944 | 2598837.4161 | 1228687.5516
30 | 2598801.4435 | 1228715.3885 | 2598805.9254 | 1228705.9984
31 | 2598800.3972 | 1228644.2047 | 2598802.8455 | 1228649.7964
32 | 2598802.8455 | 1228649.7964 | 2598812.3302 | 1228651.2079
33 | 2598853.8927 | 1228684.7656 | 2598841.894 | 1228686.7944
34 | 2598788.0335 | 1228738.5378 | 2598791.3555 | 1228733.315 | 2598797.8685 | 1228722.7851 | 2598801.2459 | 1228715.8025 | 2598801.4435 | 1228715.3885
35 | 2598800.3972 | 1228644.2047 | 2598790.6624 | 1228646.0413 | 2598785.4428 | 1228647.6544 | 2598785.4228 | 1228647.6633
36 | 2598800.3972 | 1228644.2047 | 2598795.6792 | 1228629.9678
37 | 2598832.9463 | 1228654.276 | 2598812.3302 | 1228651.2079
38 | 2598856.7061 | 1228684.2899 | 2598853.8927 | 1228684.7656
39 | 2598786.3377 | 1228741.0251 | 2598786.8645 | 1228740.3757 | 2598788.0335 | 1228738.5378
40 | 2598765.5137 | 1228663.3792 | 2598769.9143 | 1228658.4309 | 2598776.186 | 1228653.0485 | 2598780.5264 | 1228649.8235 | 2598785.4228 | 1228647.6633
41 | 2598795.6792 | 1228629.9678 | 2598794.8858 | 1228627.5739 | 2598792.8992 | 1228619.703 | 2598791.4735 | 1228613.0994 | 2598791.3229 | 1228610.1692
42 | 2598841.7951 | 1228655.2136 | 2598836.863 | 1228654.8589 | 2598832.9463 | 1228654.276
43 | 2598640.7784 | 1228648.2379 | 2598634.16 | 1228661.9865 | 2598632.1401 | 1228666.9057
44 | 2598630.4802 | 1228670.9483 | 2598632.1401 | 1228666.9057
45 | 2598640.7784 | 1228648.2379 | 2598641.3509 | 1228647.0486
46 | 2598630.4802 | 1228670.9483 | 2598652.0074 | 1228686.619 | 2598654.5305 | 1228687.8414 | 2598656.6898 | 1228688.1299 | 2598659.5005 | 1228688.1959
47 | 2598630.4802 | 1228670.9483 | 2598627.1636 | 1228678.0199 | 2598624.9824 | 1228680.9444 | 2598622.7178 | 1228683.4575 | 2598619.385 | 1228685.8931 | 2598615.3096 | 1228688.1621
48 | 2598649.2655 | 1228631.6574 | 2598643.7464 | 1228642.0724 | 2598641.3509 | 1228647.0486
49 | 2598615.3096 | 1228688.1621 | 2598608.901 | 1228690.7986 | 2598605.1952 | 1228692.3606
50 | 2598615.3096 | 1228688.1621 | 2598624.1688 | 1228694.7333
51 | 2598661.8721 | 1228609.0474 | 2598658.8009 | 1228613.6631 | 2598649.2655 | 1228631.6574
52 | 2598559.556 | 1228710.9006 | 2598564.7072 | 1228709.1983 | 2598573.3506 | 1228705.783 | 2598605.1952 | 1228692.3606
53 | 2598624.1688 | 1228694.7333 | 2598628.9733 | 1228698.297
54 | 2598664.8975 | 1228604.5007 | 2598661.8721 | 1228609.0474
55 | 2598559.556 | 1228710.9006 | 2598550.6298 | 1228704.2212 | 2598540.8321 | 1228696.8416 | 2598535.0729 | 1228691.1063 | 2598528.5637 | 1228685.8493 | 2598517.5884 | 1228678.7374
56 | 2598650.7843 | 1228703.9296 | 2598645.8149 | 1228706.1543 | 2598643.0044 | 1228706.6664 | 2598641.6407 | 1228706.7334 | 2598639.5495 | 1228705.8778 | 2598637.2461 | 1228704.4331 | 2598628.9733 | 1228698.297
57 | 2598351.6148 | 1228861.4916 | 2598355.7966 | 1228856.0531 | 2598359.4732 | 1228850.8494
58 | 2598387.497 | 1228814.3971 | 2598375.9022 | 1228827.5971 | 2598359.4732 | 1228850.8494
59 | 2598342.1138 | 1228873.8483 | 2598351.6148 | 1228861.4916
60 | 2598387.497 | 1228814.3971 | 2598395.7295 | 1228805.8008 | 2598407.1815 | 1228796.2364
61 | 2598387.497 | 1228814.3971 | 2598400.4631 | 1228823.4133
62 | 2598328.9354 | 1228890.8148 | 2598334.0017 | 1228884.3984 | 2598342.1138 | 1228873.8483
63 | 2598407.1815 | 1228796.2364 | 2598414.3775 | 1228791.1715
64 | 2598407.1815 | 1228796.2364 | 2598400.6359 | 1228795.9491 | 2598384.5953 | 1228800.7137
65 | 2598400.4631 | 1228823.4133 | 2598403.8992 | 1228825.8027
66 | 2598328.9354 | 1228890.8148 | 2598324.3021 | 1228901.1 | 2598323.5004 | 1228905.703
67 | 2598328.9354 | 1228890.8148 | 2598333.3602 | 1228892.7702 | 2598337.3001 | 1228894.5034 | 2598350.037 | 1228899.8257
68 | 2598328.9354 | 1228890.8148 | 2598320.0025 | 1228887.0041 | 2598313.081 | 1228882.4989
69 | 2598414.3775 | 1228791.1715 | 2598424.4057 | 1228784.1133 | 2598429.1168 | 1228780.2096 | 2598432.7977 | 1228776.4064 | 2598446.8008 | 1228759.4036 | 2598453.0024 | 1228750.6274
70 | 2598384.5953 | 1228800.7137 | 2598357.1011 | 1228808.8803 | 2598349.2232 | 1228811.4601
71 | 2598410.1911 | 1228830.1778 | 2598403.8992 | 1228825.8027
72 | 2598323.5004 | 1228905.703 | 2598322.1995 | 1228912.6964 | 2598321.8006 | 1228921.7019 | 2598322.204 | 1228928.2056 | 2598323.4406 | 1228932.3937
73 | 2598378.4857 | 1228909.2235 | 2598372.2281 | 1228907.6456 | 2598356.2039 | 1228902.4026 | 2598350.037 | 1228899.8257
74 | 2598313.081 | 1228882.4989 | 2598308.8792 | 1228879.7638
75 | 2598333.2963 | 1228816.6756 | 2598349.2232 | 1228811.4601
76 | 2598308.8792 | 1228879.7638 | 2598308.1973 | 1228879.32
77 | 2598308.1973 | 1228879.32 | 2598305.0981 | 1228877.3027 | 2598302.3431 | 1228875.2995
78 | 2598296.8801 | 1228871.3272 | 2598302.3431 | 1228875.2995
79 | 2598323.4406 | 1228932.3937 | 2598281.6129 | 1229053.1341
80 | 2598378.4857 | 1228909.2235 | 2598391.5172 | 1228912.5096 | 2598396.8761 | 1228914.2287
81 | 2598296.8801 | 1228871.3272 | 2598292.5457 | 1228868.1755
82 | 2598281.6129 | 1229053.1341 | 2597652.3435 | 1229212.3677
83 | 2598411.9811 | 1228919.0744 | 2598396.8761 | 1228914.2287
84 | 2599154.2045 | 1228567.965 | 2599145.7171 | 1228565.8056 | 2599139.6512 | 1228564.4055
85 | 2599139.6512 | 1228564.4055 | 2599139.6095 | 1228564.3959
86 | 2599154.2045 | 1228567.965 | 2599161.264 | 1228569.7611 | 2599162.1163 | 1228569.9577
87 | 2599118.5859 | 1228560.1399 | 2599123.2605 | 1228560.6505 | 2599127.3291 | 1228561.5615 | 2599139.6095 | 1228564.3959
88 | 2599165.1987 | 1228570.6688 | 2599162.1163 | 1228569.9577
89 | 2599118.5859 | 1228560.1399 | 2599116.2973 | 1228556.0044 | 2599114.757 | 1228552.5736
90 | 2599122.2512 | 1228597.1612 | 2599121.2335 | 1228582.019 | 2599119.9659 | 1228566.8214 | 2599118.5859 | 1228560.1399
91 | 2599114.757 | 1228552.5736 | 2599111.4013 | 1228545.0988 | 2599108.4004 | 1228540.3965 | 2599103.7022 | 1228534.9051 | 2599098.1114 | 1228529.8203
92 | 2599122.2512 | 1228597.1612 | 2599124.2836 | 1228618.8716
93 | 2599122.2512 | 1228597.1612 | 2599115.6978 | 1228597.1066 | 2599109.1503 | 1228595.2688
94 | 2599081.1411 | 1228515.6905 | 2599097.1024 | 1228528.9027 | 2599098.1114 | 1228529.8203
95 | 2599124.2836 | 1228618.8716 | 2599124.9519 | 1228626.0095
96 | 2599109.1503 | 1228595.2688 | 2599101.179 | 1228593.0313
97 | 2598786.3377 | 1228741.0251 | 2598779.4496 | 1228749.516 | 2598775.0869 | 1228754.3754 | 2598769.4969 | 1228758.8459 | 2598767.7455 | 1228760.0431
98 | 2598767.7455 | 1228760.0431 | 2598766.4301 | 1228760.9422
99 | 2598921.9427 | 1228685.6664 | 2598914.8522 | 1228684.6414
100 | 2598911.8647 | 1228684.2096 | 2598914.8522 | 1228684.6414
101 | 2598931.4197 | 1228687.0362 | 2598921.9427 | 1228685.6664
102 | 2598911.8647 | 1228684.2096 | 2598906.1506 | 1228683.3836
103 | 2598931.4197 | 1228687.0362 | 2598940.1295 | 1228688.2952
104 | 2598893.3798 | 1228681.6308 | 2598898.242 | 1228682.2404 | 2598906.1506 | 1228683.3836
105 | 2598893.3798 | 1228681.6308 | 2598891.5143 | 1228681.3968 | 2598889.7834 | 1228681.2976
106 | 2598889.7834 | 1228681.2976 | 2598884.9459 | 1228681.0201 | 2598882.0216 | 1228681.1864
107 | 2598247.2053 | 1228816.6872 | 2598254.1035 | 1228820.9736 | 2598261.6805 | 1228824.5957 | 2598275.2199 | 1228829.2944 | 2598284.7923 | 1228830.6772
108 | 2598228.0375 | 1228804.4719 | 2598231.3565 | 1228806.8389 | 2598247.2053 | 1228816.6872
109 | 2598284.7923 | 1228830.6772 | 2598286.4326 | 1228830.9142 | 2598288.0275 | 1228830.957
110 | 2598228.0375 | 1228804.4719 | 2598224.0841 | 1228808.4644 | 2598220.3883 | 1228812.2789
111 | 2598314.4087 | 1228826.1808 | 2598314.4087 | 1228826.1808 | 2598306.0005 | 1228829.4964 | 2598298.0008 | 1228830.6439 | 2598291.3418 | 1228831.0461 | 2598288.0275 | 1228830.957
112 | 2598220.3883 | 1228812.2789 | 2598221.8813 | 1228814.1573 | 2598229.6182 | 1228820.303 | 2598234.8777 | 1228824.531
113 | 2598314.4087 | 1228826.1808 | 2598315.0304 | 1228825.8408
114 | 2598316.7925 | 1228824.8773 | 2598315.0304 | 1228825.8408
115 | 2598664.8975 | 1228604.5007 | 2598663.7975 | 1228598.4974 | 2598661.9 | 1228583.7002 | 2598660.6452 | 1228578.01
116 | 2598708.6765 | 1228556.7956 | 2598702.75 | 1228548.6032 | 2598696.3244 | 1228540.3021
117 | 2598751.1963 | 1228577.1765 | 2598736.3942 | 1228575.1001 | 2598728.795 | 1228573.4231 | 2598727.742 | 1228573.0751
118 | 2599255.5512 | 1228783.0986 | 2599235.9026 | 1228772.6035 | 2599223.7457 | 1228767.1563
119 | 2599198.998 | 1228756.7994 | 2599201.2027 | 1228757.5996 | 2599205.4001 | 1228759.3 | 2599216.704 | 1228764.0011 | 2599223.7457 | 1228767.1563
120 | 2599198.998 | 1228756.7994 | 2599200.6026 | 1228746.4041 | 2599200.3974 | 1228741.9015 | 2599199.4043 | 1228737.6992 | 2599197.9331 | 1228734.4655
121 | 2599198.998 | 1228756.7994 | 2599194.3036 | 1228774.5995
122 | 2599197.9331 | 1228734.4655 | 2599195.893 | 1228729.9816
123 | 2599194.3036 | 1228774.5995 | 2599193.904 | 1228787.4294 | 2599194.0418 | 1228796.9906 | 2599194.338 | 1228802.3159 | 2599195.3995 | 1228808.4527 | 2599197.5597 | 1228815.9124
124 | 2599181.7607 | 1228707.9917 | 2599190.4016 | 1228720.9017 | 2599194.9028 | 1228727.8051 | 2599195.893 | 1228729.9816
125 | 2599203.8142 | 1228897.7822 | 2599202.5707 | 1228890.289 | 2599202.176 | 1228885.2528 | 2599202.1602 | 1228880.4833 | 2599204.6633 | 1228850.3873 | 2599204.7079 | 1228844.0836 | 2599204.3586 | 1228838.9028 | 2599203.3881 | 1228833.3997 | 2599201.3416 | 1228826.2958 | 2599197.5597 | 1228815.9124
126 | 2598608.4069 | 1228525.3861 | 2598619.097 | 1228531.0016 | 2598632.4027 | 1228538.7029 | 2598640.1014 | 1228544.0042 | 2598645.603 | 1228549.1059 | 2598650.0969 | 1228554.4969 | 2598653.9016 | 1228560.3994 | 2598657.1002 | 1228566.5023 | 2598658.8969 | 1228571.2046 | 2598660.2011 | 1228575.9961 | 2598660.6452 | 1228578.01
127 | 2598292.5457 | 1228868.1755 | 2598292.4467 | 1228868.1035
128 | 2598292.4467 | 1228868.1035 | 2598287.6064 | 1228864.584
129 | 2599041.0668 | 1228573.3188 | 2599020.8678 | 1228565.4877
130 | 2599019.1041 | 1228564.8039 | 2599020.8678 | 1228565.4877
131 | 2599049.7165 | 1228576.6723 | 2599041.0668 | 1228573.3188
132 | 2599049.7165 | 1228576.6723 | 2599064.6245 | 1228582.4521
133 | 2599091.3932 | 1228590.2845 | 2599067.6023 | 1228583.6066 | 2599064.6245 | 1228582.4521
134 | 2599091.3932 | 1228590.2845 | 2599101.179 | 1228593.0313
135 | 2598969.0467 | 1228800.7637 | 2599037.9089 | 1228830.2688 | 2599039.7501 | 1228831.6026 | 2599040.7882 | 1228832.792 | 2599041.5308 | 1228834.0926
136 | 2599041.5308 | 1228834.0926 | 2599041.7499 | 1228830.8129 | 2599041.522 | 1228826.8217 | 2599040.3623 | 1228823.7423 | 2599037.9755 | 1228820.9077 | 2599033.2021 | 1228817.7622 | 2599022.58 | 1228813.0057
137 | 2599142.6886 | 1228878.4784 | 2599041.5308 | 1228834.0926
138 | 2599081.1411 | 1228515.6905 | 2599072.2868 | 1228508.3613 | 2599057.9019 | 1228497.515
139 | 2599033.439 | 1228482.9558 | 2599039.7733 | 1228485.9091 | 2599054.4349 | 1228494.9008 | 2599057.9019 | 1228497.515
140 | 2599033.439 | 1228482.9558 | 2598999.252 | 1228467.0163 | 2598988.7429 | 1228462.5044 | 2598973.9376 | 1228455.9588 | 2598965.3985 | 1228452.6028 | 2598962.7743 | 1228449.9513
141 | 2598946.598 | 1228433.6062 | 2598962.7743 | 1228449.9513
142 | 2598896.27 | 1228479.5432 | 2598899.4365 | 1228477.4524 | 2598902.9968 | 1228475.1059 | 2598914.0872 | 1228468.2774 | 2598921.9506 | 1228464.0845 | 2598928.1318 | 1228458.7357 | 2598931.5253 | 1228455.1997 | 2598940.5919 | 1228443.4799 | 2598946.598 | 1228433.6062
143 | 2598881.3365 | 1228681.2254 | 2598882.0216 | 1228681.1864
144 | 2598881.3365 | 1228681.2254 | 2598877.4911 | 1228681.4441 | 2598866.1545 | 1228682.8733
145 | 2598866.1545 | 1228682.8733 | 2598863.3906 | 1228683.2218
146 | 2598856.7061 | 1228684.2899 | 2598861.9456 | 1228683.404 | 2598863.3906 | 1228683.2218
147 | 2598282.157 | 1228860.5968 | 2598283.5024 | 1228861.5999 | 2598287.6064 | 1228864.584
148 | 2598743.4066 | 1228891.7724 | 2598703.1367 | 1228881.3181
149 | 2598697.2767 | 1228879.58 | 2598700.2432 | 1228880.5669 | 2598703.1367 | 1228881.3181
150 | 2598796.3021 | 1228907.3058 | 2598792.203 | 1228904.7052 | 2598780.8994 | 1228901.5057 | 2598743.4066 | 1228891.7724
151 | 2598681.6929 | 1228859.7256 | 2598681.33 | 1228862.972 | 2598682.2704 | 1228867.3188 | 2598683.9227 | 1228870.6871 | 2598686.4992 | 1228873.6883 | 2598689.7877 | 1228876.2446 | 2598694.0988 | 1228878.5227 | 2598697.2767 | 1228879.58
152 | 2598796.3021 | 1228907.3058 | 2598799.8028 | 1228910.696 | 2598803.1979 | 1228916.4987 | 2598805.6997 | 1228924.703 | 2598806.8982 | 1228931.8959 | 2598809.0448 | 1228944.703 | 2598811.0808 | 1228954.8562
153 | 2598681.6929 | 1228859.7256 | 2598683.3208 | 1228856.0897 | 2598686.3652 | 1228851.3973 | 2598693.0703 | 1228842.4319
154 | 2598681.6929 | 1228859.7256 | 2598674.1863 | 1228864.0077 | 2598657.9171 | 1228876.3745
155 | 2598826.1382 | 1228993.3171 | 2598818.6583 | 1228980.2443 | 2598815.3915 | 1228972.3403 | 2598813.0642 | 1228964.7474 | 2598811.0808 | 1228954.8562
156 | 2598693.0703 | 1228842.4319 | 2598694.3118 | 1228840.772
157 | 2598657.9171 | 1228876.3745 | 2598634.2011 | 1228894.4019 | 2598630.9352 | 1228898.2137
158 | 2598853.112 | 1228942.2146 | 2598842.8082 | 1228932.6057
159 | 2598853.112 | 1228942.2146 | 2598857.6658 | 1228945.9381 | 2598859.7724 | 1228948.9616 | 2598861.8716 | 1228952.5745 | 2598864.554 | 1228955.4756 | 2598868.8491 | 1228957.7772
160 | 2598834.0045 | 1229007.068 | 2598826.1382 | 1228993.3171
161 | 2598694.3118 | 1228840.772 | 2598706.4029 | 1228824.6049
162 | 2598628.1189 | 1228901.5009 | 2598630.9352 | 1228898.2137
163 | 2598819.0341 | 1228571.4689 | 2598819.0341 | 1228571.4689 | 2598813.9587 | 1228574.3161 | 2598808.9665 | 1228576.4295 | 2598801.9363 | 1228578.5433 | 2598798.4828 | 1228579.3637
164 | 2598791.5119 | 1228580.6357 | 2598796.8302 | 1228579.7563 | 2598798.4828 | 1228579.3637
165 | 2598819.0341 | 1228571.4689 | 2598823.4504 | 1228568.3995 | 2598827.5862 | 1228564.7186 | 2598839.358 | 1228552.5094
166 | 2598791.5119 | 1228580.6357 | 2598785.4055 | 1228580.537 | 2598779.4828 | 1228579.9785
167 | 2598791.5119 | 1228580.6357 | 2598790.6975 | 1228598.0017 | 2598790.7443 | 1228598.9136
168 | 2598841.7279 | 1228550.0515 | 2598839.358 | 1228552.5094
169 | 2598779.4828 | 1228579.9785 | 2598770.2302 | 1228579.1061 | 2598755.7886 | 1228577.7472
170 | 2598790.7578 | 1228599.1751 | 2598790.7443 | 1228598.9136
171 | 2598841.7279 | 1228550.0515 | 2598851.7262 | 1228539.1541 | 2598861.6564 | 1228528.6792 | 2598866.5493 | 1228522.1521 | 2598869.1868 | 1228517.8953
172 | 2598841.7279 | 1228550.0515 | 2598823.607 | 1228535.3573
173 | 2598755.7886 | 1228577.7472 | 2598755.6909 | 1228577.738
174 | 2598790.7578 | 1228599.1751 | 2598791.3229 | 1228610.1692
175 | 2598869.1868 | 1228517.8953 | 2598870.1317 | 1228516.3702 | 2598873.2139 | 1228509.5544 | 2598875.5006 | 1228503.328 | 2598877.1213 | 1228500.2259 | 2598879.1299 | 1228497.2501
176 | 2598823.607 | 1228535.3573 | 2598799.7479 | 1228516.0102
177 | 2598755.6909 | 1228577.738 | 2598754.1987 | 1228577.5976 | 2598751.1963 | 1228577.1765
178 | 2598922.1415 | 1228500.416 | 2598915.022 | 1228494.4168
179 | 2598922.1415 | 1228500.416 | 2598932.8009 | 1228509.3981 | 2598939.2042 | 1228516.4011
180 | 2598896.27 | 1228479.5432 | 2598909.9018 | 1228490.1023 | 2598915.022 | 1228494.4168
181 | 2598950.5992 | 1228521.671 | 2598939.2042 | 1228516.4011 | 2598939.2042 | 1228516.4011
182 | 2598896.27 | 1228479.5432 | 2598886.1803 | 1228488.9507 | 2598880.4236 | 1228495.3334
183 | 2598950.5992 | 1228521.671 | 2598956.9539 | 1228524.61
184 | 2598880.4236 | 1228495.3334 | 2598879.1299 | 1228497.2501
185 | 2598880.4236 | 1228495.3334 | 2598864.2512 | 1228481.8827
186 | 2598956.9539 | 1228524.61 | 2598963.2014 | 1228527.4994
187 | 2598864.2512 | 1228481.8827 | 2598853.4551 | 1228472.9034 | 2598844.5972 | 1228467.1907 | 2598841.5125 | 1228465.6169
188 | 2598973.2063 | 1228533.732 | 2598971.497 | 1228532.2043 | 2598967.1022 | 1228529.3034 | 2598963.2014 | 1228527.4994
189 | 2598316.7925 | 1228824.8773 | 2598318.6224 | 1228823.8766
190 | 2598318.6224 | 1228823.8766 | 2598329.5428 | 1228817.9048 | 2598333.2963 | 1228816.6756
191 | 2598482.3907 | 1228965.2111 | 2598469.4222 | 1228954.6908 | 2598465.1423 | 1228951.1566
192 | 2598457.9955 | 1228945.255 | 2598465.1423 | 1228951.1566
193 | 2598482.3907 | 1228965.2111 | 2598484.5935 | 1228966.9981
194 | 2598457.9955 | 1228945.255 | 2598446.3746 | 1228958.8909
195 | 2598457.9955 | 1228945.255 | 2598451.9564 | 1228940.2759 | 2598449.8482 | 1228938.7606
196 | 2598489.3766 | 1228970.8782 | 2598484.5935 | 1228966.9981
197 | 2598442.5949 | 1228963.3259 | 2598446.3746 | 1228958.8909
198 | 2598427.4527 | 1228925.1073 | 2598439.7268 | 1228931.4852 | 2598449.8482 | 1228938.7606
199 | 2598411.9811 | 1228919.0744 | 2598427.0887 | 1228924.9181 | 2598427.4527 | 1228925.1073
200 | 2598411.9811 | 1228919.0744 | 2598422.3102 | 1228904.0849 | 2598418.6505 | 1228901.6511
201 | 2598834.0045 | 1229007.068 | 2598852.2844 | 1229006.7758
202 | 2598880.1919 | 1228963.8552 | 2598868.8491 | 1228957.7772
203 | 2598864.3652 | 1229006.5827 | 2598852.2844 | 1229006.7758
204 | 2598885.029 | 1228982.9878 | 2598883.9302 | 1228981.3092 | 2598882.9976 | 1228977.6962 | 2598883.5793 | 1228969.2021 | 2598882.4121 | 1228966.4118 | 2598880.1919 | 1228963.8552
205 | 2598877.0339 | 1229007.0259 | 2598870.64 | 1229006.4824 | 2598864.3652 | 1229006.5827
206 | 2598709.1158 | 1228821.0451 | 2598707.9042 | 1228822.5975 | 2598706.4029 | 1228824.6049
207 | 2598723.7793 | 1228802.258 | 2598709.1158 | 1228821.0451
208 | 2598723.7793 | 1228802.258 | 2598727.1715 | 1228797.9118 | 2598736.1403 | 1228787.574
209 | 2598741.4781 | 1228781.4214 | 2598736.1403 | 1228787.574
210 | 2598741.4781 | 1228781.4214 | 2598744.44 | 1228778.0073 | 2598751.3327 | 1228771.6798 | 2598758.6119 | 1228766.2861 | 2598766.4301 | 1228760.9422
211 | 2598799.3344 | 1228515.6748 | 2598781.1986 | 1228500.9686 | 2598776.2052 | 1228497.6344 | 2598775.9277 | 1228497.5105
212 | 2598799.7479 | 1228516.0102 | 2598799.3344 | 1228515.6748
213 | 2598755.8187 | 1228498.089 | 2598757.4462 | 1228496.9159 | 2598760.6052 | 1228495.67 | 2598764.1508 | 1228495.1022 | 2598767.9161 | 1228494.9568 | 2598772.3485 | 1228495.912 | 2598775.9277 | 1228497.5105
214 | 2598775.9277 | 1228497.5105 | 2598766.7983 | 1228461.1187
215 | 2598755.8187 | 1228498.089 | 2598754.4995 | 1228499.04 | 2598751.6439 | 1228501.72 | 2598746.9076 | 1228508.0253
216 | 2598748.0423 | 1228451.7774 | 2598760.6044 | 1228457.5141 | 2598766.7983 | 1228461.1187
217 | 2598735.7539 | 1228522.874 | 2598746.9076 | 1228508.0253
218 | 2598735.897 | 1228446.2311 | 2598748.0423 | 1228451.7774
219 | 2598729.4382 | 1228531.282 | 2598735.7539 | 1228522.874
220 | 2598697.9592 | 1228429.3089 | 2598707.8981 | 1228433.4451 | 2598734.0973 | 1228445.4093
221 | 2598735.897 | 1228446.2311 | 2598734.0973 | 1228445.4093
222 | 2598697.9592 | 1228429.3089 | 2598697.7668 | 1228429.2289
223 | 2598695.3762 | 1228539.0771 | 2598696.3244 | 1228540.3021
224 | 2598840.1938 | 1228464.9441 | 2598841.5125 | 1228465.6169
225 | 2598765.5137 | 1228663.3792 | 2598751.9603 | 1228650.3884
226 | 2598747.9335 | 1228646.5287 | 2598751.9603 | 1228650.3884
227 | 2598750.7461 | 1228689.2422 | 2598752.4354 | 1228688.3413 | 2598754.238 | 1228686.2619 | 2598762.189 | 1228668.7498 | 2598765.5137 | 1228663.3792
228 | 2598750.7461 | 1228689.2422 | 2598749.4546 | 1228707.0197
229 | 2598750.7461 | 1228689.2422 | 2598748.6098 | 1228689.5985 | 2598746.4354 | 1228689.4322 | 2598744.2003 | 1228688.6767 | 2598737.1028 | 1228683.9616
230 | 2598726.7281 | 1228677.0694 | 2598737.1028 | 1228683.9616
231 | 2598726.7281 | 1228677.0694 | 2598715.5837 | 1228669.6659
232 | 2598657.0037 | 1228511.2029 | 2598669.4984 | 1228517.7038 | 2598676.5984 | 1228522.2048 | 2598681.2358 | 1228525.4167 | 2598688.5256 | 1228532.0301 | 2598695.3762 | 1228539.0771
233 | 2598715.5837 | 1228669.6659 | 2598707.7466 | 1228664.4595 | 2598698.3699 | 1228663.6459
234 | 2598698.3699 | 1228663.6459 | 2598685.3945 | 1228662.5201
235 | 2598982.4668 | 1228541.4528 | 2598980.9991 | 1228540.6965 | 2598973.4936 | 1228533.9887
236 | 2598987.5986 | 1228544.0973 | 2598982.4668 | 1228541.4528
237 | 2598973.2063 | 1228533.732 | 2598973.4936 | 1228533.9887
238 | 2598987.5986 | 1228544.0973 | 2598987.5986 | 1228544.0973 | 2598992.963 | 1228545.9324
239 | 2598992.963 | 1228545.9324 | 2598999.5703 | 1228548.1926
240 | 2599001.7052 | 1228548.9229 | 2598999.5703 | 1228548.1926
241 | 2598577.9108 | 1229028.8103 | 2598586.8043 | 1229033.9962 | 2598598.2977 | 1229038.9963 | 2598603.5368 | 1229040.6516
242 | 2598627.6095 | 1229047.7589 | 2598617.0032 | 1229044.9063 | 2598603.5368 | 1229040.6516
243 | 2598885.029 | 1228982.9878 | 2598886.499 | 1228984.5662 | 2598889.772 | 1228986.4222 | 2598899.1557 | 1228990.3011
244 | 2598877.0339 | 1229007.0259 | 2598878.8277 | 1228998.7095 | 2598881.6514 | 1228988.9142 | 2598885.029 | 1228982.9878
245 | 2599135.3834 | 1228658.6411 | 2599134.1248 | 1228656.6834 | 2599132.2376 | 1228652.3144 | 2599129.6759 | 1228646.0667 | 2599127.5157 | 1228639.541 | 2599125.4006 | 1228630.8028 | 2599124.9519 | 1228626.0095
246 | 2599171.4877 | 1228691.979 | 2599170.889 | 1228691.0425 | 2599163.5389 | 1228682.0271 | 2599158.879 | 1228677.9254 | 2599154.0298 | 1228674.5686 | 2599148.2261 | 1228671.2787 | 2599141.7478 | 1228666.3657 | 2599136.8907 | 1228660.9855 | 2599135.3834 | 1228658.6411
247 | 2599307.9194 | 1228951.622 | 2599305.5337 | 1228956.4474 | 2599302.4963 | 1228959.7052 | 2599297.5345 | 1228962.0962 | 2599291.8756 | 1228963.142 | 2599283.7468 | 1228962.9549
248 | 2599255.1328 | 1228956.4319 | 2599270.2923 | 1228960.9213 | 2599279.3909 | 1228962.8546 | 2599283.7468 | 1228962.9549
249 | 2599307.9194 | 1228951.622 | 2599307.9194 | 1228951.622 | 2599309.2356 | 1228945.4758
250 | 2599307.9194 | 1228951.622 | 2599439.6094 | 1229226.1001
251 | 2599250.4427 | 1228951.1627 | 2599255.1328 | 1228956.4319
252 | 2599310.486 | 1228939.6368 | 2599309.2356 | 1228945.4758
253 | 2599439.6094 | 1229226.1001 | 2599468.4615 | 1229234.7268 | 2599468.7542 | 1229234.8035
254 | 2599250.4427 | 1228951.1627 | 2599244.3148 | 1228946.0755
255 | 2599483.3009 | 1229238.6135 | 2599468.7542 | 1229234.8035
256 | 2599491.144 | 1229240.6677 | 2599483.3009 | 1229238.6135
257 | 2599491.5835 | 1229240.7828 | 2599491.144 | 1229240.6677
258 | 2599491.5835 | 1229240.7828 | 2599493.1958 | 1229241.2051
259 | 2599203.8142 | 1228897.7822 | 2599205.6408 | 1228903.6076 | 2599208.3084 | 1228910.0555 | 2599211.2107 | 1228915.2025 | 2599214.9462 | 1228920.1382 | 2599220.2575 | 1228925.4851 | 2599226.8872 | 1228931.7545 | 2599235.3123 | 1228938.6018 | 2599244.3148 | 1228946.0755
260 | 2599203.8142 | 1228897.7822 | 2599197.5659 | 1228908.923 | 2599190.2184 | 1228915.5947 | 2599179.9844 | 1228920.5659 | 2599165.9461 | 1228917.2994 | 2599151.438 | 1228913.5438 | 2599137.0366 | 1228913.5461 | 2599130.6656 | 1228915.2592
261 | 2599130.6656 | 1228915.2592 | 2599130.1485 | 1228902.4851 | 2599130.5038 | 1228897.7155 | 2599131.3137 | 1228893.2906 | 2599134.0026 | 1228890.3884 | 2599138.0852 | 1228885.8406 | 2599141.5844 | 1228880.7259 | 2599142.6886 | 1228878.4784
262 | 2598510.8081 | 1228674.3438 | 2598517.5884 | 1228678.7374
263 | 2598635.8031 | 1228988.9748 | 2598631.4636 | 1228981.9207
264 | 2599171.4877 | 1228691.979 | 2599180.9447 | 1228706.7725 | 2599181.7607 | 1228707.9917
265 | 2598841.7951 | 1228655.2136 | 2598844.2655 | 1228642.7603
266 | 2598841.7951 | 1228655.2136 | 2598847.4924 | 1228655.6127 | 2598863.0428 | 1228656.1862
267 | 2598857.3631 | 1228614.5975 | 2598849.7431 | 1228621.7811 | 2598847.8118 | 1228624.8834 | 2598844.2655 | 1228642.7603

## bus_geodata
| x | y | coords
0 | 2598716.2056 | 1228597.9058
1 | 2598716.2046 | 1228597.9022
2 | 2598718.3029 | 1228619.3245
3 | 2598713.8501 | 1228589.5317
4 | 2598717.7247 | 1228625.9939
5 | 2598708.4447 | 1228570.3148
6 | 2598691.7688 | 1228577.6454
7 | 2598714.998 | 1228570.102
8 | 2598575.28 | 1228962.7209
9 | 2598568.3039 | 1228970.6967
10 | 2598577.2807 | 1228960.4335
11 | 2598556.9478 | 1228985.345
12 | 2598596.8854 | 1228938.0195
13 | 2598537.7222 | 1229004.7803
14 | 2598604.6416 | 1228929.1519
15 | 2598554.7701 | 1229015.4631
16 | 2598515.7771 | 1228990.4479
17 | 2598620.7001 | 1228964.424
18 | 2598612.7281 | 1228919.4645
19 | 2598825.7181 | 1228689.5295
20 | 2598828.7574 | 1228689.0156
21 | 2598810.9911 | 1228692.0197
22 | 2598837.4161 | 1228687.5516
23 | 2598805.9254 | 1228705.9984
24 | 2598802.8455 | 1228649.7964
25 | 2598841.894 | 1228686.7944
26 | 2598801.4435 | 1228715.3885
27 | 2598800.3972 | 1228644.2047
28 | 2598812.3302 | 1228651.2079
29 | 2598853.8927 | 1228684.7656
30 | 2598788.0335 | 1228738.5378
31 | 2598785.4228 | 1228647.6633
32 | 2598795.6792 | 1228629.9678
33 | 2598832.9463 | 1228654.276
34 | 2598632.1401 | 1228666.9057
35 | 2598640.7784 | 1228648.2379
36 | 2598630.4802 | 1228670.9483
37 | 2598641.3509 | 1228647.0486
38 | 2598659.5005 | 1228688.1959
39 | 2598615.3096 | 1228688.1621
40 | 2598649.2655 | 1228631.6574
41 | 2598605.1952 | 1228692.3606
42 | 2598624.1688 | 1228694.7333
43 | 2598661.8721 | 1228609.0474
44 | 2598559.556 | 1228710.9006
45 | 2598628.9733 | 1228698.297
46 | 2598359.4732 | 1228850.8494
47 | 2598351.6148 | 1228861.4916
48 | 2598387.497 | 1228814.3971
49 | 2598342.1138 | 1228873.8483
50 | 2598407.1815 | 1228796.2364
51 | 2598400.4631 | 1228823.4133
52 | 2598328.9354 | 1228890.8148
53 | 2598414.3775 | 1228791.1715
54 | 2598384.5953 | 1228800.7137
55 | 2598403.8992 | 1228825.8027
56 | 2598323.5004 | 1228905.703
57 | 2598350.037 | 1228899.8257
58 | 2598313.081 | 1228882.4989
59 | 2598453.0024 | 1228750.6274
60 | 2598349.2232 | 1228811.4601
61 | 2598410.1911 | 1228830.1778
62 | 2598308.8792 | 1228879.7638
63 | 2598308.1973 | 1228879.32
64 | 2598302.3431 | 1228875.2995
65 | 2598323.4406 | 1228932.3937
66 | 2598378.4857 | 1228909.2235
67 | 2598296.8801 | 1228871.3272
68 | 2598281.6129 | 1229053.1341
69 | 2598396.8761 | 1228914.2287
70 | 2599139.6512 | 1228564.4055
71 | 2599154.2045 | 1228567.965
72 | 2599139.6095 | 1228564.3959
73 | 2599162.1163 | 1228569.9577
74 | 2599118.5859 | 1228560.1399
75 | 2599165.1987 | 1228570.6688
76 | 2599114.757 | 1228552.5736
77 | 2599122.2512 | 1228597.1612
78 | 2599098.1114 | 1228529.8203
79 | 2599124.2836 | 1228618.8716
80 | 2599109.1503 | 1228595.2688
81 | 2598786.3377 | 1228741.0251
82 | 2598767.7455 | 1228760.0431
83 | 2598914.8522 | 1228684.6414
84 | 2598921.9427 | 1228685.6664
85 | 2598911.8647 | 1228684.2096
86 | 2598931.4197 | 1228687.0362
87 | 2598906.1506 | 1228683.3836
88 | 2598940.1295 | 1228688.2952
89 | 2598893.3798 | 1228681.6308
90 | 2598889.7834 | 1228681.2976
91 | 2598247.2053 | 1228816.6872
92 | 2598284.7923 | 1228830.6772
93 | 2598228.0375 | 1228804.4719
94 | 2598288.0275 | 1228830.957
95 | 2598220.3883 | 1228812.2789
96 | 2598314.4087 | 1228826.1808
97 | 2598234.8777 | 1228824.531
98 | 2598315.0304 | 1228825.8408
99 | 2597652.3435 | 1229212.3677
100 | 2598664.8975 | 1228604.5007
101 | 2598708.6765 | 1228556.7956
102 | 2598727.742 | 1228573.0751
103 | 2599255.5512 | 1228783.0986
104 | 2599223.7457 | 1228767.1563
105 | 2599198.998 | 1228756.7994
106 | 2599197.9331 | 1228734.4655
107 | 2599194.3036 | 1228774.5995
108 | 2599195.893 | 1228729.9816
109 | 2599197.5597 | 1228815.9124
110 | 2598660.6452 | 1228578.01
111 | 2598608.4069 | 1228525.3861
112 | 2598292.5457 | 1228868.1755
113 | 2598292.4467 | 1228868.1035
114 | 2599020.8678 | 1228565.4877
115 | 2599041.0668 | 1228573.3188
116 | 2599019.1041 | 1228564.8039
117 | 2599049.7165 | 1228576.6723
118 | 2599064.6245 | 1228582.4521
119 | 2599091.3932 | 1228590.2845
120 | 2598969.0467 | 1228800.7637
121 | 2599041.5308 | 1228834.0926
122 | 2599081.1411 | 1228515.6905
123 | 2599057.9019 | 1228497.515
124 | 2599033.439 | 1228482.9558
125 | 2598962.7743 | 1228449.9513
126 | 2598946.598 | 1228433.6062
127 | 2598882.0216 | 1228681.1864
128 | 2598881.3365 | 1228681.2254
129 | 2598866.1545 | 1228682.8733
130 | 2598863.3906 | 1228683.2218
131 | 2598856.7061 | 1228684.2899
132 | 2598287.6064 | 1228864.584
133 | 2598703.1367 | 1228881.3181
134 | 2598743.4066 | 1228891.7724
135 | 2598697.2767 | 1228879.58
136 | 2598796.3021 | 1228907.3058
137 | 2598681.6929 | 1228859.7256
138 | 2598811.0808 | 1228954.8562
139 | 2598693.0703 | 1228842.4319
140 | 2598657.9171 | 1228876.3745
141 | 2598842.8082 | 1228932.6057
142 | 2598853.112 | 1228942.2146
143 | 2598826.1382 | 1228993.3171
144 | 2598694.3118 | 1228840.772
145 | 2598630.9352 | 1228898.2137
146 | 2598798.4828 | 1228579.3637
147 | 2598819.0341 | 1228571.4689
148 | 2598791.5119 | 1228580.6357
149 | 2598839.358 | 1228552.5094
150 | 2598779.4828 | 1228579.9785
151 | 2598790.7443 | 1228598.9136
152 | 2598841.7279 | 1228550.0515
153 | 2598755.7886 | 1228577.7472
154 | 2598790.7578 | 1228599.1751
155 | 2598869.1868 | 1228517.8953
156 | 2598823.607 | 1228535.3573
157 | 2598755.6909 | 1228577.738
158 | 2598791.3229 | 1228610.1692
159 | 2598922.1415 | 1228500.416
160 | 2598915.022 | 1228494.4168
161 | 2598939.2042 | 1228516.4011
162 | 2598896.27 | 1228479.5432
163 | 2598950.5992 | 1228521.671
164 | 2598880.4236 | 1228495.3334
165 | 2598956.9539 | 1228524.61
166 | 2598879.1299 | 1228497.2501
167 | 2598864.2512 | 1228481.8827
168 | 2598963.2014 | 1228527.4994
169 | 2598316.7925 | 1228824.8773
170 | 2598318.6224 | 1228823.8766
171 | 2598333.2963 | 1228816.6756
172 | 2598465.1423 | 1228951.1566
173 | 2598482.3907 | 1228965.2111
174 | 2598457.9955 | 1228945.255
175 | 2598484.5935 | 1228966.9981
176 | 2598446.3746 | 1228958.8909
177 | 2598449.8482 | 1228938.7606
178 | 2598489.3766 | 1228970.8782
179 | 2598442.5949 | 1228963.3259
180 | 2598427.4527 | 1228925.1073
181 | 2598411.9811 | 1228919.0744
182 | 2598834.0045 | 1229007.068
183 | 2598868.8491 | 1228957.7772
184 | 2598852.2844 | 1229006.7758
185 | 2598880.1919 | 1228963.8552
186 | 2598864.3652 | 1229006.5827
187 | 2598706.4029 | 1228824.6049
188 | 2598709.1158 | 1228821.0451
189 | 2598723.7793 | 1228802.258
190 | 2598736.1403 | 1228787.574
191 | 2598741.4781 | 1228781.4214
192 | 2598799.3344 | 1228515.6748
193 | 2598775.9277 | 1228497.5105
194 | 2598799.7479 | 1228516.0102
195 | 2598755.8187 | 1228498.089
196 | 2598766.7983 | 1228461.1187
197 | 2598746.9076 | 1228508.0253
198 | 2598748.0423 | 1228451.7774
199 | 2598735.7539 | 1228522.874
200 | 2598734.0973 | 1228445.4093
201 | 2598697.9592 | 1228429.3089
202 | 2598735.897 | 1228446.2311
203 | 2598697.7668 | 1228429.2289
204 | 2598729.4382 | 1228531.282
205 | 2598696.3244 | 1228540.3021
206 | 2598841.5125 | 1228465.6169
207 | 2598751.9603 | 1228650.3884
208 | 2598765.5137 | 1228663.3792
209 | 2598747.9335 | 1228646.5287
210 | 2598750.7461 | 1228689.2422
211 | 2598749.4546 | 1228707.0197
212 | 2598737.1028 | 1228683.9616
213 | 2598726.7281 | 1228677.0694
214 | 2598840.1938 | 1228464.9441
215 | 2598751.1963 | 1228577.1765
216 | 2598695.3762 | 1228539.0771
217 | 2598418.6505 | 1228901.6511
218 | 2598715.5837 | 1228669.6659
219 | 2598698.3699 | 1228663.6459
220 | 2598685.3945 | 1228662.5201
221 | 2598982.4668 | 1228541.4528
222 | 2598973.4936 | 1228533.9887
223 | 2598987.5986 | 1228544.0973
224 | 2598973.2063 | 1228533.732
225 | 2598992.963 | 1228545.9324
226 | 2598999.5703 | 1228548.1926
227 | 2599001.7052 | 1228548.9229
228 | 2598577.9108 | 1229028.8103
229 | 2598603.5368 | 1229040.6516
230 | 2598899.1557 | 1228990.3011
231 | 2598885.029 | 1228982.9878
232 | 2598877.0339 | 1229007.0259
233 | 2599101.179 | 1228593.0313
234 | 2598766.4301 | 1228760.9422
235 | 2599124.9519 | 1228626.0095
236 | 2599135.3834 | 1228658.6411
237 | 2598282.157 | 1228860.5968
238 | 2599283.7468 | 1228962.9549
239 | 2599307.9194 | 1228951.622
240 | 2599255.1328 | 1228956.4319
241 | 2599309.2356 | 1228945.4758
242 | 2599439.6094 | 1229226.1001
243 | 2599250.4427 | 1228951.1627
244 | 2599310.486 | 1228939.6368
245 | 2599468.7542 | 1229234.8035
246 | 2599483.3009 | 1229238.6135
247 | 2599491.144 | 1229240.6677
248 | 2599491.5835 | 1229240.7828
249 | 2599493.1958 | 1229241.2051
250 | 2599244.3148 | 1228946.0755
251 | 2599203.8142 | 1228897.7822
252 | 2599130.6656 | 1228915.2592
253 | 2598517.5884 | 1228678.7374
254 | 2598510.8081 | 1228674.3438
255 | 2598628.1189 | 1228901.5009
256 | 2598631.4636 | 1228981.9207
257 | 2598635.8031 | 1228988.9748
258 | 2599171.4877 | 1228691.979
259 | 2599181.7607 | 1228707.9917
260 | 2598841.7951 | 1228655.2136
261 | 2598844.2655 | 1228642.7603
262 | 2598863.0428 | 1228656.1862
263 | 2598857.3631 | 1228614.5975
264 | 2598627.6095 | 1229047.7589
265 | 2599142.6886 | 1228878.4784
266 | 2598650.7843 | 1228703.9296
267 | 2598657.0037 | 1228511.2029
268 | 2599022.58 | 1228813.0057
269 | 2598810.9911 | 1228692.0197

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98666 | -0.25562 | 0.001174 | 0.00029423
1 | 0.98666 | -0.25562 | 0.0011795 | 0.00029561
2 | 0.9866 | -0.25681 | 0.0015499 | 0.00038844
3 | 0.98671 | -0.25478 | 0.002315 | 0.0005802
4 | 0.98659 | -0.25699 | 0.0015036 | 0.00037684
5 | 0.98685 | -0.25202 | 0 | 0
6 | 0.98626 | -0.26352 | 0.0014734 | 0.00036926
7 | 0.98711 | -0.24701 | 0 | 0
8 | 0.99081 | -0.17487 | 0.0011217 | 0.00028114
9 | 0.99059 | -0.17914 | 0.0021784 | 0.00054595
10 | 0.99087 | -0.17364 | 0.0014113 | 0.0003537
11 | 0.99021 | -0.18642 | 0.0015463 | 0.00038755
12 | 0.99152 | -0.16134 | 0.0009422 | 0.00023614
13 | 0.9891 | -0.20762 | 0 | 0
14 | 0.99177 | -0.15643 | 0 | 0
15 | 0.98899 | -0.2097 | 0.0018687 | 0.00046833
16 | 0.98713 | -0.24555 | 0.0029967 | 0.00075104
17 | 0.99165 | -0.15891 | 0.001017 | 0.00025488
18 | 0.99206 | -0.15097 | 0.0013585 | 0.00034048
19 | 0.99779 | -0.042017 | 0.001352 | 0.00033884
20 | 0.99772 | -0.043316 | 0.0011233 | 0.00028151
21 | 0.99813 | -0.035372 | 0 | 0
22 | 0.99754 | -0.046845 | 0.0011224 | 0.00028131
23 | 0.99922 | -0.014691 | 0.006454 | 0.0016175
24 | 0.99517 | -0.091772 | 0 | 0
25 | 0.99745 | -0.048582 | 0.0016586 | 0.00041568
26 | 1 | 0 | -0.4778 | -0.12178
27 | 0.99478 | -0.09932 | 0 | 0
28 | 0.99508 | -0.093602 | 0.0015427 | 0.00038664
29 | 0.99723 | -0.052882 | 0.0011256 | 0.0002821
30 | 0.9991 | -0.017067 | 0.0028271 | 0.00070853
31 | 0.9945 | -0.10465 | 0.0012946 | 0.00032445
32 | 0.99387 | -0.1166 | 0.0015964 | 0.00040011
33 | 0.9949 | -0.097015 | 0.0016614 | 0.00041639
34 | 0.9837 | -0.31341 | 0.0022175 | 0.00055576
35 | 0.984 | -0.30747 | 0.0041104 | 0.0010302
36 | 0.98364 | -0.3145 | 0 | 0
37 | 0.98403 | -0.30699 | 0.0015634 | 0.00039184
38 | 0.98359 | -0.31553 | 0.0016664 | 0.00041763
39 | 0.98338 | -0.31966 | 0 | 0
40 | 0.98437 | -0.30023 | 0.0017297 | 0.00043351
41 | 0.98332 | -0.32078 | 0.00088708 | 0.00022232
42 | 0.98331 | -0.32095 | 0.0031399 | 0.00078692
43 | 0.98493 | -0.28931 | 0.0048463 | 0.0012146
44 | 0.98311 | -0.32503 | 0 | 0
45 | 0.9833 | -0.32131 | 0.0014602 | 0.00036596
46 | 0.97366 | -0.5079 | 0.0021482 | 0.00053839
47 | 0.97404 | -0.50055 | 0.00073787 | 0.00018493
48 | 0.97246 | -0.5317 | 0 | 0
49 | 0.97449 | -0.49168 | 0.0008177 | 0.00020493
50 | 0.97188 | -0.54314 | 0 | 0
51 | 0.97238 | -0.53314 | 0.0019897 | 0.00049867
52 | 0.97512 | -0.47916 | 0 | 0
53 | 0.97182 | -0.54436 | 0.0045575 | 0.0011422
54 | 0.97154 | -0.54986 | 0.0025592 | 0.00064141
55 | 0.97237 | -0.53336 | 0.0013003 | 0.0003259
56 | 0.97503 | -0.48095 | 0 | 0
57 | 0.97611 | -0.4598 | 0.0013011 | 0.00032609
58 | 0.97499 | -0.48184 | 0.0010581 | 0.00026517
59 | 0.97166 | -0.54744 | 0.0029585 | 0.00074146
60 | 0.97109 | -0.55879 | 0.0012087 | 0.00030294
61 | 0.97236 | -0.5336 | 0.0016401 | 0.00041104
62 | 0.97495 | -0.48249 | 0.0030442 | 0.00076295
63 | 0.97495 | -0.48255 | 0.00070581 | 0.00017689
64 | 0.97493 | -0.48299 | 0.0007948 | 0.0001992
65 | 0.97488 | -0.48399 | 0.0025082 | 0.00062863
66 | 0.97743 | -0.43384 | 0.0012632 | 0.00031659
67 | 0.97491 | -0.4833 | 0.00081018 | 0.00020305
68 | 0.97445 | -0.49248 | 0.0031886 | 0.00079914
69 | 0.9783 | -0.41694 | 0.0024515 | 0.00061441
70 | 0.97927 | -0.3993 | 0.0018907 | 0.00047386
71 | 0.97919 | -0.40072 | 0.00093511 | 0.00023436
72 | 0.97927 | -0.39929 | 0.0021062 | 0.00052786
73 | 0.97916 | -0.40135 | 0.0019112 | 0.00047899
74 | 0.97945 | -0.39569 | 0 | 0
75 | 0.97916 | -0.40149 | 0.0023776 | 0.00059588
76 | 0.97959 | -0.39289 | 0.0031167 | 0.00078113
77 | 0.9789 | -0.40642 | 0 | 0
78 | 0.98009 | -0.38309 | 0.0016479 | 0.00041299
79 | 0.9787 | -0.4104 | 0.00083584 | 0.00020948
80 | 0.97862 | -0.41204 | 0.00086453 | 0.00021667
81 | 0.999 | -0.018952 | 0.0023058 | 0.00057788
82 | 0.99813 | -0.035424 | 0.0038748 | 0.00097112
83 | 0.99657 | -0.065566 | 0.0011617 | 0.00029114
84 | 0.99654 | -0.066074 | 0.0017227 | 0.00043176
85 | 0.99658 | -0.065291 | 0.0017286 | 0.00043323
86 | 0.99652 | -0.066463 | 0.001158 | 0.00029022
87 | 0.99662 | -0.064589 | 0.0011655 | 0.00029211
88 | 0.99651 | -0.066642 | 0.0011569 | 0.00028994
89 | 0.99671 | -0.062758 | 0.0016598 | 0.00041599
90 | 0.99674 | -0.062139 | 0.0016546 | 0.00041468
91 | 0.9704 | -0.57244 | 0.0016706 | 0.00041869
92 | 0.97051 | -0.57023 | 0.003892 | 0.00097543
93 | 0.97037 | -0.57298 | 0 | 0
94 | 0.97053 | -0.56982 | 0.00042505 | 0.00010653
95 | 0.97036 | -0.57324 | 0 | 0
96 | 0.97071 | -0.56617 | 0.00058433 | 0.00014645
97 | 0.97033 | -0.57369 | 0.0012796 | 0.0003207
98 | 0.97072 | -0.56607 | 0.00059647 | 0.00014949
99 | 0.97421 | -0.49748 | 0.00040956 | 0.00010264
100 | 0.98508 | -0.28653 | 0 | 0
101 | 0.98702 | -0.24871 | 0 | 0
102 | 0.9877 | -0.23545 | 0.0024384 | 0.00061113
103 | 0.97727 | -0.43855 | 0.0010775 | 0.00027005
104 | 0.9773 | -0.43785 | 0.00088791 | 0.00022253
105 | 0.97735 | -0.43689 | 0 | 0
106 | 0.97752 | -0.43361 | 0.00086915 | 0.00021783
107 | 0.97723 | -0.43936 | 0.0023023 | 0.00057701
108 | 0.97756 | -0.43288 | 0.0014342 | 0.00035943
109 | 0.97696 | -0.44453 | 0.0011272 | 0.0002825
110 | 0.98495 | -0.28909 | 0.0016795 | 0.00042093
111 | 0.98469 | -0.29411 | 0.0036124 | 0.00090535
112 | 0.97491 | -0.48347 | 0.00055873 | 0.00014003
113 | 0.9749 | -0.48347 | 0.00031215 | 7.8232e-05
114 | 0.97739 | -0.43609 | 0.0032989 | 0.00082678
115 | 0.97752 | -0.43363 | 0.0036694 | 0.00091964
116 | 0.97739 | -0.43619 | 0.0029084 | 0.00072891
117 | 0.9776 | -0.43196 | 0.0030342 | 0.00076045
118 | 0.97779 | -0.4282 | 0.0049746 | 0.0012468
119 | 0.97826 | -0.4191 | 0.0020862 | 0.00052285
120 | 0.97408 | -0.50127 | 0.0030676 | 0.00076882
121 | 0.97431 | -0.49676 | 0 | 0
122 | 0.98049 | -0.37534 | 0.0063589 | 0.0015937
123 | 0.98106 | -0.36415 | 0.00201 | 0.00050374
124 | 0.98163 | -0.35309 | 0.0031267 | 0.00078361
125 | 0.98324 | -0.3217 | 0.0053486 | 0.0013405
126 | 0.98374 | -0.31194 | 0 | 0
127 | 0.99683 | -0.060583 | 0.0016557 | 0.00041497
128 | 0.99683 | -0.060426 | 0.0011284 | 0.00028279
129 | 0.99703 | -0.056623 | 0.0016553 | 0.00041485
130 | 0.99707 | -0.055849 | 0.0011264 | 0.00028231
131 | 0.99718 | -0.053834 | 0.0020639 | 0.00051727
132 | 0.9749 | -0.48357 | 0.00047784 | 0.00011976
133 | 0.9938 | -0.11792 | 0.0016685 | 0.00041816
134 | 0.99336 | -0.1263 | 0.00061932 | 0.00015522
135 | 0.99387 | -0.11651 | 0.0014514 | 0.00036376
136 | 0.99282 | -0.13685 | 0 | 0
137 | 0.99424 | -0.10938 | 0 | 0
138 | 0.99232 | -0.14654 | 0.00042793 | 0.00010725
139 | 0.99481 | -0.098456 | 0.00141 | 0.00035337
140 | 0.99353 | -0.12283 | 0.0019412 | 0.00048652
141 | 0.99095 | -0.17301 | 0.00081098 | 0.00020325
142 | 0.99096 | -0.17281 | 0 | 0
143 | 0.99192 | -0.15417 | 0 | 0
144 | 0.99487 | -0.097353 | 0.0019401 | 0.00048624
145 | 0.9927 | -0.13866 | 0.0011486 | 0.00028787
146 | 0.9906 | -0.17925 | 0.0036077 | 0.00090418
147 | 0.98962 | -0.19811 | 0.0046197 | 0.0011578
148 | 0.99092 | -0.1731 | 0 | 0
149 | 0.98842 | -0.22134 | 0.0015749 | 0.00039471
150 | 0.99029 | -0.18531 | 0.00087325 | 0.00021886
151 | 0.99199 | -0.15263 | 0.0012224 | 0.00030636
152 | 0.98827 | -0.22417 | 0.0014165 | 0.000355
153 | 0.98906 | -0.20909 | 0.0011705 | 0.00029335
154 | 0.99201 | -0.15234 | 0.0012201 | 0.00030578
155 | 0.9868 | -0.25259 | 0.0041581 | 0.0010421
156 | 0.98754 | -0.23833 | 0.0017908 | 0.00044881
157 | 0.98906 | -0.20919 | 0.0021136 | 0.00052972
158 | 0.99265 | -0.13993 | 0.005002 | 0.0012536
159 | 0.98409 | -0.30535 | 0.0023567 | 0.00059065
160 | 0.98438 | -0.29962 | 0.0055046 | 0.0013796
161 | 0.9834 | -0.31879 | 0.003171 | 0.00079473
162 | 0.98526 | -0.28253 | 0 | 0
163 | 0.98307 | -0.32529 | 0.0020704 | 0.00051888
164 | 0.98595 | -0.2691 | 0 | 0
165 | 0.98289 | -0.32865 | 0.0020501 | 0.00051381
166 | 0.98603 | -0.26762 | 0.0032394 | 0.00081187
167 | 0.98578 | -0.27241 | 0.0018052 | 0.00045242
168 | 0.98274 | -0.3317 | 0.0019984 | 0.00050084
169 | 0.97074 | -0.56576 | 0.00061053 | 0.00015301
170 | 0.97075 | -0.56541 | 0.00064377 | 0.00016134
171 | 0.9709 | -0.56246 | 0.0021567 | 0.00054052
172 | 0.98259 | -0.33325 | 0.0031224 | 0.00078256
173 | 0.9841 | -0.30392 | 0.0020001 | 0.00050127
174 | 0.98199 | -0.34498 | 0 | 0
175 | 0.9843 | -0.30009 | 0.0018784 | 0.00047077
176 | 0.98184 | -0.34779 | 0.0031478 | 0.00078891
177 | 0.98139 | -0.35654 | 0.0016248 | 0.0004072
178 | 0.98474 | -0.29156 | 0.0010311 | 0.00025841
179 | 0.98181 | -0.34838 | 0.0055426 | 0.0013891
180 | 0.97993 | -0.38499 | 0.0026952 | 0.00067547
181 | 0.97905 | -0.40219 | 0 | 0
182 | 0.99177 | -0.15708 | 0 | 0
183 | 0.99098 | -0.17248 | 0.0022422 | 0.00056196
184 | 0.9916 | -0.16043 | 0.00045532 | 0.00011411
185 | 0.99102 | -0.17179 | 0.0050447 | 0.0012643
186 | 0.99149 | -0.16255 | 0.00065134 | 0.00016324
187 | 0.99544 | -0.086451 | 0.0021088 | 0.0005285
188 | 0.99557 | -0.083993 | 0.0015333 | 0.00038429
189 | 0.99627 | -0.070761 | 0.0021002 | 0.00052636
190 | 0.99684 | -0.059937 | 0.0023048 | 0.00057763
191 | 0.99708 | -0.055266 | 0.0023069 | 0.00057817
192 | 0.98662 | -0.25632 | 0.0027341 | 0.00068524
193 | 0.98587 | -0.27095 | 0.0038343 | 0.00096097
194 | 0.98663 | -0.25603 | 0.0019584 | 0.00049082
195 | 0.98566 | -0.27493 | 0.0030099 | 0.00075434
196 | 0.98541 | -0.27984 | 0.0034463 | 0.00086373
197 | 0.98557 | -0.27673 | 0.0039595 | 0.00099235
198 | 0.98522 | -0.28352 | 0.0018332 | 0.00045944
199 | 0.98551 | -0.27789 | 0.0015394 | 0.00038581
200 | 0.98512 | -0.28564 | 0.0023852 | 0.00059778
201 | 0.98498 | -0.28823 | 0.0023536 | 0.00058986
202 | 0.98513 | -0.28542 | 0.001901 | 0.00047644
203 | 0.98498 | -0.28823 | 0.0012925 | 0.00032394
204 | 0.98549 | -0.27826 | 0.001957 | 0.00049047
205 | 0.9869 | -0.2511 | 0.0014388 | 0.00036059
206 | 0.9856 | -0.27591 | 0.0052598 | 0.0013182
207 | 0.994 | -0.11421 | 0.0010886 | 0.00027282
208 | 0.99407 | -0.11294 | 0 | 0
209 | 0.99399 | -0.11448 | 0.0027381 | 0.00068624
210 | 0.99367 | -0.12068 | 0 | 0
211 | 0.99363 | -0.12139 | 0.0022622 | 0.00056696
212 | 0.9935 | -0.12397 | 0.001798 | 0.00045062
213 | 0.99338 | -0.12627 | 0.0042102 | 0.0010552
214 | 0.9856 | -0.27595 | 0.0016961 | 0.00042508
215 | 0.98884 | -0.21346 | 0.0011779 | 0.0002952
216 | 0.98689 | -0.25123 | 0.002768 | 0.00069372
217 | 0.97893 | -0.40462 | 0.0059147 | 0.0014824
218 | 0.99331 | -0.12775 | 0.0021851 | 0.00054764
219 | 0.99324 | -0.1291 | 0.0016038 | 0.00040195
220 | 0.99321 | -0.12966 | 0.0024547 | 0.0006152
221 | 0.98233 | -0.33964 | 0.0020789 | 0.00052103
222 | 0.98248 | -0.33667 | 0.006467 | 0.0016208
223 | 0.98227 | -0.34088 | 0.0020442 | 0.00051231
224 | 0.98249 | -0.33653 | 0.0020758 | 0.00052025
225 | 0.98222 | -0.3419 | 0.0020318 | 0.00050922
226 | 0.98217 | -0.34289 | 0.0020655 | 0.00051765
227 | 0.98215 | -0.34313 | 0.0058001 | 0.0014536
228 | 0.9889 | -0.21158 | 0.0013834 | 0.0003467
229 | 0.98883 | -0.21287 | 0.0012198 | 0.00030571
230 | 0.99115 | -0.16914 | 0.0011434 | 0.00028656
231 | 0.99117 | -0.16882 | 0 | 0
232 | 0.99138 | -0.16463 | 0 | 0
233 | 0.97845 | -0.4154 | 0.0023249 | 0.00058268
234 | 0.99808 | -0.036379 | 0.0039642 | 0.00099352
235 | 0.97864 | -0.41168 | 0.0010892 | 0.00027298
236 | 0.97833 | -0.41769 | 0.002168 | 0.00054335
237 | 0.9749 | -0.48362 | 0.00038202 | 9.5744e-05
238 | 0.97595 | -0.4644 | 0.0026206 | 0.0006568
239 | 0.9756 | -0.47139 | 0.0018006 | 0.00045128
240 | 0.97617 | -0.46017 | 0 | 0
241 | 0.97559 | -0.47153 | 0.00050991 | 0.0001278
242 | 0.97274 | -0.52768 | 0.0028871 | 0.00072357
243 | 0.97619 | -0.45967 | 0 | 0
244 | 0.97559 | -0.4716 | 0.00068129 | 0.00017075
245 | 0.97254 | -0.5317 | 0.0038356 | 0.00096129
246 | 0.97249 | -0.53263 | 0.0005022 | 0.00012586
247 | 0.97247 | -0.53305 | 0.00095001 | 0.0002381
248 | 0.97247 | -0.53307 | 0.0011372 | 0.00028501
249 | 0.97247 | -0.53309 | 0.00074866 | 0.00018763
250 | 0.97622 | -0.4591 | 0.00022676 | 5.6832e-05
251 | 0.97646 | -0.45441 | 0 | 0
252 | 0.97567 | -0.46999 | 0 | 0
253 | 0.98287 | -0.3296 | 0.0034024 | 0.00085272
254 | 0.98286 | -0.3298 | 0.0013778 | 0.00034532
255 | 0.9926 | -0.14061 | 0.0027463 | 0.0006883
256 | 0.9916 | -0.15984 | 0.0017707 | 0.00044378
257 | 0.99159 | -0.15996 | 0.00079264 | 0.00019865
258 | 0.97791 | -0.42585 | 0.0014103 | 0.00035346
259 | 0.97776 | -0.42886 | 0.00092078 | 0.00023077
260 | 0.99484 | -0.098212 | 0 | 0
261 | 0.99479 | -0.099146 | 0.002239 | 0.00056115
262 | 0.99477 | -0.099508 | 0.0034594 | 0.00086701
263 | 0.99473 | -0.10025 | 0.0019376 | 0.0004856
264 | 0.9888 | -0.21347 | 0.0013349 | 0.00033457
265 | 0.97529 | -0.47752 | 0.000581 | 0.00014561
266 | 0.98325 | -0.32216 | 0.0018763 | 0.00047024
267 | 0.98679 | -0.25317 | 0.0022567 | 0.00056558
268 | 0.97412 | -0.50049 | 0.0064212 | 0.0016093
269 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042277 | -0.0010593 | 0.0042277 | 0.0010593 | 5.6715e-11 | -2.0969e-11 | 0.0063758 | 0.0063758 | 0.0063758 | 0.98666 | -0.25562 | 0.98666 | -0.25562 | 1.7516
1 | 0.0030537 | 0.00076503 | -0.0030535 | -0.0007652 | 1.7286e-07 | -1.6694e-07 | 0.0046052 | 0.0046053 | 0.0046053 | 0.98666 | -0.25562 | 0.9866 | -0.25681 | 1.2652
2 | -0.0054072 | -0.0013549 | 0.0054074 | 0.0013549 | 2.1683e-07 | 2.7713e-08 | 0.0081546 | 0.0081546 | 0.0081546 | 0.98666 | -0.25562 | 0.98671 | -0.25478 | 2.2403
3 | 0.0015036 | 0.00037676 | -0.0015036 | -0.00037684 | 1.291e-08 | -7.7225e-08 | 0.0022677 | 0.0022678 | 0.0022678 | 0.9866 | -0.25681 | 0.98659 | -0.25699 | 0.62301
4 | -0.0077224 | -0.0019351 | 0.0077234 | 0.0019355 | 1.0153e-06 | 3.9476e-07 | 0.011646 | 0.011646 | 0.011646 | 0.98671 | -0.25478 | 0.98685 | -0.25202 | 3.1994
5 | 0.035135 | 0.0088358 | -0.035116 | -0.0088237 | 1.9299e-05 | 1.2117e-05 | 0.052989 | 0.052989 | 0.052989 | 0.98685 | -0.25202 | 0.98626 | -0.26352 | 14.5574
6 | -0.042858 | -0.010771 | 0.042869 | 0.010778 | 1.0253e-05 | 6.4786e-06 | 0.064635 | 0.064635 | 0.064635 | 0.98685 | -0.25202 | 0.98711 | -0.24701 | 17.7568
7 | 0.033642 | 0.0084544 | -0.033605 | -0.0084313 | 3.6911e-05 | 2.3136e-05 | 0.050766 | 0.050766 | 0.050766 | 0.98626 | -0.26352 | 0.98508 | -0.28653 | 13.9468
8 | 0.0064649 | 0.0016198 | -0.0064644 | -0.0016196 | 5.2447e-07 | 1.4743e-07 | 0.0097454 | 0.0097455 | 0.0097455 | 0.98711 | -0.24701 | 0.98702 | -0.24871 | 2.6773
9 | -0.049334 | -0.012398 | 0.049361 | 0.012415 | 2.7247e-05 | 1.727e-05 | 0.07438 | 0.07438 | 0.07438 | 0.98711 | -0.24701 | 0.9877 | -0.23545 | 20.4341
10 | 0.091634 | 0.023373 | -0.091616 | -0.023362 | 1.8853e-05 | 1.152e-05 | 0.13776 | 0.13776 | 0.13776 | 0.99081 | -0.17487 | 0.99059 | -0.17914 | 9.4618
11 | -0.092756 | -0.023654 | 0.092762 | 0.023658 | 5.5402e-06 | 3.3892e-06 | 0.13945 | 0.13945 | 0.13945 | 0.99081 | -0.17487 | 0.99087 | -0.17364 | 9.5775
12 | 0.089437 | 0.022816 | -0.089406 | -0.022796 | 3.144e-05 | 1.9167e-05 | 0.13449 | 0.13449 | 0.13449 | 0.99059 | -0.17914 | 0.99021 | -0.18642 | 9.2371
13 | -0.094173 | -0.024011 | 0.094229 | 0.024046 | 5.5949e-05 | 3.4272e-05 | 0.14157 | 0.14157 | 0.14157 | 0.99087 | -0.17364 | 0.99152 | -0.16134 | 9.723
14 | 0.087859 | 0.022409 | -0.08777 | -0.022352 | 8.9861e-05 | 5.6806e-05 | 0.13217 | 0.13217 | 0.13217 | 0.99021 | -0.18642 | 0.9891 | -0.20762 | 18.155
15 | -0.095171 | -0.024282 | 0.095194 | 0.024296 | 2.2579e-05 | 1.3843e-05 | 0.14298 | 0.14298 | 0.14298 | 0.99152 | -0.16134 | 0.99177 | -0.15643 | 9.8201
16 | 0.0058079 | 0.0014547 | -0.0058073 | -0.0014546 | 5.7605e-07 | 1.1043e-07 | 0.0087371 | 0.0087372 | 0.0087372 | 0.9891 | -0.20762 | 0.98899 | -0.2097 | 2.4003
17 | 0.081962 | 0.020897 | -0.081812 | -0.020802 | 0.00014976 | 9.5514e-05 | 0.12343 | 0.12343 | 0.12343 | 0.9891 | -0.20762 | 0.98713 | -0.24555 | 33.9098
18 | 0.0035809 | 0.00089678 | -0.0035804 | -0.00089701 | 4.2303e-07 | -2.3355e-07 | 0.0053723 | 0.0053725 | 0.0053725 | 0.99177 | -0.15643 | 0.99165 | -0.15891 | 1.476
19 | -0.098775 | -0.025192 | 0.098801 | 0.025208 | 2.6037e-05 | 1.6012e-05 | 0.14835 | 0.14835 | 0.14835 | 0.99177 | -0.15643 | 0.99206 | -0.15097 | 10.1891
20 | 0.0039386 | 0.00098629 | -0.0039383 | -0.00098641 | 3.5202e-07 | -1.1772e-07 | 0.0059257 | 0.0059258 | 0.0059258 | 0.98899 | -0.2097 | 0.9889 | -0.21158 | 1.628
21 | 0.078815 | 0.020051 | -0.078641 | -0.01994 | 0.00017434 | 0.00011116 | 0.11891 | 0.11891 | 0.11891 | 0.98713 | -0.24555 | 0.98474 | -0.29156 | 32.6688
22 | 0.0025634 | 0.00064213 | -0.0025633 | -0.00064233 | 1.1398e-07 | -1.9206e-07 | 0.0038465 | 0.0038466 | 0.0038466 | 0.99165 | -0.15891 | 0.9916 | -0.15984 | 1.0567
23 | -0.10016 | -0.025549 | 0.10021 | 0.02558 | 5.0158e-05 | 3.0879e-05 | 0.15039 | 0.15039 | 0.15039 | 0.99206 | -0.15097 | 0.9926 | -0.14061 | 10.329
24 | 0.024087 | 0.0060427 | -0.024085 | -0.0060418 | 1.4917e-06 | 9.144e-07 | 0.035923 | 0.035923 | 0.035923 | 0.99779 | -0.042017 | 0.99772 | -0.043316 | 9.869
25 | -0.025439 | -0.0063816 | 0.025447 | 0.0063865 | 8.062e-06 | 4.9645e-06 | 0.037939 | 0.037939 | 0.037939 | 0.99779 | -0.042017 | 0.99813 | -0.035372 | 10.4229
26 | 0.022962 | 0.0057603 | -0.022958 | -0.0057579 | 3.8625e-06 | 2.3573e-06 | 0.034248 | 0.034248 | 0.034248 | 0.99772 | -0.043316 | 0.99754 | -0.046845 | 9.4087
27 | -0.32101 | -0.081886 | 0.32133 | 0.082091 | 0.00032097 | 0.00020464 | 0.47906 | 0.47906 | 0.47906 | 0.99813 | -0.035372 | 0.99922 | -0.014691 | 32.9027
28 | 0.29556 | 0.0755 | -0.29476 | -0.074988 | 0.00080355 | 0.00051197 | 0.44112 | 0.44113 | 0.44113 | 0.99813 | -0.035372 | 0.99517 | -0.091772 | 30.2971
29 | 0.021836 | 0.0054766 | -0.021834 | -0.0054755 | 1.807e-06 | 1.0972e-06 | 0.032573 | 0.032573 | 0.032573 | 0.99754 | -0.046845 | 0.99745 | -0.048582 | 8.9488
30 | -0.32778 | -0.083709 | 0.32801 | 0.083857 | 0.00023294 | 0.00014854 | 0.48867 | 0.48867 | 0.48867 | 0.99922 | -0.014691 | 1 | 0 | 33.5628
31 | 0.28391 | 0.07227 | -0.28381 | -0.072205 | 0.00010329 | 6.5786e-05 | 0.42491 | 0.42491 | 0.42491 | 0.99517 | -0.091772 | 0.99478 | -0.09932 | 29.1835
32 | 0.010844 | 0.0027176 | -0.010843 | -0.0027171 | 9.453e-07 | 4.8041e-07 | 0.016214 | 0.016214 | 0.016214 | 0.99517 | -0.091772 | 0.99508 | -0.093602 | 4.4543
33 | 0.020175 | 0.0050599 | -0.020171 | -0.0050574 | 4.1342e-06 | 2.4871e-06 | 0.030099 | 0.030099 | 0.030099 | 0.99745 | -0.048582 | 0.99723 | -0.052882 | 8.269
34 | 0.14814 | 0.037924 | -0.14801 | -0.037847 | 0.00012233 | 7.6889e-05 | 0.22071 | 0.22071 | 0.22071 | 1 | 0 | 0.9991 | -0.017067 | 15.1589
35 | 0.019657 | 0.0049326 | -0.019652 | -0.0049296 | 4.9909e-06 | 2.9944e-06 | 0.029406 | 0.029406 | 0.029406 | 0.99478 | -0.09932 | 0.9945 | -0.10465 | 8.0785
36 | 0.26415 | 0.067272 | -0.26393 | -0.067132 | 0.00021995 | 0.00013999 | 0.39551 | 0.39551 | 0.39551 | 0.99478 | -0.09932 | 0.99387 | -0.1166 | 27.1639
37 | 0.0092998 | 0.0023305 | -0.0092983 | -0.0023298 | 1.5116e-06 | 6.9673e-07 | 0.013907 | 0.013907 | 0.013907 | 0.99508 | -0.093602 | 0.9949 | -0.097015 | 3.8205
38 | 0.019046 | 0.0047753 | -0.019045 | -0.0047747 | 8.6423e-07 | 5.1588e-07 | 0.02842 | 0.02842 | 0.02842 | 0.99723 | -0.052882 | 0.99718 | -0.053834 | 7.8076
39 | 0.14519 | 0.037138 | -0.14517 | -0.03713 | 1.3246e-05 | 8.3197e-06 | 0.2165 | 0.2165 | 0.2165 | 0.9991 | -0.017067 | 0.999 | -0.018952 | 14.8697
40 | 0.018357 | 0.0046051 | -0.01835 | -0.0046008 | 7.2565e-06 | 4.3115e-06 | 0.027469 | 0.027469 | 0.027469 | 0.9945 | -0.10465 | 0.99407 | -0.11294 | 7.5464
41 | 0.26234 | 0.066732 | -0.26204 | -0.066544 | 0.00029454 | 0.00018745 | 0.39312 | 0.39312 | 0.39312 | 0.99387 | -0.1166 | 0.99265 | -0.13993 | 26.9998
42 | 0.0076369 | 0.0019134 | -0.0076365 | -0.0019132 | 4.3564e-07 | 1.6318e-07 | 0.011422 | 0.011422 | 0.011422 | 0.9949 | -0.097015 | 0.99484 | -0.098212 | 3.1379
43 | -0.016034 | -0.0040183 | 0.016039 | 0.0040209 | 4.5392e-06 | 2.6438e-06 | 0.024254 | 0.024254 | 0.024254 | 0.9837 | -0.31341 | 0.984 | -0.30747 | 6.6633
44 | 0.013817 | 0.0034625 | -0.013816 | -0.0034621 | 7.1583e-07 | 4.0266e-07 | 0.0209 | 0.0209 | 0.0209 | 0.9837 | -0.31341 | 0.98364 | -0.3145 | 5.7418
45 | -0.020149 | -0.0050511 | 0.02015 | 0.0050514 | 4.5955e-07 | 2.7734e-07 | 0.03047 | 0.03047 | 0.03047 | 0.984 | -0.30747 | 0.98403 | -0.30699 | 8.3709
46 | 0.0016664 | 0.00041725 | -0.0016664 | -0.00041763 | 8.1855e-08 | -3.836e-07 | 0.0025208 | 0.0025209 | 0.0025209 | 0.98364 | -0.3145 | 0.98359 | -0.31553 | 0.69257
47 | 0.012149 | 0.0030449 | -0.012146 | -0.0030432 | 2.9903e-06 | 1.6142e-06 | 0.018379 | 0.018379 | 0.018379 | 0.98364 | -0.3145 | 0.98338 | -0.31966 | 5.0493
48 | -0.021713 | -0.0054432 | 0.02172 | 0.0054475 | 6.998e-06 | 4.2588e-06 | 0.032834 | 0.032834 | 0.032834 | 0.98403 | -0.30699 | 0.98437 | -0.30023 | 9.0204
49 | 0.0056696 | 0.0014203 | -0.0056693 | -0.0014203 | 3.0224e-07 | 5.4508e-08 | 0.0085789 | 0.0085789 | 0.0085789 | 0.98338 | -0.31966 | 0.98332 | -0.32078 | 2.3568
50 | 0.0064769 | 0.0016229 | -0.0064765 | -0.0016228 | 3.9729e-07 | 1.1434e-07 | 0.0098004 | 0.0098005 | 0.0098005 | 0.98338 | -0.31966 | 0.98331 | -0.32095 | 2.6924
51 | -0.02345 | -0.005881 | 0.023462 | 0.0058884 | 1.2209e-05 | 7.4842e-06 | 0.035449 | 0.035449 | 0.035449 | 0.98437 | -0.30023 | 0.98493 | -0.28931 | 9.7387
52 | 0.0047823 | 0.0011979 | -0.0047813 | -0.0011979 | 9.6772e-07 | -5.6145e-09 | 0.0072365 | 0.0072368 | 0.0072368 | 0.98332 | -0.32078 | 0.98311 | -0.32503 | 1.9881
53 | 0.0033366 | 0.00083589 | -0.0033365 | -0.00083593 | 5.7186e-08 | -3.928e-08 | 0.0050491 | 0.0050491 | 0.0050491 | 0.98331 | -0.32095 | 0.9833 | -0.32131 | 1.3871
54 | -0.028308 | -0.007103 | 0.028312 | 0.0071054 | 3.7464e-06 | 2.3282e-06 | 0.04277 | 0.04277 | 0.04277 | 0.98493 | -0.28931 | 0.98508 | -0.28653 | 11.7501
55 | 0.0047813 | 0.0011979 | -0.0047802 | -0.0011979 | 1.0407e-06 | -5.6866e-09 | 0.0072368 | 0.007237 | 0.007237 | 0.98311 | -0.32503 | 0.98287 | -0.3296 | 1.9882
56 | 0.0018764 | 0.00046997 | -0.0018763 | -0.00047024 | 7.5419e-08 | -2.6814e-07 | 0.0028394 | 0.0028395 | 0.0028395 | 0.9833 | -0.32131 | 0.98325 | -0.32216 | 0.78008
57 | -0.030283 | -0.007609 | 0.030294 | 0.0076157 | 1.0631e-05 | 6.6394e-06 | 0.046288 | 0.046288 | 0.046288 | 0.97366 | -0.5079 | 0.97404 | -0.50055 | 12.7164
58 | 0.028135 | 0.0070706 | -0.028103 | -0.0070508 | 3.193e-05 | 1.9864e-05 | 0.043005 | 0.043005 | 0.043005 | 0.97366 | -0.5079 | 0.97246 | -0.5317 | 11.8146
59 | -0.031032 | -0.0078006 | 0.031045 | 0.0078088 | 1.3141e-05 | 8.2161e-06 | 0.047415 | 0.047415 | 0.047415 | 0.97404 | -0.50055 | 0.97449 | -0.49168 | 13.0261
60 | 0.023173 | 0.0058153 | -0.02316 | -0.0058075 | 1.2629e-05 | 7.7508e-06 | 0.035461 | 0.035461 | 0.035461 | 0.97246 | -0.5317 | 0.97188 | -0.54314 | 9.742
61 | 0.0049305 | 0.0012355 | -0.0049302 | -0.0012355 | 3.3709e-07 | 1.9818e-08 | 0.0075444 | 0.0075445 | 0.0075445 | 0.97246 | -0.5317 | 0.97238 | -0.53314 | 2.0727
62 | -0.031863 | -0.0080137 | 0.031882 | 0.0080257 | 1.9079e-05 | 1.1943e-05 | 0.048664 | 0.048663 | 0.048664 | 0.97449 | -0.49168 | 0.97512 | -0.47916 | 13.3691
63 | 0.0075169 | 0.0018834 | -0.0075164 | -0.0018833 | 4.3707e-07 | 1.7069e-07 | 0.011509 | 0.011509 | 0.011509 | 0.97188 | -0.54314 | 0.97182 | -0.54436 | 3.1617
64 | 0.015643 | 0.0039241 | -0.015638 | -0.0039212 | 5.0095e-06 | 2.9177e-06 | 0.023952 | 0.023952 | 0.023952 | 0.97188 | -0.54314 | 0.97154 | -0.54986 | 6.5803
65 | 0.0029404 | 0.00073682 | -0.0029404 | -0.00073685 | 3.1777e-08 | -3.1579e-08 | 0.0044997 | 0.0044997 | 0.0044997 | 0.97238 | -0.53314 | 0.97237 | -0.53336 | 1.2362
66 | 0.0061094 | 0.0015221 | -0.0061088 | -0.0015219 | 5.1949e-07 | 1.3352e-07 | 0.0093195 | 0.0093196 | 0.0093196 | 0.97512 | -0.47916 | 0.97503 | -0.48095 | 2.5603
67 | -0.046136 | -0.011589 | 0.046179 | 0.011616 | 4.2661e-05 | 2.7017e-05 | 0.070412 | 0.070412 | 0.070412 | 0.97512 | -0.47916 | 0.97611 | -0.4598 | 19.344
68 | 0.0081452 | 0.0020412 | -0.0081442 | -0.0020408 | 1.0411e-06 | 4.4215e-07 | 0.012429 | 0.012429 | 0.012429 | 0.97512 | -0.47916 | 0.97499 | -0.48184 | 3.4147
69 | 0.0029589 | 0.00074104 | -0.0029585 | -0.00074146 | 4.3448e-07 | -4.2122e-07 | 0.0045304 | 0.0045306 | 0.0045306 | 0.97182 | -0.54436 | 0.97166 | -0.54744 | 1.2447
70 | 0.013079 | 0.0032797 | -0.013073 | -0.0032766 | 5.5637e-06 | 3.1032e-06 | 0.020032 | 0.020033 | 0.020033 | 0.97154 | -0.54986 | 0.97109 | -0.55879 | 5.5035
71 | 0.0016401 | 0.00041095 | -0.0016401 | -0.00041104 | 1.8102e-08 | -8.3474e-08 | 0.0025098 | 0.0025098 | 0.0025098 | 0.97237 | -0.53336 | 0.97236 | -0.5336 | 0.6895
72 | 0.0061088 | 0.0015219 | -0.006108 | -0.0015217 | 8.7976e-07 | 2.2621e-07 | 0.0093196 | 0.0093197 | 0.0093197 | 0.97503 | -0.48095 | 0.97488 | -0.48399 | 2.5604
73 | -0.04748 | -0.011942 | 0.047539 | 0.011979 | 5.8957e-05 | 3.7357e-05 | 0.072396 | 0.072396 | 0.072396 | 0.97611 | -0.4598 | 0.97743 | -0.43384 | 19.8889
74 | 0.0070861 | 0.0017756 | -0.0070859 | -0.0017755 | 2.1989e-07 | 7.8206e-08 | 0.010815 | 0.010815 | 0.010815 | 0.97499 | -0.48184 | 0.97495 | -0.48249 | 2.9711
75 | 0.011865 | 0.0029737 | -0.011863 | -0.0029726 | 2.0773e-06 | 1.1221e-06 | 0.01818 | 0.01818 | 0.01818 | 0.97109 | -0.55879 | 0.9709 | -0.56246 | 4.9946
76 | 0.0040417 | 0.0010126 | -0.0040417 | -0.0010126 | 1.1609e-08 | -2.716e-09 | 0.0061684 | 0.0061684 | 0.0061684 | 0.97495 | -0.48249 | 0.97495 | -0.48255 | 1.6946
77 | 0.0033359 | 0.00083569 | -0.0033358 | -0.00083574 | 6.9054e-08 | -4.4395e-08 | 0.0050912 | 0.0050912 | 0.0050912 | 0.97495 | -0.48255 | 0.97493 | -0.48299 | 1.3987
78 | 0.002541 | 0.00063654 | -0.0025409 | -0.0006366 | 3.8096e-08 | -5.9844e-08 | 0.0038781 | 0.0038782 | 0.0038782 | 0.97493 | -0.48299 | 0.97491 | -0.4833 | 1.0654
79 | 0.0035997 | 0.0008931 | -0.0035983 | -0.00089376 | 1.445e-06 | -6.6771e-07 | 0.0054912 | 0.0054918 | 0.0054918 | 0.97488 | -0.48399 | 0.97445 | -0.49248 | 1.5087
80 | -0.048802 | -0.012296 | 0.048842 | 0.012321 | 3.9493e-05 | 2.5036e-05 | 0.074319 | 0.074319 | 0.074319 | 0.97743 | -0.43384 | 0.9783 | -0.41694 | 20.4172
81 | 0.0017308 | 0.00043355 | -0.0017307 | -0.00043361 | 1.4024e-08 | -5.7849e-08 | 0.0026416 | 0.0026416 | 0.0026416 | 0.97491 | -0.4833 | 0.97491 | -0.48347 | 0.72572
82 | 0.00040965 | 9.4621e-05 | -0.00040956 | -0.00010264 | 9.482e-08 | -8.0235e-06 | 0.00062276 | 0.00062556 | 0.00062556 | 0.97445 | -0.49248 | 0.97421 | -0.49748 | 0.17186
83 | -0.051293 | -0.012935 | 0.051329 | 0.012958 | 3.6236e-05 | 2.2992e-05 | 0.078047 | 0.078047 | 0.078047 | 0.9783 | -0.41694 | 0.97905 | -0.40219 | 21.4416
84 | 0.0052244 | 0.0013092 | -0.005224 | -0.0013092 | 3.5409e-07 | 3.813e-08 | 0.0079385 | 0.0079386 | 0.0079386 | 0.97927 | -0.3993 | 0.97919 | -0.40072 | 2.1809
85 | -0.0071151 | -0.0017831 | 0.0071151 | 0.0017831 | 1.8801e-09 | 6.6491e-10 | 0.010812 | 0.010812 | 0.010812 | 0.97927 | -0.3993 | 0.97927 | -0.39929 | 2.9702
86 | 0.0042889 | 0.0010748 | -0.0042888 | -0.0010748 | 1.2997e-07 | -1.945e-08 | 0.0065175 | 0.0065176 | 0.0065176 | 0.97919 | -0.40072 | 0.97916 | -0.40135 | 1.7905
87 | -0.0092213 | -0.0023109 | 0.0092229 | 0.0023117 | 1.5811e-06 | 7.4167e-07 | 0.014012 | 0.014012 | 0.014012 | 0.97927 | -0.39929 | 0.97945 | -0.39569 | 3.8494
88 | 0.0023776 | 0.00059585 | -0.0023776 | -0.00059588 | 1.5486e-08 | -2.9877e-08 | 0.0036132 | 0.0036132 | 0.0036132 | 0.97916 | -0.40135 | 0.97916 | -0.40149 | 0.99264
89 | -0.072671 | -0.018254 | 0.072681 | 0.01826 | 9.7012e-06 | 5.7814e-06 | 0.11042 | 0.11042 | 0.11042 | 0.97945 | -0.39569 | 0.97959 | -0.39289 | 7.5837
90 | 0.063448 | 0.015943 | -0.063416 | -0.015924 | 3.2462e-05 | 1.8901e-05 | 0.096407 | 0.096408 | 0.096408 | 0.97945 | -0.39569 | 0.9789 | -0.40642 | 6.6214
91 | -0.075797 | -0.019041 | 0.075833 | 0.019063 | 3.5499e-05 | 2.1281e-05 | 0.11515 | 0.11515 | 0.11515 | 0.97959 | -0.39289 | 0.98009 | -0.38309 | 7.9089
92 | 0.040229 | 0.010105 | -0.040222 | -0.010101 | 7.6467e-06 | 3.7976e-06 | 0.06116 | 0.06116 | 0.06116 | 0.9789 | -0.40642 | 0.9787 | -0.4104 | 4.2006
93 | 0.023186 | 0.0058193 | -0.02318 | -0.0058155 | 6.2218e-06 | 3.8141e-06 | 0.035248 | 0.035248 | 0.035248 | 0.9789 | -0.40642 | 0.97862 | -0.41204 | 9.6835
94 | -0.077481 | -0.019476 | 0.077509 | 0.019493 | 2.8659e-05 | 1.7228e-05 | 0.11765 | 0.11765 | 0.11765 | 0.98009 | -0.38309 | 0.98049 | -0.37534 | 8.0807
95 | 0.039386 | 0.0098913 | -0.039384 | -0.0098901 | 2.4107e-06 | 1.1825e-06 | 0.05989 | 0.05989 | 0.05989 | 0.9787 | -0.4104 | 0.97864 | -0.41168 | 4.1133
96 | 0.022315 | 0.0055988 | -0.022312 | -0.0055967 | 3.5751e-06 | 2.184e-06 | 0.033933 | 0.033933 | 0.033933 | 0.97862 | -0.41204 | 0.97845 | -0.4154 | 9.3224
97 | 0.14287 | 0.036552 | -0.14275 | -0.036481 | 0.00011382 | 7.1446e-05 | 0.21307 | 0.21307 | 0.21307 | 0.999 | -0.018952 | 0.99813 | -0.035424 | 14.6339
98 | 0.13888 | 0.03551 | -0.13887 | -0.035505 | 6.4187e-06 | 4.0247e-06 | 0.20729 | 0.20729 | 0.20729 | 0.99813 | -0.035424 | 0.99808 | -0.036379 | 14.2371
99 | 0.0040377 | 0.0010117 | -0.0040376 | -0.0010117 | 9.7649e-08 | -3.0847e-08 | 0.0060288 | 0.0060289 | 0.0060289 | 0.99657 | -0.065566 | 0.99654 | -0.066074 | 1.6563
100 | -0.0051994 | -0.0013028 | 0.0051995 | 0.0013028 | 6.8224e-08 | 4.332e-09 | 0.0077633 | 0.0077633 | 0.0077633 | 0.99657 | -0.065566 | 0.99658 | -0.065291 | 2.1328
101 | 0.0023149 | 0.00057996 | -0.0023149 | -0.00058005 | 4.2902e-08 | -9.7296e-08 | 0.0034565 | 0.0034566 | 0.0034566 | 0.99654 | -0.066074 | 0.99652 | -0.066463 | 0.94961
102 | -0.0069281 | -0.0017361 | 0.0069283 | 0.0017361 | 2.3167e-07 | 7.304e-08 | 0.010344 | 0.010344 | 0.010344 | 0.99658 | -0.065291 | 0.99662 | -0.064589 | 2.8419
103 | 0.0011569 | 0.00028983 | -0.0011569 | -0.00028994 | 9.8478e-09 | -1.0835e-07 | 0.0017274 | 0.0017275 | 0.0017275 | 0.99652 | -0.066463 | 0.99651 | -0.066642 | 0.47458
104 | -0.0080938 | -0.0020282 | 0.0080945 | 0.0020285 | 7.0596e-07 | 2.8382e-07 | 0.012085 | 0.012084 | 0.012085 | 0.99662 | -0.064589 | 0.99671 | -0.062758 | 3.3199
105 | -0.0097544 | -0.0024445 | 0.0097547 | 0.0024446 | 2.8739e-07 | 1.3683e-07 | 0.014562 | 0.014562 | 0.014562 | 0.99671 | -0.062758 | 0.99674 | -0.062139 | 4.0007
106 | -0.011409 | -0.0028593 | 0.01141 | 0.0028598 | 8.4579e-07 | 4.3996e-07 | 0.017033 | 0.017033 | 0.017033 | 0.99674 | -0.062139 | 0.99683 | -0.060583 | 4.6793
107 | -0.0029503 | -0.00073878 | 0.0029506 | 0.00073848 | 3.1096e-07 | -3.0167e-07 | 0.0045237 | 0.0045235 | 0.0045237 | 0.9704 | -0.57244 | 0.97051 | -0.57023 | 1.2428
108 | 0.0012797 | 0.0003201 | -0.0012796 | -0.00032036 | 3.2824e-08 | -2.5987e-07 | 0.001962 | 0.0019622 | 0.0019622 | 0.9704 | -0.57244 | 0.97037 | -0.57298 | 0.53905
109 | -0.0068426 | -0.0017139 | 0.0068427 | 0.001714 | 1.3425e-07 | 4.5725e-08 | 0.010491 | 0.010491 | 0.010491 | 0.97051 | -0.57023 | 0.97053 | -0.56982 | 2.8821
110 | 0.0012796 | 0.00032036 | -0.0012796 | -0.00032048 | 1.5759e-08 | -1.2475e-07 | 0.0019622 | 0.0019622 | 0.0019622 | 0.97037 | -0.57298 | 0.97036 | -0.57324 | 0.53907
111 | -0.0072678 | -0.0018205 | 0.007269 | 0.001821 | 1.262e-06 | 4.7267e-07 | 0.011143 | 0.011142 | 0.011143 | 0.97053 | -0.56982 | 0.97071 | -0.56617 | 3.0611
112 | 0.0012796 | 0.00032048 | -0.0012796 | -0.0003207 | 2.7475e-08 | -2.1747e-07 | 0.0019622 | 0.0019623 | 0.0019623 | 0.97036 | -0.57324 | 0.97033 | -0.57369 | 0.53909
113 | -0.0078534 | -0.0019674 | 0.0078534 | 0.0019674 | 3.8505e-08 | 1.5884e-08 | 0.012038 | 0.012038 | 0.012038 | 0.97071 | -0.56617 | 0.97072 | -0.56607 | 3.3072
114 | -0.0084499 | -0.0021169 | 0.00845 | 0.002117 | 1.2635e-07 | 5.6036e-08 | 0.012953 | 0.012953 | 0.012953 | 0.97072 | -0.56607 | 0.97074 | -0.56576 | 3.5584
115 | 0.0052934 | 0.0013259 | -0.0052928 | -0.0013258 | 6.4369e-07 | 7.0209e-08 | 0.0079958 | 0.0079959 | 0.0079959 | 0.98508 | -0.28653 | 0.98495 | -0.28909 | 2.1967
116 | 0.0064644 | 0.0016196 | -0.0064637 | -0.0016194 | 7.34e-07 | 2.0639e-07 | 0.0097455 | 0.0097456 | 0.0097456 | 0.98702 | -0.24871 | 0.9869 | -0.2511 | 2.6774
117 | -0.051799 | -0.013026 | 0.051854 | 0.013061 | 5.4461e-05 | 3.455e-05 | 0.078054 | 0.078053 | 0.078054 | 0.9877 | -0.23545 | 0.98884 | -0.21346 | 21.4433
118 | -0.0010775 | -0.00027005 | 0.0010775 | 0.00026963 | 3.5928e-08 | -4.2304e-07 | 0.0016406 | 0.0016405 | 0.0016406 | 0.97727 | -0.43855 | 0.9773 | -0.43785 | 0.45073
119 | -0.0019655 | -0.00049216 | 0.0019655 | 0.00049188 | 9.0099e-08 | -2.7858e-07 | 0.0029924 | 0.0029923 | 0.0029924 | 0.9773 | -0.43785 | 0.97735 | -0.43689 | 0.82209
120 | -0.031449 | -0.007893 | 0.031454 | 0.007895 | 4.922e-06 | 2.0022e-06 | 0.047886 | 0.047885 | 0.047886 | 0.97735 | -0.43689 | 0.97752 | -0.43361 | 3.2888
121 | 0.029484 | 0.0074011 | -0.02948 | -0.0073998 | 3.4783e-06 | 1.3034e-06 | 0.044893 | 0.044894 | 0.044894 | 0.97735 | -0.43689 | 0.97723 | -0.43936 | 3.0834
122 | -0.032323 | -0.0081128 | 0.032325 | 0.0081133 | 1.1183e-06 | 4.6867e-07 | 0.049208 | 0.049208 | 0.049208 | 0.97752 | -0.43361 | 0.97756 | -0.43288 | 3.3797
123 | 0.027178 | 0.0068228 | -0.027171 | -0.0068206 | 6.7009e-06 | 2.1981e-06 | 0.041388 | 0.041389 | 0.041389 | 0.97723 | -0.43936 | 0.97696 | -0.44453 | 2.8426
124 | -0.033759 | -0.0084727 | 0.033765 | 0.0084755 | 6.4789e-06 | 2.834e-06 | 0.051391 | 0.051391 | 0.051391 | 0.97756 | -0.43288 | 0.97776 | -0.42886 | 3.5296
125 | 0.026044 | 0.0065381 | -0.026032 | -0.0065344 | 1.2268e-05 | 3.6895e-06 | 0.039672 | 0.039673 | 0.039673 | 0.97696 | -0.44453 | 0.97646 | -0.45441 | 2.7248
126 | 0.0036133 | 0.00090492 | -0.0036124 | -0.00090535 | 8.6367e-07 | -4.3071e-07 | 0.0054585 | 0.0054589 | 0.0054589 | 0.98495 | -0.28909 | 0.98469 | -0.29411 | 1.4997
127 | 0.001172 | 0.00029358 | -0.001172 | -0.00029358 | 1.4651e-10 | -1.4346e-09 | 0.0017888 | 0.0017888 | 0.0017888 | 0.97491 | -0.48347 | 0.9749 | -0.48347 | 0.49143
128 | 0.00085987 | 0.00021535 | -0.00085986 | -0.00021542 | 3.8653e-09 | -7.2148e-08 | 0.0013124 | 0.0013124 | 0.0013124 | 0.9749 | -0.48347 | 0.9749 | -0.48357 | 0.36055
129 | -0.0062073 | -0.0015557 | 0.006208 | 0.0015559 | 7.2551e-07 | 1.9278e-07 | 0.0094502 | 0.0094501 | 0.0094502 | 0.97739 | -0.43609 | 0.97752 | -0.43363 | 2.5962
130 | 0.0029084 | 0.00072889 | -0.0029084 | -0.00072891 | 1.3908e-08 | -1.4807e-08 | 0.0044278 | 0.0044278 | 0.0044278 | 0.97739 | -0.43609 | 0.97739 | -0.43619 | 1.2164
131 | -0.0098774 | -0.0024755 | 0.0098782 | 0.0024759 | 7.8649e-07 | 3.8704e-07 | 0.015036 | 0.015036 | 0.015036 | 0.97752 | -0.43363 | 0.9776 | -0.43196 | 4.1307
132 | -0.012912 | -0.0032363 | 0.012915 | 0.0032376 | 2.3162e-06 | 1.2818e-06 | 0.019654 | 0.019654 | 0.019654 | 0.9776 | -0.43196 | 0.97779 | -0.4282 | 5.3995
133 | -0.017889 | -0.0044844 | 0.017897 | 0.004489 | 7.7556e-06 | 4.6134e-06 | 0.027225 | 0.027224 | 0.027225 | 0.97779 | -0.4282 | 0.97826 | -0.4191 | 7.4793
134 | -0.019983 | -0.0050119 | 0.019987 | 0.005014 | 3.5219e-06 | 2.1264e-06 | 0.030398 | 0.030398 | 0.030398 | 0.97826 | -0.4191 | 0.97845 | -0.4154 | 8.351
135 | -0.0030676 | -0.00076882 | 0.0030683 | 0.00076825 | 6.5937e-07 | -5.7502e-07 | 0.0046861 | 0.0046858 | 0.0046861 | 0.97408 | -0.50127 | 0.97431 | -0.49676 | 1.2874
136 | 0.0064223 | 0.0016096 | -0.0064212 | -0.0016093 | 1.1398e-06 | 3.361e-07 | 0.0098085 | 0.0098087 | 0.0098087 | 0.97431 | -0.49676 | 0.97412 | -0.50049 | 2.6947
137 | -0.0094906 | -0.0023779 | 0.0094993 | 0.0023821 | 8.7025e-06 | 4.1925e-06 | 0.014494 | 0.014494 | 0.014494 | 0.97431 | -0.49676 | 0.97529 | -0.47752 | 3.982
138 | -0.083868 | -0.021087 | 0.083913 | 0.021114 | 4.4836e-05 | 2.7205e-05 | 0.1273 | 0.1273 | 0.1273 | 0.98049 | -0.37534 | 0.98106 | -0.36415 | 8.7435
139 | -0.085923 | -0.021618 | 0.085969 | 0.021645 | 4.5448e-05 | 2.7645e-05 | 0.13035 | 0.13035 | 0.13035 | 0.98106 | -0.36415 | 0.98163 | -0.35309 | 8.9528
140 | -0.089095 | -0.022429 | 0.089229 | 0.022511 | 0.00013388 | 8.1719e-05 | 0.13509 | 0.13509 | 0.13509 | 0.98163 | -0.35309 | 0.98324 | -0.3217 | 9.2783
141 | -0.094578 | -0.023851 | 0.094622 | 0.023878 | 4.42e-05 | 2.7121e-05 | 0.14318 | 0.14318 | 0.14318 | 0.98324 | -0.3217 | 0.98374 | -0.31194 | 9.8341
142 | -0.094622 | -0.023878 | 0.094755 | 0.02396 | 0.00013347 | 8.189e-05 | 0.14318 | 0.14318 | 0.14318 | 0.98374 | -0.31194 | 0.98526 | -0.28253 | 9.8341
143 | -0.013066 | -0.0032747 | 0.013066 | 0.0032748 | 9.7887e-08 | 5.3702e-08 | 0.019504 | 0.019504 | 0.019504 | 0.99683 | -0.060583 | 0.99683 | -0.060426 | 5.3583
144 | -0.014194 | -0.0035576 | 0.014197 | 0.003559 | 2.5721e-06 | 1.447e-06 | 0.021188 | 0.021188 | 0.021188 | 0.99683 | -0.060426 | 0.99703 | -0.056623 | 5.821
145 | -0.015852 | -0.0039739 | 0.015853 | 0.0039742 | 5.8473e-07 | 3.379e-07 | 0.023659 | 0.023659 | 0.023659 | 0.99703 | -0.056623 | 0.99707 | -0.055849 | 6.4997
146 | -0.016979 | -0.0042565 | 0.016981 | 0.0042575 | 1.6302e-06 | 9.5503e-07 | 0.02534 | 0.02534 | 0.02534 | 0.99707 | -0.055849 | 0.99718 | -0.053834 | 6.9615
147 | 0.00038202 | 9.5661e-05 | -0.00038202 | -9.5744e-05 | 8.609e-10 | -8.3645e-08 | 0.00058306 | 0.00058309 | 0.00058309 | 0.9749 | -0.48357 | 0.9749 | -0.48362 | 0.16019
148 | 0.011422 | 0.0028685 | -0.011418 | -0.0028661 | 4.5646e-06 | 2.3825e-06 | 0.017104 | 0.017105 | 0.017105 | 0.9938 | -0.11792 | 0.99336 | -0.1263 | 4.6991
149 | -0.013091 | -0.0032866 | 0.013091 | 0.0032871 | 8.8127e-07 | 4.8476e-07 | 0.019603 | 0.019603 | 0.019603 | 0.9938 | -0.11792 | 0.99387 | -0.11651 | 5.3853
150 | 0.010798 | 0.0027109 | -0.010793 | -0.0027081 | 5.4307e-06 | 2.7596e-06 | 0.016177 | 0.016177 | 0.016177 | 0.99336 | -0.1263 | 0.99282 | -0.13685 | 4.4443
151 | -0.014543 | -0.0036509 | 0.014548 | 0.0036537 | 4.9454e-06 | 2.8045e-06 | 0.021776 | 0.021776 | 0.021776 | 0.99387 | -0.11651 | 0.99424 | -0.10938 | 5.9823
152 | 0.010793 | 0.0027081 | -0.010788 | -0.0027056 | 4.9861e-06 | 2.5345e-06 | 0.016177 | 0.016177 | 0.016177 | 0.99282 | -0.13685 | 0.99232 | -0.14654 | 4.4443
153 | -0.12075 | -0.030794 | 0.12082 | 0.030834 | 6.3736e-05 | 3.9713e-05 | 0.18091 | 0.18091 | 0.18091 | 0.99424 | -0.10938 | 0.99481 | -0.098456 | 12.4252
154 | 0.1062 | 0.02714 | -0.10613 | -0.027098 | 6.9035e-05 | 4.2675e-05 | 0.15913 | 0.15914 | 0.15914 | 0.99424 | -0.10938 | 0.99353 | -0.12283 | 10.9296
155 | 0.01036 | 0.0025983 | -0.010356 | -0.0025965 | 3.7692e-06 | 1.8745e-06 | 0.015536 | 0.015536 | 0.015536 | 0.99232 | -0.14654 | 0.99192 | -0.15417 | 4.2681
156 | -0.12223 | -0.031187 | 0.12223 | 0.031191 | 6.5091e-06 | 4.0582e-06 | 0.18302 | 0.18302 | 0.18302 | 0.99481 | -0.098456 | 0.99487 | -0.097353 | 12.57
157 | 0.10419 | 0.026611 | -0.10411 | -0.026562 | 7.965e-05 | 4.9174e-05 | 0.15623 | 0.15623 | 0.15623 | 0.99353 | -0.12283 | 0.9927 | -0.13866 | 10.73
158 | -0.00081098 | -0.00020325 | 0.00081098 | 0.00020307 | 7.8346e-09 | -1.765e-07 | 0.0012178 | 0.0012177 | 0.0012178 | 0.99095 | -0.17301 | 0.99096 | -0.17281 | 0.33455
159 | -0.00081098 | -0.00020307 | 0.000811 | 0.00020279 | 1.2549e-08 | -2.8275e-07 | 0.0012177 | 0.0012176 | 0.0012177 | 0.99096 | -0.17281 | 0.99098 | -0.17248 | 0.33453
160 | 0.010356 | 0.0025965 | -0.010355 | -0.0025957 | 1.433e-06 | 7.1278e-07 | 0.015536 | 0.015536 | 0.015536 | 0.99192 | -0.15417 | 0.99177 | -0.15708 | 4.2681
161 | -0.12417 | -0.031677 | 0.12424 | 0.031718 | 6.5422e-05 | 4.0821e-05 | 0.18592 | 0.18592 | 0.18592 | 0.99487 | -0.097353 | 0.99544 | -0.086451 | 12.7693
162 | 0.10297 | 0.026274 | -0.10296 | -0.026268 | 9.6879e-06 | 5.9764e-06 | 0.15451 | 0.15451 | 0.15451 | 0.9927 | -0.13866 | 0.9926 | -0.14061 | 10.6118
163 | 0.19323 | 0.049012 | -0.19305 | -0.048901 | 0.00017504 | 0.00011089 | 0.29046 | 0.29046 | 0.29046 | 0.9906 | -0.17925 | 0.98962 | -0.19811 | 19.9491
164 | -0.19683 | -0.049916 | 0.19689 | 0.049953 | 5.8182e-05 | 3.6871e-05 | 0.29588 | 0.29588 | 0.29588 | 0.9906 | -0.17925 | 0.99092 | -0.1731 | 20.3212
165 | 0.18843 | 0.047743 | -0.18822 | -0.04761 | 0.00021005 | 0.000133 | 0.28351 | 0.28351 | 0.28351 | 0.98962 | -0.19811 | 0.98842 | -0.22134 | 19.472
166 | 0.057298 | 0.014467 | -0.057264 | -0.014445 | 3.3499e-05 | 2.1284e-05 | 0.086079 | 0.086079 | 0.086079 | 0.99092 | -0.1731 | 0.99029 | -0.18531 | 23.648
167 | -0.25419 | -0.06442 | 0.25444 | 0.064579 | 0.00025027 | 0.00015923 | 0.38196 | 0.38196 | 0.38196 | 0.99092 | -0.1731 | 0.99199 | -0.15263 | 26.2332
168 | 0.18665 | 0.047215 | -0.18662 | -0.047199 | 2.5301e-05 | 1.6017e-05 | 0.28114 | 0.28114 | 0.28114 | 0.98842 | -0.22134 | 0.98827 | -0.22417 | 19.3092
169 | 0.056391 | 0.014227 | -0.056327 | -0.014186 | 6.4127e-05 | 4.0736e-05 | 0.084767 | 0.084767 | 0.084767 | 0.99029 | -0.18531 | 0.98906 | -0.20909 | 23.2876
170 | -0.25566 | -0.064885 | 0.25567 | 0.064887 | 3.6165e-06 | 2.301e-06 | 0.38379 | 0.38379 | 0.38379 | 0.99199 | -0.15263 | 0.99201 | -0.15234 | 26.3591
171 | 0.15113 | 0.038276 | -0.15092 | -0.038146 | 0.00020602 | 0.00012968 | 0.22769 | 0.22769 | 0.22769 | 0.98827 | -0.22417 | 0.9868 | -0.25259 | 15.6382
172 | 0.034076 | 0.0085687 | -0.034053 | -0.0085542 | 2.304e-05 | 1.4447e-05 | 0.051318 | 0.051318 | 0.051318 | 0.98827 | -0.22417 | 0.98754 | -0.23833 | 14.0984
173 | 0.055156 | 0.013892 | -0.055156 | -0.013892 | 2.5344e-07 | 1.6094e-07 | 0.083006 | 0.083006 | 0.083006 | 0.98906 | -0.20909 | 0.98906 | -0.20919 | 22.8038
174 | -0.25689 | -0.065193 | 0.25704 | 0.065291 | 0.00015347 | 9.7651e-05 | 0.38562 | 0.38562 | 0.38562 | 0.99201 | -0.15234 | 0.99265 | -0.13993 | 26.4848
175 | 0.14676 | 0.037104 | -0.14666 | -0.037037 | 0.0001057 | 6.6477e-05 | 0.22142 | 0.22142 | 0.22142 | 0.9868 | -0.25259 | 0.98603 | -0.26762 | 15.2076
176 | 0.032263 | 0.0081054 | -0.032235 | -0.0080884 | 2.723e-05 | 1.7034e-05 | 0.04862 | 0.04862 | 0.04862 | 0.98754 | -0.23833 | 0.98663 | -0.25603 | 13.3571
177 | 0.053043 | 0.013363 | -0.053032 | -0.013356 | 1.0826e-05 | 6.8707e-06 | 0.079826 | 0.079826 | 0.079826 | 0.98906 | -0.20919 | 0.98884 | -0.21346 | 21.9302
178 | -0.034256 | -0.0086021 | 0.034265 | 0.008608 | 9.3693e-06 | 5.878e-06 | 0.051804 | 0.051804 | 0.051804 | 0.98409 | -0.30535 | 0.98438 | -0.29962 | 14.2318
179 | 0.031899 | 0.0080115 | -0.031879 | -0.0079987 | 2.0445e-05 | 1.2787e-05 | 0.04824 | 0.04824 | 0.04824 | 0.98409 | -0.30535 | 0.9834 | -0.31879 | 13.2528
180 | -0.03977 | -0.0099876 | 0.039802 | 0.010008 | 3.2452e-05 | 2.0464e-05 | 0.060125 | 0.060125 | 0.060125 | 0.98438 | -0.29962 | 0.98526 | -0.28253 | 16.5178
181 | 0.028708 | 0.0072039 | -0.028699 | -0.0071984 | 8.885e-06 | 5.5272e-06 | 0.043442 | 0.043442 | 0.043442 | 0.9834 | -0.31879 | 0.98307 | -0.32529 | 11.9347
182 | -0.13456 | -0.033968 | 0.13464 | 0.034022 | 8.6642e-05 | 5.4311e-05 | 0.20331 | 0.20331 | 0.20331 | 0.98526 | -0.28253 | 0.98595 | -0.2691 | 13.9634
183 | 0.026629 | 0.0066795 | -0.026624 | -0.0066769 | 4.2659e-06 | 2.6414e-06 | 0.040308 | 0.040308 | 0.040308 | 0.98307 | -0.32529 | 0.98289 | -0.32865 | 11.0737
184 | -0.14341 | -0.036219 | 0.14342 | 0.036225 | 1.0165e-05 | 6.3874e-06 | 0.21653 | 0.21653 | 0.21653 | 0.98595 | -0.2691 | 0.98603 | -0.26762 | 14.8718
185 | 0.0087636 | 0.0021967 | -0.0087623 | -0.0021961 | 1.3799e-06 | 6.1494e-07 | 0.013226 | 0.013226 | 0.013226 | 0.98595 | -0.2691 | 0.98578 | -0.27241 | 3.6337
186 | 0.024574 | 0.0061631 | -0.024571 | -0.0061609 | 3.5729e-06 | 2.1995e-06 | 0.037205 | 0.037205 | 0.037205 | 0.98289 | -0.32865 | 0.98274 | -0.3317 | 10.2211
187 | 0.0069571 | 0.0017437 | -0.0069559 | -0.0017433 | 1.1599e-06 | 3.8484e-07 | 0.010502 | 0.010502 | 0.010502 | 0.98578 | -0.27241 | 0.9856 | -0.27591 | 2.8851
188 | 0.022572 | 0.00566 | -0.022567 | -0.0056569 | 5.1938e-06 | 3.1739e-06 | 0.034179 | 0.034179 | 0.034179 | 0.98274 | -0.3317 | 0.98249 | -0.33653 | 9.3898
189 | -0.0090605 | -0.00227 | 0.0090607 | 0.0022701 | 1.5086e-07 | 7.0767e-08 | 0.013888 | 0.013888 | 0.013888 | 0.97074 | -0.56576 | 0.97075 | -0.56541 | 3.8155
190 | -0.0097045 | -0.0024314 | 0.0097058 | 0.0024321 | 1.3605e-06 | 6.6798e-07 | 0.014875 | 0.014875 | 0.014875 | 0.97075 | -0.56541 | 0.9709 | -0.56246 | 4.0866
191 | -0.073582 | -0.018614 | 0.073686 | 0.01868 | 0.00010372 | 6.6096e-05 | 0.11149 | 0.11149 | 0.11149 | 0.98259 | -0.33325 | 0.9841 | -0.30392 | 30.6299
192 | 0.070459 | 0.017831 | -0.07042 | -0.017806 | 3.9618e-05 | 2.5238e-05 | 0.10676 | 0.10676 | 0.10676 | 0.98259 | -0.33325 | 0.98199 | -0.34498 | 29.3309
193 | -0.075686 | -0.019181 | 0.0757 | 0.01919 | 1.3949e-05 | 8.8914e-06 | 0.11452 | 0.11452 | 0.11452 | 0.9841 | -0.30392 | 0.9843 | -0.30009 | 31.4607
194 | 0.0086917 | 0.0021786 | -0.0086905 | -0.002178 | 1.1654e-06 | 5.1926e-07 | 0.013171 | 0.013171 | 0.013171 | 0.98199 | -0.34498 | 0.98184 | -0.34779 | 3.6183
195 | 0.061728 | 0.015628 | -0.061694 | -0.015606 | 3.424e-05 | 2.1782e-05 | 0.093594 | 0.093594 | 0.093594 | 0.98199 | -0.34498 | 0.98139 | -0.35654 | 25.7125
196 | -0.077578 | -0.019661 | 0.07761 | 0.019681 | 3.1809e-05 | 2.028e-05 | 0.11736 | 0.11736 | 0.11736 | 0.9843 | -0.30009 | 0.98474 | -0.29156 | 32.2408
197 | 0.0055427 | 0.0013891 | -0.0055426 | -0.0013891 | 1.5419e-07 | 2.4989e-08 | 0.0084002 | 0.0084002 | 0.0084002 | 0.98184 | -0.34779 | 0.98181 | -0.34838 | 2.3078
198 | 0.060069 | 0.015199 | -0.059987 | -0.015146 | 8.1897e-05 | 5.2082e-05 | 0.09113 | 0.09113 | 0.09113 | 0.98139 | -0.35654 | 0.97993 | -0.38499 | 25.0358
199 | 0.057292 | 0.014471 | -0.057245 | -0.014441 | 4.7182e-05 | 2.9988e-05 | 0.087038 | 0.087038 | 0.087038 | 0.97993 | -0.38499 | 0.97905 | -0.40219 | 23.9115
200 | 0.0059154 | 0.0014825 | -0.0059147 | -0.0014824 | 6.8428e-07 | 1.5409e-07 | 0.0089905 | 0.0089906 | 0.0089906 | 0.97905 | -0.40219 | 0.97893 | -0.40462 | 2.47
201 | 0.010355 | 0.0025957 | -0.010353 | -0.0025949 | 1.6548e-06 | 8.2318e-07 | 0.015536 | 0.015536 | 0.015536 | 0.99177 | -0.15708 | 0.9916 | -0.16043 | 4.2682
202 | -0.0030532 | -0.00076475 | 0.0030533 | 0.00076465 | 1.0142e-07 | -1.0089e-07 | 0.0045845 | 0.0045844 | 0.0045845 | 0.99098 | -0.17248 | 0.99102 | -0.17179 | 1.2595
203 | 0.0098977 | 0.0024808 | -0.0098967 | -0.0024803 | 9.9954e-07 | 4.8386e-07 | 0.014853 | 0.014853 | 0.014853 | 0.9916 | -0.16043 | 0.99149 | -0.16255 | 4.0805
204 | -0.0080981 | -0.002029 | 0.0080992 | 0.0020294 | 1.1455e-06 | 4.6688e-07 | 0.012159 | 0.012159 | 0.012159 | 0.99102 | -0.17179 | 0.99117 | -0.16882 | 3.3404
205 | 0.0092454 | 0.0023171 | -0.0092445 | -0.0023167 | 9.1637e-07 | 4.228e-07 | 0.013875 | 0.013875 | 0.013875 | 0.99149 | -0.16255 | 0.99138 | -0.16463 | 3.8119
206 | -0.12635 | -0.032247 | 0.12636 | 0.032256 | 1.5001e-05 | 9.3677e-06 | 0.18907 | 0.18907 | 0.18907 | 0.99544 | -0.086451 | 0.99557 | -0.083993 | 12.9857
207 | -0.12789 | -0.03264 | 0.12798 | 0.032691 | 8.1819e-05 | 5.1124e-05 | 0.19136 | 0.19136 | 0.19136 | 0.99557 | -0.083993 | 0.99627 | -0.070761 | 13.1431
208 | -0.13008 | -0.033218 | 0.13014 | 0.03326 | 6.8093e-05 | 4.2579e-05 | 0.1945 | 0.1945 | 0.1945 | 0.99627 | -0.070761 | 0.99684 | -0.059937 | 13.3585
209 | -0.13245 | -0.033838 | 0.13248 | 0.033857 | 2.9919e-05 | 1.8723e-05 | 0.19794 | 0.19794 | 0.19794 | 0.99684 | -0.059937 | 0.99708 | -0.055266 | 13.5948
210 | -0.13479 | -0.034435 | 0.13491 | 0.034512 | 0.00012321 | 7.7162e-05 | 0.20138 | 0.20138 | 0.20138 | 0.99708 | -0.055266 | 0.99808 | -0.036379 | 13.8313
211 | 0.027542 | 0.0069121 | -0.027523 | -0.0069002 | 1.9193e-05 | 1.1905e-05 | 0.041543 | 0.041543 | 0.041543 | 0.98662 | -0.25632 | 0.98587 | -0.27095 | 11.4129
212 | -0.030277 | -0.0075973 | 0.030277 | 0.0075976 | 4.164e-07 | 2.597e-07 | 0.045666 | 0.045666 | 0.045666 | 0.98662 | -0.25632 | 0.98663 | -0.25603 | 12.5457
213 | 0.010469 | 0.002624 | -0.010467 | -0.002623 | 1.9863e-06 | 1.0008e-06 | 0.015801 | 0.015801 | 0.015801 | 0.98587 | -0.27095 | 0.98566 | -0.27493 | 4.3409
214 | 0.01322 | 0.0033152 | -0.013215 | -0.0033121 | 5.6025e-06 | 3.1074e-06 | 0.019955 | 0.019955 | 0.019955 | 0.98587 | -0.27095 | 0.98541 | -0.27984 | 5.4821
215 | 0.0074568 | 0.0018686 | -0.0074562 | -0.0018684 | 6.3814e-07 | 2.3727e-07 | 0.011257 | 0.011257 | 0.011257 | 0.98566 | -0.27493 | 0.98557 | -0.27673 | 3.0926
216 | 0.0097684 | 0.0024484 | -0.0097667 | -0.0024475 | 1.7116e-06 | 8.2824e-07 | 0.014751 | 0.014751 | 0.014751 | 0.98541 | -0.27984 | 0.98522 | -0.28352 | 4.0524
217 | 0.0034966 | 0.00087606 | -0.0034964 | -0.00087617 | 1.9409e-07 | -1.1243e-07 | 0.0052791 | 0.0052792 | 0.0052792 | 0.98557 | -0.27673 | 0.98551 | -0.27789 | 1.4503
218 | 0.0079335 | 0.0019881 | -0.0079328 | -0.0019878 | 7.1886e-07 | 2.9006e-07 | 0.011982 | 0.011982 | 0.011982 | 0.98522 | -0.28352 | 0.98513 | -0.28542 | 3.2918
219 | 0.001957 | 0.00049036 | -0.001957 | -0.00049047 | 3.4432e-08 | -1.1195e-07 | 0.0029549 | 0.0029549 | 0.0029549 | 0.98551 | -0.27789 | 0.98549 | -0.27826 | 0.81179
220 | 0.0036465 | 0.00091358 | -0.0036461 | -0.00091379 | 4.5016e-07 | -2.1559e-07 | 0.005508 | 0.0055082 | 0.0055082 | 0.98512 | -0.28564 | 0.98498 | -0.28823 | 1.5132
221 | -0.0060317 | -0.0015114 | 0.0060318 | 0.0015114 | 6.1584e-08 | 1.4225e-08 | 0.0091108 | 0.0091108 | 0.0091108 | 0.98512 | -0.28564 | 0.98513 | -0.28542 | 2.503
222 | 0.0012925 | 0.00032394 | -0.0012925 | -0.00032394 | 2.9893e-10 | -2.4619e-09 | 0.0019526 | 0.0019526 | 0.0019526 | 0.98498 | -0.28823 | 0.98498 | -0.28823 | 0.53644
223 | 0.0050249 | 0.0012588 | -0.0050249 | -0.0012588 | 3.3344e-08 | 1.5463e-09 | 0.0075762 | 0.0075762 | 0.0075762 | 0.9869 | -0.2511 | 0.98689 | -0.25123 | 2.0814
224 | 0.0016961 | 0.00042507 | -0.0016961 | -0.00042508 | 3.6403e-09 | -1.6537e-08 | 0.0025607 | 0.0025607 | 0.0025607 | 0.9856 | -0.27591 | 0.9856 | -0.27595 | 0.70349
225 | -0.0038267 | -0.00095901 | 0.003827 | 0.00095892 | 2.3103e-07 | -9.5511e-08 | 0.0057286 | 0.0057285 | 0.0057286 | 0.994 | -0.11421 | 0.99407 | -0.11294 | 1.5738
226 | 0.0027382 | 0.00068619 | -0.0027381 | -0.00068624 | 3.5145e-08 | -4.9809e-08 | 0.004099 | 0.004099 | 0.004099 | 0.994 | -0.11421 | 0.99399 | -0.11448 | 1.1261
227 | 0.014523 | 0.0036419 | -0.014518 | -0.0036389 | 5.3522e-06 | 3.0341e-06 | 0.02174 | 0.02174 | 0.02174 | 0.99407 | -0.11294 | 0.99367 | -0.12068 | 5.9727
228 | 0.0022623 | 0.00056678 | -0.0022622 | -0.00056696 | 7.6722e-08 | -1.8182e-07 | 0.0033877 | 0.0033877 | 0.0033877 | 0.99367 | -0.12068 | 0.99363 | -0.12139 | 0.9307
229 | 0.012256 | 0.0030721 | -0.012254 | -0.003071 | 1.9233e-06 | 1.0337e-06 | 0.018353 | 0.018353 | 0.018353 | 0.99367 | -0.12068 | 0.9935 | -0.12397 | 5.042
230 | 0.010456 | 0.0026204 | -0.010455 | -0.0026199 | 1.1454e-06 | 5.7181e-07 | 0.01566 | 0.01566 | 0.01566 | 0.9935 | -0.12397 | 0.99338 | -0.12627 | 4.3022
231 | 0.0062443 | 0.0015647 | -0.0062439 | -0.0015646 | 4.3895e-07 | 1.0773e-07 | 0.0093535 | 0.0093535 | 0.0093535 | 0.99338 | -0.12627 | 0.99331 | -0.12775 | 2.5697
232 | 0.0022569 | 0.0005651 | -0.0022567 | -0.00056558 | 2.0757e-07 | -4.779e-07 | 0.0034027 | 0.0034029 | 0.0034029 | 0.98689 | -0.25123 | 0.98679 | -0.25317 | 0.93487
233 | 0.0040588 | 0.0010169 | -0.0040585 | -0.001017 | 2.6092e-07 | -7.6616e-08 | 0.0060801 | 0.0060802 | 0.0060802 | 0.99331 | -0.12775 | 0.99324 | -0.1291 | 1.6704
234 | 0.0024547 | 0.00061507 | -0.0024547 | -0.0006152 | 6.6053e-08 | -1.2629e-07 | 0.0036775 | 0.0036776 | 0.0036776 | 0.99324 | -0.1291 | 0.99321 | -0.12966 | 1.0103
235 | -0.014022 | -0.0035146 | 0.014024 | 0.0035158 | 1.9824e-06 | 1.1204e-06 | 0.021241 | 0.02124 | 0.021241 | 0.98233 | -0.33964 | 0.98248 | -0.33667 | 5.8353
236 | 0.011943 | 0.0029936 | -0.011942 | -0.0029932 | 7.0857e-07 | 3.804e-07 | 0.018091 | 0.018091 | 0.018091 | 0.98233 | -0.33964 | 0.98227 | -0.34088 | 4.9702
237 | -0.020491 | -0.0051365 | 0.020491 | 0.0051366 | 1.3918e-07 | 8.4193e-08 | 0.031035 | 0.031035 | 0.031035 | 0.98248 | -0.33667 | 0.98249 | -0.33653 | 8.5261
238 | 0.0098983 | 0.0024809 | -0.0098978 | -0.0024807 | 4.7804e-07 | 2.3418e-07 | 0.014995 | 0.014995 | 0.014995 | 0.98227 | -0.34088 | 0.98222 | -0.3419 | 4.1195
239 | 0.007866 | 0.0019715 | -0.0078656 | -0.0019713 | 3.7188e-07 | 1.4962e-07 | 0.011917 | 0.011917 | 0.011917 | 0.98222 | -0.3419 | 0.98217 | -0.34289 | 3.2738
240 | 0.0058002 | 0.0014537 | -0.0058001 | -0.0014536 | 6.5338e-08 | 1.3262e-08 | 0.0087875 | 0.0087875 | 0.0087875 | 0.98217 | -0.34289 | 0.98215 | -0.34313 | 2.4141
241 | 0.0025549 | 0.00063971 | -0.0025548 | -0.00063997 | 1.5697e-07 | -2.6289e-07 | 0.0038442 | 0.0038443 | 0.0038443 | 0.9889 | -0.21158 | 0.98883 | -0.21287 | 1.0561
242 | 0.001335 | 0.00033427 | -0.0013349 | -0.00033457 | 3.7992e-08 | -2.9773e-07 | 0.0020088 | 0.0020089 | 0.0020089 | 0.98883 | -0.21287 | 0.9888 | -0.21347 | 0.5519
243 | -0.0011434 | -0.00028656 | 0.0011434 | 0.00028636 | 1.776e-08 | -1.9579e-07 | 0.0017166 | 0.0017165 | 0.0017166 | 0.99115 | -0.16914 | 0.99117 | -0.16882 | 0.47158
244 | -0.0092426 | -0.0023158 | 0.0092445 | 0.0023167 | 1.8424e-06 | 8.5014e-07 | 0.013876 | 0.013875 | 0.013876 | 0.99117 | -0.16882 | 0.99138 | -0.16463 | 3.812
245 | 0.038294 | 0.0096171 | -0.038283 | -0.0096118 | 1.0974e-05 | 5.2891e-06 | 0.058234 | 0.058234 | 0.058234 | 0.97864 | -0.41168 | 0.97833 | -0.41769 | 3.9996
246 | 0.036115 | 0.0090685 | -0.036101 | -0.009062 | 1.4059e-05 | 6.503e-06 | 0.054937 | 0.054938 | 0.054938 | 0.97833 | -0.41769 | 0.97791 | -0.42585 | 3.7732
247 | 0.013086 | 0.0032874 | -0.013081 | -0.003285 | 4.3645e-06 | 2.4282e-06 | 0.019954 | 0.019954 | 0.019954 | 0.97595 | -0.4644 | 0.9756 | -0.47139 | 5.4819
248 | -0.015706 | -0.0039442 | 0.015709 | 0.0039455 | 3.1693e-06 | 1.2917e-06 | 0.02395 | 0.02395 | 0.02395 | 0.97595 | -0.4644 | 0.97617 | -0.46017 | 3.2898
249 | 0.0011912 | 0.0002984 | -0.0011912 | -0.00029847 | 7.7806e-09 | -7.3506e-08 | 0.0018168 | 0.0018169 | 0.0018169 | 0.9756 | -0.47139 | 0.97559 | -0.47153 | 0.49914
250 | 0.010089 | 0.0025353 | -0.010062 | -0.0025218 | 2.7046e-05 | 1.3519e-05 | 0.015391 | 0.015392 | 0.015392 | 0.9756 | -0.47139 | 0.97274 | -0.52768 | 4.2287
251 | -0.015709 | -0.0039455 | 0.01571 | 0.0039454 | 3.7888e-07 | -1.0986e-07 | 0.02395 | 0.023949 | 0.02395 | 0.97617 | -0.46017 | 0.97619 | -0.45967 | 1.6449
252 | 0.0006813 | 0.00017068 | -0.00068129 | -0.00017075 | 2.4179e-09 | -7.3014e-08 | 0.0010391 | 0.0010391 | 0.0010391 | 0.97559 | -0.47153 | 0.97559 | -0.4716 | 0.28548
253 | 0.0071752 | 0.0017982 | -0.0071739 | -0.0017977 | 1.3742e-06 | 5.0196e-07 | 0.010976 | 0.010976 | 0.010976 | 0.97274 | -0.52768 | 0.97254 | -0.5317 | 3.0154
254 | -0.01571 | -0.0039454 | 0.01571 | 0.0039453 | 4.2826e-07 | -1.2421e-07 | 0.023949 | 0.023949 | 0.023949 | 0.97619 | -0.45967 | 0.97622 | -0.4591 | 1.6449
255 | 0.0033383 | 0.00083642 | -0.0033381 | -0.00083651 | 1.4711e-07 | -9.2433e-08 | 0.0051076 | 0.0051077 | 0.0051077 | 0.97254 | -0.5317 | 0.97249 | -0.53263 | 1.4032
256 | 0.0028359 | 0.00071065 | -0.0028359 | -0.00071071 | 5.7248e-08 | -6.3955e-08 | 0.0043392 | 0.0043393 | 0.0043393 | 0.97249 | -0.53263 | 0.97247 | -0.53305 | 1.1921
257 | 0.0018859 | 0.00047261 | -0.0018859 | -0.00047262 | 1.4185e-09 | -4.7288e-09 | 0.0028856 | 0.0028856 | 0.0028856 | 0.97247 | -0.53305 | 0.97247 | -0.53307 | 0.79275
258 | 0.00074866 | 0.00018761 | -0.00074866 | -0.00018763 | 8.203e-10 | -2.0154e-08 | 0.0011455 | 0.0011456 | 0.0011456 | 0.97247 | -0.53307 | 0.97247 | -0.53309 | 0.31471
259 | -0.015937 | -0.0040021 | 0.01594 | 0.0040011 | 3.5634e-06 | -9.4092e-07 | 0.024295 | 0.024294 | 0.024295 | 0.97622 | -0.4591 | 0.97646 | -0.45441 | 1.6686
260 | 0.010091 | 0.0025332 | -0.010084 | -0.0025295 | 7.4931e-06 | 3.7397e-06 | 0.01538 | 0.01538 | 0.01538 | 0.97646 | -0.45441 | 0.97567 | -0.46999 | 4.2253
261 | 0.010084 | 0.0025295 | -0.01008 | -0.0025277 | 3.6223e-06 | 1.8085e-06 | 0.01538 | 0.01538 | 0.01538 | 0.97567 | -0.46999 | 0.97529 | -0.47752 | 4.2253
262 | 0.0013779 | 0.00034523 | -0.0013778 | -0.00034532 | 1.3184e-08 | -9.3957e-08 | 0.002086 | 0.002086 | 0.002086 | 0.98287 | -0.3296 | 0.98286 | -0.3298 | 0.57308
263 | 0.00079264 | 0.00019855 | -0.00079264 | -0.00019865 | 4.3939e-09 | -1.0402e-07 | 0.0011894 | 0.0011895 | 0.0011895 | 0.9916 | -0.15984 | 0.99159 | -0.15996 | 0.32677
264 | 0.034691 | 0.0087085 | -0.034686 | -0.0087063 | 4.9708e-06 | 2.2267e-06 | 0.052792 | 0.052792 | 0.052792 | 0.97791 | -0.42585 | 0.97776 | -0.42886 | 3.6258
265 | 0.0041769 | 0.0010463 | -0.0041767 | -0.0010464 | 1.8582e-07 | -4.5915e-08 | 0.0062473 | 0.0062474 | 0.0062474 | 0.99484 | -0.098212 | 0.99479 | -0.099146 | 1.7163
266 | 0.0034596 | 0.00086687 | -0.0034594 | -0.00086701 | 2.136e-07 | -1.3948e-07 | 0.0051746 | 0.0051747 | 0.0051747 | 0.99484 | -0.098212 | 0.99477 | -0.099508 | 1.4216
267 | 0.0019377 | 0.00048525 | -0.0019376 | -0.0004856 | 1.0191e-07 | -3.5477e-07 | 0.0028983 | 0.0028984 | 0.0028984 | 0.99479 | -0.099146 | 0.99473 | -0.10025 | 0.79627

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4801 | 0.12236

## res_load
| p_mw | q_mvar
0 | 0.001174 | 0.00029423
1 | 0.0011795 | 0.00029561
2 | 0.0015499 | 0.00038844
3 | 0.002315 | 0.0005802
4 | 0.0015036 | 0.00037684
5 | 0.0014734 | 0.00036926
6 | 0.0011217 | 0.00028114
7 | 0.0021784 | 0.00054595
8 | 0.0014113 | 0.0003537
9 | 0.0015463 | 0.00038755
10 | 0.0009422 | 0.00023614
11 | 0.0018687 | 0.00046833
12 | 0.0029967 | 0.00075104
13 | 0.001017 | 0.00025488
14 | 0.0013585 | 0.00034048
15 | 0.001352 | 0.00033884
16 | 0.0011233 | 0.00028151
17 | 0.0011224 | 0.00028131
18 | 0.006454 | 0.0016175
19 | 0.0016586 | 0.00041568
20 | 0.0023015 | 0.0005768
21 | 0.0015427 | 0.00038664
22 | 0.0011256 | 0.0002821
23 | 0.0028271 | 0.00070853
24 | 0.0012946 | 0.00032445
25 | 0.0015964 | 0.00040011
26 | 0.0016614 | 0.00041639
27 | 0.0022175 | 0.00055576
28 | 0.0041104 | 0.0010302
29 | 0.0015634 | 0.00039184
30 | 0.0016664 | 0.00041763
31 | 0.0017297 | 0.00043351
32 | 0.00088708 | 0.00022232
33 | 0.0031399 | 0.00078692
34 | 0.0048463 | 0.0012146
35 | 0.0014602 | 0.00036596
36 | 0.0021482 | 0.00053839
37 | 0.00073787 | 0.00018493
38 | 0.0008177 | 0.00020493
39 | 0.0019897 | 0.00049867
40 | 0.0045575 | 0.0011422
41 | 0.0025592 | 0.00064141
42 | 0.0013003 | 0.0003259
43 | 0.0013011 | 0.00032609
44 | 0.0010581 | 0.00026517
45 | 0.0029585 | 0.00074146
46 | 0.0012087 | 0.00030294
47 | 0.0016401 | 0.00041104
48 | 0.0030442 | 0.00076295
49 | 0.00070581 | 0.00017689
50 | 0.0007948 | 0.0001992
51 | 0.0025082 | 0.00062863
52 | 0.0012632 | 0.00031659
53 | 0.00081018 | 0.00020305
54 | 0.0031886 | 0.00079914
55 | 0.0024515 | 0.00061441
56 | 0.0018907 | 0.00047386
57 | 0.00093511 | 0.00023436
58 | 0.0021062 | 0.00052786
59 | 0.0019112 | 0.00047899
60 | 0.0023776 | 0.00059588
61 | 0.0031167 | 0.00078113
62 | 0.0016479 | 0.00041299
63 | 0.00083584 | 0.00020948
64 | 0.00086453 | 0.00021667
65 | 0.0023058 | 0.00057788
66 | 0.0038748 | 0.00097112
67 | 0.0011617 | 0.00029114
68 | 0.0017227 | 0.00043176
69 | 0.0017286 | 0.00043323
70 | 0.001158 | 0.00029022
71 | 0.0011655 | 0.00029211
72 | 0.0011569 | 0.00028994
73 | 0.0016598 | 0.00041599
74 | 0.0016546 | 0.00041468
75 | 0.0016706 | 0.00041869
76 | 0.003892 | 0.00097543
77 | 0.00042505 | 0.00010653
78 | 0.00058433 | 0.00014645
79 | 0.0012796 | 0.0003207
80 | 0.00059647 | 0.00014949
81 | 0.00040956 | 0.00010264
82 | 0.0024384 | 0.00061113
83 | 0.0010775 | 0.00027005
84 | 0.00088791 | 0.00022253
85 | 0.00086915 | 0.00021783
86 | 0.0023023 | 0.00057701
87 | 0.0014342 | 0.00035943
88 | 0.0011272 | 0.0002825
89 | 0.0016795 | 0.00042093
90 | 0.0036124 | 0.00090535
91 | 0.00055873 | 0.00014003
92 | 0.00031215 | 7.8232e-05
93 | 0.0032989 | 0.00082678
94 | 0.0036694 | 0.00091964
95 | 0.0029084 | 0.00072891
96 | 0.0030342 | 0.00076045
97 | 0.0049746 | 0.0012468
98 | 0.0020862 | 0.00052285
99 | 0.0030676 | 0.00076882
100 | 0.0063589 | 0.0015937
101 | 0.00201 | 0.00050374
102 | 0.0031267 | 0.00078361
103 | 0.0053486 | 0.0013405
104 | 0.0016557 | 0.00041497
105 | 0.0011284 | 0.00028279
106 | 0.0016553 | 0.00041485
107 | 0.0011264 | 0.00028231
108 | 0.0020639 | 0.00051727
109 | 0.00047784 | 0.00011976
110 | 0.0016685 | 0.00041816
111 | 0.00061932 | 0.00015522
112 | 0.0014514 | 0.00036376
113 | 0.00042793 | 0.00010725
114 | 0.00141 | 0.00035337
115 | 0.0019412 | 0.00048652
116 | 0.00081098 | 0.00020325
117 | 0.0019401 | 0.00048624
118 | 0.0011486 | 0.00028787
119 | 0.0036077 | 0.00090418
120 | 0.0046197 | 0.0011578
121 | 0.0015749 | 0.00039471
122 | 0.00087325 | 0.00021886
123 | 0.0012224 | 0.00030636
124 | 0.0014165 | 0.000355
125 | 0.0011705 | 0.00029335
126 | 0.0012201 | 0.00030578
127 | 0.0041581 | 0.0010421
128 | 0.0017908 | 0.00044881
129 | 0.0021136 | 0.00052972
130 | 0.005002 | 0.0012536
131 | 0.0023567 | 0.00059065
132 | 0.0055046 | 0.0013796
133 | 0.003171 | 0.00079473
134 | 0.0020704 | 0.00051888
135 | 0.0020501 | 0.00051381
136 | 0.0032394 | 0.00081187
137 | 0.0018052 | 0.00045242
138 | 0.0019984 | 0.00050084
139 | 0.00061053 | 0.00015301
140 | 0.00064377 | 0.00016134
141 | 0.0021567 | 0.00054052
142 | 0.0031224 | 0.00078256
143 | 0.0020001 | 0.00050127
144 | 0.0018784 | 0.00047077
145 | 0.0031478 | 0.00078891
146 | 0.0016248 | 0.0004072
147 | 0.0010311 | 0.00025841
148 | 0.0055426 | 0.0013891
149 | 0.0026952 | 0.00067547
150 | 0.0022422 | 0.00056196
151 | 0.00045532 | 0.00011411
152 | 0.0050447 | 0.0012643
153 | 0.00065134 | 0.00016324
154 | 0.0021088 | 0.0005285
155 | 0.0015333 | 0.00038429
156 | 0.0021002 | 0.00052636
157 | 0.0023048 | 0.00057763
158 | 0.0023069 | 0.00057817
159 | 0.0027341 | 0.00068524
160 | 0.0038343 | 0.00096097
161 | 0.0019584 | 0.00049082
162 | 0.0030099 | 0.00075434
163 | 0.0034463 | 0.00086373
164 | 0.0039595 | 0.00099235
165 | 0.0018332 | 0.00045944
166 | 0.0015394 | 0.00038581
167 | 0.0023852 | 0.00059778
168 | 0.0023536 | 0.00058986
169 | 0.001901 | 0.00047644
170 | 0.0012925 | 0.00032394
171 | 0.001957 | 0.00049047
172 | 0.0014388 | 0.00036059
173 | 0.0052598 | 0.0013182
174 | 0.0010886 | 0.00027282
175 | 0.0027381 | 0.00068624
176 | 0.0022622 | 0.00056696
177 | 0.001798 | 0.00045062
178 | 0.0042102 | 0.0010552
179 | 0.0016961 | 0.00042508
180 | 0.0011779 | 0.0002952
181 | 0.002768 | 0.00069372
182 | 0.0059147 | 0.0014824
183 | 0.0021851 | 0.00054764
184 | 0.0016038 | 0.00040195
185 | 0.0024547 | 0.0006152
186 | 0.0020789 | 0.00052103
187 | 0.006467 | 0.0016208
188 | 0.0020442 | 0.00051231
189 | 0.0020758 | 0.00052025
190 | 0.0020318 | 0.00050922
191 | 0.0020655 | 0.00051765
192 | 0.0058001 | 0.0014536
193 | 0.0013834 | 0.0003467
194 | 0.0012198 | 0.00030571
195 | 0.0011434 | 0.00028656
196 | 0.0023249 | 0.00058268
197 | 0.0039642 | 0.00099352
198 | 0.0010892 | 0.00027298
199 | 0.002168 | 0.00054335
200 | 0.00038202 | 9.5744e-05
201 | 0.0026206 | 0.0006568
202 | 0.0018006 | 0.00045128
203 | 0.00050991 | 0.0001278
204 | 0.0028871 | 0.00072357
205 | 0.00068129 | 0.00017075
206 | 0.0038356 | 0.00096129
207 | 0.0005022 | 0.00012586
208 | 0.00095001 | 0.0002381
209 | 0.0011372 | 0.00028501
210 | 0.00074866 | 0.00018763
211 | 0.00022676 | 5.6832e-05
212 | 0.0034024 | 0.00085272
213 | 0.0013778 | 0.00034532
214 | 0.0027463 | 0.0006883
215 | 0.0017707 | 0.00044378
216 | 0.00079264 | 0.00019865
217 | 0.0014103 | 0.00035346
218 | 0.00092078 | 0.00023077
219 | 0.002239 | 0.00056115
220 | 0.0034594 | 0.00086701
221 | 0.0019376 | 0.0004856
222 | 0.0013349 | 0.00033457
223 | 0.000581 | 0.00014561
224 | 0.0018763 | 0.00047024
225 | 0.0022567 | 0.00056558
226 | 0.0064212 | 0.0016093

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1