## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2546-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2546-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2546-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2546-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2546-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2546-1_0_4_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_2546-1_0_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_2546-1_0_4_node_52 | 0.4 | n |  | TRUE
8 | bus_LV_2546-1_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2546-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2546-1_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2546-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2546-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2546-1_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2546-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2546-1_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2546-1_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2546-1_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2546-1_0_4_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_2546-1_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2546-1_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_2546-1_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2546-1_0_4_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_2546-1_0_4_node_58 | 0.4 | n |  | TRUE
24 | bus_LV_2546-1_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2546-1_0_4_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_2546-1_0_4_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_2546-1_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2546-1_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2546-1_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2546-1_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2546-1_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2546-1_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2546-1_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2546-1_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_2546-1_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2546-1_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2546-1_0_4_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2546-1_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_2546-1_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_2546-1_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2546-1_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_2546-1_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_2546-1_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2546-1_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_2546-1_0_4_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_2546-1_0_4_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_2546-1_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_2546-1_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_2546-1_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2546-1_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_2546-1_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_2546-1_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_2546-1_0_4_node_87 | 0.4 | n |  | TRUE
54 | bus_LV_2546-1_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_2546-1_0_4_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_2546-1_0_4_node_86 | 0.4 | n |  | TRUE
57 | bus_LV_2546-1_0_4_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2546-1_0_4_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_2546-1_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2546-1_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_2546-1_0_4_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_2546-1_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2546-1_0_4_node_88 | 0.4 | n |  | TRUE
64 | bus_LV_2546-1_0_4_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_2546-1_0_4_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_2546-1_0_4_node_66 | 0.4 | n |  | TRUE
67 | bus_LV_2546-1_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_2546-1_0_4_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_2546-1_0_4_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_2546-1_0_4_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_2546-1_0_4_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_2546-1_0_4_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_2546-1_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2546-1_0_4_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_2546-1_0_4_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_2546-1_0_4_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_2546-1_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_2546-1_0_4_node_82 | 0.4 | n |  | TRUE
79 | bus_LV_2546-1_0_4_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_2546-1_0_4_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_2546-1_0_4_node_83 | 0.4 | n |  | TRUE
82 | bus_LV_2546-1_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_2546-1_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_2546-1_0_4_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_2546-1_0_4_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_2546-1_0_4_node_92 | 0.4 | n |  | TRUE
87 | bus_LV_2546-1_0_4_node_93 | 0.4 | n |  | TRUE
88 | bus_LV_2546-1_0_4_node_94 | 0.4 | n |  | TRUE
89 | bus_LV_2546-1_0_4_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_2546-1_0_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_2546-1_0_4_node_89 | 0.4 | n |  | TRUE
92 | bus_MV_396_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2546-1_0_4_load_0 | 0 | 0.0035226 | 0.00088284 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2546-1_0_4_load_1 | 1 | 0.0075143 | 0.0018833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2546-1_0_4_load_3 | 3 | 0.028369 | 0.00711 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2546-1_0_4_load_4 | 4 | 0.0012432 | 0.00031156 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2546-1_0_4_load_30 | 5 | 0.01332 | 0.0033384 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2546-1_0_4_load_27 | 6 | 0.00087943 | 0.00022041 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2546-1_0_4_load_28 | 8 | 0.0025061 | 0.00062808 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2546-1_0_4_load_5 | 9 | 0.0030796 | 0.00077183 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2546-1_0_4_load_6 | 10 | 0.0027861 | 0.00069826 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2546-1_0_4_load_10 | 14 | 0.0056436 | 0.0014144 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2546-1_0_4_load_13 | 15 | 0.0055731 | 0.0013968 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2546-1_0_4_load_15 | 17 | 0.0014653 | 0.00036724 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2546-1_0_4_load_50 | 18 | 0.0075806 | 0.0018999 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2546-1_0_4_load_11 | 19 | 0.0035977 | 0.00090167 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2546-1_0_4_load_51 | 20 | 0.0024754 | 0.00062039 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2546-1_0_4_load_12 | 21 | 0.0017294 | 0.00043344 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2546-1_0_4_load_60 | 22 | 0.0054839 | 0.0013744 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2546-1_0_4_load_58 | 23 | 0.0056693 | 0.0014209 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2546-1_0_4_load_59 | 25 | 0.0056179 | 0.001408 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2546-1_0_4_load_57 | 26 | 0.0026024 | 0.00065223 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2546-1_0_4_load_20 | 27 | 0.0032265 | 0.00080863 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2546-1_0_4_load_16 | 28 | 0.015975 | 0.0040038 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2546-1_0_4_load_21 | 32 | 0.01196 | 0.0029975 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2546-1_0_4_load_22 | 33 | 0.0025325 | 0.00063471 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2546-1_0_4_load_25 | 35 | 0.001968 | 0.00049324 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2546-1_0_4_load_34 | 36 | 0.0015644 | 0.00039207 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2546-1_0_4_load_35 | 37 | 0.0043863 | 0.0010993 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2546-1_0_4_load_31 | 38 | 0.01178 | 0.0029524 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2546-1_0_4_load_24 | 39 | 0.0023909 | 0.00059922 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2546-1_0_4_load_26 | 40 | 0.017103 | 0.0042863 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2546-1_0_4_load_29 | 41 | 0.0010541 | 0.00026418 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2546-1_0_4_load_40 | 42 | 0.0034545 | 0.00086578 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2546-1_0_4_load_36 | 43 | 0.026272 | 0.0065843 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2546-1_0_4_load_53 | 44 | 0.0065891 | 0.0016514 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2546-1_0_4_load_54 | 45 | 0.03682 | 0.009228 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2546-1_0_4_load_55 | 46 | 0.0079956 | 0.0020039 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2546-1_0_4_load_37 | 48 | 0.0030301 | 0.00075941 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2546-1_0_4_load_38 | 49 | 0.0015703 | 0.00039355 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2546-1_0_4_load_41 | 51 | 0.0022581 | 0.00056594 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2546-1_0_4_load_47 | 52 | 0.0011752 | 0.00029452 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2546-1_0_4_load_87 | 53 | 0.013985 | 0.003505 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2546-1_0_4_load_42 | 54 | 0.087913 | 0.022033 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2546-1_0_4_load_48 | 55 | 0.00088821 | 0.00022261 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2546-1_0_4_load_86 | 56 | 0.016931 | 0.0042432 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2546-1_0_4_load_43 | 57 | 0.0022627 | 0.00056709 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2546-1_0_4_load_49 | 62 | 0.0011692 | 0.00029302 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2546-1_0_4_load_88 | 63 | 0.039803 | 0.0099755 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2546-1_0_4_load_73 | 64 | 0.0019539 | 0.0004897 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2546-1_0_4_load_66 | 66 | 0.0044837 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2546-1_0_4_load_85 | 68 | 0.0019898 | 0.00049869 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2546-1_0_4_load_69 | 70 | 0.012674 | 0.0031763 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2546-1_0_4_load_67 | 71 | 0.0017563 | 0.00044018 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2546-1_0_4_load_62 | 72 | 0.0066663 | 0.0016707 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2546-1_0_4_load_65 | 74 | 0.00070691 | 0.00017717 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2546-1_0_4_load_80 | 75 | 0.0058437 | 0.0014646 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2546-1_0_4_load_81 | 76 | 0.0019932 | 0.00049955 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2546-1_0_4_load_77 | 79 | 0.0031324 | 0.00078506 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2546-1_0_4_load_75 | 80 | 0.0008314 | 0.00020837 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2546-1_0_4_load_74 | 82 | 0.00036205 | 9.0738e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2546-1_0_4_load_92 | 86 | 0.035019 | 0.0087765 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2546-1_0_4_load_94 | 88 | 0.00091693 | 0.0002298 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2546-1_0_4_load_91 | 89 | 0.00090936 | 0.00022791 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2546-1_0_4_load_89 | 91 | 0.019837 | 0.0049716 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2546-1_0_4_line_0 |  | 0 | 1 | 0.022423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2546-1_0_4_line_1 |  | 1 | 2 | 0.032644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2546-1_0_4_line_2 |  | 2 | 3 | 0.079887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2546-1_0_4_line_3 |  | 2 | 4 | 0.0083432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2546-1_0_4_line_4 |  | 3 | 5 | 0.03268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2546-1_0_4_line_5 |  | 4 | 6 | 0.02136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2546-1_0_4_line_6 |  | 5 | 7 | 0.045638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2546-1_0_4_line_7 |  | 6 | 8 | 0.0054483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2546-1_0_4_line_8 |  | 7 | 44 | 0.04788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2546-1_0_4_line_9 |  | 7 | 45 | 0.03712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2546-1_0_4_line_10 |  | 7 | 46 | 0.070107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2546-1_0_4_line_11 |  | 8 | 41 | 0.011773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2546-1_0_4_line_12 |  | 9 | 10 | 0.014515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2546-1_0_4_line_13 |  | 9 | 11 | 0.0048895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2546-1_0_4_line_14 |  | 11 | 12 | 0.01303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2546-1_0_4_line_15 |  | 11 | 13 | 0.045779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2546-1_0_4_line_16 |  | 12 | 14 | 0.01724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2546-1_0_4_line_17 |  | 12 | 15 | 0.014943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2546-1_0_4_line_18 |  | 13 | 16 | 0.011887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2546-1_0_4_line_19 |  | 13 | 17 | 0.022301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2546-1_0_4_line_20 |  | 14 | 18 | 0.0096635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2546-1_0_4_line_21 |  | 15 | 21 | 0.017934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2546-1_0_4_line_22 |  | 16 | 22 | 0.016695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2546-1_0_4_line_23 |  | 16 | 23 | 0.017505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2546-1_0_4_line_24 |  | 17 | 24 | 0.052867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2546-1_0_4_line_25 |  | 18 | 20 | 0.0034483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2546-1_0_4_line_26 |  | 19 | 20 | 0.0030547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2546-1_0_4_line_27 |  | 22 | 25 | 0.01265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2546-1_0_4_line_28 |  | 23 | 26 | 0.011335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2546-1_0_4_line_29 |  | 24 | 27 | 0.11927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2546-1_0_4_line_30 |  | 27 | 30 | 0.055176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2546-1_0_4_line_31 |  | 28 | 29 | 0.02373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2546-1_0_4_line_32 |  | 28 | 30 | 0.035558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2546-1_0_4_line_33 |  | 29 | 31 | 0.060753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2546-1_0_4_line_34 |  | 31 | 32 | 0.026378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2546-1_0_4_line_35 |  | 31 | 33 | 0.022501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2546-1_0_4_line_36 |  | 32 | 34 | 0.030668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2546-1_0_4_line_37 |  | 33 | 35 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2546-1_0_4_line_38 |  | 34 | 36 | 0.022656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2546-1_0_4_line_39 |  | 34 | 37 | 0.066079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2546-1_0_4_line_40 |  | 34 | 38 | 0.02735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2546-1_0_4_line_41 |  | 35 | 39 | 0.0041974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2546-1_0_4_line_42 |  | 36 | 49 | 0.039631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2546-1_0_4_line_43 |  | 37 | 50 | 0.018804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2546-1_0_4_line_44 |  | 38 | 47 | 0.027539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2546-1_0_4_line_45 |  | 39 | 40 | 0.0026472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2546-1_0_4_line_46 |  | 41 | 42 | 0.017997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2546-1_0_4_line_47 |  | 42 | 43 | 0.008221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2546-1_0_4_line_48 |  | 43 | 47 | 0.029039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2546-1_0_4_line_49 |  | 45 | 66 | 0.039293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2546-1_0_4_line_50 |  | 46 | 67 | 0.063874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2546-1_0_4_line_51 |  | 47 | 48 | 0.055913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2546-1_0_4_line_52 |  | 48 | 51 | 0.035218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2546-1_0_4_line_53 |  | 49 | 52 | 0.039841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2546-1_0_4_line_54 |  | 50 | 53 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2546-1_0_4_line_55 |  | 51 | 54 | 0.021889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2546-1_0_4_line_56 |  | 52 | 55 | 0.019495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2546-1_0_4_line_57 |  | 53 | 56 | 0.080875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2546-1_0_4_line_58 |  | 54 | 57 | 0.013371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2546-1_0_4_line_59 |  | 55 | 62 | 0.017963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2546-1_0_4_line_60 |  | 58 | 59 | 0.051837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2546-1_0_4_line_61 |  | 58 | 60 | 0.089126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2546-1_0_4_line_62 |  | 59 | 61 | 0.004748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2546-1_0_4_line_63 |  | 59 | 62 | 0.060879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2546-1_0_4_line_64 |  | 60 | 63 | 0.05177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2546-1_0_4_line_65 |  | 61 | 64 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2546-1_0_4_line_66 |  | 61 | 65 | 0.020738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2546-1_0_4_line_67 |  | 65 | 70 | 0.043905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2546-1_0_4_line_68 |  | 65 | 71 | 0.029589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2546-1_0_4_line_69 |  | 66 | 68 | 0.025809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2546-1_0_4_line_70 |  | 67 | 69 | 0.064543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2546-1_0_4_line_71 |  | 69 | 73 | 0.057871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2546-1_0_4_line_72 |  | 69 | 74 | 0.037503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2546-1_0_4_line_73 |  | 70 | 77 | 0.11216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2546-1_0_4_line_74 |  | 72 | 73 | 0.057609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2546-1_0_4_line_75 |  | 74 | 75 | 0.045357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2546-1_0_4_line_76 |  | 75 | 76 | 0.045426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2546-1_0_4_line_77 |  | 76 | 84 | 0.07185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2546-1_0_4_line_78 |  | 77 | 78 | 0.008004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2546-1_0_4_line_79 |  | 78 | 81 | 0.02752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2546-1_0_4_line_80 |  | 79 | 80 | 0.087192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2546-1_0_4_line_81 |  | 80 | 82 | 0.06324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2546-1_0_4_line_82 |  | 81 | 89 | 0.056797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2546-1_0_4_line_83 |  | 81 | 90 | 0.027144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2546-1_0_4_line_84 |  | 82 | 83 | 0.080346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2546-1_0_4_line_85 |  | 83 | 84 | 0.012327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2546-1_0_4_line_86 |  | 83 | 85 | 0.11883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2546-1_0_4_line_87 |  | 85 | 86 | 0.042385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2546-1_0_4_line_88 |  | 85 | 87 | 0.075902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2546-1_0_4_line_89 |  | 87 | 88 | 0.016449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2546-1_0_4_line_90 |  | 90 | 91 | 0.047668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2546-1_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 92 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2597380.4468 | 1226277.6955 | 2597371.1557 | 1226298.1028
1 | 2597357.629 | 1226327.8129 | 2597371.1557 | 1226298.1028
2 | 2597357.629 | 1226327.8129 | 2597281.107 | 1226304.8711
3 | 2597357.629 | 1226327.8129 | 2597365.6124 | 1226330.2367
4 | 2597281.107 | 1226304.8711 | 2597249.8033 | 1226295.486
5 | 2597386.0507 | 1226336.4419 | 2597365.6124 | 1226330.2367
6 | 2597206.0873 | 1226282.3797 | 2597249.8033 | 1226295.486
7 | 2597391.2641 | 1226338.0246 | 2597386.0507 | 1226336.4419
8 | 2597206.0873 | 1226282.3797 | 2597160.3192 | 1226268.3175
9 | 2597206.0873 | 1226282.3797 | 2597193.7221 | 1226317.3796
10 | 2597206.0873 | 1226282.3797 | 2597235.0038 | 1226218.5138
11 | 2597402.5298 | 1226341.4449 | 2597391.2641 | 1226338.0246
12 | 2597358.798 | 1226466.6552 | 2597372.769 | 1226470.5936
13 | 2597354.0919 | 1226465.3286 | 2597358.798 | 1226466.6552
14 | 2597359.1036 | 1226453.297 | 2597354.0919 | 1226465.3286
15 | 2597309.9166 | 1226452.8527 | 2597354.0919 | 1226465.3286
16 | 2597359.1036 | 1226453.297 | 2597363.4983 | 1226451.1048 | 2597367.9576 | 1226439.6106
17 | 2597359.1036 | 1226453.297 | 2597358.0024 | 1226448.4057 | 2597361.8272 | 1226439.2421
18 | 2597314.2996 | 1226441.7998 | 2597309.9166 | 1226452.8527
19 | 2597309.9166 | 1226452.8527 | 2597289.8982 | 1226447.2032 | 2597288.3976 | 1226447.2039
20 | 2597367.9576 | 1226439.6106 | 2597371.4528 | 1226430.6013
21 | 2597371.8026 | 1226429.6996 | 2597366.6026 | 1226427.8008 | 2597361.8272 | 1226439.2421
22 | 2597314.2996 | 1226441.7998 | 2597312.403 | 1226437.7983 | 2597316.4869 | 1226426.2315
23 | 2597314.2996 | 1226441.7998 | 2597318.7017 | 1226439.0961 | 2597323.1323 | 1226427.5804
24 | 2597263.1968 | 1226493.1983 | 2597269.6032 | 1226481.8998 | 2597284.5037 | 1226450.7967 | 2597287.1019 | 1226447.8049 | 2597288.3976 | 1226447.2039
25 | 2597369.472 | 1226428.8486 | 2597371.8026 | 1226429.6996 | 2597371.4528 | 1226430.6013
26 | 2597369.472 | 1226428.8486 | 2597366.6026 | 1226427.8008 | 2597366.6026 | 1226427.8008
27 | 2597320.6986 | 1226414.3029 | 2597316.4869 | 1226426.2315
28 | 2597327.2026 | 1226417.0015 | 2597323.1323 | 1226427.5804
29 | 2597263.1968 | 1226493.1983 | 2597270.6022 | 1226495.0959 | 2597357.3286 | 1226516.3015 | 2597379.0139 | 1226521.6936
30 | 2597432.5639 | 1226534.9897 | 2597411.197 | 1226529.6961 | 2597379.0139 | 1226521.6936
31 | 2597458.6947 | 1226481.7802 | 2597448.3918 | 1226503.1573
32 | 2597432.5639 | 1226534.9897 | 2597437.0695 | 1226526.6494 | 2597448.3918 | 1226503.1573
33 | 2597484.6283 | 1226426.8144 | 2597471.9226 | 1226453.5356 | 2597458.6947 | 1226481.7802
34 | 2597484.6283 | 1226426.8144 | 2597495.5787 | 1226402.8169
35 | 2597484.6283 | 1226426.8144 | 2597463.7044 | 1226418.5398
36 | 2597507.5622 | 1226374.596 | 2597501.1346 | 1226390.6416 | 2597495.5787 | 1226402.8169
37 | 2597463.7044 | 1226418.5398 | 2597440.418 | 1226409.3309
38 | 2597507.5622 | 1226374.596 | 2597513.6486 | 1226358.1504 | 2597515.8176 | 1226353.5121
39 | 2597507.5622 | 1226374.596 | 2597534.4262 | 1226384.368 | 2597570.5598 | 1226394.3705
40 | 2597507.5622 | 1226374.596 | 2597481.5727 | 1226366.0762
41 | 2597436.5147 | 1226407.7873 | 2597440.418 | 1226409.3309
42 | 2597515.8176 | 1226353.5121 | 2597529.8149 | 1226323.5788 | 2597532.5353 | 1226317.5798
43 | 2597588.6826 | 1226399.3872 | 2597570.5598 | 1226394.3705
44 | 2597455.4038 | 1226357.4976 | 2597481.5727 | 1226366.0762
45 | 2597434.053 | 1226406.8138 | 2597436.5147 | 1226407.7873
46 | 2597419.751 | 1226346.6733 | 2597402.5298 | 1226341.4449
47 | 2597419.751 | 1226346.6733 | 2597427.6175 | 1226349.0616
48 | 2597455.4038 | 1226357.4976 | 2597427.6175 | 1226349.0616
49 | 2597177.5281 | 1226353.1773 | 2597193.5006 | 1226318.0066 | 2597193.7221 | 1226317.3796
50 | 2597261.3493 | 1226160.3262 | 2597235.0038 | 1226218.5138
51 | 2597455.4038 | 1226357.4976 | 2597478.6684 | 1226306.6543
52 | 2597478.6684 | 1226306.6543 | 2597493.3221 | 1226274.6293
53 | 2597532.5353 | 1226317.5798 | 2597548.9897 | 1226281.295
54 | 2597588.6826 | 1226399.3872 | 2597608.4461 | 1226404.9352
55 | 2597493.3221 | 1226274.6293 | 2597502.4296 | 1226254.7253
56 | 2597557.0413 | 1226263.5398 | 2597548.9897 | 1226281.295
57 | 2597686.2058 | 1226427.1567 | 2597667.1031 | 1226421.4013 | 2597608.4461 | 1226404.9352
58 | 2597507.993 | 1226242.567 | 2597502.4296 | 1226254.7253
59 | 2597557.0413 | 1226263.5398 | 2597564.4599 | 1226247.1804
60 | 2597588.156 | 1226191.2209 | 2597561.7616 | 1226182.6048 | 2597538.4981 | 1226175.8996
61 | 2597538.4981 | 1226175.8996 | 2597452.5996 | 1226151.2446
62 | 2597592.6498 | 1226189.6515 | 2597588.156 | 1226191.2209
63 | 2597588.156 | 1226191.2209 | 2597585.8026 | 1226200.116 | 2597564.4599 | 1226247.1804
64 | 2597452.5996 | 1226151.2446 | 2597430.6645 | 1226198.138
65 | 2597592.6498 | 1226189.6515 | 2597594.2198 | 1226192.2746 | 2597596.6614 | 1226195.1197 | 2597601.2784 | 1226197.9639 | 2597610.7242 | 1226202.3748
66 | 2597592.6498 | 1226189.6515 | 2597611.6246 | 1226181.1608
67 | 2597611.6246 | 1226181.1608 | 2597615.5842 | 1226189.1305 | 2597620.3005 | 1226194.1871 | 2597631.1873 | 1226201.5092 | 2597643.3992 | 1226206.0179 | 2597645.2698 | 1226206.5818
68 | 2597611.6246 | 1226181.1608 | 2597609.6418 | 1226170.0885 | 2597611.3714 | 1226155.457 | 2597612.5992 | 1226152.0651
69 | 2597177.5281 | 1226353.1773 | 2597166.8562 | 1226376.6763
70 | 2597285.9841 | 1226100.7241 | 2597282.2075 | 1226112.3771 | 2597278.6953 | 1226122.0177 | 2597261.3493 | 1226160.3262
71 | 2597285.9841 | 1226100.7241 | 2597230.7377 | 1226082.9843
72 | 2597285.9841 | 1226100.7241 | 2597289.0797 | 1226091.4172 | 2597291.2147 | 1226086.2798 | 2597300.2403 | 1226066.0726
73 | 2597752.6658 | 1226238.938 | 2597667.1931 | 1226213.1902 | 2597645.2698 | 1226206.5818
74 | 2597230.7377 | 1226082.9843 | 2597207.2677 | 1226135.5955
75 | 2597318.7378 | 1226024.6589 | 2597300.2403 | 1226066.0726
76 | 2597318.7378 | 1226024.6589 | 2597333.5016 | 1225991.6047 | 2597337.2978 | 1225983.1977
77 | 2597366.863 | 1225917.7128 | 2597364.9549 | 1225921.9495 | 2597337.2978 | 1225983.1977
78 | 2597749.5158 | 1226246.2991 | 2597752.6658 | 1226238.938
79 | 2597749.5158 | 1226246.2991 | 2597743.0188 | 1226261.4772 | 2597738.4298 | 1226271.4849
80 | 2597508.2628 | 1225944.4803 | 2597590.5492 | 1225969.2899 | 2597591.6712 | 1225969.8342
81 | 2597447.7145 | 1225926.2249 | 2597508.2628 | 1225944.4803
82 | 2597738.4298 | 1226271.4849 | 2597714.7741 | 1226323.1212
83 | 2597718.6739 | 1226259.2077 | 2597723.2483 | 1226270.0345 | 2597730.1157 | 1226271.8884 | 2597738.4298 | 1226271.4849
84 | 2597378.6735 | 1225921.2429 | 2597382.4435 | 1225911.0797 | 2597383.0341 | 1225909.7119 | 2597383.9356 | 1225908.5997 | 2597384.8676 | 1225908.1213 | 2597386.2546 | 1225907.9316 | 2597388.2179 | 1225908.2865 | 2597447.7145 | 1225926.2249
85 | 2597366.863 | 1225917.7128 | 2597370.7973 | 1225918.8895 | 2597378.6735 | 1225921.2429
86 | 2597378.6735 | 1225921.2429 | 2597398.9667 | 1225927.315 | 2597469.7838 | 1225948.2181 | 2597459.5609 | 1225969.7241
87 | 2597441.6449 | 1226008.1545 | 2597459.5609 | 1225969.7241
88 | 2597459.5609 | 1225969.7241 | 2597474.7912 | 1225976.7659 | 2597488.9448 | 1225983.1969 | 2597501.6884 | 1225989.0392 | 2597514.1818 | 1225994.7705 | 2597507.6015 | 1226009.1485
89 | 2597507.6015 | 1226009.1485 | 2597522.4678 | 1226016.2796
90 | 2597718.6739 | 1226259.2077 | 2597673.3946 | 1226244.3062

## bus_geodata
| x | y | coords
0 | 2597380.4468 | 1226277.6955
1 | 2597371.1557 | 1226298.1028
2 | 2597357.629 | 1226327.8129
3 | 2597281.107 | 1226304.8711
4 | 2597365.6124 | 1226330.2367
5 | 2597249.8033 | 1226295.486
6 | 2597386.0507 | 1226336.4419
7 | 2597206.0873 | 1226282.3797
8 | 2597391.2641 | 1226338.0246
9 | 2597358.798 | 1226466.6552
10 | 2597372.769 | 1226470.5936
11 | 2597354.0919 | 1226465.3286
12 | 2597359.1036 | 1226453.297
13 | 2597309.9166 | 1226452.8527
14 | 2597367.9576 | 1226439.6106
15 | 2597361.8272 | 1226439.2421
16 | 2597314.2996 | 1226441.7998
17 | 2597288.3976 | 1226447.2039
18 | 2597371.4528 | 1226430.6013
19 | 2597366.6026 | 1226427.8008
20 | 2597369.472 | 1226428.8486
21 | 2597371.8026 | 1226429.6996
22 | 2597316.4869 | 1226426.2315
23 | 2597323.1323 | 1226427.5804
24 | 2597263.1968 | 1226493.1983
25 | 2597320.6986 | 1226414.3029
26 | 2597327.2026 | 1226417.0015
27 | 2597379.0139 | 1226521.6936
28 | 2597448.3918 | 1226503.1573
29 | 2597458.6947 | 1226481.7802
30 | 2597432.5639 | 1226534.9897
31 | 2597484.6283 | 1226426.8144
32 | 2597495.5787 | 1226402.8169
33 | 2597463.7044 | 1226418.5398
34 | 2597507.5622 | 1226374.596
35 | 2597440.418 | 1226409.3309
36 | 2597515.8176 | 1226353.5121
37 | 2597570.5598 | 1226394.3705
38 | 2597481.5727 | 1226366.0762
39 | 2597436.5147 | 1226407.7873
40 | 2597434.053 | 1226406.8138
41 | 2597402.5298 | 1226341.4449
42 | 2597419.751 | 1226346.6733
43 | 2597427.6175 | 1226349.0616
44 | 2597160.3192 | 1226268.3175
45 | 2597193.7221 | 1226317.3796
46 | 2597235.0038 | 1226218.5138
47 | 2597455.4038 | 1226357.4976
48 | 2597478.6684 | 1226306.6543
49 | 2597532.5353 | 1226317.5798
50 | 2597588.6826 | 1226399.3872
51 | 2597493.3221 | 1226274.6293
52 | 2597548.9897 | 1226281.295
53 | 2597608.4461 | 1226404.9352
54 | 2597502.4296 | 1226254.7253
55 | 2597557.0413 | 1226263.5398
56 | 2597686.2058 | 1226427.1567
57 | 2597507.993 | 1226242.567
58 | 2597538.4981 | 1226175.8996
59 | 2597588.156 | 1226191.2209
60 | 2597452.5996 | 1226151.2446
61 | 2597592.6498 | 1226189.6515
62 | 2597564.4599 | 1226247.1804
63 | 2597430.6645 | 1226198.138
64 | 2597610.7242 | 1226202.3748
65 | 2597611.6246 | 1226181.1608
66 | 2597177.5281 | 1226353.1773
67 | 2597261.3493 | 1226160.3262
68 | 2597166.8562 | 1226376.6763
69 | 2597285.9841 | 1226100.7241
70 | 2597645.2698 | 1226206.5818
71 | 2597612.5992 | 1226152.0651
72 | 2597207.2677 | 1226135.5955
73 | 2597230.7377 | 1226082.9843
74 | 2597300.2403 | 1226066.0726
75 | 2597318.7378 | 1226024.6589
76 | 2597337.2978 | 1225983.1977
77 | 2597752.6658 | 1226238.938
78 | 2597749.5158 | 1226246.2991
79 | 2597591.6712 | 1225969.8342
80 | 2597508.2628 | 1225944.4803
81 | 2597738.4298 | 1226271.4849
82 | 2597447.7145 | 1225926.2249
83 | 2597378.6735 | 1225921.2429
84 | 2597366.863 | 1225917.7128
85 | 2597459.5609 | 1225969.7241
86 | 2597441.6449 | 1226008.1545
87 | 2597507.6015 | 1226009.1485
88 | 2597522.4678 | 1226016.2796
89 | 2597714.7741 | 1226323.1212
90 | 2597718.6739 | 1226259.2077
91 | 2597673.3946 | 1226244.3062
92 | 2597363.4283 | 1226264.2397

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.54433 | -0.13998
1 | 0.99723 | -0.052171 | 0.0075143 | 0.0018833
2 | 0.99326 | -0.12756 | 0 | 0
3 | 0.9904 | -0.18245 | 0.028369 | 0.00711
4 | 0.99254 | -0.1412 | 0.0012432 | 0.00031156
5 | 0.98945 | -0.20087 | 0.01332 | 0.0033384
6 | 0.99071 | -0.17609 | 0.00087943 | 0.00022041
7 | 0.98826 | -0.22393 | 0 | 0
8 | 0.99025 | -0.18498 | 0.0025061 | 0.00062808
9 | 0.97203 | -0.53926 | 0.0030796 | 0.00077183
10 | 0.97199 | -0.54 | 0.0027861 | 0.00069826
11 | 0.97206 | -0.53873 | 0 | 0
12 | 0.97173 | -0.54513 | 0 | 0
13 | 0.97344 | -0.51135 | 0 | 0
14 | 0.97142 | -0.55127 | 0.0056436 | 0.0014144
15 | 0.97163 | -0.54714 | 0.0055731 | 0.0013968
16 | 0.97323 | -0.51559 | 0 | 0
17 | 0.97452 | -0.49011 | 0.0014653 | 0.00036724
18 | 0.9713 | -0.55371 | 0.0075806 | 0.0018999
19 | 0.97127 | -0.5543 | 0.0035977 | 0.00090167
20 | 0.97128 | -0.55409 | 0.0024754 | 0.00062039
21 | 0.9716 | -0.54771 | 0.0017294 | 0.00043344
22 | 0.97306 | -0.519 | 0.0054839 | 0.0013744
23 | 0.97309 | -0.51825 | 0.0056693 | 0.0014209
24 | 0.97584 | -0.46428 | 0 | 0
25 | 0.97299 | -0.52031 | 0.0056179 | 0.001408
26 | 0.97307 | -0.5188 | 0.0026024 | 0.00065223
27 | 0.97781 | -0.42556 | 0.0032265 | 0.00080863
28 | 0.97901 | -0.4022 | 0.015975 | 0.0040038
29 | 0.97941 | -0.39437 | 0 | 0
30 | 0.97854 | -0.41134 | 0 | 0
31 | 0.98044 | -0.37437 | 0 | 0
32 | 0.98103 | -0.36284 | 0.01196 | 0.0029975
33 | 0.97994 | -0.38417 | 0.0025325 | 0.00063471
34 | 0.9818 | -0.34778 | 0 | 0
35 | 0.97944 | -0.39393 | 0.001968 | 0.00049324
36 | 0.98136 | -0.35632 | 0.0015644 | 0.00039207
37 | 0.97964 | -0.39006 | 0.0043863 | 0.0010993
38 | 0.98325 | -0.31974 | 0.01178 | 0.0029524
39 | 0.97936 | -0.39542 | 0.0023909 | 0.00059922
40 | 0.97932 | -0.39624 | 0.017103 | 0.0042863
41 | 0.98925 | -0.20411 | 0.0010541 | 0.00026418
42 | 0.98772 | -0.23334 | 0.0034545 | 0.00086578
43 | 0.98703 | -0.24659 | 0.026272 | 0.0065843
44 | 0.98797 | -0.22957 | 0.0065891 | 0.0016514
45 | 0.98678 | -0.25266 | 0.03682 | 0.009228
46 | 0.98722 | -0.24382 | 0.0079956 | 0.0020039
47 | 0.98478 | -0.29012 | 0 | 0
48 | 0.97981 | -0.38654 | 0.0030301 | 0.00075941
49 | 0.98061 | -0.37099 | 0.0015703 | 0.00039355
50 | 0.9791 | -0.40062 | 0 | 0
51 | 0.97678 | -0.44583 | 0.0022581 | 0.00056594
52 | 0.97986 | -0.38548 | 0.0011752 | 0.00029452
53 | 0.97851 | -0.41217 | 0.013985 | 0.003505
54 | 0.97495 | -0.48196 | 0.087913 | 0.022033
55 | 0.9795 | -0.39248 | 0.00088821 | 0.00022261
56 | 0.97724 | -0.43713 | 0.016931 | 0.0042432
57 | 0.97492 | -0.48251 | 0.0022627 | 0.00056709
58 | 0.97579 | -0.46498 | 0 | 0
59 | 0.97772 | -0.42729 | 0 | 0
60 | 0.97247 | -0.53015 | 0 | 0
61 | 0.97755 | -0.4305 | 0 | 0
62 | 0.97917 | -0.39885 | 0.0011692 | 0.00029302
63 | 0.97055 | -0.5682 | 0.039803 | 0.0099755
64 | 0.97751 | -0.43131 | 0.0019539 | 0.0004897
65 | 0.97687 | -0.44382 | 0 | 0
66 | 0.98654 | -0.25721 | 0.0044837 | 0.0011237
67 | 0.9864 | -0.25969 | 0 | 0
68 | 0.9865 | -0.25813 | 0.0019898 | 0.00049869
69 | 0.98557 | -0.27575 | 0 | 0
70 | 0.9755 | -0.47067 | 0.012674 | 0.0031763
71 | 0.97682 | -0.44477 | 0.0017563 | 0.00044018
72 | 0.98486 | -0.28958 | 0.0066663 | 0.0016707
73 | 0.98522 | -0.28268 | 0 | 0
74 | 0.98515 | -0.28397 | 0.00070691 | 0.00017717
75 | 0.98464 | -0.29377 | 0.0058437 | 0.0014646
76 | 0.98285 | -0.32836 | 0.0019932 | 0.00049955
77 | 0.97333 | -0.5134 | 0 | 0
78 | 0.97318 | -0.51645 | 0 | 0
79 | 0.97889 | -0.40558 | 0.0031324 | 0.00078506
80 | 0.97915 | -0.40061 | 0.0008314 | 0.00020837
81 | 0.97264 | -0.52697 | 0 | 0
82 | 0.97938 | -0.39605 | 0.00036205 | 9.0738e-05
83 | 0.9797 | -0.38973 | 0 | 0
84 | 0.98016 | -0.38072 | 0 | 0
85 | 0.97572 | -0.4676 | 0 | 0
86 | 0.97434 | -0.49482 | 0.035019 | 0.0087765
87 | 0.97566 | -0.46888 | 0 | 0
88 | 0.97565 | -0.46916 | 0.00091693 | 0.0002298
89 | 0.9726 | -0.52792 | 0.00090936 | 0.00022791
90 | 0.97214 | -0.53689 | 0 | 0
91 | 0.97126 | -0.55435 | 0.019837 | 0.0049716
92 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.54268 | 0.13998 | -0.5413 | -0.1391 | 0.0013756 | 0.00087919 | 0.80893 | 0.80893 | 0.80893 | 1 | 0 | 0.99723 | -0.052171 | 55.5582
1 | 0.53379 | 0.13721 | -0.53184 | -0.13597 | 0.0019475 | 0.0012447 | 0.79772 | 0.79772 | 0.79772 | 0.99723 | -0.052171 | 0.99326 | -0.12756 | 54.7882
2 | 0.15632 | 0.039641 | -0.15591 | -0.039382 | 0.00041131 | 0.00025912 | 0.23435 | 0.23435 | 0.23435 | 0.99326 | -0.12756 | 0.9904 | -0.18245 | 16.0954
3 | 0.37552 | 0.096327 | -0.37528 | -0.096169 | 0.00024825 | 0.00015845 | 0.56337 | 0.56337 | 0.56337 | 0.99326 | -0.12756 | 0.99254 | -0.1412 | 38.6929
4 | 0.12754 | 0.032272 | -0.12743 | -0.032202 | 0.00011262 | 7.0398e-05 | 0.19173 | 0.19173 | 0.19173 | 0.9904 | -0.18245 | 0.98945 | -0.20087 | 13.1681
5 | 0.37403 | 0.095857 | -0.3734 | -0.095454 | 0.00063135 | 0.00040296 | 0.56151 | 0.56151 | 0.56151 | 0.99254 | -0.1412 | 0.99071 | -0.17609 | 38.5649
6 | 0.11411 | 0.028864 | -0.11398 | -0.028785 | 0.00012613 | 7.8382e-05 | 0.1717 | 0.1717 | 0.1717 | 0.98945 | -0.20087 | 0.98826 | -0.22393 | 11.7923
7 | 0.37252 | 0.095234 | -0.37236 | -0.095131 | 0.00016029 | 0.0001023 | 0.56018 | 0.56018 | 0.56018 | 0.99071 | -0.17609 | 0.99025 | -0.18498 | 38.4742
8 | 0.0065908 | 0.0016519 | -0.0065891 | -0.0016514 | 1.7683e-06 | 5.184e-07 | 0.0099238 | 0.0099241 | 0.0099241 | 0.98826 | -0.22393 | 0.98797 | -0.22957 | 2.7264
9 | 0.043355 | 0.010888 | -0.043295 | -0.010851 | 5.9333e-05 | 3.7498e-05 | 0.065287 | 0.065287 | 0.065287 | 0.98826 | -0.22393 | 0.98678 | -0.25266 | 17.9361
10 | 0.064033 | 0.016245 | -0.063972 | -0.01621 | 6.1188e-05 | 3.5571e-05 | 0.096485 | 0.096487 | 0.096487 | 0.98826 | -0.22393 | 0.98722 | -0.24382 | 6.6268
11 | 0.36986 | 0.094503 | -0.36951 | -0.094285 | 0.00034173 | 0.0002181 | 0.55642 | 0.55642 | 0.55642 | 0.99025 | -0.18498 | 0.98925 | -0.20411 | 38.2156
12 | 0.0027862 | 0.00069815 | -0.0027861 | -0.00069826 | 9.9024e-08 | -1.1655e-07 | 0.0042652 | 0.0042652 | 0.0042652 | 0.97203 | -0.53926 | 0.97199 | -0.54 | 1.1718
13 | -0.0058659 | -0.00147 | 0.005866 | 0.00147 | 1.4784e-07 | 3.401e-08 | 0.0089796 | 0.0089796 | 0.0089796 | 0.97203 | -0.53926 | 0.97206 | -0.53873 | 2.4669
14 | 0.026616 | 0.006676 | -0.026608 | -0.0066709 | 8.1122e-06 | 5.0303e-06 | 0.040746 | 0.040746 | 0.040746 | 0.97206 | -0.53873 | 0.97173 | -0.54513 | 11.1939
15 | -0.032482 | -0.008146 | 0.032525 | 0.0081726 | 4.2447e-05 | 2.6598e-05 | 0.049725 | 0.049725 | 0.049725 | 0.97206 | -0.53873 | 0.97344 | -0.51135 | 13.6608
16 | 0.019305 | 0.0048407 | -0.019299 | -0.0048373 | 5.65e-06 | 3.4025e-06 | 0.029562 | 0.029562 | 0.029562 | 0.97173 | -0.54513 | 0.97142 | -0.55127 | 8.1215
17 | 0.0073033 | 0.0018303 | -0.0073026 | -0.00183 | 7.0087e-07 | 2.6346e-07 | 0.011183 | 0.011184 | 0.011184 | 0.97173 | -0.54513 | 0.97163 | -0.54714 | 3.0724
18 | 0.019381 | 0.0048592 | -0.019377 | -0.0048568 | 3.9125e-06 | 2.3563e-06 | 0.029626 | 0.029626 | 0.029626 | 0.97344 | -0.51135 | 0.97323 | -0.51559 | 8.1391
19 | -0.051905 | -0.013032 | 0.051958 | 0.013065 | 5.2658e-05 | 3.3423e-05 | 0.079351 | 0.079351 | 0.079351 | 0.97344 | -0.51135 | 0.97452 | -0.49011 | 21.7998
20 | 0.013655 | 0.0034229 | -0.013654 | -0.003422 | 1.5856e-06 | 8.9514e-07 | 0.020917 | 0.020917 | 0.020917 | 0.97142 | -0.55127 | 0.9713 | -0.55371 | 5.7466
21 | 0.0017295 | 0.00043325 | -0.0017294 | -0.00043344 | 4.7177e-08 | -1.9192e-07 | 0.0026486 | 0.0026486 | 0.0026486 | 0.97163 | -0.54714 | 0.9716 | -0.54771 | 0.72765
22 | 0.011104 | 0.0027834 | -0.011102 | -0.0027825 | 1.8045e-06 | 9.4748e-07 | 0.016978 | 0.016978 | 0.016978 | 0.97323 | -0.51559 | 0.97306 | -0.519 | 4.6642
23 | 0.0082729 | 0.0020734 | -0.0082718 | -0.002073 | 1.0502e-06 | 4.5466e-07 | 0.012649 | 0.012649 | 0.012649 | 0.97323 | -0.51559 | 0.97309 | -0.51825 | 3.475
24 | -0.053423 | -0.013432 | 0.053489 | 0.013473 | 6.5985e-05 | 4.0911e-05 | 0.081589 | 0.081588 | 0.081589 | 0.97452 | -0.49011 | 0.97584 | -0.46428 | 11.2072
25 | 0.0060732 | 0.0015221 | -0.0060731 | -0.001522 | 1.1194e-07 | 2.8963e-08 | 0.0093041 | 0.0093041 | 0.0093041 | 0.9713 | -0.55371 | 0.97128 | -0.55409 | 2.5561
26 | -0.0035977 | -0.00090167 | 0.0035977 | 0.00090165 | 3.48e-08 | -1.5534e-08 | 0.0055118 | 0.0055118 | 0.0055118 | 0.97127 | -0.5543 | 0.97128 | -0.55409 | 1.5142
27 | 0.0056183 | 0.0014081 | -0.0056179 | -0.001408 | 3.5017e-07 | 6.6981e-08 | 0.0085916 | 0.0085917 | 0.0085917 | 0.97306 | -0.519 | 0.97299 | -0.52031 | 2.3603
28 | 0.0026025 | 0.00065213 | -0.0026024 | -0.00065223 | 6.7318e-08 | -9.7725e-08 | 0.0039796 | 0.0039796 | 0.0039796 | 0.97309 | -0.51825 | 0.97307 | -0.5188 | 1.0933
29 | -0.053489 | -0.013473 | 0.053589 | 0.013532 | 9.9241e-05 | 5.9035e-05 | 0.081588 | 0.081586 | 0.081588 | 0.97584 | -0.46428 | 0.97781 | -0.42556 | 7.4714
30 | -0.056815 | -0.014341 | 0.056854 | 0.014363 | 3.87e-05 | 2.1998e-05 | 0.086496 | 0.086495 | 0.086496 | 0.97781 | -0.42556 | 0.97854 | -0.41134 | 5.9407
31 | -0.072854 | -0.018381 | 0.072881 | 0.018397 | 2.73e-05 | 1.6278e-05 | 0.11078 | 0.11078 | 0.11078 | 0.97901 | -0.4022 | 0.97941 | -0.39437 | 7.6083
32 | 0.056879 | 0.014377 | -0.056854 | -0.014363 | 2.494e-05 | 1.4174e-05 | 0.086495 | 0.086495 | 0.086495 | 0.97901 | -0.4022 | 0.97854 | -0.41134 | 5.9406
33 | -0.072881 | -0.018397 | 0.072951 | 0.018439 | 6.9891e-05 | 4.1669e-05 | 0.11078 | 0.11077 | 0.11078 | 0.97941 | -0.39437 | 0.98044 | -0.37437 | 7.6082
34 | -0.096969 | -0.024467 | 0.097022 | 0.0245 | 5.3604e-05 | 3.2975e-05 | 0.14723 | 0.14723 | 0.14723 | 0.98044 | -0.37437 | 0.98103 | -0.36284 | 10.1119
35 | 0.024017 | 0.0060277 | -0.024006 | -0.0060208 | 1.1213e-05 | 6.8927e-06 | 0.036454 | 0.036454 | 0.036454 | 0.98044 | -0.37437 | 0.97994 | -0.38417 | 10.0149
36 | -0.10898 | -0.027497 | 0.10906 | 0.027546 | 7.8626e-05 | 4.8771e-05 | 0.16537 | 0.16537 | 0.16537 | 0.98103 | -0.36284 | 0.9818 | -0.34778 | 11.3578
37 | 0.021474 | 0.0053861 | -0.021464 | -0.00538 | 9.9853e-06 | 6.0753e-06 | 0.032609 | 0.032609 | 0.032609 | 0.97994 | -0.38417 | 0.97944 | -0.39393 | 8.9585
38 | 0.084028 | 0.021326 | -0.083994 | -0.021305 | 3.4501e-05 | 2.0935e-05 | 0.12745 | 0.12745 | 0.12745 | 0.9818 | -0.34778 | 0.98136 | -0.35632 | 8.7534
39 | 0.035426 | 0.0089247 | -0.035355 | -0.0088798 | 7.1479e-05 | 4.4913e-05 | 0.053708 | 0.053709 | 0.053709 | 0.9818 | -0.34778 | 0.97964 | -0.39006 | 14.7551
40 | -0.22852 | -0.057797 | 0.22882 | 0.057992 | 0.0003079 | 0.00019567 | 0.34653 | 0.34653 | 0.34653 | 0.9818 | -0.34778 | 0.98325 | -0.31974 | 23.7998
41 | 0.019496 | 0.0048868 | -0.019494 | -0.0048859 | 1.3809e-06 | 8.3094e-07 | 0.029619 | 0.029619 | 0.029619 | 0.97944 | -0.39393 | 0.97936 | -0.39542 | 8.1371
42 | 0.082429 | 0.020913 | -0.082371 | -0.020878 | 5.8125e-05 | 3.5199e-05 | 0.12508 | 0.12508 | 0.12508 | 0.98136 | -0.35632 | 0.98061 | -0.37099 | 8.5905
43 | 0.030968 | 0.0077805 | -0.030953 | -0.0077707 | 1.5608e-05 | 9.7523e-06 | 0.047046 | 0.047046 | 0.047046 | 0.97964 | -0.39006 | 0.9791 | -0.40062 | 12.9248
44 | -0.2406 | -0.060945 | 0.24095 | 0.061163 | 0.00034274 | 0.00021795 | 0.36435 | 0.36435 | 0.36435 | 0.98325 | -0.31974 | 0.98478 | -0.29012 | 25.0243
45 | 0.017103 | 0.0042867 | -0.017103 | -0.0042863 | 6.7035e-07 | 3.9572e-07 | 0.025986 | 0.025986 | 0.025986 | 0.97936 | -0.39542 | 0.97932 | -0.39624 | 7.1391
46 | 0.36846 | 0.094021 | -0.36794 | -0.093689 | 0.00051941 | 0.0003315 | 0.55483 | 0.55483 | 0.55483 | 0.98925 | -0.20411 | 0.98772 | -0.23334 | 38.1067
47 | 0.36449 | 0.092824 | -0.36425 | -0.092675 | 0.00023283 | 0.00014859 | 0.54963 | 0.54963 | 0.54963 | 0.98772 | -0.23334 | 0.98703 | -0.24659 | 37.7493
48 | 0.33798 | 0.086091 | -0.33727 | -0.085639 | 0.00070816 | 0.00045174 | 0.51002 | 0.51002 | 0.51002 | 0.98703 | -0.24659 | 0.98478 | -0.29012 | 35.0291
49 | 0.006475 | 0.0016225 | -0.0064736 | -0.0016221 | 1.4048e-06 | 3.9721e-07 | 0.0097639 | 0.0097641 | 0.0097641 | 0.98678 | -0.25266 | 0.98654 | -0.25721 | 2.6825
50 | 0.055977 | 0.014206 | -0.055934 | -0.014182 | 4.2692e-05 | 2.4059e-05 | 0.084435 | 0.084436 | 0.084436 | 0.98722 | -0.24382 | 0.9864 | -0.25969 | 5.7992
51 | 0.096327 | 0.024476 | -0.095882 | -0.024192 | 0.00044493 | 0.00028405 | 0.14567 | 0.14567 | 0.14567 | 0.98478 | -0.29012 | 0.97981 | -0.38654 | 40.0198
52 | 0.092852 | 0.023433 | -0.092589 | -0.023265 | 0.00026283 | 0.00016777 | 0.14107 | 0.14107 | 0.14107 | 0.97981 | -0.38654 | 0.97678 | -0.44583 | 38.7556
53 | 0.080801 | 0.020484 | -0.080744 | -0.02045 | 5.6229e-05 | 3.3978e-05 | 0.12269 | 0.1227 | 0.1227 | 0.98061 | -0.37099 | 0.97986 | -0.38548 | 8.4269
54 | 0.030953 | 0.0077707 | -0.030936 | -0.0077601 | 1.7038e-05 | 1.0646e-05 | 0.047046 | 0.047046 | 0.047046 | 0.9791 | -0.40062 | 0.97851 | -0.41217 | 12.9248
55 | 0.090331 | 0.022699 | -0.090175 | -0.0226 | 0.00015548 | 9.9235e-05 | 0.13763 | 0.13763 | 0.13763 | 0.97678 | -0.44583 | 0.97495 | -0.48196 | 37.8106
56 | 0.079569 | 0.020156 | -0.079543 | -0.02014 | 2.672e-05 | 1.6119e-05 | 0.12091 | 0.12091 | 0.12091 | 0.97986 | -0.38548 | 0.9795 | -0.39248 | 8.3043
57 | 0.016951 | 0.0042551 | -0.016931 | -0.0042432 | 2.0156e-05 | 1.1885e-05 | 0.02578 | 0.02578 | 0.02578 | 0.97851 | -0.41217 | 0.97724 | -0.43713 | 7.0824
58 | 0.0022628 | 0.00056697 | -0.0022627 | -0.00056709 | 5.9803e-08 | -1.2846e-07 | 0.0034535 | 0.0034536 | 0.0034536 | 0.97495 | -0.48196 | 0.97492 | -0.48251 | 0.94879
59 | 0.078654 | 0.019917 | -0.07863 | -0.019903 | 2.4073e-05 | 1.4503e-05 | 0.11956 | 0.11956 | 0.11956 | 0.9795 | -0.39248 | 0.97917 | -0.39885 | 8.2117
60 | -0.04 | -0.0101 | 0.040072 | 0.010145 | 7.2388e-05 | 4.568e-05 | 0.061024 | 0.061024 | 0.061024 | 0.97579 | -0.46498 | 0.97772 | -0.42729 | 16.7648
61 | 0.04 | 0.0101 | -0.039875 | -0.010021 | 0.00012446 | 7.8546e-05 | 0.061024 | 0.061024 | 0.061024 | 0.97579 | -0.46498 | 0.97247 | -0.53015 | 16.7649
62 | 0.037284 | 0.0093989 | -0.037278 | -0.0093953 | 5.7368e-06 | 3.612e-06 | 0.056763 | 0.056763 | 0.056763 | 0.97772 | -0.42729 | 0.97755 | -0.4305 | 15.5942
63 | -0.077356 | -0.019544 | 0.077461 | 0.01961 | 0.00010558 | 6.5274e-05 | 0.11779 | 0.11779 | 0.11779 | 0.97772 | -0.42729 | 0.97917 | -0.39885 | 10.7863
64 | 0.039875 | 0.010021 | -0.039803 | -0.0099755 | 7.2296e-05 | 4.5629e-05 | 0.061024 | 0.061024 | 0.061024 | 0.97247 | -0.53015 | 0.97055 | -0.5682 | 16.765
65 | 0.001954 | 0.00048946 | -0.0019539 | -0.0004897 | 7.5152e-08 | -2.359e-07 | 0.0029742 | 0.0029743 | 0.0029743 | 0.97755 | -0.4305 | 0.97751 | -0.43131 | 0.81713
66 | 0.035324 | 0.0089058 | -0.035301 | -0.0088917 | 2.25e-05 | 1.414e-05 | 0.053789 | 0.053789 | 0.053789 | 0.97755 | -0.4305 | 0.97687 | -0.44382 | 14.7771
67 | 0.033545 | 0.0084518 | -0.033502 | -0.0084248 | 4.3015e-05 | 2.6981e-05 | 0.051113 | 0.051114 | 0.051114 | 0.97687 | -0.44382 | 0.9755 | -0.47067 | 14.0422
68 | 0.0017564 | 0.00043986 | -0.0017563 | -0.00044018 | 7.9421e-08 | -3.1959e-07 | 0.0026753 | 0.0026755 | 0.0026755 | 0.97687 | -0.44382 | 0.97682 | -0.44477 | 0.73501
69 | 0.0019899 | 0.00049842 | -0.0019898 | -0.00049869 | 8.7181e-08 | -2.7373e-07 | 0.0030013 | 0.0030014 | 0.0030014 | 0.98654 | -0.25721 | 0.9865 | -0.25813 | 0.82455
70 | 0.055934 | 0.014182 | -0.055891 | -0.014157 | 4.3141e-05 | 2.4317e-05 | 0.084436 | 0.084438 | 0.084438 | 0.9864 | -0.25969 | 0.98557 | -0.27575 | 5.7993
71 | 0.0066707 | 0.0016721 | -0.0066685 | -0.0016714 | 2.2014e-06 | 6.7169e-07 | 0.010072 | 0.010072 | 0.010072 | 0.98557 | -0.27575 | 0.98522 | -0.28268 | 2.767
72 | 0.04922 | 0.012485 | -0.049201 | -0.012475 | 1.9444e-05 | 1.0533e-05 | 0.074366 | 0.074367 | 0.074367 | 0.98557 | -0.27575 | 0.98515 | -0.28397 | 5.1076
73 | 0.020828 | 0.0052485 | -0.020786 | -0.0052227 | 4.2485e-05 | 2.5793e-05 | 0.031781 | 0.031782 | 0.031782 | 0.9755 | -0.47067 | 0.97333 | -0.5134 | 8.7313
74 | -0.0066663 | -0.0016707 | 0.0066685 | 0.0016714 | 2.1915e-06 | 6.6925e-07 | 0.010072 | 0.010072 | 0.010072 | 0.98486 | -0.28958 | 0.98522 | -0.28268 | 2.7671
75 | 0.048494 | 0.012298 | -0.048471 | -0.012285 | 2.2846e-05 | 1.2313e-05 | 0.073299 | 0.0733 | 0.0733 | 0.98515 | -0.28397 | 0.98464 | -0.29377 | 5.0343
76 | 0.042627 | 0.010821 | -0.042556 | -0.010776 | 7.08e-05 | 4.4735e-05 | 0.064469 | 0.064469 | 0.064469 | 0.98464 | -0.29377 | 0.98285 | -0.32836 | 17.7113
77 | 0.040563 | 0.010276 | -0.040461 | -0.010212 | 0.00010175 | 6.421e-05 | 0.061451 | 0.061452 | 0.061452 | 0.98285 | -0.32836 | 0.98016 | -0.38072 | 16.8823
78 | 0.020786 | 0.0052227 | -0.020783 | -0.0052209 | 3.0318e-06 | 1.8409e-06 | 0.031782 | 0.031782 | 0.031782 | 0.97333 | -0.5134 | 0.97318 | -0.51645 | 8.7313
79 | 0.020783 | 0.0052209 | -0.020772 | -0.0052145 | 1.0424e-05 | 6.3297e-06 | 0.031782 | 0.031782 | 0.031782 | 0.97318 | -0.51645 | 0.97264 | -0.52697 | 8.7313
80 | -0.0031324 | -0.00078506 | 0.0031332 | 0.00078444 | 7.4127e-07 | -6.2199e-07 | 0.0047616 | 0.0047612 | 0.0047616 | 0.97889 | -0.40558 | 0.97915 | -0.40061 | 1.3081
81 | -0.0039646 | -0.0009928 | 0.0039654 | 0.00099256 | 8.6074e-07 | -2.4474e-07 | 0.0060247 | 0.0060244 | 0.0060247 | 0.97915 | -0.40061 | 0.97938 | -0.39605 | 1.6551
82 | 0.0009094 | 0.00022723 | -0.00090936 | -0.00022791 | 4.1219e-08 | -6.7851e-07 | 0.001391 | 0.0013913 | 0.0013913 | 0.97264 | -0.52697 | 0.9726 | -0.52792 | 0.38222
83 | 0.019863 | 0.0049873 | -0.019854 | -0.0049816 | 9.4015e-06 | 5.6802e-06 | 0.030391 | 0.030391 | 0.030391 | 0.97264 | -0.52697 | 0.97214 | -0.53689 | 8.3492
84 | -0.0043275 | -0.0010833 | 0.0043288 | 0.0010831 | 1.3023e-06 | -1.7795e-07 | 0.0065745 | 0.0065741 | 0.0065745 | 0.97938 | -0.39605 | 0.9797 | -0.38973 | 1.8062
85 | -0.040444 | -0.010201 | 0.040461 | 0.010212 | 1.7456e-05 | 1.1017e-05 | 0.061452 | 0.061452 | 0.061452 | 0.9797 | -0.38973 | 0.98016 | -0.38072 | 16.8823
86 | 0.036115 | 0.0091181 | -0.035981 | -0.0090337 | 0.0001342 | 8.4399e-05 | 0.054878 | 0.054878 | 0.054878 | 0.9797 | -0.38973 | 0.97572 | -0.4676 | 15.0764
87 | 0.035064 | 0.008805 | -0.035019 | -0.0087765 | 4.546e-05 | 2.8566e-05 | 0.05348 | 0.05348 | 0.05348 | 0.97572 | -0.4676 | 0.97434 | -0.49482 | 14.6924
88 | 0.000917 | 0.00022869 | -0.00091694 | -0.00022961 | 5.5646e-08 | -9.1235e-07 | 0.0013981 | 0.0013984 | 0.0013984 | 0.97572 | -0.4676 | 0.97566 | -0.46888 | 0.38417
89 | 0.00091694 | 0.00022961 | -0.00091693 | -0.0002298 | 1.2063e-08 | -1.977e-07 | 0.0013984 | 0.0013985 | 0.0013985 | 0.97566 | -0.46888 | 0.97565 | -0.46916 | 0.38419
90 | 0.019854 | 0.0049816 | -0.019837 | -0.0049716 | 1.651e-05 | 9.9762e-06 | 0.030391 | 0.030391 | 0.030391 | 0.97214 | -0.53689 | 0.97126 | -0.55435 | 8.3493

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54785 | 0.14086

## res_load
| p_mw | q_mvar
0 | 0.0035226 | 0.00088284
1 | 0.0075143 | 0.0018833
2 | 0.028369 | 0.00711
3 | 0.0012432 | 0.00031156
4 | 0.01332 | 0.0033384
5 | 0.00087943 | 0.00022041
6 | 0.0025061 | 0.00062808
7 | 0.0030796 | 0.00077183
8 | 0.0027861 | 0.00069826
9 | 0.0056436 | 0.0014144
10 | 0.0055731 | 0.0013968
11 | 0.0014653 | 0.00036724
12 | 0.0075806 | 0.0018999
13 | 0.0035977 | 0.00090167
14 | 0.0024754 | 0.00062039
15 | 0.0017294 | 0.00043344
16 | 0.0054839 | 0.0013744
17 | 0.0056693 | 0.0014209
18 | 0.0056179 | 0.001408
19 | 0.0026024 | 0.00065223
20 | 0.0032265 | 0.00080863
21 | 0.015975 | 0.0040038
22 | 0.01196 | 0.0029975
23 | 0.0025325 | 0.00063471
24 | 0.001968 | 0.00049324
25 | 0.0015644 | 0.00039207
26 | 0.0043863 | 0.0010993
27 | 0.01178 | 0.0029524
28 | 0.0023909 | 0.00059922
29 | 0.017103 | 0.0042863
30 | 0.0010541 | 0.00026418
31 | 0.0034545 | 0.00086578
32 | 0.026272 | 0.0065843
33 | 0.0065891 | 0.0016514
34 | 0.03682 | 0.009228
35 | 0.0079956 | 0.0020039
36 | 0.0030301 | 0.00075941
37 | 0.0015703 | 0.00039355
38 | 0.0022581 | 0.00056594
39 | 0.0011752 | 0.00029452
40 | 0.013985 | 0.003505
41 | 0.087913 | 0.022033
42 | 0.00088821 | 0.00022261
43 | 0.016931 | 0.0042432
44 | 0.0022627 | 0.00056709
45 | 0.0011692 | 0.00029302
46 | 0.039803 | 0.0099755
47 | 0.0019539 | 0.0004897
48 | 0.0044837 | 0.0011237
49 | 0.0019898 | 0.00049869
50 | 0.012674 | 0.0031763
51 | 0.0017563 | 0.00044018
52 | 0.0066663 | 0.0016707
53 | 0.00070691 | 0.00017717
54 | 0.0058437 | 0.0014646
55 | 0.0019932 | 0.00049955
56 | 0.0031324 | 0.00078506
57 | 0.0008314 | 0.00020837
58 | 0.00036205 | 9.0738e-05
59 | 0.035019 | 0.0087765
60 | 0.00091693 | 0.0002298
61 | 0.00090936 | 0.00022791
62 | 0.019837 | 0.0049716

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1