## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2546-31_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2546-31_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2546-31_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2546-31_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2546-31_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2546-31_0_5_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_2546-31_0_5_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_2546-31_0_5_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_2546-31_0_5_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_2546-31_0_5_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_2546-31_0_5_node_89 | 0.4 | n |  | TRUE
11 | bus_LV_2546-31_0_5_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_2546-31_0_5_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_2546-31_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_2546-31_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2546-31_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2546-31_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2546-31_0_5_node_73 | 0.4 | n |  | TRUE
18 | bus_LV_2546-31_0_5_node_92 | 0.4 | n |  | TRUE
19 | bus_LV_2546-31_0_5_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_2546-31_0_5_node_91 | 0.4 | n |  | TRUE
21 | bus_LV_2546-31_0_5_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2546-31_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2546-31_0_5_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2546-31_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2546-31_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2546-31_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2546-31_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2546-31_0_5_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_2546-31_0_5_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2546-31_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2546-31_0_5_node_116 | 0.4 | n |  | TRUE
32 | bus_LV_2546-31_0_5_node_101 | 0.4 | n |  | TRUE
33 | bus_LV_2546-31_0_5_node_114 | 0.4 | n |  | TRUE
34 | bus_LV_2546-31_0_5_node_123 | 0.4 | n |  | TRUE
35 | bus_LV_2546-31_0_5_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_2546-31_0_5_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_2546-31_0_5_node_126 | 0.4 | n |  | TRUE
38 | bus_LV_2546-31_0_5_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_2546-31_0_5_node_65 | 0.4 | n |  | TRUE
40 | bus_LV_2546-31_0_5_node_113 | 0.4 | n |  | TRUE
41 | bus_LV_2546-31_0_5_node_60 | 0.4 | n |  | TRUE
42 | bus_LV_2546-31_0_5_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_2546-31_0_5_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2546-31_0_5_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2546-31_0_5_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_2546-31_0_5_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_2546-31_0_5_node_115 | 0.4 | n |  | TRUE
48 | bus_LV_2546-31_0_5_node_117 | 0.4 | n |  | TRUE
49 | bus_LV_2546-31_0_5_node_22 | 0.4 | n |  | TRUE
50 | bus_LV_2546-31_0_5_node_19 | 0.4 | n |  | TRUE
51 | bus_LV_2546-31_0_5_node_20 | 0.4 | n |  | TRUE
52 | bus_LV_2546-31_0_5_node_21 | 0.4 | n |  | TRUE
53 | bus_LV_2546-31_0_5_node_23 | 0.4 | n |  | TRUE
54 | bus_LV_2546-31_0_5_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_2546-31_0_5_node_97 | 0.4 | n |  | TRUE
56 | bus_LV_2546-31_0_5_node_128 | 0.4 | n |  | TRUE
57 | bus_LV_2546-31_0_5_node_26 | 0.4 | n |  | TRUE
58 | bus_LV_2546-31_0_5_node_27 | 0.4 | n |  | TRUE
59 | bus_LV_2546-31_0_5_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_2546-31_0_5_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_2546-31_0_5_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_2546-31_0_5_node_90 | 0.4 | n |  | TRUE
63 | bus_LV_2546-31_0_5_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_2546-31_0_5_node_32 | 0.4 | n |  | TRUE
65 | bus_LV_2546-31_0_5_node_33 | 0.4 | n |  | TRUE
66 | bus_LV_2546-31_0_5_node_34 | 0.4 | n |  | TRUE
67 | bus_LV_2546-31_0_5_node_35 | 0.4 | n |  | TRUE
68 | bus_LV_2546-31_0_5_node_36 | 0.4 | n |  | TRUE
69 | bus_LV_2546-31_0_5_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_2546-31_0_5_node_119 | 0.4 | n |  | TRUE
71 | bus_LV_2546-31_0_5_node_108 | 0.4 | n |  | TRUE
72 | bus_LV_2546-31_0_5_node_37 | 0.4 | n |  | TRUE
73 | bus_LV_2546-31_0_5_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_2546-31_0_5_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_2546-31_0_5_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_2546-31_0_5_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_2546-31_0_5_node_122 | 0.4 | n |  | TRUE
78 | bus_LV_2546-31_0_5_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_2546-31_0_5_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_2546-31_0_5_node_42 | 0.4 | n |  | TRUE
81 | bus_LV_2546-31_0_5_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_2546-31_0_5_node_44 | 0.4 | n |  | TRUE
83 | bus_LV_2546-31_0_5_node_45 | 0.4 | n |  | TRUE
84 | bus_LV_2546-31_0_5_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_2546-31_0_5_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_2546-31_0_5_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_2546-31_0_5_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_2546-31_0_5_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_2546-31_0_5_node_48 | 0.4 | n |  | TRUE
90 | bus_LV_2546-31_0_5_node_52 | 0.4 | n |  | TRUE
91 | bus_LV_2546-31_0_5_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_2546-31_0_5_node_55 | 0.4 | n |  | TRUE
93 | bus_LV_2546-31_0_5_node_94 | 0.4 | n |  | TRUE
94 | bus_LV_2546-31_0_5_node_93 | 0.4 | n |  | TRUE
95 | bus_LV_2546-31_0_5_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_2546-31_0_5_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_2546-31_0_5_node_61 | 0.4 | n |  | TRUE
98 | bus_LV_2546-31_0_5_node_104 | 0.4 | n |  | TRUE
99 | bus_LV_2546-31_0_5_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_2546-31_0_5_node_129 | 0.4 | n |  | TRUE
101 | bus_LV_2546-31_0_5_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_2546-31_0_5_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_2546-31_0_5_node_68 | 0.4 | n |  | TRUE
104 | bus_LV_2546-31_0_5_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_2546-31_0_5_node_75 | 0.4 | n |  | TRUE
106 | bus_LV_2546-31_0_5_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_2546-31_0_5_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_2546-31_0_5_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_2546-31_0_5_node_124 | 0.4 | n |  | TRUE
110 | bus_LV_2546-31_0_5_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_2546-31_0_5_node_78 | 0.4 | n |  | TRUE
112 | bus_LV_2546-31_0_5_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2546-31_0_5_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_2546-31_0_5_node_120 | 0.4 | n |  | TRUE
115 | bus_LV_2546-31_0_5_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_2546-31_0_5_node_81 | 0.4 | n |  | TRUE
117 | bus_LV_2546-31_0_5_node_82 | 0.4 | n |  | TRUE
118 | bus_LV_2546-31_0_5_node_83 | 0.4 | n |  | TRUE
119 | bus_LV_2546-31_0_5_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_2546-31_0_5_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_2546-31_0_5_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_2546-31_0_5_node_112 | 0.4 | n |  | TRUE
123 | bus_MV_521_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2546-31_0_5_load_0 | 0 | 0.0022216 | 0.00055678 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2546-31_0_5_load_1 | 1 | 0.0015551 | 0.00038976 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2546-31_0_5_load_2 | 2 | 0.001772 | 0.0004441 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2546-31_0_5_load_3 | 3 | 0.0010847 | 0.00027185 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2546-31_0_5_load_71 | 6 | 0.0019715 | 0.0004941 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2546-31_0_5_load_25 | 7 | 0.0020189 | 0.00050598 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2546-31_0_5_load_51 | 8 | 0.0032018 | 0.00080245 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2546-31_0_5_load_47 | 9 | 0.0023293 | 0.00058379 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2546-31_0_5_load_24 | 11 | 0.0024492 | 0.00061382 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2546-31_0_5_load_5 | 12 | 0.0014985 | 0.00037555 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2546-31_0_5_load_6 | 13 | 0.0024608 | 0.00061673 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2546-31_0_5_load_7 | 14 | 0.0022706 | 0.00056906 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2546-31_0_5_load_8 | 15 | 0.00078358 | 0.00019638 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2546-31_0_5_load_73 | 17 | 0.00086623 | 0.0002171 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2546-31_0_5_load_91 | 20 | 0.0022928 | 0.00057462 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2546-31_0_5_load_10 | 21 | 0.002495 | 0.0006253 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2546-31_0_5_load_11 | 23 | 0.0063582 | 0.0015935 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2546-31_0_5_load_116 | 31 | 0.0023716 | 0.00059439 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2546-31_0_5_load_114 | 33 | 0.005751 | 0.0014413 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2546-31_0_5_load_123 | 34 | 0.093001 | 0.023308 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2546-31_0_5_load_126 | 37 | 0.02468 | 0.0061853 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2546-31_0_5_load_60 | 41 | 0.02469 | 0.006188 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2546-31_0_5_load_109 | 42 | 0.073366 | 0.018387 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2546-31_0_5_load_102 | 45 | 0.0008573 | 0.00021486 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2546-31_0_5_load_115 | 47 | 0.0042636 | 0.0010686 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2546-31_0_5_load_117 | 48 | 0.0011485 | 0.00028784 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2546-31_0_5_load_19 | 50 | 0.00060874 | 0.00015256 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2546-31_0_5_load_20 | 51 | 0.0018694 | 0.00046851 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2546-31_0_5_load_21 | 52 | 0.0021979 | 0.00055085 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2546-31_0_5_load_28 | 54 | 0.0010759 | 0.00026966 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2546-31_0_5_load_128 | 56 | 0.0068806 | 0.0017244 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2546-31_0_5_load_26 | 57 | 0.0018991 | 0.00047597 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2546-31_0_5_load_27 | 58 | 0.0024361 | 0.00061054 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2546-31_0_5_load_72 | 59 | 0.0048892 | 0.0012254 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2546-31_0_5_load_127 | 60 | 0.0014126 | 0.00035402 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2546-31_0_5_load_90 | 62 | 0.0022994 | 0.00057628 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2546-31_0_5_load_31 | 63 | 0.001896 | 0.00047517 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2546-31_0_5_load_32 | 64 | 0.0016541 | 0.00041454 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2546-31_0_5_load_34 | 66 | 0.0029443 | 0.0007379 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2546-31_0_5_load_35 | 67 | 0.0013197 | 0.00033075 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2546-31_0_5_load_36 | 68 | 0.0021991 | 0.00055114 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2546-31_0_5_load_107 | 69 | 0.0037173 | 0.00093163 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2546-31_0_5_load_119 | 70 | 0.0026717 | 0.00066959 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2546-31_0_5_load_108 | 71 | 0.0040498 | 0.001015 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2546-31_0_5_load_37 | 72 | 0.0015494 | 0.00038831 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2546-31_0_5_load_38 | 73 | 0.0006212 | 0.00015569 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2546-31_0_5_load_39 | 74 | 0.0022896 | 0.00057383 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2546-31_0_5_load_40 | 75 | 0.0016481 | 0.00041306 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2546-31_0_5_load_41 | 76 | 0.0009125 | 0.00022869 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2546-31_0_5_load_122 | 77 | 0.0061317 | 0.0015367 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2546-31_0_5_load_70 | 78 | 0.0035414 | 0.00088756 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2546-31_0_5_load_54 | 79 | 0.0012952 | 0.00032461 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2546-31_0_5_load_42 | 80 | 0.0012995 | 0.0003257 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2546-31_0_5_load_43 | 81 | 0.001285 | 0.00032205 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2546-31_0_5_load_44 | 82 | 0.0012993 | 0.00032562 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2546-31_0_5_load_45 | 83 | 0.0009167 | 0.00022975 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2546-31_0_5_load_46 | 84 | 0.0047843 | 0.001199 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2546-31_0_5_load_86 | 85 | 0.00091133 | 0.0002284 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2546-31_0_5_load_77 | 86 | 0.0051388 | 0.0012879 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2546-31_0_5_load_85 | 87 | 0.00086163 | 0.00021594 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2546-31_0_5_load_76 | 88 | 0.0017422 | 0.00043664 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2546-31_0_5_load_48 | 89 | 0.0023199 | 0.00058143 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2546-31_0_5_load_52 | 90 | 0.001323 | 0.00033157 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2546-31_0_5_load_94 | 93 | 0.0022154 | 0.00055523 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2546-31_0_5_load_93 | 94 | 0.0012485 | 0.0003129 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2546-31_0_5_load_57 | 95 | 0.0014389 | 0.00036062 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2546-31_0_5_load_58 | 96 | 0.0248 | 0.0062155 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2546-31_0_5_load_104 | 98 | 0.0014414 | 0.00036126 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2546-31_0_5_load_105 | 99 | 0.0014407 | 0.00036106 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2546-31_0_5_load_129 | 100 | 0.0057841 | 0.0014496 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2546-31_0_5_load_66 | 101 | 0.0014517 | 0.00036384 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2546-31_0_5_load_67 | 102 | 0.0010859 | 0.00027216 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2546-31_0_5_load_68 | 103 | 0.011422 | 0.0028627 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2546-31_0_5_load_69 | 104 | 0.0022939 | 0.00057489 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2546-31_0_5_load_75 | 105 | 0.0016655 | 0.00041741 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2546-31_0_5_load_87 | 106 | 0.0028408 | 0.00071198 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2546-31_0_5_load_103 | 107 | 0.00067701 | 0.00016967 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2546-31_0_5_load_99 | 108 | 0.0022468 | 0.00056309 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2546-31_0_5_load_124 | 109 | 0.00057373 | 0.00014379 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2546-31_0_5_load_98 | 110 | 0.0021399 | 0.00053632 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2546-31_0_5_load_80 | 113 | 0.0055052 | 0.0013797 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2546-31_0_5_load_120 | 114 | 0.001893 | 0.00047444 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2546-31_0_5_load_118 | 115 | 0.0014413 | 0.00036123 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2546-31_0_5_load_81 | 116 | 0.0018814 | 0.00047153 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2546-31_0_5_load_83 | 118 | 0.0010378 | 0.00026009 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2546-31_0_5_load_84 | 119 | 0.0011862 | 0.00029729 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2546-31_0_5_load_95 | 120 | 0.0015749 | 0.00039471 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2546-31_0_5_load_112 | 122 | 0.0057587 | 0.0014433 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2546-31_0_5_line_0 |  | 0 | 1 | 0.013104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2546-31_0_5_line_1 |  | 0 | 2 | 0.0047345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2546-31_0_5_line_2 |  | 1 | 3 | 0.006137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2546-31_0_5_line_3 |  | 2 | 4 | 0.012644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2546-31_0_5_line_4 |  | 3 | 5 | 0.021167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2546-31_0_5_line_5 |  | 4 | 6 | 0.039398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2546-31_0_5_line_6 |  | 4 | 7 | 0.035601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2546-31_0_5_line_7 |  | 5 | 8 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2546-31_0_5_line_8 |  | 5 | 9 | 0.025128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2546-31_0_5_line_9 |  | 6 | 10 | 0.031122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2546-31_0_5_line_10 |  | 7 | 11 | 0.024347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2546-31_0_5_line_11 |  | 8 | 71 | 0.018962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2546-31_0_5_line_12 |  | 9 | 89 | 0.025164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2546-31_0_5_line_13 |  | 10 | 106 | 0.049447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2546-31_0_5_line_14 |  | 11 | 57 | 0.050542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2546-31_0_5_line_15 |  | 12 | 13 | 0.0048628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2546-31_0_5_line_16 |  | 12 | 14 | 0.032832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2546-31_0_5_line_17 |  | 13 | 15 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2546-31_0_5_line_18 |  | 14 | 16 | 0.064522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2546-31_0_5_line_19 |  | 15 | 17 | 0.0067673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2546-31_0_5_line_20 |  | 16 | 18 | 0.025239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2546-31_0_5_line_21 |  | 17 | 19 | 0.0058307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2546-31_0_5_line_22 |  | 18 | 20 | 0.1195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2546-31_0_5_line_23 |  | 19 | 107 | 0.0377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2546-31_0_5_line_24 |  | 19 | 108 | 0.021149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2546-31_0_5_line_25 |  | 20 | 25 | 0.026221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2546-31_0_5_line_26 |  | 21 | 22 | 0.038308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2546-31_0_5_line_27 |  | 22 | 25 | 0.009007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2546-31_0_5_line_28 |  | 22 | 26 | 0.10979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2546-31_0_5_line_29 |  | 23 | 24 | 0.020379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2546-31_0_5_line_30 |  | 24 | 27 | 0.074571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2546-31_0_5_line_31 |  | 24 | 28 | 0.03203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2546-31_0_5_line_32 |  | 26 | 32 | 0.020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2546-31_0_5_line_33 |  | 26 | 33 | 0.056038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2546-31_0_5_line_34 |  | 27 | 34 | 0.0098425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2546-31_0_5_line_35 |  | 28 | 41 | 0.0052648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2546-31_0_5_line_36 |  | 29 | 30 | 0.042407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2546-31_0_5_line_37 |  | 29 | 31 | 0.025714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2546-31_0_5_line_38 |  | 30 | 34 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2546-31_0_5_line_39 |  | 31 | 46 | 0.011136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2546-31_0_5_line_40 |  | 32 | 48 | 0.038885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2546-31_0_5_line_41 |  | 32 | 49 | 0.024374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2546-31_0_5_line_42 |  | 33 | 46 | 0.027837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2546-31_0_5_line_43 |  | 35 | 36 | 0.038957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2546-31_0_5_line_44 |  | 35 | 37 | 0.011697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2546-31_0_5_line_45 |  | 35 | 38 | 0.034419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2546-31_0_5_line_46 |  | 36 | 42 | 0.024726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2546-31_0_5_line_47 |  | 37 | 39 | 0.027749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2546-31_0_5_line_48 |  | 38 | 97 | 0.019556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2546-31_0_5_line_49 |  | 38 | 95 | 0.011968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2546-31_0_5_line_50 |  | 39 | 40 | 0.032122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2546-31_0_5_line_51 |  | 40 | 100 | 0.011374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2546-31_0_5_line_52 |  | 41 | 96 | 0.024303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2546-31_0_5_line_53 |  | 43 | 44 | 0.092197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2546-31_0_5_line_54 |  | 43 | 45 | 0.017832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2546-31_0_5_line_55 |  | 44 | 56 | 0.006078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2546-31_0_5_line_56 |  | 45 | 49 | 0.014052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2546-31_0_5_line_57 |  | 46 | 47 | 0.01784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2546-31_0_5_line_58 |  | 48 | 115 | 0.025433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2546-31_0_5_line_59 |  | 49 | 51 | 0.034385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2546-31_0_5_line_60 |  | 50 | 51 | 0.0014042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2546-31_0_5_line_61 |  | 50 | 52 | 0.017652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2546-31_0_5_line_62 |  | 52 | 53 | 0.0025941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2546-31_0_5_line_63 |  | 53 | 54 | 0.022507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2546-31_0_5_line_64 |  | 54 | 55 | 0.005695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2546-31_0_5_line_65 |  | 55 | 61 | 0.011793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2546-31_0_5_line_66 |  | 55 | 62 | 0.034864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2546-31_0_5_line_67 |  | 57 | 58 | 0.028181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2546-31_0_5_line_68 |  | 58 | 59 | 0.011462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2546-31_0_5_line_69 |  | 58 | 60 | 0.049848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2546-31_0_5_line_70 |  | 61 | 78 | 0.02418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2546-31_0_5_line_71 |  | 61 | 89 | 0.0010066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2546-31_0_5_line_72 |  | 62 | 105 | 0.0016891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2546-31_0_5_line_73 |  | 63 | 64 | 0.00052043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2546-31_0_5_line_74 |  | 63 | 65 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2546-31_0_5_line_75 |  | 64 | 66 | 0.011004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2546-31_0_5_line_76 |  | 65 | 67 | 0.013864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2546-31_0_5_line_77 |  | 65 | 68 | 0.010933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2546-31_0_5_line_78 |  | 67 | 69 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2546-31_0_5_line_79 |  | 68 | 70 | 0.015448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2546-31_0_5_line_80 |  | 69 | 71 | 0.0017077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2546-31_0_5_line_81 |  | 72 | 73 | 0.015974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2546-31_0_5_line_82 |  | 72 | 74 | 0.0020007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2546-31_0_5_line_83 |  | 73 | 75 | 0.0092479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2546-31_0_5_line_84 |  | 74 | 76 | 0.0079283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2546-31_0_5_line_85 |  | 75 | 77 | 0.023217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2546-31_0_5_line_86 |  | 76 | 78 | 0.019729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2546-31_0_5_line_87 |  | 77 | 79 | 0.051499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2546-31_0_5_line_88 |  | 79 | 90 | 0.0095195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2546-31_0_5_line_89 |  | 80 | 81 | 0.0039703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2546-31_0_5_line_90 |  | 80 | 82 | 0.0056421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2546-31_0_5_line_91 |  | 81 | 83 | 0.0034578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2546-31_0_5_line_92 |  | 82 | 84 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2546-31_0_5_line_93 |  | 83 | 85 | 0.0021234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2546-31_0_5_line_94 |  | 84 | 86 | 0.0098328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2546-31_0_5_line_95 |  | 85 | 87 | 0.0041152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2546-31_0_5_line_96 |  | 86 | 88 | 0.017675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2546-31_0_5_line_97 |  | 87 | 118 | 0.0096876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2546-31_0_5_line_98 |  | 88 | 111 | 0.027027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2546-31_0_5_line_99 |  | 90 | 91 | 0.019613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2546-31_0_5_line_100 |  | 91 | 92 | 0.005438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2546-31_0_5_line_101 |  | 92 | 93 | 0.014407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2546-31_0_5_line_102 |  | 93 | 94 | 0.00092947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2546-31_0_5_line_103 |  | 94 | 120 | 0.029969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2546-31_0_5_line_104 |  | 95 | 96 | 0.024279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_2546-31_0_5_line_105 |  | 97 | 98 | 0.016774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2546-31_0_5_line_106 |  | 98 | 99 | 0.02429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2546-31_0_5_line_107 |  | 99 | 121 | 0.011114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2546-31_0_5_line_108 |  | 101 | 102 | 0.012787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2546-31_0_5_line_109 |  | 101 | 103 | 0.00050011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2546-31_0_5_line_110 |  | 102 | 104 | 0.0013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2546-31_0_5_line_111 |  | 104 | 105 | 0.018769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2546-31_0_5_line_112 |  | 107 | 109 | 0.038525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2546-31_0_5_line_113 |  | 108 | 110 | 0.014556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2546-31_0_5_line_114 |  | 111 | 112 | 0.040029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2546-31_0_5_line_115 |  | 111 | 113 | 0.017947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2546-31_0_5_line_116 |  | 112 | 114 | 0.028707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2546-31_0_5_line_117 |  | 113 | 115 | 0.025277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2546-31_0_5_line_118 |  | 116 | 117 | 0.0022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2546-31_0_5_line_119 |  | 117 | 118 | 0.003888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2546-31_0_5_line_120 |  | 117 | 119 | 0.01202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2546-31_0_5_line_121 |  | 121 | 122 | 0.013192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2546-31_0_5_trafo_114 | 0.63 MVA 20/0.4 kV | 123 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2595621.8211 | 1226678.2557 | 2595627.2032 | 1226683.6972 | 2595630.5631 | 1226687.989
1 | 2595621.8211 | 1226678.2557 | 2595618.4917 | 1226674.8897
2 | 2595630.5631 | 1226687.989 | 2595634.3461 | 1226692.8214
3 | 2595609.6 | 1226665.9 | 2595618.4917 | 1226674.8897
4 | 2595647.8662 | 1226709.0967 | 2595640.9032 | 1226701.1973 | 2595634.3461 | 1226692.8214
5 | 2595609.6 | 1226665.9 | 2595594.6985 | 1226683.2992 | 2595583.4426 | 1226695.3497
6 | 2595609.6 | 1226665.9 | 2595631.2358 | 1226637.6281
7 | 2595647.8662 | 1226709.0967 | 2595632.1529 | 1226715.2676 | 2595632.043 | 1226715.3439
8 | 2595647.8662 | 1226709.0967 | 2595658.5019 | 1226723.3972 | 2595663.1003 | 1226729.0746
9 | 2595562.0991 | 1226717.9998 | 2595574.7981 | 1226704.6045 | 2595583.4426 | 1226695.3497
10 | 2595631.2358 | 1226637.6281 | 2595646.0321 | 1226618.2934
11 | 2595632.043 | 1226715.3439 | 2595616.4674 | 1226726.1579
12 | 2595679.013 | 1226748.5639 | 2595678.1027 | 1226747.5969 | 2595663.1003 | 1226729.0746
13 | 2595562.0991 | 1226717.9998 | 2595523.5322 | 1226687.0539
14 | 2595678.8132 | 1226599.7985 | 2595671.4997 | 1226591.1988 | 2595667.3006 | 1226590.5015 | 2595646.0321 | 1226618.2934
15 | 2595933.1266 | 1227018.0249 | 2595930.906 | 1227019.6976 | 2595929.1495 | 1227020.8166
16 | 2595933.1266 | 1227018.0249 | 2595945.5015 | 1227008.7032 | 2595954.4982 | 1226999.8251 | 2595957.0913 | 1226995.9058
17 | 2595910.9217 | 1227032.4285 | 2595929.1495 | 1227020.8166
18 | 2595992.6979 | 1226942.0982 | 2595976.6715 | 1226966.3123 | 2595957.0913 | 1226995.9058
19 | 2595910.9217 | 1227032.4285 | 2595905.2141 | 1227036.0644
20 | 2595992.6979 | 1226942.0982 | 2596007.598 | 1226921.6982
21 | 2595900.2965 | 1227039.1972 | 2595905.2141 | 1227036.0644
22 | 2596007.598 | 1226921.6982 | 2595975.7018 | 1226900.7633 | 2595974.3844 | 1226891.5477 | 2595924.1346 | 1226839.935
23 | 2595900.2965 | 1227039.1972 | 2595892.5324 | 1227044.15 | 2595874.974 | 1227054.9354 | 2595868.2568 | 1227059.0631
24 | 2595900.2965 | 1227039.1972 | 2595905.9994 | 1227045.1967 | 2595909.3968 | 1227048.5963 | 2595915.7036 | 1227053.623
25 | 2595908.1982 | 1226819.796 | 2595909.657 | 1226825.0647 | 2595924.1346 | 1226839.935
26 | 2595899.3555 | 1226821.6366 | 2595890.6744 | 1226837.641 | 2595877.105 | 1226852.4701
27 | 2595908.1982 | 1226819.796 | 2595899.3555 | 1226821.6366
28 | 2595790.3847 | 1226830.5638 | 2595802.3968 | 1226831.0999 | 2595820.0773 | 1226831.254 | 2595842.797 | 1226830.8042 | 2595851.7391 | 1226830.253 | 2595863.0979 | 1226828.6996 | 2595899.3555 | 1226821.6366
29 | 2595875.4869 | 1226933.5859 | 2595888.6666 | 1226945.8949 | 2595890.2473 | 1226944.1624
30 | 2595820.3243 | 1226901.106 | 2595837.1129 | 1226915.458 | 2595844.4424 | 1226906.7032 | 2595875.4869 | 1226933.5859
31 | 2595853.0488 | 1226956.5041 | 2595875.4869 | 1226933.5859
32 | 2595790.3847 | 1226830.5638 | 2595781.1839 | 1226829.6921 | 2595778.9178 | 1226829.4825 | 2595769.6939 | 1226828.0661
33 | 2595790.3847 | 1226830.5638 | 2595787.5603 | 1226844.3628 | 2595758.6726 | 1226874.7856
34 | 2595820.3243 | 1226901.106 | 2595813.0024 | 1226894.5285
35 | 2595853.0488 | 1226956.5041 | 2595849.6236 | 1226960.5023
36 | 2595767.2856 | 1226893.0727 | 2595788.0342 | 1226870.878 | 2595796.3463 | 1226879.5661
37 | 2595767.2856 | 1226893.0727 | 2595755.3583 | 1226904.7549 | 2595746.4 | 1226903.7164
38 | 2595796.3463 | 1226879.5661 | 2595813.0024 | 1226894.5285
39 | 2595739.505 | 1226894.9718 | 2595746.4 | 1226903.7164
40 | 2595769.6939 | 1226828.0661 | 2595763.6254 | 1226830.5386 | 2595759.3992 | 1226833.9771 | 2595755.8399 | 1226837.5484 | 2595750.802 | 1226839.7978 | 2595736.2233 | 1226847.1428
41 | 2595769.6939 | 1226828.0661 | 2595752.2034 | 1226818.2063 | 2595748.8593 | 1226815.4294
42 | 2595739.505 | 1226894.9718 | 2595758.6726 | 1226874.7856
43 | 2595784.7808 | 1226983.2353 | 2595799.7586 | 1226966.7037 | 2595797.0892 | 1226964.1264 | 2595791.851 | 1226961.9177 | 2595788.2667 | 1226962.1982 | 2595785.5783 | 1226964.6794
44 | 2595784.7808 | 1226983.2353 | 2595776.7987 | 1226991.7862
45 | 2595784.7808 | 1226983.2353 | 2595810.2299 | 1227006.4863
46 | 2595785.5783 | 1226964.6794 | 2595780.5964 | 1226960.4805 | 2595785.3742 | 1226954.9739 | 2595777.646 | 1226947.2586
47 | 2595757.027 | 1227011.1719 | 2595763.8131 | 1227005.6971 | 2595776.7987 | 1226991.7862
48 | 2595810.2299 | 1227006.4863 | 2595796.7889 | 1227020.7265
49 | 2595810.2299 | 1227006.4863 | 2595818.0164 | 1226997.3971
50 | 2595757.027 | 1227011.1719 | 2595735.515 | 1227035.0794
51 | 2595726.8705 | 1227027.6591 | 2595735.515 | 1227035.0794
52 | 2595849.6236 | 1226960.5023 | 2595833.812 | 1226978.9591
53 | 2595770.6986 | 1226792.1999 | 2595815.2941 | 1226744.9622 | 2595835.0116 | 1226763.7481
54 | 2595770.6986 | 1226792.1999 | 2595758.4844 | 1226805.1915
55 | 2595835.0116 | 1226763.7481 | 2595839.4177 | 1226767.9474
56 | 2595748.8593 | 1226815.4294 | 2595758.4844 | 1226805.1915
57 | 2595739.505 | 1226894.9718 | 2595727.9533 | 1226881.35
58 | 2595736.2233 | 1226847.1428 | 2595713.5097 | 1226858.5862
59 | 2595748.8593 | 1226815.4294 | 2595745.1977 | 1226813.6977 | 2595735.7039 | 1226806.0001 | 2595723.8969 | 1226795.9028 | 2595722.1066 | 1226794.0504
60 | 2595721.1307 | 1226793.0407 | 2595722.1066 | 1226794.0504
61 | 2595721.1307 | 1226793.0407 | 2595708.8629 | 1226780.3479
62 | 2595707.06 | 1226778.4826 | 2595708.8629 | 1226780.3479
63 | 2595707.06 | 1226778.4826 | 2595691.4803 | 1226762.2395
64 | 2595687.5381 | 1226758.1295 | 2595691.4803 | 1226762.2395
65 | 2595679.703 | 1226749.2968 | 2595687.5381 | 1226758.1295
66 | 2595687.5381 | 1226758.1295 | 2595678.2494 | 1226771.7777 | 2595665.8638 | 1226785.3232
67 | 2595697.0698 | 1226621.2657 | 2595678.8132 | 1226599.7985
68 | 2595704.4955 | 1226629.9973 | 2595697.0698 | 1226621.2657
69 | 2595697.0698 | 1226621.2657 | 2595738.4514 | 1226593.4732
70 | 2595679.703 | 1226749.2968 | 2595694.8912 | 1226730.4827
71 | 2595679.703 | 1226749.2968 | 2595679.013 | 1226748.5639
72 | 2595664.724 | 1226786.5697 | 2595665.8638 | 1226785.3232
73 | 2595601.8354 | 1226763.5774 | 2595602.242 | 1226763.9023
74 | 2595592.0324 | 1226755.7437 | 2595601.8354 | 1226763.5774
75 | 2595610.8383 | 1226770.7718 | 2595602.242 | 1226763.9023
76 | 2595592.0324 | 1226755.7437 | 2595599.0195 | 1226743.7692
77 | 2595592.0324 | 1226755.7437 | 2595583.2618 | 1226749.2171
78 | 2595599.0195 | 1226743.7692 | 2595600.3655 | 1226741.4624 | 2595615.0646 | 1226727.1318 | 2595615.0646 | 1226727.1318
79 | 2595570.8689 | 1226739.9949 | 2595583.2618 | 1226749.2171
80 | 2595616.4674 | 1226726.1579 | 2595615.0646 | 1226727.1318
81 | 2595712.4358 | 1226706.7381 | 2595719.9228 | 1226698.5707 | 2595723.2153 | 1226694.949
82 | 2595711.0839 | 1226708.2129 | 2595712.4358 | 1226706.7381
83 | 2595729.4362 | 1226688.1063 | 2595723.2153 | 1226694.949
84 | 2595705.9994 | 1226714.2563 | 2595706.7466 | 1226712.9444 | 2595711.0839 | 1226708.2129
85 | 2595744.9269 | 1226670.8139 | 2595739.0281 | 1226677.5555 | 2595729.4362 | 1226688.1063
86 | 2595705.9994 | 1226714.2563 | 2595701.229 | 1226722.6319 | 2595694.8912 | 1226730.4827
87 | 2595744.9269 | 1226670.8139 | 2595782.5974 | 1226635.6993
88 | 2595782.5974 | 1226635.6993 | 2595789.3309 | 1226628.9701
89 | 2595605.3147 | 1226866.5431 | 2595601.3992 | 1226866.3017 | 2595601.3518 | 1226866.3013
90 | 2595605.3147 | 1226866.5431 | 2595610.9462 | 1226866.8902
91 | 2595601.3518 | 1226866.3013 | 2595597.8941 | 1226866.2742
92 | 2595623.2891 | 1226869.1447 | 2595611.1985 | 1226866.9058 | 2595610.9462 | 1226866.8902
93 | 2595595.7708 | 1226866.2576 | 2595597.8941 | 1226866.2742
94 | 2595623.2891 | 1226869.1447 | 2595632.9575 | 1226870.9351
95 | 2595591.6557 | 1226866.2254 | 2595595.7708 | 1226866.2576
96 | 2595650.2936 | 1226874.3776 | 2595634.3989 | 1226871.2021 | 2595632.9575 | 1226870.9351
97 | 2595581.9684 | 1226866.1496 | 2595591.6557 | 1226866.2254
98 | 2595676.5188 | 1226880.8209 | 2595669.803 | 1226878.8024 | 2595661.8972 | 1226876.6959 | 2595650.2936 | 1226874.3776
99 | 2595803.2041 | 1226615.1057 | 2595789.3309 | 1226628.9701
100 | 2595807.2007 | 1226618.805 | 2595803.2041 | 1226615.1057
101 | 2595807.2007 | 1226618.805 | 2595817.9891 | 1226628.3537
102 | 2595818.6851 | 1226628.9697 | 2595817.9891 | 1226628.3537
103 | 2595818.6851 | 1226628.9697 | 2595834.1977 | 1226642.6998 | 2595839.1032 | 1226645.698 | 2595842.4134 | 1226646.8474
104 | 2595818.0164 | 1226997.3971 | 2595833.812 | 1226978.9591
105 | 2595796.7889 | 1227020.7265 | 2595785.5793 | 1227033.2045
106 | 2595785.5793 | 1227033.2045 | 2595769.3469 | 1227051.2737
107 | 2595761.9197 | 1227059.5412 | 2595769.3469 | 1227051.2737
108 | 2595642.5353 | 1226810.8363 | 2595651.164 | 1226801.3995
109 | 2595642.1978 | 1226811.2054 | 2595642.5353 | 1226810.8363
110 | 2595651.164 | 1226801.3995 | 2595652.0585 | 1226800.4213
111 | 2595652.0585 | 1226800.4213 | 2595664.724 | 1226786.5697
112 | 2595840.902 | 1227085.6999 | 2595843.3398 | 1227082.3739 | 2595846.3984 | 1227078.2026 | 2595851.4035 | 1227072.5958 | 2595855.9017 | 1227068.1011 | 2595861.9983 | 1227062.9048 | 2595865.8994 | 1227060.5117 | 2595868.2568 | 1227059.0631
113 | 2595927.0156 | 1227062.7826 | 2595921.7029 | 1227058.4046 | 2595915.7036 | 1227053.623
114 | 2595676.5188 | 1226880.8209 | 2595656.8018 | 1226903.5044 | 2595650.6086 | 1226911.3803
115 | 2595676.5188 | 1226880.8209 | 2595687.4943 | 1226873.3083 | 2595691.4363 | 1226870.8482
116 | 2595650.6086 | 1226911.3803 | 2595644.5997 | 1226912.2964 | 2595638.6 | 1226915.4027 | 2595624.9612 | 1226923.5226
117 | 2595713.5097 | 1226858.5862 | 2595700.9245 | 1226864.9269 | 2595691.4363 | 1226870.8482
118 | 2595578.0805 | 1226866.1192 | 2595575.8645 | 1226866.0756
119 | 2595578.0805 | 1226866.1192 | 2595581.9684 | 1226866.1496
120 | 2595578.0805 | 1226866.1192 | 2595577.9025 | 1226878.1381
121 | 2595761.9197 | 1227059.5412 | 2595752.8884 | 1227069.1566

## bus_geodata
| x | y | coords
0 | 2595621.8211 | 1226678.2557
1 | 2595630.5631 | 1226687.989
2 | 2595618.4917 | 1226674.8897
3 | 2595634.3461 | 1226692.8214
4 | 2595609.6 | 1226665.9
5 | 2595647.8662 | 1226709.0967
6 | 2595583.4426 | 1226695.3497
7 | 2595631.2358 | 1226637.6281
8 | 2595632.043 | 1226715.3439
9 | 2595663.1003 | 1226729.0746
10 | 2595562.0991 | 1226717.9998
11 | 2595646.0321 | 1226618.2934
12 | 2595933.1266 | 1227018.0249
13 | 2595929.1495 | 1227020.8166
14 | 2595957.0913 | 1226995.9058
15 | 2595910.9217 | 1227032.4285
16 | 2595992.6979 | 1226942.0982
17 | 2595905.2141 | 1227036.0644
18 | 2596007.598 | 1226921.6982
19 | 2595900.2965 | 1227039.1972
20 | 2595924.1346 | 1226839.935
21 | 2595877.105 | 1226852.4701
22 | 2595899.3555 | 1226821.6366
23 | 2595890.2473 | 1226944.1624
24 | 2595875.4869 | 1226933.5859
25 | 2595908.1982 | 1226819.796
26 | 2595790.3847 | 1226830.5638
27 | 2595820.3243 | 1226901.106
28 | 2595853.0488 | 1226956.5041
29 | 2595767.2856 | 1226893.0727
30 | 2595796.3463 | 1226879.5661
31 | 2595746.4 | 1226903.7164
32 | 2595769.6939 | 1226828.0661
33 | 2595758.6726 | 1226874.7856
34 | 2595813.0024 | 1226894.5285
35 | 2595784.7808 | 1226983.2353
36 | 2595785.5783 | 1226964.6794
37 | 2595776.7987 | 1226991.7862
38 | 2595810.2299 | 1227006.4863
39 | 2595757.027 | 1227011.1719
40 | 2595735.515 | 1227035.0794
41 | 2595849.6236 | 1226960.5023
42 | 2595777.646 | 1226947.2586
43 | 2595770.6986 | 1226792.1999
44 | 2595835.0116 | 1226763.7481
45 | 2595758.4844 | 1226805.1915
46 | 2595739.505 | 1226894.9718
47 | 2595727.9533 | 1226881.35
48 | 2595736.2233 | 1226847.1428
49 | 2595748.8593 | 1226815.4294
50 | 2595721.1307 | 1226793.0407
51 | 2595722.1066 | 1226794.0504
52 | 2595708.8629 | 1226780.3479
53 | 2595707.06 | 1226778.4826
54 | 2595691.4803 | 1226762.2395
55 | 2595687.5381 | 1226758.1295
56 | 2595839.4177 | 1226767.9474
57 | 2595678.8132 | 1226599.7985
58 | 2595697.0698 | 1226621.2657
59 | 2595704.4955 | 1226629.9973
60 | 2595738.4514 | 1226593.4732
61 | 2595679.703 | 1226749.2968
62 | 2595665.8638 | 1226785.3232
63 | 2595601.8354 | 1226763.5774
64 | 2595602.242 | 1226763.9023
65 | 2595592.0324 | 1226755.7437
66 | 2595610.8383 | 1226770.7718
67 | 2595599.0195 | 1226743.7692
68 | 2595583.2618 | 1226749.2171
69 | 2595615.0646 | 1226727.1318
70 | 2595570.8689 | 1226739.9949
71 | 2595616.4674 | 1226726.1579
72 | 2595712.4358 | 1226706.7381
73 | 2595723.2153 | 1226694.949
74 | 2595711.0839 | 1226708.2129
75 | 2595729.4362 | 1226688.1063
76 | 2595705.9994 | 1226714.2563
77 | 2595744.9269 | 1226670.8139
78 | 2595694.8912 | 1226730.4827
79 | 2595782.5974 | 1226635.6993
80 | 2595605.3147 | 1226866.5431
81 | 2595601.3518 | 1226866.3013
82 | 2595610.9462 | 1226866.8902
83 | 2595597.8941 | 1226866.2742
84 | 2595623.2891 | 1226869.1447
85 | 2595595.7708 | 1226866.2576
86 | 2595632.9575 | 1226870.9351
87 | 2595591.6557 | 1226866.2254
88 | 2595650.2936 | 1226874.3777
89 | 2595679.013 | 1226748.5639
90 | 2595789.3309 | 1226628.9701
91 | 2595803.2041 | 1226615.1057
92 | 2595807.2007 | 1226618.805
93 | 2595817.9891 | 1226628.3537
94 | 2595818.6851 | 1226628.9697
95 | 2595818.0164 | 1226997.3971
96 | 2595833.812 | 1226978.9591
97 | 2595796.7889 | 1227020.7265
98 | 2595785.5793 | 1227033.2045
99 | 2595769.3469 | 1227051.2737
100 | 2595726.8705 | 1227027.6591
101 | 2595642.5353 | 1226810.8363
102 | 2595651.164 | 1226801.3995
103 | 2595642.1978 | 1226811.2054
104 | 2595652.0585 | 1226800.4213
105 | 2595664.724 | 1226786.5697
106 | 2595523.5322 | 1226687.0539
107 | 2595868.2568 | 1227059.0631
108 | 2595915.7036 | 1227053.623
109 | 2595840.902 | 1227085.6999
110 | 2595927.0156 | 1227062.7826
111 | 2595676.5188 | 1226880.8209
112 | 2595650.6086 | 1226911.3803
113 | 2595691.4363 | 1226870.8482
114 | 2595624.9612 | 1226923.5226
115 | 2595713.5097 | 1226858.5862
116 | 2595575.8645 | 1226866.0756
117 | 2595578.0805 | 1226866.1192
118 | 2595581.9684 | 1226866.1496
119 | 2595577.9025 | 1226878.1381
120 | 2595842.4134 | 1226646.8474
121 | 2595761.9197 | 1227059.5412
122 | 2595752.8884 | 1227069.1566
123 | 2595739.505 | 1226894.9718

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97956 | -0.39357 | 0.0022216 | 0.00055678
1 | 0.97985 | -0.38787 | 0.0015551 | 0.00038976
2 | 0.97946 | -0.39543 | 0.001772 | 0.0004441
3 | 0.97999 | -0.38504 | 0.0010847 | 0.00027185
4 | 0.97923 | -0.40001 | 0 | 0
5 | 0.98051 | -0.37484 | 0 | 0
6 | 0.97905 | -0.40346 | 0.0019715 | 0.0004941
7 | 0.97873 | -0.40979 | 0.0020189 | 0.00050598
8 | 0.98014 | -0.38214 | 0.0032018 | 0.00080245
9 | 0.98168 | -0.35199 | 0.0023293 | 0.00058379
10 | 0.97897 | -0.40507 | 0 | 0
11 | 0.97844 | -0.4156 | 0.0024492 | 0.00061382
12 | 0.9905 | -0.18219 | 0.0014985 | 0.00037555
13 | 0.99046 | -0.18303 | 0.0024608 | 0.00061673
14 | 0.99084 | -0.17563 | 0.0022706 | 0.00056906
15 | 0.99031 | -0.18583 | 0.00078358 | 0.00019638
16 | 0.99164 | -0.16015 | 0 | 0
17 | 0.99027 | -0.18661 | 0.00086623 | 0.0002171
18 | 0.99195 | -0.1541 | 0 | 0
19 | 0.99024 | -0.1872 | 0 | 0
20 | 0.99343 | -0.12551 | 0.0022928 | 0.00057462
21 | 0.99385 | -0.11735 | 0.002495 | 0.0006253
22 | 0.99394 | -0.11567 | 0 | 0
23 | 0.98489 | -0.2888 | 0.0063582 | 0.0015935
24 | 0.98501 | -0.28647 | 0 | 0
25 | 0.99381 | -0.11818 | 0 | 0
26 | 0.99577 | -0.080243 | 0 | 0
27 | 0.98893 | -0.21096 | 0 | 0
28 | 0.98338 | -0.31787 | 0 | 0
29 | 0.99469 | -0.10052 | 0 | 0
30 | 0.99126 | -0.16619 | 0 | 0
31 | 0.99678 | -0.060926 | 0.0023716 | 0.00059439
32 | 0.99438 | -0.10683 | 0 | 0
33 | 1 | 0 | -0.44155 | -0.11292
34 | 0.98944 | -0.20104 | 0.093001 | 0.023308
35 | 0.97663 | -0.44949 | 0 | 0
36 | 0.97396 | -0.50186 | 0 | 0
37 | 0.9763 | -0.456 | 0.02468 | 0.0061853
38 | 0.97996 | -0.3844 | 0 | 0
39 | 0.97615 | -0.45894 | 0 | 0
40 | 0.97598 | -0.46234 | 0 | 0
41 | 0.98312 | -0.32304 | 0.02469 | 0.006188
42 | 0.97227 | -0.53525 | 0.073366 | 0.018387
43 | 0.99162 | -0.15958 | 0 | 0
44 | 0.99104 | -0.17083 | 0 | 0
45 | 0.99174 | -0.15741 | 0.0008573 | 0.00021486
46 | 0.99769 | -0.043675 | 0 | 0
47 | 0.99762 | -0.045007 | 0.0042636 | 0.0010686
48 | 0.99323 | -0.12902 | 0.0011485 | 0.00028784
49 | 0.99184 | -0.15548 | 0 | 0
50 | 0.98836 | -0.22238 | 0.00060874 | 0.00015256
51 | 0.98849 | -0.21979 | 0.0018694 | 0.00046851
52 | 0.98668 | -0.25479 | 0.0021979 | 0.00055085
53 | 0.98644 | -0.25946 | 0 | 0
54 | 0.98435 | -0.30007 | 0.0010759 | 0.00026966
55 | 0.98382 | -0.31026 | 0 | 0
56 | 0.99101 | -0.17158 | 0.0068806 | 0.0017244
57 | 0.97794 | -0.42539 | 0.0018991 | 0.00047597
58 | 0.97771 | -0.42988 | 0.0024361 | 0.00061054
59 | 0.97766 | -0.4309 | 0.0048892 | 0.0012254
60 | 0.97764 | -0.43117 | 0.0014126 | 0.00035402
61 | 0.98296 | -0.3271 | 0 | 0
62 | 0.98317 | -0.32297 | 0.0022994 | 0.00057628
63 | 0.97926 | -0.39938 | 0.001896 | 0.00047517
64 | 0.97926 | -0.39942 | 0.0016541 | 0.00041454
65 | 0.97934 | -0.39789 | 0 | 0
66 | 0.97923 | -0.40001 | 0.0029443 | 0.0007379
67 | 0.97948 | -0.39503 | 0.0013197 | 0.00033075
68 | 0.97929 | -0.39886 | 0.0021991 | 0.00055114
69 | 0.97976 | -0.38969 | 0.0037173 | 0.00093163
70 | 0.97925 | -0.39961 | 0.0026717 | 0.00066959
71 | 0.97978 | -0.38918 | 0.0040498 | 0.001015
72 | 0.98186 | -0.34864 | 0.0015494 | 0.00038831
73 | 0.98162 | -0.35328 | 0.0006212 | 0.00015569
74 | 0.98189 | -0.348 | 0.0022896 | 0.00057383
75 | 0.98149 | -0.35587 | 0.0016481 | 0.00041306
76 | 0.98203 | -0.34515 | 0.0009125 | 0.00022869
77 | 0.98119 | -0.36166 | 0.0061317 | 0.0015367
78 | 0.98241 | -0.33773 | 0.0035414 | 0.00088756
79 | 0.98083 | -0.36881 | 0.0012952 | 0.00032461
80 | 0.99022 | -0.18728 | 0.0012995 | 0.0003257
81 | 0.99019 | -0.18785 | 0.001285 | 0.00032205
82 | 0.99027 | -0.18634 | 0.0012993 | 0.00032562
83 | 0.99017 | -0.18827 | 0.0009167 | 0.00022975
84 | 0.99039 | -0.18396 | 0.0047843 | 0.001199
85 | 0.99016 | -0.18849 | 0.00091133 | 0.0002284
86 | 0.99053 | -0.18126 | 0.0051388 | 0.0012879
87 | 0.99014 | -0.18885 | 0.00086163 | 0.00021594
88 | 0.99087 | -0.17479 | 0.0017422 | 0.00043664
89 | 0.98291 | -0.3281 | 0.0023199 | 0.00058143
90 | 0.98077 | -0.3699 | 0.001323 | 0.00033157
91 | 0.98068 | -0.3717 | 0 | 0
92 | 0.98065 | -0.37219 | 0 | 0
93 | 0.98059 | -0.37351 | 0.0022154 | 0.00055523
94 | 0.98058 | -0.37356 | 0.0012485 | 0.0003129
95 | 0.98121 | -0.36 | 0.0014389 | 0.00036062
96 | 0.98207 | -0.34333 | 0.0248 | 0.0062155
97 | 0.9798 | -0.38747 | 0 | 0
98 | 0.97967 | -0.3901 | 0.0014414 | 0.00036126
99 | 0.97951 | -0.39328 | 0.0014407 | 0.00036106
100 | 0.97592 | -0.46354 | 0.0057841 | 0.0014496
101 | 0.98269 | -0.33232 | 0.0014517 | 0.00036384
102 | 0.98285 | -0.32935 | 0.0010859 | 0.00027216
103 | 0.98269 | -0.33242 | 0.011422 | 0.0028627
104 | 0.98286 | -0.32901 | 0.0022939 | 0.00057489
105 | 0.98314 | -0.32351 | 0.0016655 | 0.00041741
106 | 0.97884 | -0.40763 | 0.0028408 | 0.00071198
107 | 0.9902 | -0.18804 | 0.00067701 | 0.00016967
108 | 0.99016 | -0.18885 | 0.0022468 | 0.00056309
109 | 0.99018 | -0.18843 | 0.00057373 | 0.00014379
110 | 0.99013 | -0.1894 | 0.0021399 | 0.00053632
111 | 0.99142 | -0.16407 | 0 | 0
112 | 0.99135 | -0.16542 | 0 | 0
113 | 0.99182 | -0.15636 | 0.0055052 | 0.0013797
114 | 0.9913 | -0.16638 | 0.001893 | 0.00047444
115 | 0.9925 | -0.14305 | 0.0014413 | 0.00036123
116 | 0.99009 | -0.18985 | 0.0018814 | 0.00047153
117 | 0.99009 | -0.18977 | 0 | 0
118 | 0.9901 | -0.18956 | 0.0010378 | 0.00026009
119 | 0.99008 | -0.19003 | 0.0011862 | 0.00029729
120 | 0.98054 | -0.37441 | 0.0015749 | 0.00039471
121 | 0.97945 | -0.39444 | 0 | 0
122 | 0.97938 | -0.39582 | 0.0057587 | 0.0014433
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.023936 | -0.0060047 | 0.023943 | 0.0060087 | 6.4977e-06 | 3.9935e-06 | 0.036363 | 0.036363 | 0.036363 | 0.97956 | -0.39357 | 0.97985 | -0.38787 | 9.9899
1 | 0.021715 | 0.0054479 | -0.021713 | -0.0054468 | 1.9321e-06 | 1.1769e-06 | 0.032988 | 0.032988 | 0.032988 | 0.97956 | -0.39357 | 0.97946 | -0.39543 | 9.0627
2 | -0.025498 | -0.0063985 | 0.025502 | 0.0064006 | 3.4512e-06 | 2.1314e-06 | 0.038725 | 0.038725 | 0.038725 | 0.97985 | -0.38787 | 0.97999 | -0.38504 | 10.6387
3 | 0.019941 | 0.0050027 | -0.019937 | -0.005 | 4.3522e-06 | 2.6263e-06 | 0.030296 | 0.030296 | 0.030296 | 0.97946 | -0.39543 | 0.97923 | -0.40001 | 8.3232
4 | -0.026586 | -0.0066724 | 0.026599 | 0.0066805 | 1.2938e-05 | 8.0132e-06 | 0.040372 | 0.040372 | 0.040372 | 0.97999 | -0.38504 | 0.98051 | -0.37484 | 11.0911
5 | 0.0048137 | 0.0012054 | -0.0048129 | -0.0012054 | 7.9045e-07 | 1.0353e-08 | 0.0073144 | 0.0073146 | 0.0073146 | 0.97923 | -0.40001 | 0.97905 | -0.40346 | 2.0095
6 | 0.015123 | 0.0037946 | -0.015116 | -0.0037905 | 7.0513e-06 | 4.0652e-06 | 0.022982 | 0.022982 | 0.022982 | 0.97923 | -0.40001 | 0.97873 | -0.40979 | 6.3138
7 | 0.023675 | 0.0059401 | -0.023667 | -0.0059351 | 8.2378e-06 | 5.0577e-06 | 0.035931 | 0.035931 | 0.035931 | 0.98051 | -0.37484 | 0.98014 | -0.38214 | 9.8712
8 | -0.050274 | -0.012621 | 0.050329 | 0.012655 | 5.4861e-05 | 3.4794e-05 | 0.076303 | 0.076302 | 0.076303 | 0.98051 | -0.37484 | 0.98168 | -0.35199 | 20.9622
9 | 0.0028414 | 0.00071133 | -0.0028412 | -0.00071158 | 2.1763e-07 | -2.5206e-07 | 0.0043182 | 0.0043184 | 0.0043184 | 0.97905 | -0.40346 | 0.97897 | -0.40507 | 1.1864
10 | 0.013097 | 0.0032845 | -0.013093 | -0.0032825 | 3.6203e-06 | 2.0111e-06 | 0.019913 | 0.019913 | 0.019913 | 0.97873 | -0.40979 | 0.97844 | -0.4156 | 5.4706
11 | 0.020465 | 0.0051326 | -0.020458 | -0.0051285 | 6.8643e-06 | 4.1542e-06 | 0.03107 | 0.03107 | 0.03107 | 0.98014 | -0.38214 | 0.97978 | -0.38918 | 8.5358
12 | -0.052658 | -0.013239 | 0.052718 | 0.013277 | 6.0142e-05 | 3.8172e-05 | 0.079833 | 0.079833 | 0.079833 | 0.98168 | -0.35199 | 0.98291 | -0.3281 | 21.9322
13 | 0.0028412 | 0.00071158 | -0.0028408 | -0.00071198 | 3.4581e-07 | -4.0032e-07 | 0.0043184 | 0.0043186 | 0.0043186 | 0.97897 | -0.40507 | 0.97884 | -0.40763 | 1.1864
14 | 0.010644 | 0.0026687 | -0.010639 | -0.0026662 | 4.9669e-06 | 2.5444e-06 | 0.016188 | 0.016188 | 0.016188 | 0.97844 | -0.4156 | 0.97794 | -0.42539 | 4.4474
15 | 0.0097503 | 0.0024426 | -0.0097499 | -0.0024424 | 3.9123e-07 | 1.878e-07 | 0.014647 | 0.014647 | 0.014647 | 0.9905 | -0.18219 | 0.99046 | -0.18303 | 4.024
16 | -0.011249 | -0.0028181 | 0.011252 | 0.00282 | 3.5158e-06 | 1.8274e-06 | 0.016898 | 0.016898 | 0.016898 | 0.9905 | -0.18219 | 0.99084 | -0.17563 | 4.6424
17 | 0.0072891 | 0.0018256 | -0.0072881 | -0.0018253 | 9.7184e-07 | 3.4386e-07 | 0.01095 | 0.01095 | 0.01095 | 0.99046 | -0.18303 | 0.99031 | -0.18583 | 3.0084
18 | -0.013523 | -0.003389 | 0.013533 | 0.0033946 | 9.9788e-06 | 5.5547e-06 | 0.020308 | 0.020308 | 0.020308 | 0.99084 | -0.17563 | 0.99164 | -0.16015 | 5.5792
19 | 0.0065045 | 0.0016289 | -0.0065043 | -0.0016289 | 2.4239e-07 | 6.8062e-08 | 0.0097731 | 0.0097731 | 0.0097731 | 0.99031 | -0.18583 | 0.99027 | -0.18661 | 2.6849
20 | -0.013533 | -0.0033946 | 0.013537 | 0.0033967 | 3.9033e-06 | 2.1724e-06 | 0.020308 | 0.020308 | 0.020308 | 0.99164 | -0.16015 | 0.99195 | -0.1541 | 5.5791
21 | 0.0056381 | 0.0014118 | -0.0056379 | -0.0014117 | 1.5692e-07 | 2.5417e-08 | 0.0084715 | 0.0084715 | 0.0084715 | 0.99027 | -0.18661 | 0.99024 | -0.1872 | 2.3273
22 | -0.013537 | -0.0033967 | 0.013555 | 0.003407 | 1.848e-05 | 1.0282e-05 | 0.020308 | 0.020307 | 0.020308 | 0.99195 | -0.1541 | 0.99343 | -0.12551 | 5.5791
23 | 0.0012508 | 0.00031252 | -0.0012507 | -0.00031298 | 4.993e-08 | -4.5301e-07 | 0.0018792 | 0.0018794 | 0.0018794 | 0.99024 | -0.1872 | 0.9902 | -0.18804 | 0.51631
24 | 0.0043871 | 0.0010992 | -0.0043868 | -0.0010993 | 3.4466e-07 | -5.1458e-08 | 0.0065923 | 0.0065924 | 0.0065924 | 0.99024 | -0.1872 | 0.99016 | -0.18885 | 1.8111
25 | -0.015848 | -0.0039816 | 0.015854 | 0.0039848 | 5.5424e-06 | 3.2075e-06 | 0.023742 | 0.023741 | 0.023742 | 0.99343 | -0.12551 | 0.99381 | -0.11818 | 6.5224
26 | -0.002495 | -0.0006253 | 0.0024952 | 0.00062493 | 2.0045e-07 | -3.6816e-07 | 0.0037355 | 0.0037353 | 0.0037355 | 0.99385 | -0.11735 | 0.99394 | -0.11567 | 1.0262
27 | 0.015855 | 0.003986 | -0.015854 | -0.0039848 | 1.9038e-06 | 1.1017e-06 | 0.023741 | 0.023741 | 0.023741 | 0.99394 | -0.11567 | 0.99381 | -0.11818 | 6.5224
28 | -0.018351 | -0.0046109 | 0.018382 | 0.0046293 | 3.1083e-05 | 1.8468e-05 | 0.027477 | 0.027476 | 0.027477 | 0.99394 | -0.11567 | 0.99577 | -0.080243 | 7.5485
29 | -0.0063582 | -0.0015935 | 0.0063589 | 0.0015937 | 7.0522e-07 | 1.9197e-07 | 0.0096063 | 0.0096062 | 0.0096063 | 0.98489 | -0.2888 | 0.98501 | -0.28647 | 2.6391
30 | -0.17105 | -0.043365 | 0.17167 | 0.043761 | 0.00062325 | 0.00039602 | 0.25858 | 0.25858 | 0.25858 | 0.98501 | -0.28647 | 0.98893 | -0.21096 | 23.6793
31 | 0.16469 | 0.041772 | -0.16444 | -0.041614 | 0.00024818 | 0.00015761 | 0.24897 | 0.24897 | 0.24897 | 0.98501 | -0.28647 | 0.98338 | -0.31787 | 22.7996
32 | 0.14689 | 0.037435 | -0.1467 | -0.037315 | 0.00018818 | 0.00011989 | 0.21972 | 0.21972 | 0.21972 | 0.99577 | -0.080243 | 0.99438 | -0.10683 | 30.1813
33 | -0.16527 | -0.042064 | 0.16591 | 0.042474 | 0.00064204 | 0.00040944 | 0.2472 | 0.2472 | 0.2472 | 0.99577 | -0.080243 | 1 | 0 | 33.9554
34 | -0.17167 | -0.043761 | 0.17176 | 0.043814 | 8.2261e-05 | 5.2268e-05 | 0.25858 | 0.25858 | 0.25858 | 0.98893 | -0.21096 | 0.98944 | -0.20104 | 23.6792
35 | 0.16444 | 0.041614 | -0.1644 | -0.041588 | 4.0793e-05 | 2.5907e-05 | 0.24897 | 0.24897 | 0.24897 | 0.98338 | -0.31787 | 0.98312 | -0.32304 | 22.7996
36 | 0.26604 | 0.067942 | -0.2652 | -0.067405 | 0.00084152 | 0.00053693 | 0.39844 | 0.39844 | 0.39844 | 0.99469 | -0.10052 | 0.99126 | -0.16619 | 36.4871
37 | -0.26604 | -0.067942 | 0.26655 | 0.068268 | 0.00051027 | 0.00032557 | 0.39844 | 0.39844 | 0.39844 | 0.99469 | -0.10052 | 0.99678 | -0.060926 | 36.487
38 | 0.2652 | 0.067405 | -0.26476 | -0.067122 | 0.00044431 | 0.00028349 | 0.39844 | 0.39844 | 0.39844 | 0.99126 | -0.16619 | 0.98944 | -0.20104 | 36.4871
39 | -0.26892 | -0.068862 | 0.26915 | 0.069006 | 0.00022493 | 0.00014352 | 0.40198 | 0.40198 | 0.40198 | 0.99678 | -0.060926 | 0.99769 | -0.043675 | 36.8112
40 | 0.032438 | 0.0081669 | -0.032403 | -0.0081454 | 3.4376e-05 | 2.1497e-05 | 0.048554 | 0.048554 | 0.048554 | 0.99438 | -0.10683 | 0.99323 | -0.12902 | 13.339
41 | 0.11426 | 0.029148 | -0.11399 | -0.028977 | 0.00026779 | 0.00017107 | 0.17117 | 0.17117 | 0.17117 | 0.99438 | -0.10683 | 0.99184 | -0.15548 | 47.0237
42 | 0.27399 | 0.070445 | -0.27341 | -0.070074 | 0.00058019 | 0.00037023 | 0.40834 | 0.40834 | 0.40834 | 1 | 0 | 0.99769 | -0.043675 | 37.3936
43 | 0.073667 | 0.018579 | -0.073483 | -0.018462 | 0.00018418 | 0.00011739 | 0.11228 | 0.11228 | 0.11228 | 0.97663 | -0.44949 | 0.97396 | -0.50186 | 30.8469
44 | 0.030475 | 0.0076413 | -0.030466 | -0.0076354 | 9.458e-06 | 5.9068e-06 | 0.046434 | 0.046434 | 0.046434 | 0.97663 | -0.44949 | 0.9763 | -0.456 | 12.7567
45 | -0.10414 | -0.02622 | 0.10447 | 0.026428 | 0.00032514 | 0.00020766 | 0.15872 | 0.15872 | 0.15872 | 0.97663 | -0.44949 | 0.97996 | -0.3844 | 43.6035
46 | 0.073483 | 0.018462 | -0.073366 | -0.018387 | 0.0001169 | 7.4508e-05 | 0.11228 | 0.11228 | 0.11228 | 0.97396 | -0.50186 | 0.97227 | -0.53525 | 30.8469
47 | 0.0057862 | 0.0014501 | -0.0057854 | -0.0014499 | 8.0932e-07 | 1.7102e-07 | 0.0088189 | 0.008819 | 0.008819 | 0.9763 | -0.456 | 0.97615 | -0.45894 | 2.4228
48 | 0.0086449 | 0.0021672 | -0.0086437 | -0.0021666 | 1.2637e-06 | 5.6244e-07 | 0.013127 | 0.013127 | 0.013127 | 0.97996 | -0.3844 | 0.9798 | -0.38747 | 3.6064
49 | -0.11311 | -0.028595 | 0.11324 | 0.02868 | 0.00013254 | 8.4673e-05 | 0.17184 | 0.17184 | 0.17184 | 0.97996 | -0.3844 | 0.98121 | -0.36 | 47.2098
50 | 0.0057854 | 0.0014499 | -0.0057844 | -0.0014497 | 9.3688e-07 | 1.9812e-07 | 0.008819 | 0.0088192 | 0.0088192 | 0.97615 | -0.45894 | 0.97598 | -0.46234 | 2.4229
51 | 0.0057844 | 0.0014497 | -0.0057841 | -0.0014496 | 3.3175e-07 | 7.019e-08 | 0.0088192 | 0.0088192 | 0.0088192 | 0.97598 | -0.46234 | 0.97592 | -0.46354 | 2.4229
52 | 0.13971 | 0.0354 | -0.13958 | -0.035314 | 0.00013602 | 8.6132e-05 | 0.2116 | 0.2116 | 0.2116 | 0.98312 | -0.32304 | 0.98207 | -0.34333 | 19.3775
53 | 0.0068845 | 0.0017257 | -0.0068808 | -0.0017245 | 3.6901e-06 | 1.173e-06 | 0.010331 | 0.010331 | 0.010331 | 0.99162 | -0.15958 | 0.99104 | -0.17083 | 2.8383
54 | -0.0068845 | -0.0017257 | 0.0068852 | 0.0017259 | 7.1366e-07 | 2.2668e-07 | 0.010331 | 0.010331 | 0.010331 | 0.99162 | -0.15958 | 0.99174 | -0.15741 | 2.8381
55 | 0.0068808 | 0.0017245 | -0.0068806 | -0.0017244 | 2.4328e-07 | 7.7383e-08 | 0.010331 | 0.010331 | 0.010331 | 0.99104 | -0.17083 | 0.99101 | -0.17158 | 2.8383
56 | -0.0077425 | -0.0019408 | 0.0077432 | 0.001941 | 7.1115e-07 | 2.738e-07 | 0.011617 | 0.011617 | 0.011617 | 0.99174 | -0.15741 | 0.99184 | -0.15548 | 3.1915
57 | 0.0042639 | 0.0010685 | -0.0042636 | -0.0010686 | 2.7056e-07 | -5.979e-08 | 0.0063594 | 0.0063595 | 0.0063595 | 0.99769 | -0.043675 | 0.99762 | -0.045007 | 1.7471
58 | 0.031255 | 0.0078576 | -0.031234 | -0.0078445 | 2.0919e-05 | 1.3059e-05 | 0.046833 | 0.046833 | 0.046833 | 0.99323 | -0.12902 | 0.9925 | -0.14305 | 12.8663
59 | 0.10625 | 0.027036 | -0.10592 | -0.026826 | 0.00032824 | 0.00020963 | 0.15955 | 0.15955 | 0.15955 | 0.99184 | -0.15548 | 0.98849 | -0.21979 | 43.8323
60 | -0.10404 | -0.026349 | 0.10405 | 0.026358 | 1.2936e-05 | 8.2611e-06 | 0.15674 | 0.15674 | 0.15674 | 0.98836 | -0.22238 | 0.98849 | -0.21979 | 43.0592
61 | 0.10343 | 0.026197 | -0.10327 | -0.026094 | 0.00016072 | 0.00010264 | 0.15582 | 0.15582 | 0.15582 | 0.98836 | -0.22238 | 0.98668 | -0.25479 | 42.8074
62 | 0.10107 | 0.025543 | -0.10105 | -0.025529 | 2.2625e-05 | 1.4447e-05 | 0.1525 | 0.1525 | 0.1525 | 0.98668 | -0.25479 | 0.98644 | -0.25946 | 41.8968
63 | 0.10105 | 0.025529 | -0.10085 | -0.025404 | 0.0001963 | 0.00012534 | 0.1525 | 0.1525 | 0.1525 | 0.98644 | -0.25946 | 0.98435 | -0.30007 | 41.8968
64 | 0.099778 | 0.025134 | -0.099729 | -0.025103 | 4.8616e-05 | 3.1042e-05 | 0.15088 | 0.15088 | 0.15088 | 0.98435 | -0.30007 | 0.98382 | -0.31026 | 41.45
65 | 0.079492 | 0.020024 | -0.079428 | -0.019983 | 6.3965e-05 | 4.0788e-05 | 0.12027 | 0.12027 | 0.12027 | 0.98382 | -0.31026 | 0.98296 | -0.3271 | 33.0403
66 | 0.020238 | 0.0050786 | -0.020225 | -0.0050712 | 1.2251e-05 | 7.3983e-06 | 0.030612 | 0.030612 | 0.030612 | 0.98382 | -0.31026 | 0.98317 | -0.32297 | 8.4098
67 | 0.0087401 | 0.0021902 | -0.0087382 | -0.0021894 | 1.869e-06 | 8.4266e-07 | 0.013299 | 0.013299 | 0.013299 | 0.97794 | -0.42539 | 0.97771 | -0.42988 | 3.6535
68 | 0.0048895 | 0.0012254 | -0.0048892 | -0.0012254 | 2.3802e-07 | 8.5965e-09 | 0.0074415 | 0.0074415 | 0.0074415 | 0.97771 | -0.42988 | 0.97766 | -0.4309 | 2.0444
69 | 0.0014127 | 0.00035345 | -0.0014126 | -0.00035402 | 8.64e-08 | -5.6981e-07 | 0.0021498 | 0.00215 | 0.00215 | 0.97771 | -0.42988 | 0.97764 | -0.43117 | 0.59066
70 | 0.024387 | 0.0061231 | -0.024375 | -0.0061155 | 1.2361e-05 | 7.6044e-06 | 0.036921 | 0.036921 | 0.036921 | 0.98296 | -0.3271 | 0.98241 | -0.33773 | 10.1433
71 | 0.055041 | 0.01386 | -0.055038 | -0.013859 | 2.6221e-06 | 1.6654e-06 | 0.083345 | 0.083345 | 0.083345 | 0.98296 | -0.3271 | 0.98291 | -0.3281 | 22.897
72 | 0.017926 | 0.0044949 | -0.017926 | -0.0044946 | 4.6626e-07 | 2.7699e-07 | 0.027132 | 0.027132 | 0.027132 | 0.98317 | -0.32297 | 0.98314 | -0.32351 | 7.4537
73 | 0.0045984 | 0.0011524 | -0.0045984 | -0.0011524 | 9.5282e-09 | -4.4902e-10 | 0.0069874 | 0.0069874 | 0.0069874 | 0.97926 | -0.39938 | 0.97926 | -0.39942 | 1.9196
74 | -0.0064944 | -0.0016275 | 0.0064948 | 0.0016277 | 4.5826e-07 | 1.354e-07 | 0.0098683 | 0.0098683 | 0.0098683 | 0.97926 | -0.39938 | 0.97934 | -0.39789 | 2.7111
75 | 0.0029443 | 0.00073782 | -0.0029443 | -0.0007379 | 8.2598e-08 | -8.557e-08 | 0.004474 | 0.004474 | 0.004474 | 0.97926 | -0.39942 | 0.97923 | -0.40001 | 1.2291
76 | -0.011366 | -0.0028483 | 0.011367 | 0.0028491 | 1.5505e-06 | 8.1784e-07 | 0.017269 | 0.017269 | 0.017269 | 0.97934 | -0.39789 | 0.97948 | -0.39503 | 4.7443
77 | 0.0048711 | 0.0012206 | -0.0048709 | -0.0012206 | 2.2457e-07 | 6.1695e-09 | 0.0074011 | 0.0074012 | 0.0074012 | 0.97934 | -0.39789 | 0.97929 | -0.39886 | 2.0333
78 | -0.012687 | -0.0031798 | 0.01269 | 0.0031816 | 3.2319e-06 | 1.7764e-06 | 0.019274 | 0.019274 | 0.019274 | 0.97948 | -0.39503 | 0.97976 | -0.38969 | 5.2951
79 | 0.0026718 | 0.00066946 | -0.0026717 | -0.00066959 | 9.5476e-08 | -1.3324e-07 | 0.0040597 | 0.0040598 | 0.0040598 | 0.97929 | -0.39886 | 0.97925 | -0.39961 | 1.1153
80 | -0.016408 | -0.0041133 | 0.016408 | 0.0041135 | 3.9768e-07 | 2.3301e-07 | 0.02492 | 0.02492 | 0.02492 | 0.97976 | -0.38969 | 0.97978 | -0.38918 | 6.8461
81 | 0.016071 | 0.0040306 | -0.016068 | -0.0040286 | 3.5539e-06 | 2.0725e-06 | 0.024357 | 0.024357 | 0.024357 | 0.98186 | -0.34864 | 0.98162 | -0.35328 | 6.6915
82 | -0.017621 | -0.004419 | 0.017621 | 0.0044193 | 5.3507e-07 | 3.1714e-07 | 0.026705 | 0.026705 | 0.026705 | 0.98186 | -0.34864 | 0.98189 | -0.348 | 7.3366
83 | 0.015446 | 0.0038729 | -0.015444 | -0.0038718 | 1.9014e-06 | 1.1e-06 | 0.023415 | 0.023415 | 0.023415 | 0.98162 | -0.35328 | 0.98149 | -0.35587 | 6.4328
84 | -0.019911 | -0.0049931 | 0.019913 | 0.0049947 | 2.7071e-06 | 1.6322e-06 | 0.030175 | 0.030175 | 0.030175 | 0.98189 | -0.348 | 0.98203 | -0.34515 | 8.2898
85 | 0.013796 | 0.0034587 | -0.013793 | -0.0034566 | 3.8092e-06 | 2.1445e-06 | 0.020917 | 0.020917 | 0.020917 | 0.98149 | -0.35587 | 0.98119 | -0.36166 | 5.7464
86 | -0.020826 | -0.0052234 | 0.020833 | 0.0052279 | 7.3677e-06 | 4.4656e-06 | 0.031558 | 0.031557 | 0.031558 | 0.98203 | -0.34515 | 0.98241 | -0.33773 | 8.6697
87 | 0.0076608 | 0.0019198 | -0.0076582 | -0.0019188 | 2.6067e-06 | 1.0181e-06 | 0.011618 | 0.011618 | 0.011618 | 0.98119 | -0.36166 | 0.98083 | -0.36881 | 3.1918
88 | 0.006363 | 0.0015942 | -0.0063627 | -0.0015941 | 3.3265e-07 | 9.2756e-08 | 0.0096532 | 0.0096532 | 0.0096532 | 0.98083 | -0.36881 | 0.98077 | -0.3699 | 2.652
89 | 0.0080808 | 0.002025 | -0.0080806 | -0.0020249 | 2.1954e-07 | 8.9431e-08 | 0.012143 | 0.012143 | 0.012143 | 0.99022 | -0.18728 | 0.99019 | -0.18785 | 3.336
90 | -0.0093803 | -0.0023507 | 0.0093808 | 0.0023509 | 4.2039e-07 | 1.9647e-07 | 0.014096 | 0.014096 | 0.014096 | 0.99022 | -0.18728 | 0.99027 | -0.18634 | 3.8725
91 | 0.0067956 | 0.0017028 | -0.0067954 | -0.0017028 | 1.3522e-07 | 4.2065e-08 | 0.010212 | 0.010212 | 0.010212 | 0.99019 | -0.18785 | 0.99017 | -0.18827 | 2.8055
92 | -0.01068 | -0.0026765 | 0.010681 | 0.0026771 | 1.212e-06 | 6.1418e-07 | 0.016048 | 0.016048 | 0.016048 | 0.99027 | -0.18634 | 0.99039 | -0.18396 | 4.4088
93 | 0.0058787 | 0.001473 | -0.0058787 | -0.001473 | 6.2146e-08 | 1.2461e-08 | 0.0088344 | 0.0088344 | 0.0088344 | 0.99017 | -0.18827 | 0.99016 | -0.18849 | 2.427
94 | -0.015465 | -0.0038762 | 0.015467 | 0.0038773 | 1.9908e-06 | 1.1476e-06 | 0.023236 | 0.023236 | 0.023236 | 0.99039 | -0.18396 | 0.99053 | -0.18126 | 6.3836
95 | 0.0049673 | 0.0012446 | -0.0049672 | -0.0012446 | 8.5993e-08 | 2.1051e-09 | 0.0074648 | 0.0074648 | 0.0074648 | 0.99016 | -0.18849 | 0.99014 | -0.18885 | 2.0508
96 | -0.020606 | -0.0051652 | 0.020613 | 0.005169 | 6.3514e-06 | 3.8373e-06 | 0.030956 | 0.030956 | 0.030956 | 0.99053 | -0.18126 | 0.99087 | -0.17479 | 8.5043
97 | 0.0041056 | 0.0010287 | -0.0041055 | -0.0010287 | 1.383e-07 | -3.6086e-08 | 0.00617 | 0.00617 | 0.00617 | 0.99014 | -0.18885 | 0.9901 | -0.18956 | 1.6951
98 | -0.022355 | -0.0056057 | 0.022366 | 0.0056126 | 1.1423e-05 | 6.9625e-06 | 0.033572 | 0.033572 | 0.033572 | 0.99087 | -0.17479 | 0.99142 | -0.16407 | 9.2231
99 | 0.0050397 | 0.0012625 | -0.0050393 | -0.0012625 | 4.2999e-07 | 2.7702e-08 | 0.007646 | 0.0076461 | 0.0076461 | 0.98077 | -0.3699 | 0.98068 | -0.3717 | 2.1006
100 | 0.0050393 | 0.0012625 | -0.0050391 | -0.0012625 | 1.1922e-07 | 7.6899e-09 | 0.0076461 | 0.0076461 | 0.0076461 | 0.98068 | -0.3717 | 0.98065 | -0.37219 | 2.1006
101 | 0.0050391 | 0.0012625 | -0.0050388 | -0.0012625 | 3.1586e-07 | 2.0393e-08 | 0.0076461 | 0.0076462 | 0.0076462 | 0.98065 | -0.37219 | 0.98059 | -0.37351 | 2.1006
102 | 0.0028234 | 0.00070726 | -0.0028234 | -0.00070727 | 6.3979e-09 | -7.6304e-09 | 0.0042844 | 0.0042844 | 0.0042844 | 0.98059 | -0.37351 | 0.98058 | -0.37356 | 1.177
103 | 0.001575 | 0.00039437 | -0.0015749 | -0.00039471 | 6.4191e-08 | -3.3696e-07 | 0.0023898 | 0.00239 | 0.00239 | 0.98058 | -0.37356 | 0.98054 | -0.37441 | 0.65659
104 | -0.11468 | -0.029041 | 0.11478 | 0.029098 | 9.191e-05 | 5.7902e-05 | 0.17403 | 0.17403 | 0.17403 | 0.98121 | -0.36 | 0.98207 | -0.34333 | 15.9364
105 | 0.0086437 | 0.0021666 | -0.0086426 | -0.0021661 | 1.0839e-06 | 4.8249e-07 | 0.013127 | 0.013127 | 0.013127 | 0.9798 | -0.38747 | 0.97967 | -0.3901 | 3.6064
106 | 0.0072011 | 0.0018049 | -0.0072001 | -0.0018045 | 1.0897e-06 | 3.9164e-07 | 0.010938 | 0.010938 | 0.010938 | 0.97967 | -0.3901 | 0.97951 | -0.39328 | 3.0049
107 | 0.0057594 | 0.0014434 | -0.0057591 | -0.0014433 | 3.1904e-07 | 6.4304e-08 | 0.0087493 | 0.0087494 | 0.0087494 | 0.97951 | -0.39328 | 0.97945 | -0.39444 | 2.4037
108 | -0.012874 | -0.0032265 | 0.012876 | 0.0032276 | 1.8223e-06 | 1.0042e-06 | 0.019494 | 0.019494 | 0.019494 | 0.98269 | -0.33232 | 0.98285 | -0.32935 | 5.3555
109 | 0.011422 | 0.0028627 | -0.011422 | -0.0028627 | 5.6102e-08 | 2.957e-08 | 0.017296 | 0.017296 | 0.017296 | 0.98269 | -0.33232 | 0.98269 | -0.33242 | 4.7516
110 | -0.013962 | -0.0034997 | 0.013962 | 0.0034998 | 2.221e-07 | 1.2535e-07 | 0.021138 | 0.021138 | 0.021138 | 0.98285 | -0.32935 | 0.98286 | -0.32901 | 5.8072
111 | -0.016256 | -0.0040747 | 0.01626 | 0.0040772 | 4.2631e-06 | 2.4905e-06 | 0.024611 | 0.024611 | 0.024611 | 0.98286 | -0.32901 | 0.98314 | -0.32351 | 6.7612
112 | 0.00057374 | 0.0001433 | -0.00057373 | -0.00014379 | 1.0737e-08 | -4.8868e-07 | 0.00086201 | 0.00086219 | 0.00086219 | 0.9902 | -0.18804 | 0.99018 | -0.18843 | 0.23686
113 | 0.00214 | 0.00053617 | -0.0021399 | -0.00053632 | 5.6454e-08 | -1.5109e-07 | 0.0032159 | 0.003216 | 0.003216 | 0.99016 | -0.18885 | 0.99013 | -0.1894 | 0.88352
114 | 0.0018933 | 0.00047369 | -0.0018931 | -0.00047413 | 1.2119e-07 | -4.3858e-07 | 0.0028413 | 0.0028415 | 0.0028415 | 0.99142 | -0.16407 | 0.99135 | -0.16542 | 0.78062
115 | -0.024259 | -0.0060863 | 0.024268 | 0.0060918 | 8.9236e-06 | 5.4796e-06 | 0.036413 | 0.036413 | 0.036413 | 0.99142 | -0.16407 | 0.99182 | -0.15636 | 10.0036
116 | 0.0018931 | 0.00047413 | -0.001893 | -0.00047444 | 8.6923e-08 | -3.1448e-07 | 0.0028415 | 0.0028416 | 0.0028416 | 0.99135 | -0.16542 | 0.9913 | -0.16638 | 0.78066
117 | -0.029774 | -0.0074715 | 0.029793 | 0.0074833 | 1.8916e-05 | 1.178e-05 | 0.044673 | 0.044672 | 0.044673 | 0.99182 | -0.15636 | 0.9925 | -0.14305 | 12.2727
118 | -0.0018814 | -0.00047153 | 0.0018815 | 0.00047151 | 6.6456e-09 | -2.4252e-08 | 0.0028276 | 0.0028276 | 0.0028276 | 0.99009 | -0.18985 | 0.99009 | -0.18977 | 0.77683
119 | -0.0030677 | -0.00076865 | 0.0030677 | 0.00076862 | 3.099e-08 | -3.0169e-08 | 0.0046103 | 0.0046103 | 0.0046103 | 0.99009 | -0.18977 | 0.9901 | -0.18956 | 1.2666
120 | 0.0011862 | 0.00029714 | -0.0011862 | -0.00029729 | 1.4326e-08 | -1.4542e-07 | 0.0017827 | 0.0017828 | 0.0017828 | 0.99009 | -0.18977 | 0.99008 | -0.19003 | 0.48977
121 | 0.0057591 | 0.0014433 | -0.0057587 | -0.0014433 | 3.787e-07 | 7.6352e-08 | 0.0087494 | 0.0087495 | 0.0087495 | 0.97945 | -0.39444 | 0.97938 | -0.39582 | 2.4037

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44731 | 0.11436

## res_load
| p_mw | q_mvar
0 | 0.0022216 | 0.00055678
1 | 0.0015551 | 0.00038976
2 | 0.001772 | 0.0004441
3 | 0.0010847 | 0.00027185
4 | 0.0019715 | 0.0004941
5 | 0.0020189 | 0.00050598
6 | 0.0032018 | 0.00080245
7 | 0.0023293 | 0.00058379
8 | 0.0024492 | 0.00061382
9 | 0.0014985 | 0.00037555
10 | 0.0024608 | 0.00061673
11 | 0.0022706 | 0.00056906
12 | 0.00078358 | 0.00019638
13 | 0.00086623 | 0.0002171
14 | 0.0022928 | 0.00057462
15 | 0.002495 | 0.0006253
16 | 0.0063582 | 0.0015935
17 | 0.0023716 | 0.00059439
18 | 0.005751 | 0.0014413
19 | 0.093001 | 0.023308
20 | 0.02468 | 0.0061853
21 | 0.02469 | 0.006188
22 | 0.073366 | 0.018387
23 | 0.0008573 | 0.00021486
24 | 0.0042636 | 0.0010686
25 | 0.0011485 | 0.00028784
26 | 0.00060874 | 0.00015256
27 | 0.0018694 | 0.00046851
28 | 0.0021979 | 0.00055085
29 | 0.0010759 | 0.00026966
30 | 0.0068806 | 0.0017244
31 | 0.0018991 | 0.00047597
32 | 0.0024361 | 0.00061054
33 | 0.0048892 | 0.0012254
34 | 0.0014126 | 0.00035402
35 | 0.0022994 | 0.00057628
36 | 0.001896 | 0.00047517
37 | 0.0016541 | 0.00041454
38 | 0.0029443 | 0.0007379
39 | 0.0013197 | 0.00033075
40 | 0.0021991 | 0.00055114
41 | 0.0037173 | 0.00093163
42 | 0.0026717 | 0.00066959
43 | 0.0040498 | 0.001015
44 | 0.0015494 | 0.00038831
45 | 0.0006212 | 0.00015569
46 | 0.0022896 | 0.00057383
47 | 0.0016481 | 0.00041306
48 | 0.0009125 | 0.00022869
49 | 0.0061317 | 0.0015367
50 | 0.0035414 | 0.00088756
51 | 0.0012952 | 0.00032461
52 | 0.0012995 | 0.0003257
53 | 0.001285 | 0.00032205
54 | 0.0012993 | 0.00032562
55 | 0.0009167 | 0.00022975
56 | 0.0047843 | 0.001199
57 | 0.00091133 | 0.0002284
58 | 0.0051388 | 0.0012879
59 | 0.00086163 | 0.00021594
60 | 0.0017422 | 0.00043664
61 | 0.0023199 | 0.00058143
62 | 0.001323 | 0.00033157
63 | 0.0022154 | 0.00055523
64 | 0.0012485 | 0.0003129
65 | 0.0014389 | 0.00036062
66 | 0.0248 | 0.0062155
67 | 0.0014414 | 0.00036126
68 | 0.0014407 | 0.00036106
69 | 0.0057841 | 0.0014496
70 | 0.0014517 | 0.00036384
71 | 0.0010859 | 0.00027216
72 | 0.011422 | 0.0028627
73 | 0.0022939 | 0.00057489
74 | 0.0016655 | 0.00041741
75 | 0.0028408 | 0.00071198
76 | 0.00067701 | 0.00016967
77 | 0.0022468 | 0.00056309
78 | 0.00057373 | 0.00014379
79 | 0.0021399 | 0.00053632
80 | 0.0055052 | 0.0013797
81 | 0.001893 | 0.00047444
82 | 0.0014413 | 0.00036123
83 | 0.0018814 | 0.00047153
84 | 0.0010378 | 0.00026009
85 | 0.0011862 | 0.00029729
86 | 0.0015749 | 0.00039471
87 | 0.0057587 | 0.0014433

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1