## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2546-45_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2546-45_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2546-45_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2546-45_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2546-45_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2546-45_0_3_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_2546-45_0_3_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_2546-45_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2546-45_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_2546-45_0_3_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2546-45_0_3_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_2546-45_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2546-45_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2546-45_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2546-45_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2546-45_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2546-45_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_2546-45_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2546-45_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2546-45_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2546-45_0_3_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_2546-45_0_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_2546-45_0_3_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_2546-45_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_2546-45_0_3_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_2546-45_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2546-45_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2546-45_0_3_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_2546-45_0_3_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_2546-45_0_3_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_2546-45_0_3_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_2546-45_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2546-45_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2546-45_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_2546-45_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2546-45_0_3_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_2546-45_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2546-45_0_3_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_2546-45_0_3_node_44 | 0.4 | n |  | TRUE
39 | bus_LV_2546-45_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_2546-45_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_MV_396_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2546-45_0_3_load_0 | 0 | 0.0055741 | 0.001397 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2546-45_0_3_load_28 | 6 | 0.00037879 | 9.4933e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2546-45_0_3_load_18 | 7 | 0.0025171 | 0.00063086 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2546-45_0_3_load_25 | 8 | 0.0074152 | 0.0018584 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2546-45_0_3_load_5 | 11 | 0.014142 | 0.0035444 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2546-45_0_3_load_22 | 17 | 0.014118 | 0.0035382 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2546-45_0_3_load_38 | 20 | 0.0014317 | 0.00035882 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2546-45_0_3_load_42 | 21 | 0.0025239 | 0.00063255 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2546-45_0_3_load_40 | 22 | 0.014149 | 0.0035461 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2546-45_0_3_load_43 | 24 | 0.0023875 | 0.00059836 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2546-45_0_3_load_13 | 25 | 0.0017146 | 0.00042972 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2546-45_0_3_load_39 | 27 | 0.00097345 | 0.00024397 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2546-45_0_3_load_12 | 29 | 0.0052972 | 0.0013276 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2546-45_0_3_load_37 | 30 | 0.014621 | 0.0036644 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2546-45_0_3_load_26 | 31 | 0.091715 | 0.022986 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2546-45_0_3_load_27 | 32 | 0.043233 | 0.010835 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2546-45_0_3_load_30 | 33 | 0.0019597 | 0.00049115 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2546-45_0_3_load_36 | 37 | 0.089132 | 0.022339 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2546-45_0_3_load_44 | 38 | 0.0020303 | 0.00050884 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2546-45_0_3_load_33 | 39 | 0.020246 | 0.0050741 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2546-45_0_3_load_34 | 40 | 0.00067646 | 0.00016954 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2546-45_0_3_line_0 |  | 0 | 1 | 0.040277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2546-45_0_3_line_1 |  | 1 | 2 | 0.019297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2546-45_0_3_line_2 |  | 1 | 3 | 0.051899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2546-45_0_3_line_3 |  | 2 | 5 | 0.033483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2546-45_0_3_line_4 |  | 2 | 6 | 0.036472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2546-45_0_3_line_5 |  | 3 | 4 | 0.016725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2546-45_0_3_line_6 |  | 4 | 7 | 0.037271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2546-45_0_3_line_7 |  | 5 | 8 | 0.066663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2546-45_0_3_line_8 |  | 6 | 9 | 0.011682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2546-45_0_3_line_9 |  | 7 | 10 | 0.043926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2546-45_0_3_line_10 |  | 8 | 31 | 0.048006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2546-45_0_3_line_11 |  | 9 | 33 | 0.02951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2546-45_0_3_line_12 |  | 9 | 34 | 0.075414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2546-45_0_3_line_13 |  | 10 | 26 | 0.085933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2546-45_0_3_line_14 |  | 11 | 12 | 0.030395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2546-45_0_3_line_15 |  | 11 | 13 | 0.03744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2546-45_0_3_line_16 |  | 12 | 14 | 0.031415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2546-45_0_3_line_17 |  | 13 | 15 | 0.025861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2546-45_0_3_line_18 |  | 14 | 16 | 0.030523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2546-45_0_3_line_19 |  | 14 | 17 | 0.030616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2546-45_0_3_line_20 |  | 15 | 21 | 0.06348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2546-45_0_3_line_21 |  | 16 | 22 | 0.033014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2546-45_0_3_line_22 |  | 16 | 23 | 0.032757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2546-45_0_3_line_23 |  | 18 | 19 | 0.16413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2546-45_0_3_line_24 |  | 18 | 20 | 0.0051972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2546-45_0_3_line_25 |  | 19 | 24 | 0.030236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2546-45_0_3_line_26 |  | 19 | 25 | 0.016061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2546-45_0_3_line_27 |  | 20 | 26 | 0.0099938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2546-45_0_3_line_28 |  | 21 | 28 | 0.028254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2546-45_0_3_line_29 |  | 23 | 30 | 0.030369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2546-45_0_3_line_30 |  | 25 | 29 | 0.066863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2546-45_0_3_line_31 |  | 26 | 27 | 0.034545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2546-45_0_3_line_32 |  | 27 | 28 | 0.030265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2546-45_0_3_line_33 |  | 31 | 32 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2546-45_0_3_line_34 |  | 33 | 35 | 0.052554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2546-45_0_3_line_35 |  | 34 | 36 | 0.05739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2546-45_0_3_line_36 |  | 34 | 37 | 0.032108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2546-45_0_3_line_37 |  | 35 | 38 | 0.030764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2546-45_0_3_line_38 |  | 36 | 39 | 0.039618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2546-45_0_3_line_39 |  | 37 | 40 | 0.029916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2546-45_0_3_trafo_27 | 0.63 MVA 20/0.4 kV | 41 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2597645.93 | 1226928.3187 | 2597606.8757 | 1226918.4697
1 | 2597645.93 | 1226928.3187 | 2597664.6655 | 1226933.1583
2 | 2597645.93 | 1226928.3187 | 2597643.0095 | 1226939.7599 | 2597642.3281 | 1226941.3945 | 2597641.0177 | 1226942.9293 | 2597638.9267 | 1226944.2087 | 2597636.6686 | 1226944.7543 | 2597634.054 | 1226944.4997 | 2597605.9888 | 1226937.1848
3 | 2597655.6453 | 1226965.4032 | 2597663.6666 | 1226936.7386 | 2597664.6655 | 1226933.1583
4 | 2597664.6655 | 1226933.1583 | 2597674.4835 | 1226898.0326
5 | 2597598.9623 | 1226951.8963 | 2597601.1357 | 1226948.3044 | 2597603.7492 | 1226945.8463 | 2597605.9888 | 1226937.1848
6 | 2597598.9623 | 1226951.8963 | 2597597.8407 | 1226951.8523 | 2597595.4462 | 1226952.3759 | 2597591.7184 | 1226954.1006 | 2597584.6728 | 1226959.1399 | 2597582.1503 | 1226961.7981 | 2597580.1511 | 1226965.2454 | 2597576.5504 | 1226978.0265
7 | 2597655.6453 | 1226965.4032 | 2597663.0124 | 1226968.124 | 2597667.8031 | 1226971.1794 | 2597687.8859 | 1226991.5833 | 2597689.2205 | 1226993.7063 | 2597689.2217 | 1226996.6191 | 2597684.8414 | 1227015.1873
8 | 2597677.6283 | 1226886.7814 | 2597674.4835 | 1226898.0326
9 | 2597564.6391 | 1227020.3065 | 2597576.5504 | 1226978.0265
10 | 2597712.9306 | 1227006.3342 | 2597708.3823 | 1227023.2604 | 2597707.1857 | 1227025.1176 | 2597705.4583 | 1227026.1855 | 2597703.4653 | 1227026.3086 | 2597691.0966 | 1227023.2673 | 2597688.2999 | 1227022.3457 | 2597686.0409 | 1227020.6234 | 2597684.8426 | 1227018.2336 | 2597684.8414 | 1227015.1873 | 2597684.8414 | 1227015.1873
11 | 2597677.6283 | 1226886.7814 | 2597649.171 | 1226878.9684
12 | 2597677.6283 | 1226886.7814 | 2597687.6022 | 1226851.1009 | 2597723.1633 | 1226859.9697 | 2597724.8231 | 1226860.4026
13 | 2597564.6391 | 1227020.3065 | 2597620.0942 | 1227034.6029 | 2597635.199 | 1227038.499 | 2597631.7334 | 1227051.0967
14 | 2597744.9685 | 1227078.5897 | 2597742.299 | 1227092.699 | 2597736.9018 | 1227107.7989
15 | 2597727.7541 | 1227143.7792 | 2597734.9989 | 1227125.0987 | 2597736.9018 | 1227107.7989
16 | 2597744.9685 | 1227078.5897 | 2597753.5026 | 1227081.7993 | 2597775.5411 | 1227085.7153
17 | 2597702.6987 | 1227137.0963 | 2597727.7541 | 1227143.7792
18 | 2597805.4541 | 1227092.0186 | 2597796.8975 | 1227089.4982 | 2597775.5411 | 1227085.7153
19 | 2597775.5411 | 1227085.7153 | 2597773.2968 | 1227102.1036 | 2597767.8987 | 1227115.1022
20 | 2597702.6987 | 1227137.0963 | 2597641.3634 | 1227120.7342
21 | 2597805.4541 | 1227092.0186 | 2597804.301 | 1227108.7067 | 2597798.1989 | 1227123.8068
22 | 2597836.9671 | 1227101.2788 | 2597805.4541 | 1227092.0186
23 | 2597646.298 | 1227050.0012 | 2597648.0604 | 1227041.8623 | 2597798.8343 | 1227081.1259
24 | 2597646.298 | 1227050.0012 | 2597641.3256 | 1227051.5133
25 | 2597798.8343 | 1227081.1259 | 2597808.0802 | 1227052.3383
26 | 2597798.8343 | 1227081.1259 | 2597814.3762 | 1227085.1749
27 | 2597631.7334 | 1227051.0967 | 2597637.4024 | 1227052.7064 | 2597641.3256 | 1227051.5133
28 | 2597614.0643 | 1227113.4517 | 2597641.3634 | 1227120.7342
29 | 2597836.9671 | 1227101.2788 | 2597830.2007 | 1227123.3054 | 2597828.5166 | 1227130.4352
30 | 2597814.3762 | 1227085.1749 | 2597847.4978 | 1227093.8038 | 2597879.0799 | 1227102.0292
31 | 2597631.7334 | 1227051.0967 | 2597622.3115 | 1227084.3322
32 | 2597614.0643 | 1227113.4517 | 2597615.2826 | 1227109.1265 | 2597622.3115 | 1227084.3322
33 | 2597715.6844 | 1226996.086 | 2597712.9306 | 1227006.3342
34 | 2597641.1421 | 1226839.4462 | 2597632.6525 | 1226871.802 | 2597633.798 | 1226874.7477 | 2597649.171 | 1226878.9684
35 | 2597724.8231 | 1226860.4026 | 2597780.4765 | 1226875.0451
36 | 2597724.8231 | 1226860.4026 | 2597716.647 | 1226891.4525
37 | 2597641.1421 | 1226839.4462 | 2597611.304 | 1226831.9558
38 | 2597780.4765 | 1226875.0451 | 2597770.3448 | 1226913.3455
39 | 2597709.7434 | 1226920.4105 | 2597709.4929 | 1226919.4879 | 2597709.5077 | 1226918.5651 | 2597716.647 | 1226891.4525

## bus_geodata
| x | y | coords
0 | 2597606.8757 | 1226918.4697
1 | 2597645.93 | 1226928.3187
2 | 2597664.6654 | 1226933.1583
3 | 2597605.9888 | 1226937.1848
4 | 2597598.9623 | 1226951.8963
5 | 2597655.6453 | 1226965.4032
6 | 2597674.4835 | 1226898.0326
7 | 2597576.5504 | 1226978.0265
8 | 2597684.8414 | 1227015.1873
9 | 2597677.6283 | 1226886.7814
10 | 2597564.6391 | 1227020.3065
11 | 2597736.9018 | 1227107.7989
12 | 2597744.9685 | 1227078.5897
13 | 2597727.7541 | 1227143.7792
14 | 2597775.5411 | 1227085.7153
15 | 2597702.6987 | 1227137.0963
16 | 2597805.4541 | 1227092.0186
17 | 2597767.8987 | 1227115.1022
18 | 2597646.298 | 1227050.0012
19 | 2597798.8343 | 1227081.1259
20 | 2597641.3256 | 1227051.5133
21 | 2597641.3634 | 1227120.7342
22 | 2597798.1989 | 1227123.8068
23 | 2597836.9671 | 1227101.2788
24 | 2597808.0802 | 1227052.3383
25 | 2597814.3762 | 1227085.1749
26 | 2597631.7334 | 1227051.0967
27 | 2597622.3115 | 1227084.3322
28 | 2597614.0643 | 1227113.4517
29 | 2597879.0799 | 1227102.0292
30 | 2597828.5166 | 1227130.4352
31 | 2597712.9306 | 1227006.3342
32 | 2597715.6844 | 1226996.086
33 | 2597649.171 | 1226878.9684
34 | 2597724.8231 | 1226860.4026
35 | 2597641.1421 | 1226839.4462
36 | 2597780.4765 | 1226875.0451
37 | 2597716.647 | 1226891.4525
38 | 2597611.304 | 1226831.9558
39 | 2597770.3448 | 1226913.3455
40 | 2597709.7434 | 1226920.4105
41 | 2597655.6453 | 1226965.4032

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98934 | -0.20205 | 0.0055741 | 0.001397
1 | 0.98954 | -0.19806 | 0 | 0
2 | 0.99002 | -0.18896 | 0 | 0
3 | 0.98835 | -0.22085 | 0 | 0
4 | 0.98797 | -0.2282 | 0 | 0
5 | 0.99203 | -0.15055 | 0 | 0
6 | 0.98613 | -0.26347 | 0.00037879 | 9.4933e-05
7 | 0.98711 | -0.24462 | 0.0025171 | 0.00063086
8 | 0.99604 | -0.074526 | 0.0074152 | 0.0018584
9 | 0.98489 | -0.28738 | 0 | 0
10 | 0.98614 | -0.26333 | 0 | 0
11 | 0.97522 | -0.47568 | 0.014142 | 0.0035444
12 | 0.974 | -0.4996 | 0 | 0
13 | 0.97721 | -0.43662 | 0 | 0
14 | 0.97274 | -0.52439 | 0 | 0
15 | 0.97858 | -0.40974 | 0 | 0
16 | 0.97192 | -0.54058 | 0 | 0
17 | 0.97234 | -0.53236 | 0.014118 | 0.0035382
18 | 0.98409 | -0.30289 | 0 | 0
19 | 0.98267 | -0.33071 | 0 | 0
20 | 0.98414 | -0.30201 | 0.0014317 | 0.00035882
21 | 0.98196 | -0.34406 | 0.0025239 | 0.00063255
22 | 0.97149 | -0.5492 | 0.014149 | 0.0035461
23 | 0.97148 | -0.54942 | 0 | 0
24 | 0.9826 | -0.33201 | 0.0023875 | 0.00059836
25 | 0.98257 | -0.33274 | 0.0017146 | 0.00042972
26 | 0.98424 | -0.30006 | 0 | 0
27 | 0.98359 | -0.31261 | 0.00097345 | 0.00024397
28 | 0.98275 | -0.32886 | 0 | 0
29 | 0.98224 | -0.33914 | 0.0052972 | 0.0013276
30 | 0.97106 | -0.55763 | 0.014621 | 0.0036644
31 | 0.99904 | -0.018087 | 0.091715 | 0.022986
32 | 1 | 0 | -0.29923 | -0.076333
33 | 0.98478 | -0.2895 | 0.0019597 | 0.00049115
34 | 0.97717 | -0.4377 | 0 | 0
35 | 0.98469 | -0.29142 | 0 | 0
36 | 0.97609 | -0.45894 | 0 | 0
37 | 0.97448 | -0.49048 | 0.089132 | 0.022339
38 | 0.98463 | -0.29254 | 0.0020303 | 0.00050884
39 | 0.97534 | -0.47362 | 0.020246 | 0.0050741
40 | 0.97446 | -0.49085 | 0.00067646 | 0.00016954
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0055741 | -0.001397 | 0.0055752 | 0.0013972 | 1.0616e-06 | 1.6211e-07 | 0.0083837 | 0.0083836 | 0.0083837 | 0.98934 | -0.20205 | 0.98954 | -0.19806 | 2.3032
1 | -0.080463 | -0.02054 | 0.080499 | 0.020562 | 3.5392e-05 | 2.1907e-05 | 0.12113 | 0.12113 | 0.12113 | 0.98954 | -0.19806 | 0.99002 | -0.18896 | 11.0925
2 | 0.074888 | 0.019143 | -0.074806 | -0.019092 | 8.2467e-05 | 5.0781e-05 | 0.11275 | 0.11275 | 0.11275 | 0.98954 | -0.19806 | 0.98835 | -0.22085 | 10.3249
3 | -0.19653 | -0.050265 | 0.1969 | 0.050498 | 0.00036609 | 0.000233 | 0.29575 | 0.29575 | 0.29575 | 0.99002 | -0.18896 | 0.99203 | -0.15055 | 27.0836
4 | 0.11603 | 0.029703 | -0.11562 | -0.029436 | 0.00041706 | 0.00026645 | 0.17462 | 0.17462 | 0.17462 | 0.99002 | -0.18896 | 0.98613 | -0.26347 | 47.9734
5 | 0.074806 | 0.019092 | -0.074779 | -0.019076 | 2.6576e-05 | 1.6366e-05 | 0.11275 | 0.11275 | 0.11275 | 0.98835 | -0.22085 | 0.98797 | -0.2282 | 10.3249
6 | 0.074779 | 0.019076 | -0.07472 | -0.01904 | 5.9225e-05 | 3.6473e-05 | 0.11275 | 0.11275 | 0.11275 | 0.98797 | -0.2282 | 0.98711 | -0.24462 | 10.3249
7 | -0.1969 | -0.050498 | 0.19763 | 0.050962 | 0.00072887 | 0.00046389 | 0.29575 | 0.29575 | 0.29575 | 0.99203 | -0.15055 | 0.99604 | -0.074526 | 27.0836
8 | 0.11524 | 0.029341 | -0.1151 | -0.029256 | 0.00013272 | 8.4789e-05 | 0.17405 | 0.17405 | 0.17405 | 0.98613 | -0.26347 | 0.98489 | -0.28738 | 47.8164
9 | 0.072203 | 0.018409 | -0.072138 | -0.018369 | 6.518e-05 | 4.0033e-05 | 0.10895 | 0.10895 | 0.10895 | 0.98711 | -0.24462 | 0.98614 | -0.26333 | 9.9775
10 | -0.20504 | -0.05282 | 0.20561 | 0.05318 | 0.00056493 | 0.00035968 | 0.30683 | 0.30683 | 0.30683 | 0.99604 | -0.074526 | 0.99904 | -0.018087 | 28.0979
11 | 0.0039907 | 0.00099901 | -0.0039903 | -0.00099913 | 4.0225e-07 | -1.1806e-07 | 0.006029 | 0.0060291 | 0.0060291 | 0.98489 | -0.28738 | 0.98478 | -0.2895 | 1.6563
12 | 0.11111 | 0.028257 | -0.11032 | -0.027747 | 0.0007984 | 0.00051002 | 0.16802 | 0.16802 | 0.16802 | 0.98489 | -0.28738 | 0.97717 | -0.4377 | 46.1602
13 | 0.072138 | 0.018369 | -0.07201 | -0.01829 | 0.00012752 | 7.8328e-05 | 0.10895 | 0.10896 | 0.10896 | 0.98614 | -0.26333 | 0.98424 | -0.30006 | 9.9776
14 | 0.043033 | 0.010839 | -0.042984 | -0.010808 | 4.9172e-05 | 3.1091e-05 | 0.065681 | 0.065681 | 0.065681 | 0.97522 | -0.47568 | 0.974 | -0.4996 | 18.0442
15 | -0.057175 | -0.014383 | 0.057282 | 0.014451 | 0.0001069 | 6.7951e-05 | 0.087259 | 0.087259 | 0.087259 | 0.97522 | -0.47568 | 0.97721 | -0.43662 | 23.9724
16 | 0.042984 | 0.010808 | -0.042933 | -0.010776 | 5.0822e-05 | 3.2135e-05 | 0.065681 | 0.065681 | 0.065681 | 0.974 | -0.4996 | 0.97274 | -0.52439 | 18.0443
17 | -0.057282 | -0.014451 | 0.057356 | 0.014498 | 7.3841e-05 | 4.6934e-05 | 0.087259 | 0.087259 | 0.087259 | 0.97721 | -0.43662 | 0.97858 | -0.40974 | 23.9723
18 | 0.02881 | 0.0072345 | -0.028788 | -0.0072206 | 2.2237e-05 | 1.3853e-05 | 0.044076 | 0.044076 | 0.044076 | 0.97274 | -0.52439 | 0.97192 | -0.54058 | 12.1089
19 | 0.014123 | 0.0035413 | -0.014118 | -0.0035382 | 5.359e-06 | 3.0499e-06 | 0.021605 | 0.021605 | 0.021605 | 0.97274 | -0.52439 | 0.97234 | -0.53236 | 5.9354
20 | -0.057356 | -0.014498 | 0.057537 | 0.014613 | 0.00018126 | 0.0001152 | 0.087259 | 0.087259 | 0.087259 | 0.97858 | -0.40974 | 0.98196 | -0.34406 | 23.9723
21 | 0.014155 | 0.0035494 | -0.014149 | -0.0035461 | 5.8146e-06 | 3.3124e-06 | 0.021672 | 0.021672 | 0.021672 | 0.97192 | -0.54058 | 0.97149 | -0.5492 | 5.9538
22 | 0.014633 | 0.0036712 | -0.014627 | -0.0036677 | 6.1662e-06 | 3.5406e-06 | 0.022405 | 0.022405 | 0.022405 | 0.97192 | -0.54058 | 0.97148 | -0.54942 | 6.1552
23 | 0.0094142 | 0.0023617 | -0.0094018 | -0.0023558 | 1.2474e-05 | 5.9011e-06 | 0.014236 | 0.014237 | 0.014237 | 0.98409 | -0.30289 | 0.98267 | -0.33071 | 3.9111
24 | -0.0094142 | -0.0023617 | 0.0094146 | 0.0023619 | 3.9497e-07 | 1.8675e-07 | 0.014236 | 0.014236 | 0.014236 | 0.98409 | -0.30289 | 0.98414 | -0.30201 | 3.9109
25 | 0.0023876 | 0.00059807 | -0.0023875 | -0.00059836 | 1.4821e-07 | -2.8816e-07 | 0.0036154 | 0.0036155 | 0.0036155 | 0.98267 | -0.33071 | 0.9826 | -0.33201 | 0.99327
26 | 0.0070142 | 0.0017578 | -0.0070135 | -0.0017575 | 6.7943e-07 | 2.3139e-07 | 0.010621 | 0.010621 | 0.010621 | 0.98267 | -0.33071 | 0.98257 | -0.33274 | 2.9179
27 | -0.010846 | -0.0027207 | 0.010847 | 0.0027212 | 1.008e-06 | 5.1814e-07 | 0.0164 | 0.0164 | 0.0164 | 0.98414 | -0.30201 | 0.98424 | -0.30006 | 4.5056
28 | -0.060061 | -0.015246 | 0.060105 | 0.015273 | 4.395e-05 | 2.7412e-05 | 0.091084 | 0.091083 | 0.091084 | 0.98196 | -0.34406 | 0.98275 | -0.32886 | 12.5115
29 | 0.014627 | 0.0036677 | -0.014621 | -0.0036644 | 5.7166e-06 | 3.2828e-06 | 0.022405 | 0.022405 | 0.022405 | 0.97148 | -0.54942 | 0.97106 | -0.55763 | 6.1552
30 | 0.0052989 | 0.0013278 | -0.0052972 | -0.0013276 | 1.6147e-06 | 1.8679e-07 | 0.0080246 | 0.0080249 | 0.0080249 | 0.98257 | -0.33274 | 0.98224 | -0.33914 | 2.2046
31 | 0.061163 | 0.015569 | -0.061126 | -0.015547 | 3.6991e-05 | 2.2358e-05 | 0.092555 | 0.092556 | 0.092556 | 0.98424 | -0.30006 | 0.98359 | -0.31261 | 8.4758
32 | 0.060152 | 0.015303 | -0.060105 | -0.015273 | 4.7078e-05 | 2.9362e-05 | 0.091083 | 0.091083 | 0.091083 | 0.98359 | -0.31261 | 0.98275 | -0.32886 | 12.5114
33 | -0.29732 | -0.076166 | 0.29758 | 0.076332 | 0.00026082 | 0.00016651 | 0.44343 | 0.44343 | 0.44343 | 0.99904 | -0.018087 | 1 | 0 | 40.6072
34 | 0.0020306 | 0.00050797 | -0.0020304 | -0.00050852 | 1.8551e-07 | -5.4985e-07 | 0.0030679 | 0.0030682 | 0.0030682 | 0.98478 | -0.2895 | 0.98469 | -0.29142 | 0.8429
35 | 0.020281 | 0.0050951 | -0.02026 | -0.0050827 | 2.0532e-05 | 1.2423e-05 | 0.030888 | 0.030888 | 0.030888 | 0.97717 | -0.4377 | 0.97609 | -0.45894 | 8.4857
36 | 0.090035 | 0.022652 | -0.089809 | -0.022508 | 0.00022644 | 0.00014452 | 0.13714 | 0.13714 | 0.13714 | 0.97717 | -0.4377 | 0.97448 | -0.49048 | 37.6747
37 | 0.0020304 | 0.00050852 | -0.0020303 | -0.00050884 | 1.0861e-07 | -3.218e-07 | 0.0030682 | 0.0030683 | 0.0030683 | 0.98469 | -0.29142 | 0.98463 | -0.29254 | 0.84294
38 | 0.02026 | 0.0050827 | -0.020246 | -0.0050741 | 1.4174e-05 | 8.5767e-06 | 0.030888 | 0.030888 | 0.030888 | 0.97609 | -0.45894 | 0.97534 | -0.47362 | 8.4857
39 | 0.00067647 | 0.00016917 | -0.00067646 | -0.00016954 | 1.1969e-08 | -3.6503e-07 | 0.0010328 | 0.001033 | 0.001033 | 0.97448 | -0.49048 | 0.97446 | -0.49085 | 0.28378

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34247 | 0.087168

## res_load
| p_mw | q_mvar
0 | 0.0055741 | 0.001397
1 | 0.00037879 | 9.4933e-05
2 | 0.0025171 | 0.00063086
3 | 0.0074152 | 0.0018584
4 | 0.014142 | 0.0035444
5 | 0.014118 | 0.0035382
6 | 0.0014317 | 0.00035882
7 | 0.0025239 | 0.00063255
8 | 0.014149 | 0.0035461
9 | 0.0023875 | 0.00059836
10 | 0.0017146 | 0.00042972
11 | 0.00097345 | 0.00024397
12 | 0.0052972 | 0.0013276
13 | 0.014621 | 0.0036644
14 | 0.091715 | 0.022986
15 | 0.043233 | 0.010835
16 | 0.0019597 | 0.00049115
17 | 0.089132 | 0.022339
18 | 0.0020303 | 0.00050884
19 | 0.020246 | 0.0050741
20 | 0.00067646 | 0.00016954

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1