## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2546-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2546-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2546-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2546-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2546-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2546-9_0_4_node_62 | 0.4 | n |  | TRUE
6 | bus_LV_2546-9_0_4_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_2546-9_0_4_node_112 | 0.4 | n |  | TRUE
8 | bus_LV_2546-9_0_4_node_63 | 0.4 | n |  | TRUE
9 | bus_LV_2546-9_0_4_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_2546-9_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_2546-9_0_4_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_2546-9_0_4_node_113 | 0.4 | n |  | TRUE
13 | bus_LV_2546-9_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_2546-9_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2546-9_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2546-9_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2546-9_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2546-9_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2546-9_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_2546-9_0_4_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_2546-9_0_4_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_2546-9_0_4_node_108 | 0.4 | n |  | TRUE
23 | bus_LV_2546-9_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_2546-9_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_2546-9_0_4_node_89 | 0.4 | n |  | TRUE
26 | bus_LV_2546-9_0_4_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_2546-9_0_4_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_2546-9_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2546-9_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2546-9_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_2546-9_0_4_node_116 | 0.4 | n |  | TRUE
32 | bus_LV_2546-9_0_4_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_2546-9_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2546-9_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2546-9_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2546-9_0_4_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2546-9_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_2546-9_0_4_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_2546-9_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_2546-9_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2546-9_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2546-9_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2546-9_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2546-9_0_4_node_87 | 0.4 | n |  | TRUE
45 | bus_LV_2546-9_0_4_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_2546-9_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2546-9_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2546-9_0_4_node_102 | 0.4 | n |  | TRUE
49 | bus_LV_2546-9_0_4_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_2546-9_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2546-9_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2546-9_0_4_node_129 | 0.4 | n |  | TRUE
53 | bus_LV_2546-9_0_4_node_94 | 0.4 | n |  | TRUE
54 | bus_LV_2546-9_0_4_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_2546-9_0_4_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2546-9_0_4_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2546-9_0_4_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_2546-9_0_4_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_2546-9_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_2546-9_0_4_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_2546-9_0_4_node_122 | 0.4 | n |  | TRUE
62 | bus_LV_2546-9_0_4_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_2546-9_0_4_node_126 | 0.4 | n |  | TRUE
64 | bus_LV_2546-9_0_4_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_2546-9_0_4_node_131 | 0.4 | n |  | TRUE
66 | bus_LV_2546-9_0_4_node_98 | 0.4 | n |  | TRUE
67 | bus_LV_2546-9_0_4_node_127 | 0.4 | n |  | TRUE
68 | bus_LV_2546-9_0_4_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_2546-9_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_2546-9_0_4_node_117 | 0.4 | n |  | TRUE
71 | bus_LV_2546-9_0_4_node_118 | 0.4 | n |  | TRUE
72 | bus_LV_2546-9_0_4_node_103 | 0.4 | n |  | TRUE
73 | bus_LV_2546-9_0_4_node_93 | 0.4 | n |  | TRUE
74 | bus_LV_2546-9_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_2546-9_0_4_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_2546-9_0_4_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_2546-9_0_4_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_2546-9_0_4_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_2546-9_0_4_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_2546-9_0_4_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_2546-9_0_4_node_123 | 0.4 | n |  | TRUE
82 | bus_LV_2546-9_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_2546-9_0_4_node_52 | 0.4 | n |  | TRUE
84 | bus_LV_2546-9_0_4_node_53 | 0.4 | n |  | TRUE
85 | bus_LV_2546-9_0_4_node_54 | 0.4 | n |  | TRUE
86 | bus_LV_2546-9_0_4_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_2546-9_0_4_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_2546-9_0_4_node_107 | 0.4 | n |  | TRUE
89 | bus_LV_2546-9_0_4_node_120 | 0.4 | n |  | TRUE
90 | bus_LV_2546-9_0_4_node_111 | 0.4 | n |  | TRUE
91 | bus_LV_2546-9_0_4_node_121 | 0.4 | n |  | TRUE
92 | bus_LV_2546-9_0_4_node_57 | 0.4 | n |  | TRUE
93 | bus_LV_2546-9_0_4_node_58 | 0.4 | n |  | TRUE
94 | bus_LV_2546-9_0_4_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_2546-9_0_4_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_2546-9_0_4_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_2546-9_0_4_node_105 | 0.4 | n |  | TRUE
98 | bus_LV_2546-9_0_4_node_124 | 0.4 | n |  | TRUE
99 | bus_LV_2546-9_0_4_node_67 | 0.4 | n |  | TRUE
100 | bus_LV_2546-9_0_4_node_115 | 0.4 | n |  | TRUE
101 | bus_LV_2546-9_0_4_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_2546-9_0_4_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_2546-9_0_4_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_2546-9_0_4_node_71 | 0.4 | n |  | TRUE
105 | bus_LV_2546-9_0_4_node_76 | 0.4 | n |  | TRUE
106 | bus_LV_2546-9_0_4_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_2546-9_0_4_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_2546-9_0_4_node_77 | 0.4 | n |  | TRUE
109 | bus_LV_2546-9_0_4_node_78 | 0.4 | n |  | TRUE
110 | bus_LV_2546-9_0_4_node_79 | 0.4 | n |  | TRUE
111 | bus_LV_2546-9_0_4_node_80 | 0.4 | n |  | TRUE
112 | bus_LV_2546-9_0_4_node_81 | 0.4 | n |  | TRUE
113 | bus_LV_2546-9_0_4_node_82 | 0.4 | n |  | TRUE
114 | bus_LV_2546-9_0_4_node_83 | 0.4 | n |  | TRUE
115 | bus_LV_2546-9_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_2546-9_0_4_node_134 | 0.4 | n |  | TRUE
117 | bus_LV_2546-9_0_4_node_84 | 0.4 | n |  | TRUE
118 | bus_LV_2546-9_0_4_node_128 | 0.4 | n |  | TRUE
119 | bus_LV_2546-9_0_4_node_130 | 0.4 | n |  | TRUE
120 | bus_LV_2546-9_0_4_node_90 | 0.4 | n |  | TRUE
121 | bus_LV_2546-9_0_4_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_2546-9_0_4_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_2546-9_0_4_node_97 | 0.4 | n |  | TRUE
124 | bus_LV_2546-9_0_4_node_99 | 0.4 | n |  | TRUE
125 | bus_LV_2546-9_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_2546-9_0_4_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2546-9_0_4_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_2546-9_0_4_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_2546-9_0_4_node_132 | 0.4 | n |  | TRUE
130 | bus_LV_2546-9_0_4_node_135 | 0.4 | n |  | TRUE
131 | bus_MV_521_0_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2546-9_0_4_load_0 | 0 | 0.0026591 | 0.00066644 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2546-9_0_4_load_1 | 1 | 0.0026117 | 0.00065455 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2546-9_0_4_load_2 | 2 | 0.0021949 | 0.0005501 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2546-9_0_4_load_3 | 3 | 0.0042234 | 0.0010585 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2546-9_0_4_load_112 | 7 | 0.0019525 | 0.00048934 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2546-9_0_4_load_64 | 9 | 0.0013713 | 0.00034368 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2546-9_0_4_load_32 | 10 | 0.0022677 | 0.00056833 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2546-9_0_4_load_28 | 11 | 0.0011241 | 0.00028173 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2546-9_0_4_load_113 | 12 | 0.0017311 | 0.00043386 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2546-9_0_4_load_5 | 13 | 0.0060283 | 0.0015108 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2546-9_0_4_load_6 | 14 | 0.0041706 | 0.0010452 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2546-9_0_4_load_8 | 16 | 0.0033125 | 0.0008302 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2546-9_0_4_load_9 | 17 | 0.0082823 | 0.0020757 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2546-9_0_4_load_25 | 19 | 0.0024539 | 0.000615 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2546-9_0_4_load_39 | 20 | 0.0070031 | 0.0017551 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2546-9_0_4_load_91 | 21 | 0.0038797 | 0.00097234 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2546-9_0_4_load_108 | 22 | 0.0043842 | 0.0010988 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2546-9_0_4_load_26 | 23 | 0.0032421 | 0.00081255 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2546-9_0_4_load_40 | 24 | 0.0031648 | 0.00079318 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2546-9_0_4_load_89 | 25 | 0.0017125 | 0.00042919 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2546-9_0_4_load_109 | 26 | 0.0048656 | 0.0012194 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2546-9_0_4_load_11 | 27 | 0.0067496 | 0.0016916 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2546-9_0_4_load_12 | 28 | 0.0101 | 0.0025313 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2546-9_0_4_load_13 | 29 | 0.0018223 | 0.0004567 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2546-9_0_4_load_14 | 30 | 0.0066811 | 0.0016744 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2546-9_0_4_load_116 | 31 | 0.0067368 | 0.0016884 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2546-9_0_4_load_15 | 32 | 0.0027698 | 0.00069417 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2546-9_0_4_load_16 | 33 | 0.002469 | 0.00061879 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2546-9_0_4_load_18 | 35 | 0.0018129 | 0.00045437 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2546-9_0_4_load_19 | 36 | 0.001735 | 0.00043484 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2546-9_0_4_load_51 | 37 | 0.0041376 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2546-9_0_4_load_20 | 39 | 0.0080605 | 0.0020202 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2546-9_0_4_load_21 | 40 | 0.0026101 | 0.00065415 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2546-9_0_4_load_22 | 41 | 0.008042 | 0.0020155 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2546-9_0_4_load_23 | 42 | 0.0085394 | 0.0021402 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2546-9_0_4_load_24 | 43 | 0.0052411 | 0.0013136 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2546-9_0_4_load_87 | 44 | 0.0025318 | 0.00063452 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2546-9_0_4_load_88 | 45 | 0.0092481 | 0.0023178 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2546-9_0_4_load_27 | 46 | 0.0065537 | 0.0016425 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2546-9_0_4_load_42 | 47 | 0.0046397 | 0.0011628 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2546-9_0_4_load_102 | 48 | 0.0050049 | 0.0012543 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2546-9_0_4_load_29 | 49 | 0.0017349 | 0.0004348 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2546-9_0_4_load_31 | 50 | 0.0014762 | 0.00036998 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2546-9_0_4_load_43 | 51 | 0.001736 | 0.00043509 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2546-9_0_4_load_94 | 53 | 0.0010952 | 0.00027449 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2546-9_0_4_load_33 | 55 | 0.0033767 | 0.00084628 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2546-9_0_4_load_34 | 56 | 0.0061247 | 0.001535 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2546-9_0_4_load_38 | 60 | 0.00057354 | 0.00014374 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2546-9_0_4_load_122 | 61 | 0.0027364 | 0.0006858 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2546-9_0_4_load_100 | 62 | 0.0021618 | 0.0005418 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2546-9_0_4_load_126 | 63 | 0.010884 | 0.0027277 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2546-9_0_4_load_45 | 64 | 0.0014134 | 0.00035424 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2546-9_0_4_load_131 | 65 | 0.0029464 | 0.00073843 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2546-9_0_4_load_127 | 67 | 0.0033671 | 0.00084387 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2546-9_0_4_load_44 | 68 | 0.0053569 | 0.0013426 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2546-9_0_4_load_41 | 69 | 0.0057684 | 0.0014457 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2546-9_0_4_load_117 | 70 | 0.0075495 | 0.0018921 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2546-9_0_4_load_118 | 71 | 0.0038077 | 0.00095429 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2546-9_0_4_load_103 | 72 | 0.0061113 | 0.0015316 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2546-9_0_4_load_93 | 73 | 0.00098743 | 0.00024747 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2546-9_0_4_load_72 | 74 | 0.0035928 | 0.00090045 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2546-9_0_4_load_46 | 75 | 0.0035562 | 0.00089127 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2546-9_0_4_load_47 | 76 | 0.0020293 | 0.0005086 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2546-9_0_4_load_49 | 77 | 0.0012534 | 0.00031412 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2546-9_0_4_load_50 | 78 | 0.0012332 | 0.00030907 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2546-9_0_4_load_75 | 79 | 0.0021106 | 0.00052896 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2546-9_0_4_load_65 | 80 | 0.0018662 | 0.00046771 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2546-9_0_4_load_123 | 81 | 0.0012188 | 0.00030547 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2546-9_0_4_load_66 | 82 | 0.0024971 | 0.00062582 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2546-9_0_4_load_52 | 83 | 0.007084 | 0.0017754 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2546-9_0_4_load_53 | 84 | 0.01359 | 0.003406 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2546-9_0_4_load_55 | 86 | 0.0068237 | 0.0017102 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2546-9_0_4_load_56 | 87 | 0.0086174 | 0.0021597 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2546-9_0_4_load_107 | 88 | 0.0092805 | 0.0023259 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2546-9_0_4_load_120 | 89 | 0.0032001 | 0.00080201 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2546-9_0_4_load_111 | 90 | 0.0061784 | 0.0015484 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2546-9_0_4_load_121 | 91 | 0.0057687 | 0.0014458 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2546-9_0_4_load_57 | 92 | 0.0022767 | 0.00057059 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2546-9_0_4_load_58 | 93 | 0.0023386 | 0.00058611 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2546-9_0_4_load_59 | 94 | 0.0022871 | 0.00057321 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2546-9_0_4_load_60 | 95 | 0.0019559 | 0.00049019 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2546-9_0_4_load_61 | 96 | 0.0040416 | 0.0010129 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2546-9_0_4_load_105 | 97 | 0.0022369 | 0.00056062 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2546-9_0_4_load_124 | 98 | 0.0013757 | 0.00034479 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2546-9_0_4_load_67 | 99 | 0.0015591 | 0.00039076 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2546-9_0_4_load_115 | 100 | 0.0012259 | 0.00030725 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2546-9_0_4_load_68 | 101 | 0.0014957 | 0.00037485 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2546-9_0_4_load_69 | 102 | 0.0020788 | 0.00052098 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2546-9_0_4_load_70 | 103 | 0.0022679 | 0.00056838 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2546-9_0_4_load_71 | 104 | 0.0027608 | 0.00069192 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2546-9_0_4_load_76 | 105 | 0.0036267 | 0.00090894 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2546-9_0_4_load_125 | 106 | 0.0024743 | 0.00062012 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2546-9_0_4_load_77 | 108 | 0.0069591 | 0.0017441 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2546-9_0_4_load_80 | 111 | 0.0063722 | 0.001597 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2546-9_0_4_load_81 | 112 | 0.0069732 | 0.0017476 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2546-9_0_4_load_82 | 113 | 0.0025463 | 0.00063816 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2546-9_0_4_load_83 | 114 | 0.0031934 | 0.00080034 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2546-9_0_4_load_101 | 115 | 0.0032686 | 0.00081918 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2546-9_0_4_load_84 | 117 | 0.0054859 | 0.0013749 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2546-9_0_4_load_90 | 120 | 0.0043148 | 0.0010814 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2546-9_0_4_load_96 | 121 | 0.0053743 | 0.0013469 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2546-9_0_4_load_95 | 122 | 0.001366 | 0.00034234 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2546-9_0_4_load_97 | 123 | 0.0030246 | 0.00075805 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2546-9_0_4_load_99 | 124 | 0.013837 | 0.003468 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2546-9_0_4_load_119 | 125 | 0.0022076 | 0.00055329 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2546-9_0_4_load_114 | 126 | 0.0018752 | 0.00046997 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2546-9_0_4_load_104 | 127 | 0.0035215 | 0.00088257 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2546-9_0_4_load_110 | 128 | 0.0074104 | 0.0018572 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2546-9_0_4_load_132 | 129 | 0.0057158 | 0.0014325 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2546-9_0_4_load_135 | 130 | 0.003265 | 0.00081829 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2546-9_0_4_line_0 |  | 0 | 1 | 0.0053788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2546-9_0_4_line_1 |  | 0 | 2 | 0.019359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2546-9_0_4_line_2 |  | 1 | 3 | 0.019931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2546-9_0_4_line_3 |  | 2 | 4 | 0.0070094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2546-9_0_4_line_4 |  | 3 | 5 | 0.0219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2546-9_0_4_line_5 |  | 4 | 6 | 0.024094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2546-9_0_4_line_6 |  | 4 | 7 | 0.014023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2546-9_0_4_line_7 |  | 5 | 8 | 0.027947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2546-9_0_4_line_8 |  | 5 | 9 | 0.018017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2546-9_0_4_line_9 |  | 6 | 10 | 0.026642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2546-9_0_4_line_10 |  | 6 | 11 | 0.019403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2546-9_0_4_line_11 |  | 7 | 12 | 0.016535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2546-9_0_4_line_12 |  | 8 | 31 | 0.023248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2546-9_0_4_line_13 |  | 8 | 43 | 0.0043532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2546-9_0_4_line_14 |  | 9 | 98 | 0.011672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2546-9_0_4_line_15 |  | 10 | 52 | 0.036052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2546-9_0_4_line_16 |  | 11 | 49 | 0.0073782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2546-9_0_4_line_17 |  | 12 | 126 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2546-9_0_4_line_18 |  | 13 | 14 | 0.0031711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2546-9_0_4_line_19 |  | 13 | 15 | 0.011442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2546-9_0_4_line_20 |  | 14 | 16 | 0.00913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2546-9_0_4_line_21 |  | 15 | 17 | 0.010963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2546-9_0_4_line_22 |  | 15 | 18 | 0.00378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2546-9_0_4_line_23 |  | 16 | 19 | 0.0010997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2546-9_0_4_line_24 |  | 17 | 20 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2546-9_0_4_line_25 |  | 18 | 21 | 0.01943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2546-9_0_4_line_26 |  | 18 | 22 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_2546-9_0_4_line_27 |  | 19 | 23 | 0.0092883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2546-9_0_4_line_28 |  | 20 | 24 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2546-9_0_4_line_29 |  | 21 | 25 | 0.013448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2546-9_0_4_line_30 |  | 22 | 26 | 0.013444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2546-9_0_4_line_31 |  | 23 | 46 | 0.0076733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2546-9_0_4_line_32 |  | 24 | 69 | 0.00010071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2546-9_0_4_line_33 |  | 25 | 120 | 0.0044244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2546-9_0_4_line_34 |  | 26 | 45 | 0.0015766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2546-9_0_4_line_35 |  | 27 | 28 | 0.012359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2546-9_0_4_line_36 |  | 27 | 29 | 0.02102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2546-9_0_4_line_37 |  | 28 | 30 | 0.0071472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2546-9_0_4_line_38 |  | 30 | 31 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2546-9_0_4_line_39 |  | 32 | 33 | 2.4074e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2546-9_0_4_line_40 |  | 32 | 34 | 0.062328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2546-9_0_4_line_41 |  | 33 | 35 | 0.0008597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2546-9_0_4_line_42 |  | 34 | 36 | 0.026078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2546-9_0_4_line_43 |  | 36 | 37 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2546-9_0_4_line_44 |  | 37 | 38 | 0.0038548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2546-9_0_4_line_45 |  | 38 | 78 | 0.011992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2546-9_0_4_line_46 |  | 38 | 75 | 0.012186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2546-9_0_4_line_47 |  | 39 | 40 | 0.0043726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2546-9_0_4_line_48 |  | 39 | 41 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2546-9_0_4_line_49 |  | 40 | 42 | 0.0073696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2546-9_0_4_line_50 |  | 41 | 43 | 0.010921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2546-9_0_4_line_51 |  | 42 | 44 | 0.0040653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2546-9_0_4_line_52 |  | 44 | 45 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2546-9_0_4_line_53 |  | 46 | 47 | 0.0069879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2546-9_0_4_line_54 |  | 47 | 48 | 0.013642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2546-9_0_4_line_55 |  | 48 | 72 | 0.0059764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2546-9_0_4_line_56 |  | 49 | 50 | 0.014878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2546-9_0_4_line_57 |  | 50 | 51 | 0.00051487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2546-9_0_4_line_58 |  | 51 | 53 | 0.019177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2546-9_0_4_line_59 |  | 52 | 54 | 0.021762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2546-9_0_4_line_60 |  | 53 | 73 | 0.0046721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2546-9_0_4_line_61 |  | 54 | 97 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2546-9_0_4_line_62 |  | 54 | 116 | 0.015888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2546-9_0_4_line_63 |  | 55 | 56 | 0.04527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2546-9_0_4_line_64 |  | 55 | 57 | 0.0069891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2546-9_0_4_line_65 |  | 56 | 58 | 0.02518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2546-9_0_4_line_66 |  | 57 | 59 | 0.008865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2546-9_0_4_line_67 |  | 57 | 60 | 0.036979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2546-9_0_4_line_68 |  | 58 | 61 | 0.016879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2546-9_0_4_line_69 |  | 58 | 62 | 0.024159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2546-9_0_4_line_70 |  | 59 | 63 | 0.016236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2546-9_0_4_line_71 |  | 60 | 64 | 0.025515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2546-9_0_4_line_72 |  | 61 | 65 | 0.011901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2546-9_0_4_line_73 |  | 62 | 66 | 0.014571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2546-9_0_4_line_74 |  | 63 | 67 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2546-9_0_4_line_75 |  | 64 | 68 | 0.04814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2546-9_0_4_line_76 |  | 65 | 129 | 0.035777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2546-9_0_4_line_77 |  | 66 | 121 | 0.017581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2546-9_0_4_line_78 |  | 66 | 107 | 0.015952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2546-9_0_4_line_79 |  | 68 | 74 | 0.062218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2546-9_0_4_line_80 |  | 69 | 70 | 0.00642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2546-9_0_4_line_81 |  | 70 | 71 | 0.0040947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2546-9_0_4_line_82 |  | 71 | 91 | 0.004985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2546-9_0_4_line_83 |  | 72 | 127 | 0.01216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2546-9_0_4_line_84 |  | 73 | 122 | 0.02269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2546-9_0_4_line_85 |  | 75 | 76 | 0.0034594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2546-9_0_4_line_86 |  | 76 | 77 | 0.0054822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2546-9_0_4_line_87 |  | 77 | 79 | 0.0089313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2546-9_0_4_line_88 |  | 78 | 80 | 0.0031942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2546-9_0_4_line_89 |  | 79 | 81 | 0.0077289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2546-9_0_4_line_90 |  | 80 | 82 | 0.036571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2546-9_0_4_line_91 |  | 81 | 98 | 0.0069655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2546-9_0_4_line_92 |  | 82 | 99 | 0.0016665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2546-9_0_4_line_93 |  | 83 | 84 | 0.0043886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2546-9_0_4_line_94 |  | 83 | 85 | 0.015668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2546-9_0_4_line_95 |  | 84 | 86 | 0.013077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2546-9_0_4_line_96 |  | 85 | 87 | 0.034582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2546-9_0_4_line_97 |  | 86 | 88 | 0.015445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2546-9_0_4_line_98 |  | 87 | 89 | 0.0025668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2546-9_0_4_line_99 |  | 88 | 90 | 0.0014083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2546-9_0_4_line_100 |  | 89 | 91 | 0.00524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2546-9_0_4_line_101 |  | 90 | 128 | 0.021156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2546-9_0_4_line_102 |  | 92 | 93 | 0.0025504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2546-9_0_4_line_103 |  | 92 | 94 | 0.0062284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2546-9_0_4_line_104 |  | 93 | 95 | 0.011035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2546-9_0_4_line_105 |  | 94 | 96 | 0.0035185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2546-9_0_4_line_106 |  | 96 | 97 | 0.0062527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2546-9_0_4_line_107 |  | 99 | 100 | 0.00060514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2546-9_0_4_line_108 |  | 101 | 102 | 0.0085693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2546-9_0_4_line_109 |  | 101 | 103 | 0.025362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2546-9_0_4_line_110 |  | 102 | 104 | 0.0030904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2546-9_0_4_line_111 |  | 104 | 105 | 0.010151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2546-9_0_4_line_112 |  | 105 | 106 | 0.014707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2546-9_0_4_line_113 |  | 106 | 107 | 0.020925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2546-9_0_4_line_114 |  | 107 | 120 | 0.011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2546-9_0_4_line_115 |  | 108 | 109 | 0.022354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2546-9_0_4_line_116 |  | 108 | 110 | 0.019118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2546-9_0_4_line_117 |  | 109 | 111 | 0.023811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2546-9_0_4_line_118 |  | 109 | 112 | 0.034196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2546-9_0_4_line_119 |  | 110 | 113 | 0.016449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2546-9_0_4_line_120 |  | 110 | 114 | 0.0092072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2546-9_0_4_line_121 |  | 111 | 115 | 0.0016179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2546-9_0_4_line_122 |  | 112 | 116 | 0.017239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2546-9_0_4_line_123 |  | 113 | 117 | 0.002473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2546-9_0_4_line_124 |  | 114 | 118 | 0.022933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2546-9_0_4_line_125 |  | 118 | 119 | 0.035993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2546-9_0_4_line_126 |  | 119 | 130 | 0.024144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2546-9_0_4_line_127 |  | 121 | 123 | 0.0063898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2546-9_0_4_line_128 |  | 124 | 125 | 0.025926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2546-9_0_4_line_129 |  | 125 | 126 | 0.0055594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2546-9_0_4_trafo_87 | 0.63 MVA 20/0.4 kV | 131 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2596332.8343 | 1227233.0814 | 2596335.5647 | 1227228.4472
1 | 2596332.8343 | 1227233.0814 | 2596323.0073 | 1227249.7603
2 | 2596345.6825 | 1227211.2748 | 2596335.5647 | 1227228.4472
3 | 2596318.5022 | 1227255.0009 | 2596320.9032 | 1227253.0983 | 2596322.8033 | 1227250.1064 | 2596323.0073 | 1227249.7603
4 | 2596356.7993 | 1227192.4067 | 2596345.6825 | 1227211.2748
5 | 2596318.5022 | 1227255.0009 | 2596317.1008 | 1227255.8023 | 2596314.1004 | 1227256.5046 | 2596294.8013 | 1227259.0517
6 | 2596318.5022 | 1227255.0009 | 2596320.8982 | 1227257.2007 | 2596330.4982 | 1227262.084
7 | 2596356.7993 | 1227192.4067 | 2596380.7016 | 1227207.0004
8 | 2596356.7993 | 1227192.4067 | 2596342.0527 | 1227182.0557
9 | 2596294.8013 | 1227259.0517 | 2596291.9502 | 1227267.9809 | 2596283.3727 | 1227282.9689
10 | 2596294.8013 | 1227259.0517 | 2596275.475 | 1227260.7765
11 | 2596330.4982 | 1227262.084 | 2596345.2358 | 1227269.5808
12 | 2596380.7016 | 1227207.0004 | 2596392.3031 | 1227186.8545
13 | 2596380.7016 | 1227207.0004 | 2596384.4718 | 1227209.1766
14 | 2596332.603 | 1227175.2052 | 2596341.4018 | 1227181.5989 | 2596342.0527 | 1227182.0557
15 | 2596263.126 | 1227306.3553 | 2596264.836 | 1227302.3963 | 2596270.8316 | 1227304.8828 | 2596283.3727 | 1227282.9689
16 | 2596268.2118 | 1227259.9263 | 2596270 | 1227260.5017 | 2596274.0999 | 1227260.8993 | 2596275.475 | 1227260.7765
17 | 2596345.2358 | 1227269.5808 | 2596354.3606 | 1227274.2224
18 | 2596475.003 | 1227258.2681 | 2596477.8855 | 1227259.5899
19 | 2596464.602 | 1227253.4985 | 2596475.003 | 1227258.2681
20 | 2596477.8855 | 1227259.5899 | 2596486.1846 | 1227263.3955
21 | 2596464.602 | 1227253.4985 | 2596470.303 | 1227245.0789 | 2596470.7487 | 1227244.4208
22 | 2596462.3002 | 1227256.5016 | 2596464.602 | 1227253.4985
23 | 2596487.1841 | 1227263.8539 | 2596486.1846 | 1227263.3955
24 | 2596470.7487 | 1227244.4208 | 2596478.4711 | 1227233.0179
25 | 2596462.3002 | 1227256.5016 | 2596451.5584 | 1227272.6921
26 | 2596462.3002 | 1227256.5016 | 2596454.2343 | 1227251.5481 | 2596449.7381 | 1227248.7672
27 | 2596487.1841 | 1227263.8539 | 2596489.9038 | 1227265.1011 | 2596495.7242 | 1227267.5026
28 | 2596487.6802 | 1227219.4198 | 2596478.4711 | 1227233.0179
29 | 2596444.2156 | 1227283.9587 | 2596448.8997 | 1227276.6994 | 2596451.5584 | 1227272.6921
30 | 2596449.7381 | 1227248.7672 | 2596438.3038 | 1227241.6952
31 | 2596495.7242 | 1227267.5026 | 2596502.8174 | 1227270.4293
32 | 2596487.6802 | 1227219.4198 | 2596487.7366 | 1227219.3365
33 | 2596444.2156 | 1227283.9587 | 2596441.8168 | 1227287.6763
34 | 2596438.3038 | 1227241.6952 | 2596436.9629 | 1227240.8659
35 | 2596411.7829 | 1227153.0278 | 2596405.6155 | 1227163.7374
36 | 2596411.7829 | 1227153.0278 | 2596417.8997 | 1227142.406 | 2596422.2479 | 1227134.7975
37 | 2596402.0488 | 1227169.9311 | 2596405.6155 | 1227163.7374
38 | 2596402.0488 | 1227169.9311 | 2596392.3031 | 1227186.8545
39 | 2596224.4138 | 1227171.7797 | 2596224.424 | 1227171.7579
40 | 2596257.838 | 1227119.5598 | 2596234.9338 | 1227149.3477 | 2596224.424 | 1227171.7579
41 | 2596224.0487 | 1227172.5581 | 2596224.4138 | 1227171.7797
42 | 2596257.838 | 1227119.5598 | 2596278.5921 | 1227135.3497
43 | 2596278.5921 | 1227135.3497 | 2596293.3305 | 1227146.5628
44 | 2596296.3984 | 1227148.8969 | 2596293.3305 | 1227146.5628
45 | 2596296.3984 | 1227148.8969 | 2596301.9504 | 1227138.2675
46 | 2596296.3984 | 1227148.8969 | 2596306.257 | 1227156.0607
47 | 2596410.5307 | 1227224.5179 | 2596414.2496 | 1227226.818
48 | 2596393.9299 | 1227214.6368 | 2596403.36 | 1227220.0829 | 2596410.5307 | 1227224.5179
49 | 2596420.5172 | 1227230.6944 | 2596414.2496 | 1227226.818
50 | 2596393.9299 | 1227214.6368 | 2596390.5336 | 1227212.6754 | 2596384.4718 | 1227209.1766
51 | 2596420.5172 | 1227230.6944 | 2596423.9747 | 1227232.8328
52 | 2596423.9747 | 1227232.8328 | 2596436.9629 | 1227240.8659
53 | 2596509.2771 | 1227273.0946 | 2596502.8174 | 1227270.4293
54 | 2596522.0795 | 1227277.8017 | 2596510.9981 | 1227273.8047 | 2596509.2771 | 1227273.0946
55 | 2596522.0795 | 1227277.8017 | 2596525.3991 | 1227278.9991 | 2596527.7696 | 1227279.6079
56 | 2596268.2118 | 1227259.9263 | 2596264.1032 | 1227258.6043 | 2596254.2346 | 1227254.8409
57 | 2596253.7536 | 1227254.6574 | 2596254.2346 | 1227254.8409
58 | 2596235.835 | 1227247.8241 | 2596253.7536 | 1227254.6574
59 | 2596283.1974 | 1227314.903 | 2596263.126 | 1227306.3553
60 | 2596231.4696 | 1227246.1593 | 2596235.835 | 1227247.8241
61 | 2596283.1974 | 1227314.903 | 2596302.3096 | 1227321.9604
62 | 2596283.1974 | 1227314.903 | 2596280.0303 | 1227327.4902 | 2596279.1076 | 1227330.248
63 | 2596371.7183 | 1227398.5463 | 2596378.8546 | 1227393.0444 | 2596395.3958 | 1227379.5484 | 2596402.1587 | 1227373.0404 | 2596405.7443 | 1227368.8374
64 | 2596366.1833 | 1227402.8136 | 2596371.7183 | 1227398.5463
65 | 2596422.1194 | 1227350.2036 | 2596418.2106 | 1227352.3183 | 2596414.826 | 1227356.4562 | 2596410.3291 | 1227363.4631 | 2596405.7443 | 1227368.8374
66 | 2596366.1833 | 1227402.8136 | 2596358.3582 | 1227407.021
67 | 2596366.1833 | 1227402.8136 | 2596375.5051 | 1227417.1385 | 2596385.5041 | 1227423.7139 | 2596393.2212 | 1227425.4991
68 | 2596422.1194 | 1227350.2036 | 2596426.3252 | 1227350.4567 | 2596428.2955 | 1227350.5889 | 2596437.7431 | 1227355.5919
69 | 2596422.1194 | 1227350.2036 | 2596421.5378 | 1227340.8428 | 2596425.8983 | 1227326.7209
70 | 2596358.3582 | 1227407.021 | 2596349.9195 | 1227411.5511 | 2596343.9205 | 1227414.4406
71 | 2596393.2212 | 1227425.4991 | 2596399.6914 | 1227426.9959 | 2596413.4233 | 1227429.0109 | 2596418.2234 | 1227430.3937
72 | 2596448.26 | 1227361.1612 | 2596437.7431 | 1227355.5919
73 | 2596430.1971 | 1227312.7988 | 2596425.8983 | 1227326.7209
74 | 2596326.8032 | 1227422.6855 | 2596343.9205 | 1227414.4406
75 | 2596464.8599 | 1227437.3902 | 2596454.4091 | 1227439.0139 | 2596434.1045 | 1227432.1445 | 2596424.3218 | 1227432.1505 | 2596418.2234 | 1227430.3937
76 | 2596448.26 | 1227361.1612 | 2596460.7992 | 1227367.8014 | 2596478.5589 | 1227380.0753
77 | 2596430.1971 | 1227312.7988 | 2596414.5273 | 1227304.8279
78 | 2596430.1971 | 1227312.7988 | 2596435.9016 | 1227297.8976
79 | 2596464.8599 | 1227437.3902 | 2596460.6468 | 1227499.465
80 | 2596487.7366 | 1227219.3365 | 2596491.3366 | 1227214.0207
81 | 2596493.6327 | 1227210.6304 | 2596491.3366 | 1227214.0207
82 | 2596493.6327 | 1227210.6304 | 2596496.428 | 1227206.5028
83 | 2596527.7696 | 1227279.6079 | 2596539.5477 | 1227282.6326
84 | 2596231.4696 | 1227246.1593 | 2596210.2685 | 1227238.0742
85 | 2596306.257 | 1227156.0607 | 2596309.0555 | 1227158.0943
86 | 2596309.0555 | 1227158.0943 | 2596313.4905 | 1227161.317
87 | 2596320.7157 | 1227166.5672 | 2596313.4905 | 1227161.317
88 | 2596303.4293 | 1227135.4362 | 2596301.9504 | 1227138.2675
89 | 2596320.7157 | 1227166.5672 | 2596326.9681 | 1227171.1106
90 | 2596303.4293 | 1227135.4362 | 2596320.3606 | 1227103.0208
91 | 2596332.603 | 1227175.2052 | 2596326.9681 | 1227171.1106
92 | 2596320.3606 | 1227103.0208 | 2596321.1322 | 1227101.5436
93 | 2596534.0616 | 1227178.7039 | 2596537.945 | 1227180.7482
94 | 2596520.197 | 1227171.4055 | 2596534.0616 | 1227178.7039
95 | 2596537.945 | 1227180.7482 | 2596549.5165 | 1227186.8395
96 | 2596520.197 | 1227171.4055 | 2596500.8056 | 1227200.0389
97 | 2596563.1837 | 1227194.0339 | 2596549.5165 | 1227186.8395
98 | 2596499.3663 | 1227202.1641 | 2596500.8056 | 1227200.0389
99 | 2596563.1837 | 1227194.0339 | 2596564.4299 | 1227194.69
100 | 2596499.3663 | 1227202.1641 | 2596496.428 | 1227206.5028
101 | 2596583.1503 | 1227204.5445 | 2596564.4299 | 1227194.69
102 | 2596317.1994 | 1227327.8002 | 2596318.983 | 1227329.6231
103 | 2596311.4759 | 1227325.3452 | 2596311.9011 | 1227325.5022 | 2596317.1994 | 1227327.8002 | 2596317.1994 | 1227327.8002
104 | 2596326.7004 | 1227337.511 | 2596318.983 | 1227329.6231
105 | 2596311.4759 | 1227325.3452 | 2596308.1752 | 1227324.1263
106 | 2596308.1752 | 1227324.1263 | 2596302.3096 | 1227321.9604
107 | 2596321.1322 | 1227101.5436 | 2596321.4123 | 1227101.0073
108 | 2596483.9704 | 1227329.3465 | 2596476.7994 | 1227324.6549
109 | 2596483.9704 | 1227329.3465 | 2596505.194 | 1227343.232
110 | 2596476.7994 | 1227324.6549 | 2596474.2133 | 1227322.9629
111 | 2596465.7192 | 1227317.4057 | 2596474.2133 | 1227322.9629
112 | 2596453.412 | 1227309.3538 | 2596465.7192 | 1227317.4057
113 | 2596435.9016 | 1227297.8976 | 2596453.412 | 1227309.3538
114 | 2596435.9016 | 1227297.8976 | 2596439.7998 | 1227290.8022 | 2596441.8168 | 1227287.6763
115 | 2596241.7685 | 1227336.3756 | 2596222.5666 | 1227324.931
116 | 2596206.9445 | 1227318.2096 | 2596221.5827 | 1227326.7496 | 2596222.4832 | 1227324.8813 | 2596222.5666 | 1227324.931
117 | 2596241.7685 | 1227336.3756 | 2596237.2036 | 1227343.3048 | 2596228.68 | 1227356.2662
118 | 2596241.7685 | 1227336.3756 | 2596254.4281 | 1227343.9163 | 2596265.1023 | 1227327.6443
119 | 2596206.9445 | 1227318.2096 | 2596198.0552 | 1227332.0499
120 | 2596206.9445 | 1227318.2096 | 2596209.8969 | 1227313.605 | 2596211.9889 | 1227310.508
121 | 2596228.68 | 1227356.2662 | 2596227.791 | 1227357.618
122 | 2596279.1076 | 1227330.248 | 2596269.2834 | 1227324.8845 | 2596267.1941 | 1227328.1655 | 2596265.1023 | 1227327.6443
123 | 2596196.7188 | 1227334.1307 | 2596198.0552 | 1227332.0499
124 | 2596224.8259 | 1227291.5045 | 2596211.9889 | 1227310.508
125 | 2596191.0207 | 1227278.8857 | 2596211.4022 | 1227286.2991 | 2596224.8259 | 1227291.5045
126 | 2596191.0207 | 1227278.8857 | 2596176.9974 | 1227298.54
127 | 2596414.5273 | 1227304.8279 | 2596408.832 | 1227301.9308
128 | 2596359.3158 | 1227276.7429 | 2596382.4241 | 1227288.4977
129 | 2596359.3158 | 1227276.7429 | 2596354.3606 | 1227274.2224

## bus_geodata
| x | y | coords
0 | 2596332.8343 | 1227233.0814
1 | 2596335.5647 | 1227228.4472
2 | 2596323.0073 | 1227249.7603
3 | 2596345.6825 | 1227211.2748
4 | 2596318.5022 | 1227255.0009
5 | 2596356.7993 | 1227192.4067
6 | 2596294.8013 | 1227259.0517
7 | 2596330.4982 | 1227262.084
8 | 2596380.7016 | 1227207.0004
9 | 2596342.0527 | 1227182.0557
10 | 2596283.3727 | 1227282.9689
11 | 2596275.475 | 1227260.7765
12 | 2596345.2358 | 1227269.5808
13 | 2596475.003 | 1227258.2681
14 | 2596477.8855 | 1227259.5899
15 | 2596464.602 | 1227253.4985
16 | 2596486.1846 | 1227263.3955
17 | 2596470.7487 | 1227244.4208
18 | 2596462.3002 | 1227256.5016
19 | 2596487.1841 | 1227263.8539
20 | 2596478.4711 | 1227233.0179
21 | 2596451.5584 | 1227272.6921
22 | 2596449.7381 | 1227248.7672
23 | 2596495.7242 | 1227267.5026
24 | 2596487.6802 | 1227219.4198
25 | 2596444.2156 | 1227283.9587
26 | 2596438.3038 | 1227241.6952
27 | 2596411.7829 | 1227153.0278
28 | 2596405.6155 | 1227163.7374
29 | 2596422.2479 | 1227134.7975
30 | 2596402.0488 | 1227169.9311
31 | 2596392.3031 | 1227186.8545
32 | 2596224.424 | 1227171.7579
33 | 2596224.4138 | 1227171.7797
34 | 2596257.838 | 1227119.5598
35 | 2596224.0487 | 1227172.5581
36 | 2596278.5921 | 1227135.3497
37 | 2596293.3305 | 1227146.5628
38 | 2596296.3984 | 1227148.8969
39 | 2596410.5307 | 1227224.5179
40 | 2596414.2496 | 1227226.818
41 | 2596393.9299 | 1227214.6368
42 | 2596420.5172 | 1227230.6944
43 | 2596384.4718 | 1227209.1766
44 | 2596423.9747 | 1227232.8328
45 | 2596436.9629 | 1227240.8659
46 | 2596502.8174 | 1227270.4293
47 | 2596509.2771 | 1227273.0946
48 | 2596522.0795 | 1227277.8017
49 | 2596268.2118 | 1227259.9263
50 | 2596254.2346 | 1227254.8409
51 | 2596253.7536 | 1227254.6574
52 | 2596263.126 | 1227306.3553
53 | 2596235.835 | 1227247.8241
54 | 2596283.1974 | 1227314.903
55 | 2596371.7183 | 1227398.5463
56 | 2596405.7443 | 1227368.8374
57 | 2596366.1833 | 1227402.8136
58 | 2596422.1194 | 1227350.2036
59 | 2596358.3582 | 1227407.021
60 | 2596393.2212 | 1227425.4991
61 | 2596437.7431 | 1227355.5919
62 | 2596425.8983 | 1227326.7209
63 | 2596343.9205 | 1227414.4406
64 | 2596418.2234 | 1227430.3937
65 | 2596448.26 | 1227361.1612
66 | 2596430.1971 | 1227312.7988
67 | 2596326.8032 | 1227422.6855
68 | 2596464.8599 | 1227437.3902
69 | 2596487.7366 | 1227219.3365
70 | 2596491.3366 | 1227214.0207
71 | 2596493.6327 | 1227210.6304
72 | 2596527.7696 | 1227279.6079
73 | 2596231.4696 | 1227246.1593
74 | 2596460.6468 | 1227499.465
75 | 2596306.257 | 1227156.0607
76 | 2596309.0555 | 1227158.0943
77 | 2596313.4905 | 1227161.317
78 | 2596301.9504 | 1227138.2675
79 | 2596320.7157 | 1227166.5672
80 | 2596303.4293 | 1227135.4362
81 | 2596326.9681 | 1227171.1106
82 | 2596320.3606 | 1227103.0208
83 | 2596534.0616 | 1227178.7039
84 | 2596537.945 | 1227180.7482
85 | 2596520.197 | 1227171.4055
86 | 2596549.5165 | 1227186.8395
87 | 2596500.8056 | 1227200.0389
88 | 2596563.1837 | 1227194.0339
89 | 2596499.3663 | 1227202.1641
90 | 2596564.4299 | 1227194.69
91 | 2596496.428 | 1227206.5028
92 | 2596317.1994 | 1227327.8002
93 | 2596318.983 | 1227329.6231
94 | 2596311.4759 | 1227325.3452
95 | 2596326.7004 | 1227337.511
96 | 2596308.1752 | 1227324.1263
97 | 2596302.3096 | 1227321.9604
98 | 2596332.603 | 1227175.2052
99 | 2596321.1322 | 1227101.5436
100 | 2596321.4123 | 1227101.0073
101 | 2596483.9704 | 1227329.3465
102 | 2596476.7994 | 1227324.6549
103 | 2596505.194 | 1227343.232
104 | 2596474.2133 | 1227322.9629
105 | 2596465.7192 | 1227317.4057
106 | 2596453.412 | 1227309.3538
107 | 2596435.9016 | 1227297.8976
108 | 2596222.5666 | 1227324.931
109 | 2596241.7685 | 1227336.3756
110 | 2596206.9445 | 1227318.2096
111 | 2596228.68 | 1227356.2662
112 | 2596265.1023 | 1227327.6443
113 | 2596198.0552 | 1227332.0499
114 | 2596211.9889 | 1227310.508
115 | 2596227.791 | 1227357.618
116 | 2596279.1076 | 1227330.248
117 | 2596196.7188 | 1227334.1307
118 | 2596224.8259 | 1227291.5045
119 | 2596191.0207 | 1227278.8857
120 | 2596441.8168 | 1227287.6763
121 | 2596414.5273 | 1227304.8279
122 | 2596210.2685 | 1227238.0742
123 | 2596408.832 | 1227301.9308
124 | 2596382.4241 | 1227288.4977
125 | 2596359.3158 | 1227276.7429
126 | 2596354.3606 | 1227274.2224
127 | 2596539.5477 | 1227282.6326
128 | 2596583.1503 | 1227204.5445
129 | 2596478.5589 | 1227380.0753
130 | 2596176.9974 | 1227298.54
131 | 2596462.3002 | 1227256.5016

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98826 | -0.22451 | 0.0026591 | 0.00066644
1 | 0.98872 | -0.21574 | 0.0026117 | 0.00065455
2 | 0.98668 | -0.25524 | 0.0021949 | 0.0005501
3 | 0.99045 | -0.18237 | 0.0042234 | 0.0010585
4 | 0.98611 | -0.26612 | 0 | 0
5 | 0.99244 | -0.14419 | 0 | 0
6 | 0.98466 | -0.29423 | 0 | 0
7 | 0.98584 | -0.27155 | 0.0019525 | 0.00048934
8 | 0.99586 | -0.078876 | 0 | 0
9 | 0.99188 | -0.15511 | 0.0013713 | 0.00034368
10 | 0.98329 | -0.32084 | 0.0022677 | 0.00056833
11 | 0.98449 | -0.29755 | 0.0011241 | 0.00028173
12 | 0.98554 | -0.27738 | 0.0017311 | 0.00043386
13 | 0.99437 | -0.10782 | 0.0060283 | 0.0015108
14 | 0.99425 | -0.11 | 0.0041706 | 0.0010452
15 | 0.99484 | -0.098737 | 0 | 0
16 | 0.99396 | -0.11561 | 0.0033125 | 0.0008302
17 | 0.9938 | -0.11875 | 0.0082823 | 0.0020757
18 | 0.99509 | -0.093793 | 0 | 0
19 | 0.99393 | -0.11622 | 0.0024539 | 0.000615
20 | 0.99259 | -0.14193 | 0.0070031 | 0.0017551
21 | 0.99365 | -0.12163 | 0.0038797 | 0.00097234
22 | 0.99665 | -0.063997 | 0.0043842 | 0.0010988
23 | 0.99369 | -0.12099 | 0.0032421 | 0.00081255
24 | 0.99126 | -0.1676 | 0.0031648 | 0.00079318
25 | 0.99269 | -0.14002 | 0.0017125 | 0.00042919
26 | 0.99809 | -0.036408 | 0.0048656 | 0.0012194
27 | 0.99451 | -0.10493 | 0.0067496 | 0.0016916
28 | 0.9946 | -0.10307 | 0.0101 | 0.0025313
29 | 0.99447 | -0.10561 | 0.0018223 | 0.0004567
30 | 0.99473 | -0.10072 | 0.0066811 | 0.0016744
31 | 0.99518 | -0.091997 | 0.0067368 | 0.0016884
32 | 0.98966 | -0.19804 | 0.0027698 | 0.00069417
33 | 0.98966 | -0.19804 | 0.002469 | 0.00061879
34 | 0.99007 | -0.19022 | 0 | 0
35 | 0.98966 | -0.19807 | 0.0018129 | 0.00045437
36 | 0.99024 | -0.18695 | 0.001735 | 0.00043484
37 | 0.99038 | -0.18405 | 0.0041376 | 0.001037
38 | 0.99043 | -0.18317 | 0 | 0
39 | 0.99862 | -0.026218 | 0.0080605 | 0.0020202
40 | 0.99899 | -0.019114 | 0.0026101 | 0.00065415
41 | 0.99704 | -0.056304 | 0.008042 | 0.0020155
42 | 0.99963 | -0.0069861 | 0.0085394 | 0.0021402
43 | 0.99619 | -0.072581 | 0.0052411 | 0.0013136
44 | 1 | 0 | -0.45139 | -0.11438
45 | 0.99826 | -0.033111 | 0.0092481 | 0.0023178
46 | 0.9935 | -0.12449 | 0.0065537 | 0.0016425
47 | 0.99338 | -0.12687 | 0.0046397 | 0.0011628
48 | 0.9932 | -0.13039 | 0.0050049 | 0.0012543
49 | 0.98444 | -0.29867 | 0.0017349 | 0.0004348
50 | 0.98435 | -0.30045 | 0.0014762 | 0.00036998
51 | 0.98434 | -0.3005 | 0.001736 | 0.00043509
52 | 0.98152 | -0.35548 | 0 | 0
53 | 0.98428 | -0.30169 | 0.0010952 | 0.00027449
54 | 0.98044 | -0.37646 | 0 | 0
55 | 0.98712 | -0.24792 | 0.0033767 | 0.00084628
56 | 0.98831 | -0.22481 | 0.0061247 | 0.001535
57 | 0.98696 | -0.25107 | 0 | 0
58 | 0.98911 | -0.20923 | 0 | 0
59 | 0.98684 | -0.25333 | 0 | 0
60 | 0.98659 | -0.25831 | 0.00057354 | 0.00014374
61 | 0.98894 | -0.21266 | 0.0027364 | 0.0006858
62 | 0.99014 | -0.18941 | 0.0021618 | 0.0005418
63 | 0.98663 | -0.25747 | 0.010884 | 0.0027277
64 | 0.98635 | -0.26305 | 0.0014134 | 0.00035424
65 | 0.98884 | -0.2145 | 0.0029464 | 0.00073843
66 | 0.99078 | -0.17692 | 0 | 0
67 | 0.98657 | -0.25862 | 0.0033671 | 0.00084387
68 | 0.98595 | -0.27077 | 0.0053569 | 0.0013426
69 | 0.99126 | -0.16775 | 0.0057684 | 0.0014457
70 | 0.99079 | -0.17679 | 0.0075495 | 0.0018921
71 | 0.99052 | -0.18201 | 0.0038077 | 0.00095429
72 | 0.99315 | -0.13141 | 0.0061113 | 0.0015316
73 | 0.98427 | -0.30189 | 0.00098743 | 0.00024747
74 | 0.98574 | -0.27478 | 0.0035928 | 0.00090045
75 | 0.99067 | -0.17856 | 0.0035562 | 0.00089127
76 | 0.99075 | -0.17703 | 0.0020293 | 0.0005086
77 | 0.99088 | -0.17441 | 0.0012534 | 0.00031412
78 | 0.99034 | -0.18496 | 0.0012332 | 0.00030907
79 | 0.99111 | -0.16995 | 0.0021106 | 0.00052896
80 | 0.99032 | -0.18536 | 0.0018662 | 0.00046771
81 | 0.99133 | -0.1658 | 0.0012188 | 0.00030547
82 | 0.99014 | -0.1888 | 0.0024971 | 0.00062582
83 | 0.98744 | -0.24165 | 0.007084 | 0.0017754
84 | 0.98727 | -0.24505 | 0.01359 | 0.003406
85 | 0.98817 | -0.22755 | 0 | 0
86 | 0.98691 | -0.25199 | 0.0068237 | 0.0017102
87 | 0.98977 | -0.19651 | 0.0086174 | 0.0021597
88 | 0.98659 | -0.25832 | 0.0092805 | 0.0023259
89 | 0.98991 | -0.19382 | 0.0032001 | 0.00080201
90 | 0.98657 | -0.25866 | 0.0061784 | 0.0015484
91 | 0.99021 | -0.18803 | 0.0057687 | 0.0014458
92 | 0.98002 | -0.38482 | 0.0022767 | 0.00057059
93 | 0.98001 | -0.38502 | 0.0023386 | 0.00058611
94 | 0.98006 | -0.38408 | 0.0022871 | 0.00057321
95 | 0.97999 | -0.38541 | 0.0019559 | 0.00049019
96 | 0.98008 | -0.38351 | 0.0040416 | 0.0010129
97 | 0.98016 | -0.38205 | 0.0022369 | 0.00056062
98 | 0.99153 | -0.16191 | 0.0013757 | 0.00034479
99 | 0.99014 | -0.18888 | 0.0015591 | 0.00039076
100 | 0.99014 | -0.18889 | 0.0012259 | 0.00030725
101 | 0.99104 | -0.17197 | 0.0014957 | 0.00037485
102 | 0.99107 | -0.1714 | 0.0020788 | 0.00052098
103 | 0.99099 | -0.17299 | 0.0022679 | 0.00056838
104 | 0.99109 | -0.17108 | 0.0027608 | 0.00069192
105 | 0.99117 | -0.16953 | 0.0036267 | 0.00090894
106 | 0.99133 | -0.16634 | 0.0024743 | 0.00062012
107 | 0.99161 | -0.16088 | 0 | 0
108 | 0.97784 | -0.42744 | 0.0069591 | 0.0017441
109 | 0.97829 | -0.4187 | 0 | 0
110 | 0.97759 | -0.43249 | 0 | 0
111 | 0.97808 | -0.42288 | 0.0063722 | 0.001597
112 | 0.97928 | -0.39935 | 0.0069732 | 0.0017476
113 | 0.97747 | -0.4349 | 0.0025463 | 0.00063816
114 | 0.97753 | -0.43357 | 0.0031934 | 0.00080034
115 | 0.97807 | -0.42298 | 0.0032686 | 0.00081918
116 | 0.97988 | -0.38743 | 0 | 0
117 | 0.97745 | -0.43515 | 0.0054859 | 0.0013749
118 | 0.97746 | -0.43494 | 0 | 0
119 | 0.97735 | -0.43708 | 0 | 0
120 | 0.99238 | -0.14595 | 0.0043148 | 0.0010814
121 | 0.99065 | -0.17954 | 0.0053743 | 0.0013469
122 | 0.98424 | -0.30245 | 0.001366 | 0.00034234
123 | 0.99063 | -0.17988 | 0.0030246 | 0.00075805
124 | 0.98496 | -0.28872 | 0.013837 | 0.003468
125 | 0.98529 | -0.28227 | 0.0022076 | 0.00055329
126 | 0.98537 | -0.28067 | 0.0018752 | 0.00046997
127 | 0.99311 | -0.13217 | 0.0035215 | 0.00088257
128 | 0.98643 | -0.26147 | 0.0074104 | 0.0018572
129 | 0.98866 | -0.21815 | 0.0057158 | 0.0014325
130 | 0.97728 | -0.43852 | 0.003265 | 0.00081829
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.092038 | -0.02329 | 0.092077 | 0.023315 | 3.8781e-05 | 2.4751e-05 | 0.13866 | 0.13866 | 0.13866 | 0.98826 | -0.22451 | 0.98872 | -0.21574 | 38.0934
1 | 0.089379 | 0.022624 | -0.089247 | -0.02254 | 0.00013163 | 8.3996e-05 | 0.13466 | 0.13466 | 0.13466 | 0.98826 | -0.22451 | 0.98668 | -0.25524 | 36.9935
2 | -0.094689 | -0.023969 | 0.094841 | 0.024066 | 0.00015197 | 9.7003e-05 | 0.14259 | 0.14259 | 0.14259 | 0.98872 | -0.21574 | 0.99045 | -0.18237 | 39.1733
3 | 0.087052 | 0.02199 | -0.087007 | -0.021961 | 4.5347e-05 | 2.8933e-05 | 0.13135 | 0.13135 | 0.13135 | 0.98668 | -0.25524 | 0.98611 | -0.26612 | 36.0841
4 | -0.099064 | -0.025125 | 0.099246 | 0.025241 | 0.00018216 | 0.0001163 | 0.14894 | 0.14894 | 0.14894 | 0.99045 | -0.18237 | 0.99244 | -0.14419 | 40.9164
5 | 0.065384 | 0.016535 | -0.065296 | -0.016479 | 8.8046e-05 | 5.6042e-05 | 0.098715 | 0.098715 | 0.098715 | 0.98611 | -0.26612 | 0.98466 | -0.29423 | 27.1196
6 | 0.021623 | 0.0054259 | -0.021618 | -0.0054225 | 5.5994e-06 | 3.4048e-06 | 0.032631 | 0.032631 | 0.032631 | 0.98611 | -0.26612 | 0.98584 | -0.27155 | 8.9646
7 | -0.13353 | -0.033855 | 0.13395 | 0.034124 | 0.00042066 | 0.00026886 | 0.20035 | 0.20035 | 0.20035 | 0.99244 | -0.14419 | 0.99586 | -0.078876 | 55.0406
8 | 0.034285 | 0.0086141 | -0.034267 | -0.008603 | 1.7858e-05 | 1.1197e-05 | 0.051412 | 0.051412 | 0.051412 | 0.99244 | -0.14419 | 0.99188 | -0.15511 | 14.1243
9 | 0.055773 | 0.014092 | -0.055702 | -0.014047 | 7.1042e-05 | 4.5128e-05 | 0.084325 | 0.084325 | 0.084325 | 0.98466 | -0.29423 | 0.98329 | -0.32084 | 23.1662
10 | 0.0095226 | 0.0023866 | -0.0095211 | -0.0023858 | 1.5068e-06 | 7.1759e-07 | 0.014391 | 0.014391 | 0.014391 | 0.98466 | -0.29423 | 0.98449 | -0.29755 | 3.9535
11 | 0.019665 | 0.0049331 | -0.01966 | -0.0049299 | 5.4636e-06 | 3.2859e-06 | 0.029684 | 0.029684 | 0.029684 | 0.98584 | -0.27155 | 0.98554 | -0.27738 | 8.155
12 | 0.032123 | 0.0080628 | -0.032103 | -0.0080503 | 2.0088e-05 | 1.2554e-05 | 0.048003 | 0.048003 | 0.048003 | 0.99586 | -0.078876 | 0.99518 | -0.091997 | 13.1877
13 | -0.16607 | -0.042187 | 0.16612 | 0.042219 | 5.0343e-05 | 3.2106e-05 | 0.24835 | 0.24835 | 0.24835 | 0.99586 | -0.078876 | 0.99619 | -0.072581 | 34.114
14 | 0.032896 | 0.0082593 | -0.032885 | -0.0082526 | 1.0662e-05 | 6.673e-06 | 0.049355 | 0.049355 | 0.049355 | 0.99188 | -0.15511 | 0.99153 | -0.16191 | 13.5591
15 | 0.053435 | 0.013479 | -0.053346 | -0.013423 | 8.8468e-05 | 5.6163e-05 | 0.080893 | 0.080894 | 0.080894 | 0.98329 | -0.32084 | 0.98152 | -0.35548 | 22.2235
16 | 0.008397 | 0.0021041 | -0.0083966 | -0.0021039 | 4.4567e-07 | 1.9142e-07 | 0.012692 | 0.012692 | 0.012692 | 0.98449 | -0.29755 | 0.98444 | -0.29867 | 3.4867
17 | 0.017928 | 0.004496 | -0.017926 | -0.0044943 | 2.8133e-06 | 1.6701e-06 | 0.02707 | 0.02707 | 0.02707 | 0.98554 | -0.27738 | 0.98537 | -0.28067 | 7.4369
18 | 0.039041 | 0.0097955 | -0.039037 | -0.0097929 | 4.0593e-06 | 2.5568e-06 | 0.058426 | 0.058426 | 0.058426 | 0.99437 | -0.10782 | 0.99425 | -0.11 | 16.0511
19 | -0.045069 | -0.011306 | 0.045088 | 0.011319 | 1.952e-05 | 1.2344e-05 | 0.067447 | 0.067447 | 0.067447 | 0.99437 | -0.10782 | 0.99484 | -0.098737 | 18.5294
20 | 0.034866 | 0.0087477 | -0.034857 | -0.0087418 | 9.3236e-06 | 5.8487e-06 | 0.052184 | 0.052184 | 0.052184 | 0.99425 | -0.11 | 0.99396 | -0.11561 | 14.3363
21 | 0.10407 | 0.026294 | -0.10397 | -0.02623 | 9.9718e-05 | 6.3677e-05 | 0.15574 | 0.15574 | 0.15574 | 0.99484 | -0.098737 | 0.9938 | -0.11875 | 42.7864
22 | -0.14916 | -0.037612 | 0.1492 | 0.037635 | 3.5305e-05 | 2.2497e-05 | 0.22319 | 0.22319 | 0.22319 | 0.99484 | -0.098737 | 0.99509 | -0.093793 | 30.6579
23 | 0.031544 | 0.0079116 | -0.031543 | -0.007911 | 9.1969e-07 | 5.7435e-07 | 0.047225 | 0.047225 | 0.047225 | 0.99396 | -0.11561 | 0.99393 | -0.11622 | 12.974
24 | 0.095692 | 0.024154 | -0.095586 | -0.024087 | 0.00010611 | 6.7733e-05 | 0.14334 | 0.14334 | 0.14334 | 0.9938 | -0.11875 | 0.99259 | -0.14193 | 39.3796
25 | 0.081712 | 0.020648 | -0.081603 | -0.020579 | 0.00010889 | 6.9437e-05 | 0.12225 | 0.12225 | 0.12225 | 0.99509 | -0.093793 | 0.99365 | -0.12163 | 33.5848
26 | -0.23091 | -0.058283 | 0.23124 | 0.058494 | 0.00033007 | 0.00021086 | 0.34544 | 0.34544 | 0.34544 | 0.99509 | -0.093793 | 0.99665 | -0.063997 | 47.4503
27 | 0.029089 | 0.007296 | -0.029083 | -0.0072919 | 6.6066e-06 | 4.1079e-06 | 0.043552 | 0.043552 | 0.043552 | 0.99393 | -0.11622 | 0.99369 | -0.12099 | 11.9647
28 | 0.088583 | 0.022331 | -0.088475 | -0.022262 | 0.00010868 | 6.9345e-05 | 0.13284 | 0.13284 | 0.13284 | 0.99259 | -0.14193 | 0.99126 | -0.1676 | 36.4954
29 | 0.077724 | 0.019606 | -0.077655 | -0.019563 | 6.8375e-05 | 4.3586e-05 | 0.11644 | 0.11644 | 0.11644 | 0.99365 | -0.12163 | 0.99269 | -0.14002 | 31.9887
30 | -0.23562 | -0.059593 | 0.23594 | 0.059792 | 0.00031231 | 0.00019953 | 0.35198 | 0.35198 | 0.35198 | 0.99665 | -0.063997 | 0.99809 | -0.036408 | 48.3494
31 | 0.025841 | 0.0064794 | -0.025836 | -0.0064767 | 4.3088e-06 | 2.6583e-06 | 0.038697 | 0.038697 | 0.038697 | 0.99369 | -0.12099 | 0.9935 | -0.12449 | 10.631
32 | 0.08531 | 0.021469 | -0.085309 | -0.021469 | 6.1963e-07 | 3.9526e-07 | 0.12809 | 0.12809 | 0.12809 | 0.99126 | -0.1676 | 0.99126 | -0.16775 | 35.1902
33 | 0.075943 | 0.019134 | -0.075921 | -0.01912 | 2.1514e-05 | 1.3712e-05 | 0.11387 | 0.11387 | 0.11387 | 0.99269 | -0.14002 | 0.99238 | -0.14595 | 31.2835
34 | -0.2408 | -0.061012 | 0.24084 | 0.061036 | 3.815e-05 | 2.4375e-05 | 0.35924 | 0.35924 | 0.35924 | 0.99809 | -0.036408 | 0.99826 | -0.033111 | 49.3458
35 | -0.0085719 | -0.0021481 | 0.0085727 | 0.0021484 | 7.6234e-07 | 3.2752e-07 | 0.012826 | 0.012825 | 0.012826 | 0.99451 | -0.10493 | 0.9946 | -0.10307 | 3.5235
36 | 0.0018223 | 0.00045646 | -0.0018223 | -0.0004567 | 5.8601e-08 | -2.3524e-07 | 0.0027265 | 0.0027266 | 0.0027266 | 0.99451 | -0.10493 | 0.99447 | -0.10561 | 0.74907
37 | -0.018673 | -0.0046797 | 0.018675 | 0.0046809 | 2.0917e-06 | 1.2459e-06 | 0.027936 | 0.027936 | 0.027936 | 0.9946 | -0.10307 | 0.99473 | -0.10072 | 7.6747
38 | -0.025356 | -0.0063554 | 0.025366 | 0.0063619 | 1.0536e-05 | 6.4895e-06 | 0.03793 | 0.03793 | 0.03793 | 0.99473 | -0.10072 | 0.99518 | -0.091997 | 10.4204
39 | 0.004282 | 0.0010732 | -0.004282 | -0.0010732 | 3.7315e-10 | -6.6537e-11 | 0.0064382 | 0.0064382 | 0.0064382 | 0.98966 | -0.19804 | 0.98966 | -0.19804 | 1.7687
40 | -0.0070517 | -0.0017673 | 0.0070544 | 0.0017682 | 2.6274e-06 | 8.8036e-07 | 0.010603 | 0.010602 | 0.010603 | 0.98966 | -0.19804 | 0.99007 | -0.19022 | 2.9128
41 | 0.001813 | 0.00045436 | -0.0018129 | -0.00045437 | 2.3953e-09 | -9.5136e-09 | 0.0027259 | 0.0027259 | 0.0027259 | 0.98966 | -0.19804 | 0.98966 | -0.19807 | 0.74887
42 | -0.0070544 | -0.0017682 | 0.0070555 | 0.0017686 | 1.0993e-06 | 3.6812e-07 | 0.010602 | 0.010602 | 0.010602 | 0.99007 | -0.19022 | 0.99024 | -0.18695 | 2.9127
43 | -0.0087905 | -0.0022034 | 0.0087917 | 0.0022039 | 1.2118e-06 | 5.3726e-07 | 0.013209 | 0.013209 | 0.013209 | 0.99024 | -0.18695 | 0.99038 | -0.18405 | 3.629
44 | -0.012929 | -0.0032409 | 0.01293 | 0.0032412 | 5.4551e-07 | 2.9952e-07 | 0.019426 | 0.019426 | 0.019426 | 0.99038 | -0.18405 | 0.99043 | -0.18317 | 5.3368
45 | 0.0083833 | 0.002101 | -0.0083826 | -0.0021007 | 7.1338e-07 | 3.0225e-07 | 0.012595 | 0.012595 | 0.012595 | 0.99043 | -0.18317 | 0.99034 | -0.18496 | 3.4602
46 | -0.021313 | -0.0053423 | 0.021318 | 0.0053451 | 4.6857e-06 | 2.842e-06 | 0.032021 | 0.032021 | 0.032021 | 0.99043 | -0.18317 | 0.99067 | -0.17856 | 8.797
47 | -0.18786 | -0.04782 | 0.18793 | 0.047861 | 6.4365e-05 | 4.1079e-05 | 0.28019 | 0.28019 | 0.28019 | 0.99862 | -0.026218 | 0.99899 | -0.019114 | 38.4878
48 | 0.1798 | 0.0458 | -0.17954 | -0.045634 | 0.00026055 | 0.00016625 | 0.26818 | 0.26818 | 0.26818 | 0.99862 | -0.026218 | 0.99704 | -0.056304 | 36.838
49 | -0.19054 | -0.048516 | 0.19065 | 0.048587 | 0.00011151 | 7.1175e-05 | 0.28408 | 0.28408 | 0.28408 | 0.99899 | -0.019114 | 0.99963 | -0.0069861 | 39.0219
50 | 0.1715 | 0.043618 | -0.17137 | -0.043533 | 0.00013439 | 8.5722e-05 | 0.25618 | 0.25618 | 0.25618 | 0.99704 | -0.056304 | 0.99619 | -0.072581 | 35.1894
51 | -0.19919 | -0.050727 | 0.19926 | 0.05077 | 6.7142e-05 | 4.2864e-05 | 0.29679 | 0.29679 | 0.29679 | 0.99963 | -0.0069861 | 1 | 0 | 40.7679
52 | 0.25049 | 0.063608 | -0.25009 | -0.063354 | 0.00039844 | 0.0002546 | 0.37302 | 0.37302 | 0.37302 | 1 | 0 | 0.99826 | -0.033111 | 51.2393
53 | 0.019283 | 0.0048342 | -0.01928 | -0.0048329 | 2.1858e-06 | 1.3084e-06 | 0.028881 | 0.028881 | 0.028881 | 0.9935 | -0.12449 | 0.99338 | -0.12687 | 7.9343
54 | 0.014641 | 0.0036701 | -0.014638 | -0.0036687 | 2.4605e-06 | 1.3981e-06 | 0.021931 | 0.021931 | 0.021931 | 0.99338 | -0.12687 | 0.9932 | -0.13039 | 6.025
55 | 0.0096334 | 0.0024143 | -0.0096329 | -0.0024141 | 4.6684e-07 | 2.2144e-07 | 0.014433 | 0.014433 | 0.014433 | 0.9932 | -0.13039 | 0.99315 | -0.13141 | 3.965
56 | 0.0066617 | 0.0016691 | -0.0066611 | -0.0016689 | 5.6568e-07 | 1.7289e-07 | 0.010069 | 0.010069 | 0.010069 | 0.98444 | -0.29867 | 0.98435 | -0.30045 | 2.7663
57 | 0.0051849 | 0.001299 | -0.0051849 | -0.001299 | 1.1861e-08 | 1.0456e-09 | 0.0078378 | 0.0078378 | 0.0078378 | 0.98435 | -0.30045 | 0.98434 | -0.3005 | 2.1532
58 | 0.0034489 | 0.00086388 | -0.0034487 | -0.00086399 | 1.9547e-07 | -1.1866e-07 | 0.0052134 | 0.0052135 | 0.0052135 | 0.98434 | -0.3005 | 0.98428 | -0.30169 | 1.4323
59 | 0.053346 | 0.013423 | -0.053293 | -0.013389 | 5.3402e-05 | 3.3903e-05 | 0.080894 | 0.080894 | 0.080894 | 0.98152 | -0.35548 | 0.98044 | -0.37646 | 22.2235
60 | 0.0023535 | 0.00058951 | -0.0023534 | -0.00058955 | 2.2177e-08 | -4.5189e-08 | 0.0035578 | 0.0035578 | 0.0035578 | 0.98428 | -0.30169 | 0.98427 | -0.30189 | 0.97742
61 | 0.015142 | 0.0037965 | -0.015138 | -0.0037942 | 4.0353e-06 | 2.3257e-06 | 0.022982 | 0.022982 | 0.022982 | 0.98044 | -0.37646 | 0.98016 | -0.38205 | 6.3137
62 | 0.03815 | 0.0095921 | -0.03813 | -0.0095795 | 1.9981e-05 | 1.2588e-05 | 0.057912 | 0.057912 | 0.057912 | 0.98044 | -0.37646 | 0.97988 | -0.38743 | 15.9098
63 | -0.028583 | -0.0071678 | 0.028614 | 0.0071874 | 3.1517e-05 | 1.9591e-05 | 0.043088 | 0.043087 | 0.043088 | 0.98712 | -0.24792 | 0.98831 | -0.22481 | 11.8373
64 | 0.025206 | 0.0063215 | -0.025202 | -0.0063192 | 3.7841e-06 | 2.3325e-06 | 0.037998 | 0.037998 | 0.037998 | 0.98712 | -0.24792 | 0.98696 | -0.25107 | 10.4389
65 | -0.034739 | -0.0087224 | 0.034765 | 0.0087386 | 2.5837e-05 | 1.6213e-05 | 0.052309 | 0.052309 | 0.052309 | 0.98831 | -0.22481 | 0.98911 | -0.20923 | 14.3706
66 | 0.014255 | 0.0035739 | -0.014254 | -0.003573 | 1.5357e-06 | 8.6955e-07 | 0.021493 | 0.021493 | 0.021493 | 0.98696 | -0.25107 | 0.98684 | -0.25333 | 5.9046
67 | 0.010947 | 0.0027452 | -0.010943 | -0.0027433 | 3.7776e-06 | 1.9453e-06 | 0.016505 | 0.016505 | 0.016505 | 0.98696 | -0.25107 | 0.98659 | -0.25831 | 4.5343
68 | 0.011402 | 0.0028582 | -0.0114 | -0.0028573 | 1.8624e-06 | 9.7535e-07 | 0.017154 | 0.017154 | 0.017154 | 0.98911 | -0.20923 | 0.98894 | -0.21266 | 4.7125
69 | -0.046167 | -0.011597 | 0.04621 | 0.011624 | 4.3712e-05 | 2.7665e-05 | 0.069462 | 0.069462 | 0.069462 | 0.98911 | -0.20923 | 0.99014 | -0.18941 | 19.083
70 | 0.014254 | 0.003573 | -0.014251 | -0.0035715 | 2.8126e-06 | 1.5927e-06 | 0.021493 | 0.021493 | 0.021493 | 0.98684 | -0.25333 | 0.98663 | -0.25747 | 5.9046
71 | 0.010369 | 0.0025996 | -0.010367 | -0.0025984 | 2.3405e-06 | 1.1722e-06 | 0.01564 | 0.01564 | 0.01564 | 0.98659 | -0.25831 | 0.98635 | -0.26305 | 4.2967
72 | 0.0086639 | 0.0021715 | -0.0086632 | -0.0021711 | 7.5842e-07 | 3.3271e-07 | 0.013036 | 0.013036 | 0.013036 | 0.98894 | -0.21266 | 0.98884 | -0.2145 | 3.5814
73 | -0.048372 | -0.012166 | 0.048401 | 0.012185 | 2.8888e-05 | 1.8301e-05 | 0.072711 | 0.072711 | 0.072711 | 0.99014 | -0.18941 | 0.99078 | -0.17692 | 19.9756
74 | 0.0033673 | 0.00084374 | -0.0033671 | -0.00084387 | 1.8375e-07 | -1.2503e-07 | 0.0050784 | 0.0050784 | 0.0050784 | 0.98663 | -0.25747 | 0.98657 | -0.25862 | 1.3952
75 | 0.0089537 | 0.0022441 | -0.0089504 | -0.0022427 | 3.2939e-06 | 1.4939e-06 | 0.013508 | 0.013508 | 0.013508 | 0.98635 | -0.26305 | 0.98595 | -0.27077 | 3.711
76 | 0.0057168 | 0.0014327 | -0.0057158 | -0.0014325 | 9.9291e-07 | 1.7659e-07 | 0.0086026 | 0.0086028 | 0.0086028 | 0.98884 | -0.2145 | 0.98866 | -0.21815 | 2.3634
77 | 0.0084001 | 0.0021054 | -0.008399 | -0.0021049 | 1.0493e-06 | 4.4516e-07 | 0.012616 | 0.012616 | 0.012616 | 0.99078 | -0.17692 | 0.99065 | -0.17954 | 3.4659
78 | -0.056801 | -0.01429 | 0.056845 | 0.014318 | 4.3553e-05 | 2.7668e-05 | 0.085327 | 0.085327 | 0.085327 | 0.99078 | -0.17692 | 0.99161 | -0.16088 | 23.4414
79 | 0.0035935 | 0.00090009 | -0.0035928 | -0.00090045 | 6.8625e-07 | -3.5411e-07 | 0.0054232 | 0.0054235 | 0.0054235 | 0.98595 | -0.27077 | 0.98574 | -0.27478 | 1.49
80 | 0.079541 | 0.020023 | -0.079506 | -0.020001 | 3.4341e-05 | 2.1896e-05 | 0.11943 | 0.11943 | 0.11943 | 0.99126 | -0.16775 | 0.99079 | -0.17679 | 32.8113
81 | 0.071957 | 0.018109 | -0.071939 | -0.018097 | 1.7942e-05 | 1.143e-05 | 0.10809 | 0.10809 | 0.10809 | 0.99079 | -0.17679 | 0.99052 | -0.18201 | 29.6964
82 | 0.068131 | 0.017143 | -0.068112 | -0.017131 | 1.9592e-05 | 1.2475e-05 | 0.10237 | 0.10237 | 0.10237 | 0.99052 | -0.18201 | 0.99021 | -0.18803 | 28.125
83 | 0.0035216 | 0.0008825 | -0.0035215 | -0.00088257 | 1.2696e-07 | -7.6098e-08 | 0.0052764 | 0.0052764 | 0.0052764 | 0.99315 | -0.13141 | 0.99311 | -0.13217 | 1.4496
84 | 0.001366 | 0.00034208 | -0.001366 | -0.00034234 | 3.6286e-08 | -2.6516e-07 | 0.002065 | 0.0020651 | 0.0020651 | 0.98427 | -0.30189 | 0.98424 | -0.30245 | 0.56734
85 | -0.024874 | -0.0062364 | 0.024876 | 0.0062375 | 1.811e-06 | 1.1145e-06 | 0.037362 | 0.037362 | 0.037362 | 0.99067 | -0.17856 | 0.99075 | -0.17703 | 10.2644
86 | -0.026905 | -0.0067461 | 0.026909 | 0.0067482 | 3.3572e-06 | 2.078e-06 | 0.04041 | 0.04041 | 0.04041 | 0.99075 | -0.17703 | 0.99088 | -0.17441 | 11.1017
87 | -0.028162 | -0.0070623 | 0.028168 | 0.007066 | 5.9906e-06 | 3.7189e-06 | 0.042292 | 0.042292 | 0.042292 | 0.99088 | -0.17441 | 0.99111 | -0.16995 | 11.6188
88 | 0.0071494 | 0.0017917 | -0.0071492 | -0.0017916 | 1.3822e-07 | 4.7363e-08 | 0.010742 | 0.010742 | 0.010742 | 0.99034 | -0.18496 | 0.99032 | -0.18536 | 2.9511
89 | -0.030278 | -0.007595 | 0.030284 | 0.0075987 | 5.99e-06 | 3.734e-06 | 0.045461 | 0.045461 | 0.045461 | 0.99111 | -0.16995 | 0.99133 | -0.1658 | 12.4893
90 | 0.005283 | 0.0013239 | -0.0052822 | -0.0013238 | 8.6417e-07 | 8.2618e-08 | 0.007938 | 0.0079382 | 0.0079382 | 0.99032 | -0.18536 | 0.99014 | -0.1888 | 2.1808
91 | -0.031503 | -0.0079042 | 0.031509 | 0.0079078 | 5.8416e-06 | 3.6488e-06 | 0.047291 | 0.047291 | 0.047291 | 0.99133 | -0.1658 | 0.99153 | -0.16191 | 12.9919
92 | 0.0027851 | 0.00069799 | -0.0027851 | -0.000698 | 1.0948e-08 | -1.4428e-08 | 0.0041855 | 0.0041855 | 0.0041855 | 0.99014 | -0.1888 | 0.99014 | -0.18888 | 1.1499
93 | 0.043308 | 0.010863 | -0.043301 | -0.010859 | 7.01e-06 | 4.4303e-06 | 0.065266 | 0.065266 | 0.065266 | 0.98744 | -0.24165 | 0.98727 | -0.24505 | 17.9301
94 | -0.050392 | -0.012638 | 0.050426 | 0.01266 | 3.3884e-05 | 2.1485e-05 | 0.075941 | 0.075941 | 0.075941 | 0.98744 | -0.24165 | 0.98817 | -0.22755 | 20.8628
95 | 0.029711 | 0.0074526 | -0.029701 | -0.0074464 | 9.8345e-06 | 6.1269e-06 | 0.044783 | 0.044783 | 0.044783 | 0.98727 | -0.24505 | 0.98691 | -0.25199 | 12.3029
96 | -0.050426 | -0.01266 | 0.050501 | 0.012707 | 7.4787e-05 | 4.742e-05 | 0.075941 | 0.075941 | 0.075941 | 0.98817 | -0.22755 | 0.98977 | -0.19651 | 20.8628
97 | 0.022877 | 0.0057363 | -0.02287 | -0.0057321 | 6.8916e-06 | 4.2133e-06 | 0.034494 | 0.034494 | 0.034494 | 0.98691 | -0.25199 | 0.98659 | -0.25832 | 9.4765
98 | -0.059118 | -0.014867 | 0.059126 | 0.014872 | 7.6064e-06 | 4.8351e-06 | 0.088896 | 0.088896 | 0.088896 | 0.98977 | -0.19651 | 0.98991 | -0.19382 | 24.4219
99 | 0.01359 | 0.0034061 | -0.01359 | -0.003406 | 2.2188e-07 | 1.2402e-07 | 0.020497 | 0.020497 | 0.020497 | 0.98659 | -0.25832 | 0.98657 | -0.25866 | 5.6311
100 | -0.062326 | -0.015674 | 0.062343 | 0.015685 | 1.7254e-05 | 1.0975e-05 | 0.093706 | 0.093706 | 0.093706 | 0.98991 | -0.19382 | 0.99021 | -0.18803 | 25.7434
101 | 0.0074114 | 0.0018576 | -0.0074104 | -0.0018572 | 9.9134e-07 | 3.6435e-07 | 0.011178 | 0.011178 | 0.011178 | 0.98657 | -0.25866 | 0.98643 | -0.26147 | 3.071
102 | 0.0042945 | 0.0010762 | -0.0042945 | -0.0010762 | 4.0664e-08 | -6.1099e-09 | 0.0065206 | 0.0065206 | 0.0065206 | 0.98002 | -0.38482 | 0.98001 | -0.38502 | 1.7914
103 | -0.0065712 | -0.0016468 | 0.0065715 | 0.0016468 | 2.3251e-07 | 7.0325e-08 | 0.0099774 | 0.0099774 | 0.0099774 | 0.98002 | -0.38482 | 0.98006 | -0.38408 | 2.7411
104 | 0.0019559 | 0.00049007 | -0.0019559 | -0.00049019 | 3.6497e-08 | -1.1568e-07 | 0.0029697 | 0.0029698 | 0.0029698 | 0.98001 | -0.38502 | 0.97999 | -0.38541 | 0.81588
105 | -0.0088586 | -0.00222 | 0.0088588 | 0.0022202 | 2.3869e-07 | 1.0842e-07 | 0.01345 | 0.01345 | 0.01345 | 0.98006 | -0.38408 | 0.98008 | -0.38351 | 3.695
106 | -0.0129 | -0.0032331 | 0.012901 | 0.0032336 | 8.9948e-07 | 4.9686e-07 | 0.019586 | 0.019586 | 0.019586 | 0.98008 | -0.38351 | 0.98016 | -0.38205 | 5.3808
107 | 0.0012259 | 0.00030724 | -0.0012259 | -0.00030725 | 7.703e-10 | -7.2902e-09 | 0.0018424 | 0.0018424 | 0.0018424 | 0.99014 | -0.18888 | 0.99014 | -0.18889 | 0.50615
108 | -0.0037637 | -0.00094298 | 0.0037638 | 0.00094294 | 1.0262e-07 | -4.4746e-08 | 0.0056509 | 0.0056509 | 0.0056509 | 0.99104 | -0.17197 | 0.99107 | -0.1714 | 1.5525
109 | 0.002268 | 0.00056813 | -0.0022679 | -0.00056838 | 1.1029e-07 | -2.562e-07 | 0.0034052 | 0.0034053 | 0.0034053 | 0.99104 | -0.17197 | 0.99099 | -0.17299 | 0.93553
110 | -0.0058425 | -0.0014639 | 0.0058426 | 0.0014639 | 8.9176e-08 | 1.7249e-08 | 0.008772 | 0.008772 | 0.008772 | 0.99107 | -0.1714 | 0.99109 | -0.17108 | 2.4099
111 | -0.0086034 | -0.0021559 | 0.008604 | 0.0021561 | 6.351e-07 | 2.7565e-07 | 0.012917 | 0.012917 | 0.012917 | 0.99109 | -0.17108 | 0.99117 | -0.16953 | 3.5486
112 | -0.012231 | -0.0030651 | 0.012233 | 0.0030661 | 1.8594e-06 | 1.0005e-06 | 0.018362 | 0.018362 | 0.018362 | 0.99117 | -0.16953 | 0.99133 | -0.16634 | 5.0444
113 | -0.014707 | -0.0036862 | 0.014711 | 0.0036884 | 3.824e-06 | 2.1775e-06 | 0.022076 | 0.022076 | 0.022076 | 0.99133 | -0.16634 | 0.99161 | -0.16088 | 6.0647
114 | -0.071556 | -0.018006 | 0.071607 | 0.018039 | 5.1112e-05 | 3.2559e-05 | 0.1074 | 0.1074 | 0.1074 | 0.99161 | -0.16088 | 0.99238 | -0.14595 | 29.5061
115 | -0.021455 | -0.0053777 | 0.021464 | 0.0053832 | 8.9357e-06 | 5.4383e-06 | 0.032649 | 0.032649 | 0.032649 | 0.97784 | -0.42744 | 0.97829 | -0.4187 | 8.9696
116 | 0.014496 | 0.0036336 | -0.014493 | -0.0036316 | 3.4888e-06 | 1.993e-06 | 0.022059 | 0.02206 | 0.02206 | 0.97784 | -0.42744 | 0.97759 | -0.43249 | 6.0603
117 | 0.0096427 | 0.0024171 | -0.0096408 | -0.0024162 | 1.9208e-06 | 9.3044e-07 | 0.014667 | 0.014667 | 0.014667 | 0.97829 | -0.4187 | 0.97808 | -0.42288 | 4.0294
118 | -0.031107 | -0.0078003 | 0.031136 | 0.0078182 | 2.871e-05 | 1.7944e-05 | 0.047316 | 0.047316 | 0.047316 | 0.97829 | -0.4187 | 0.97928 | -0.39935 | 12.999
119 | 0.0080332 | 0.0020134 | -0.0080322 | -0.0020131 | 9.2226e-07 | 3.8404e-07 | 0.012228 | 0.012228 | 0.012228 | 0.97759 | -0.43249 | 0.97747 | -0.4349 | 3.3592
120 | 0.0064595 | 0.0016182 | -0.0064592 | -0.0016181 | 3.3377e-07 | 9.8178e-08 | 0.009832 | 0.009832 | 0.009832 | 0.97759 | -0.43249 | 0.97753 | -0.43357 | 2.7011
121 | 0.0032686 | 0.00081917 | -0.0032686 | -0.00081918 | 1.5003e-08 | -1.0704e-08 | 0.0049727 | 0.0049727 | 0.0049727 | 0.97808 | -0.42288 | 0.97807 | -0.42298 | 1.3661
122 | -0.038109 | -0.0095659 | 0.03813 | 0.0095795 | 2.168e-05 | 1.3658e-05 | 0.057912 | 0.057912 | 0.057912 | 0.97928 | -0.39935 | 0.97988 | -0.38743 | 15.9099
123 | 0.0054859 | 0.0013749 | -0.0054859 | -0.0013749 | 6.468e-08 | 1.0397e-08 | 0.0083514 | 0.0083514 | 0.0083514 | 0.97747 | -0.4349 | 0.97745 | -0.43515 | 2.2943
124 | 0.0032658 | 0.00081775 | -0.0032656 | -0.0008179 | 2.1251e-07 | -1.5147e-07 | 0.004971 | 0.0049711 | 0.0049711 | 0.97753 | -0.43357 | 0.97746 | -0.43494 | 1.3657
125 | 0.0032656 | 0.0008179 | -0.0032653 | -0.00081814 | 3.3356e-07 | -2.3763e-07 | 0.0049711 | 0.0049713 | 0.0049713 | 0.97746 | -0.43494 | 0.97735 | -0.43708 | 1.3657
126 | 0.0032653 | 0.00081814 | -0.003265 | -0.00081829 | 2.2376e-07 | -1.5934e-07 | 0.0049713 | 0.0049714 | 0.0049714 | 0.97735 | -0.43708 | 0.97728 | -0.43852 | 1.3658
127 | 0.0030247 | 0.000758 | -0.0030246 | -0.00075805 | 4.946e-08 | -5.0613e-08 | 0.0045433 | 0.0045433 | 0.0045433 | 0.99065 | -0.17954 | 0.99063 | -0.17988 | 1.2482
128 | -0.013837 | -0.003468 | 0.013842 | 0.0034704 | 4.2487e-06 | 2.3891e-06 | 0.020905 | 0.020905 | 0.020905 | 0.98496 | -0.28872 | 0.98529 | -0.28227 | 5.7431
129 | -0.016049 | -0.0040236 | 0.01605 | 0.0040244 | 1.2248e-06 | 7.1308e-07 | 0.024239 | 0.024239 | 0.024239 | 0.98529 | -0.28227 | 0.98537 | -0.28067 | 6.659

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45393 | 0.11501

## res_load
| p_mw | q_mvar
0 | 0.0026591 | 0.00066644
1 | 0.0026117 | 0.00065455
2 | 0.0021949 | 0.0005501
3 | 0.0042234 | 0.0010585
4 | 0.0019525 | 0.00048934
5 | 0.0013713 | 0.00034368
6 | 0.0022677 | 0.00056833
7 | 0.0011241 | 0.00028173
8 | 0.0017311 | 0.00043386
9 | 0.0060283 | 0.0015108
10 | 0.0041706 | 0.0010452
11 | 0.0033125 | 0.0008302
12 | 0.0082823 | 0.0020757
13 | 0.0024539 | 0.000615
14 | 0.0070031 | 0.0017551
15 | 0.0038797 | 0.00097234
16 | 0.0043842 | 0.0010988
17 | 0.0032421 | 0.00081255
18 | 0.0031648 | 0.00079318
19 | 0.0017125 | 0.00042919
20 | 0.0048656 | 0.0012194
21 | 0.0067496 | 0.0016916
22 | 0.0101 | 0.0025313
23 | 0.0018223 | 0.0004567
24 | 0.0066811 | 0.0016744
25 | 0.0067368 | 0.0016884
26 | 0.0027698 | 0.00069417
27 | 0.002469 | 0.00061879
28 | 0.0018129 | 0.00045437
29 | 0.001735 | 0.00043484
30 | 0.0041376 | 0.001037
31 | 0.0080605 | 0.0020202
32 | 0.0026101 | 0.00065415
33 | 0.008042 | 0.0020155
34 | 0.0085394 | 0.0021402
35 | 0.0052411 | 0.0013136
36 | 0.0025318 | 0.00063452
37 | 0.0092481 | 0.0023178
38 | 0.0065537 | 0.0016425
39 | 0.0046397 | 0.0011628
40 | 0.0050049 | 0.0012543
41 | 0.0017349 | 0.0004348
42 | 0.0014762 | 0.00036998
43 | 0.001736 | 0.00043509
44 | 0.0010952 | 0.00027449
45 | 0.0033767 | 0.00084628
46 | 0.0061247 | 0.001535
47 | 0.00057354 | 0.00014374
48 | 0.0027364 | 0.0006858
49 | 0.0021618 | 0.0005418
50 | 0.010884 | 0.0027277
51 | 0.0014134 | 0.00035424
52 | 0.0029464 | 0.00073843
53 | 0.0033671 | 0.00084387
54 | 0.0053569 | 0.0013426
55 | 0.0057684 | 0.0014457
56 | 0.0075495 | 0.0018921
57 | 0.0038077 | 0.00095429
58 | 0.0061113 | 0.0015316
59 | 0.00098743 | 0.00024747
60 | 0.0035928 | 0.00090045
61 | 0.0035562 | 0.00089127
62 | 0.0020293 | 0.0005086
63 | 0.0012534 | 0.00031412
64 | 0.0012332 | 0.00030907
65 | 0.0021106 | 0.00052896
66 | 0.0018662 | 0.00046771
67 | 0.0012188 | 0.00030547
68 | 0.0024971 | 0.00062582
69 | 0.007084 | 0.0017754
70 | 0.01359 | 0.003406
71 | 0.0068237 | 0.0017102
72 | 0.0086174 | 0.0021597
73 | 0.0092805 | 0.0023259
74 | 0.0032001 | 0.00080201
75 | 0.0061784 | 0.0015484
76 | 0.0057687 | 0.0014458
77 | 0.0022767 | 0.00057059
78 | 0.0023386 | 0.00058611
79 | 0.0022871 | 0.00057321
80 | 0.0019559 | 0.00049019
81 | 0.0040416 | 0.0010129
82 | 0.0022369 | 0.00056062
83 | 0.0013757 | 0.00034479
84 | 0.0015591 | 0.00039076
85 | 0.0012259 | 0.00030725
86 | 0.0014957 | 0.00037485
87 | 0.0020788 | 0.00052098
88 | 0.0022679 | 0.00056838
89 | 0.0027608 | 0.00069192
90 | 0.0036267 | 0.00090894
91 | 0.0024743 | 0.00062012
92 | 0.0069591 | 0.0017441
93 | 0.0063722 | 0.001597
94 | 0.0069732 | 0.0017476
95 | 0.0025463 | 0.00063816
96 | 0.0031934 | 0.00080034
97 | 0.0032686 | 0.00081918
98 | 0.0054859 | 0.0013749
99 | 0.0043148 | 0.0010814
100 | 0.0053743 | 0.0013469
101 | 0.001366 | 0.00034234
102 | 0.0030246 | 0.00075805
103 | 0.013837 | 0.003468
104 | 0.0022076 | 0.00055329
105 | 0.0018752 | 0.00046997
106 | 0.0035215 | 0.00088257
107 | 0.0074104 | 0.0018572
108 | 0.0057158 | 0.0014325
109 | 0.003265 | 0.00081829

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1