## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2550-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2550-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2550-1_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2550-1_0_5_node_59 | 0.4 | n |  | TRUE
4 | bus_LV_2550-1_0_5_node_60 | 0.4 | n |  | TRUE
5 | bus_LV_2550-1_0_5_node_109 | 0.4 | n |  | TRUE
6 | bus_LV_2550-1_0_5_node_108 | 0.4 | n |  | TRUE
7 | bus_LV_2550-1_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2550-1_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2550-1_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2550-1_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2550-1_0_5_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2550-1_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2550-1_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2550-1_0_5_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_2550-1_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2550-1_0_5_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_2550-1_0_5_node_121 | 0.4 | n |  | TRUE
18 | bus_LV_2550-1_0_5_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_2550-1_0_5_node_79 | 0.4 | n |  | TRUE
20 | bus_LV_2550-1_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_2550-1_0_5_node_101 | 0.4 | n |  | TRUE
22 | bus_LV_2550-1_0_5_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_2550-1_0_5_node_140 | 0.4 | n |  | TRUE
24 | bus_LV_2550-1_0_5_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_2550-1_0_5_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_2550-1_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2550-1_0_5_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2550-1_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2550-1_0_5_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2550-1_0_5_node_105 | 0.4 | n |  | TRUE
31 | bus_LV_2550-1_0_5_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_2550-1_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2550-1_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2550-1_0_5_node_72 | 0.4 | n |  | TRUE
35 | bus_LV_2550-1_0_5_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_2550-1_0_5_node_137 | 0.4 | n |  | TRUE
37 | bus_LV_2550-1_0_5_node_149 | 0.4 | n |  | TRUE
38 | bus_LV_2550-1_0_5_node_157 | 0.4 | n |  | TRUE
39 | bus_LV_2550-1_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2550-1_0_5_node_135 | 0.4 | n |  | TRUE
41 | bus_LV_2550-1_0_5_node_123 | 0.4 | n |  | TRUE
42 | bus_LV_2550-1_0_5_node_134 | 0.4 | n |  | TRUE
43 | bus_LV_2550-1_0_5_node_138 | 0.4 | n |  | TRUE
44 | bus_LV_2550-1_0_5_node_94 | 0.4 | n |  | TRUE
45 | bus_LV_2550-1_0_5_node_58 | 0.4 | n |  | TRUE
46 | bus_LV_2550-1_0_5_node_151 | 0.4 | n |  | TRUE
47 | bus_LV_2550-1_0_5_node_13 | 0.4 | n |  | TRUE
48 | bus_LV_2550-1_0_5_node_14 | 0.4 | n |  | TRUE
49 | bus_LV_2550-1_0_5_node_15 | 0.4 | n |  | TRUE
50 | bus_LV_2550-1_0_5_node_16 | 0.4 | n |  | TRUE
51 | bus_LV_2550-1_0_5_node_17 | 0.4 | n |  | TRUE
52 | bus_LV_2550-1_0_5_node_18 | 0.4 | n |  | TRUE
53 | bus_LV_2550-1_0_5_node_122 | 0.4 | n |  | TRUE
54 | bus_LV_2550-1_0_5_node_71 | 0.4 | n |  | TRUE
55 | bus_LV_2550-1_0_5_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_2550-1_0_5_node_84 | 0.4 | n |  | TRUE
57 | bus_LV_2550-1_0_5_node_20 | 0.4 | n |  | TRUE
58 | bus_LV_2550-1_0_5_node_22 | 0.4 | n |  | TRUE
59 | bus_LV_2550-1_0_5_node_99 | 0.4 | n |  | TRUE
60 | bus_LV_2550-1_0_5_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_2550-1_0_5_node_156 | 0.4 | n |  | TRUE
62 | bus_LV_2550-1_0_5_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_2550-1_0_5_node_86 | 0.4 | n |  | TRUE
64 | bus_LV_2550-1_0_5_node_152 | 0.4 | n |  | TRUE
65 | bus_LV_2550-1_0_5_node_141 | 0.4 | n |  | TRUE
66 | bus_LV_2550-1_0_5_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_2550-1_0_5_node_32 | 0.4 | n |  | TRUE
68 | bus_LV_2550-1_0_5_node_33 | 0.4 | n |  | TRUE
69 | bus_LV_2550-1_0_5_node_34 | 0.4 | n |  | TRUE
70 | bus_LV_2550-1_0_5_node_36 | 0.4 | n |  | TRUE
71 | bus_LV_2550-1_0_5_node_35 | 0.4 | n |  | TRUE
72 | bus_LV_2550-1_0_5_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_2550-1_0_5_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_2550-1_0_5_node_80 | 0.4 | n |  | TRUE
75 | bus_LV_2550-1_0_5_node_127 | 0.4 | n |  | TRUE
76 | bus_LV_2550-1_0_5_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_2550-1_0_5_node_81 | 0.4 | n |  | TRUE
78 | bus_LV_2550-1_0_5_node_82 | 0.4 | n |  | TRUE
79 | bus_LV_2550-1_0_5_node_37 | 0.4 | n |  | TRUE
80 | bus_LV_2550-1_0_5_node_39 | 0.4 | n |  | TRUE
81 | bus_LV_2550-1_0_5_node_41 | 0.4 | n |  | TRUE
82 | bus_LV_2550-1_0_5_node_45 | 0.4 | n |  | TRUE
83 | bus_LV_2550-1_0_5_node_46 | 0.4 | n |  | TRUE
84 | bus_LV_2550-1_0_5_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_2550-1_0_5_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_2550-1_0_5_node_91 | 0.4 | n |  | TRUE
87 | bus_LV_2550-1_0_5_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_2550-1_0_5_node_49 | 0.4 | n |  | TRUE
89 | bus_LV_2550-1_0_5_node_50 | 0.4 | n |  | TRUE
90 | bus_LV_2550-1_0_5_node_51 | 0.4 | n |  | TRUE
91 | bus_LV_2550-1_0_5_node_52 | 0.4 | n |  | TRUE
92 | bus_LV_2550-1_0_5_node_53 | 0.4 | n |  | TRUE
93 | bus_LV_2550-1_0_5_node_54 | 0.4 | n |  | TRUE
94 | bus_LV_2550-1_0_5_node_55 | 0.4 | n |  | TRUE
95 | bus_LV_2550-1_0_5_node_95 | 0.4 | n |  | TRUE
96 | bus_LV_2550-1_0_5_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_2550-1_0_5_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_2550-1_0_5_node_124 | 0.4 | n |  | TRUE
99 | bus_LV_2550-1_0_5_node_144 | 0.4 | n |  | TRUE
100 | bus_LV_2550-1_0_5_node_118 | 0.4 | n |  | TRUE
101 | bus_LV_2550-1_0_5_node_61 | 0.4 | n |  | TRUE
102 | bus_LV_2550-1_0_5_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_2550-1_0_5_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_2550-1_0_5_node_64 | 0.4 | n |  | TRUE
105 | bus_LV_2550-1_0_5_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_2550-1_0_5_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_2550-1_0_5_node_65 | 0.4 | n |  | TRUE
108 | bus_LV_2550-1_0_5_node_66 | 0.4 | n |  | TRUE
109 | bus_LV_2550-1_0_5_node_68 | 0.4 | n |  | TRUE
110 | bus_LV_2550-1_0_5_node_70 | 0.4 | n |  | TRUE
111 | bus_LV_2550-1_0_5_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2550-1_0_5_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_2550-1_0_5_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_2550-1_0_5_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_2550-1_0_5_node_78 | 0.4 | n |  | TRUE
116 | bus_LV_2550-1_0_5_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_2550-1_0_5_node_76 | 0.4 | n |  | TRUE
118 | bus_LV_2550-1_0_5_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_2550-1_0_5_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_2550-1_0_5_node_73 | 0.4 | n |  | TRUE
121 | bus_LV_2550-1_0_5_node_77 | 0.4 | n |  | TRUE
122 | bus_LV_2550-1_0_5_node_104 | 0.4 | n |  | TRUE
123 | bus_LV_2550-1_0_5_node_139 | 0.4 | n |  | TRUE
124 | bus_LV_2550-1_0_5_node_136 | 0.4 | n |  | TRUE
125 | bus_LV_2550-1_0_5_node_85 | 0.4 | n |  | TRUE
126 | bus_LV_2550-1_0_5_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_2550-1_0_5_node_87 | 0.4 | n |  | TRUE
128 | bus_LV_2550-1_0_5_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_2550-1_0_5_node_92 | 0.4 | n |  | TRUE
130 | bus_LV_2550-1_0_5_node_116 | 0.4 | n |  | TRUE
131 | bus_LV_2550-1_0_5_node_142 | 0.4 | n |  | TRUE
132 | bus_LV_2550-1_0_5_node_158 | 0.4 | n |  | TRUE
133 | bus_LV_2550-1_0_5_node_113 | 0.4 | n |  | TRUE
134 | bus_LV_2550-1_0_5_node_107 | 0.4 | n |  | TRUE
135 | bus_LV_2550-1_0_5_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_2550-1_0_5_node_143 | 0.4 | n |  | TRUE
137 | bus_LV_2550-1_0_5_node_119 | 0.4 | n |  | TRUE
138 | bus_LV_2550-1_0_5_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_2550-1_0_5_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_2550-1_0_5_node_128 | 0.4 | n |  | TRUE
141 | bus_LV_2550-1_0_5_node_160 | 0.4 | n |  | TRUE
142 | bus_LV_2550-1_0_5_node_129 | 0.4 | n |  | TRUE
143 | bus_LV_2550-1_0_5_node_159 | 0.4 | n |  | TRUE
144 | bus_LV_2550-1_0_5_node_147 | 0.4 | n |  | TRUE
145 | bus_LV_2550-1_0_5_node_148 | 0.4 | n |  | TRUE
146 | bus_LV_2550-1_0_5_node_154 | 0.4 | n |  | TRUE
147 | bus_MV_292_0_node_126 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2550-1_0_5_load_0 | 0 | 0.0025988 | 0.00065133 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2550-1_0_5_load_1 | 1 | 0.003515 | 0.00088095 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2550-1_0_5_load_3 | 2 | 0.0021515 | 0.00053921 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2550-1_0_5_load_59 | 3 | 0.0025898 | 0.00064908 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2550-1_0_5_load_109 | 5 | 0.004019 | 0.0010073 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2550-1_0_5_load_108 | 6 | 0.0075594 | 0.0018946 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2550-1_0_5_load_5 | 7 | 0.0028519 | 0.00071476 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2550-1_0_5_load_11 | 12 | 0.0063024 | 0.0015795 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2550-1_0_5_load_42 | 14 | 0.014627 | 0.003666 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2550-1_0_5_load_121 | 17 | 0.013999 | 0.0035086 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2550-1_0_5_load_40 | 18 | 0.0036923 | 0.00092537 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2550-1_0_5_load_79 | 19 | 0.006417 | 0.0016083 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2550-1_0_5_load_101 | 21 | 0.0011517 | 0.00028863 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2550-1_0_5_load_140 | 23 | 0.0037557 | 0.00094126 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2550-1_0_5_load_23 | 27 | 0.0046596 | 0.0011678 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2550-1_0_5_load_19 | 28 | 0.0093313 | 0.0023386 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2550-1_0_5_load_105 | 30 | 0.00099687 | 0.00024984 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2550-1_0_5_load_47 | 31 | 0.0081036 | 0.0020309 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2550-1_0_5_load_72 | 34 | 0.0080458 | 0.0020165 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2550-1_0_5_load_56 | 35 | 0.0014583 | 0.0003655 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2550-1_0_5_load_149 | 37 | 0.0048597 | 0.001218 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2550-1_0_5_load_38 | 39 | 0.0050339 | 0.0012616 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2550-1_0_5_load_123 | 41 | 0.029727 | 0.0074503 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2550-1_0_5_load_134 | 42 | 0.0077873 | 0.0019517 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2550-1_0_5_load_94 | 44 | 0.002604 | 0.00065262 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2550-1_0_5_load_58 | 45 | 0.002156 | 0.00054034 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2550-1_0_5_load_151 | 46 | 0.0029581 | 0.00074138 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2550-1_0_5_load_13 | 47 | 0.01324 | 0.0033183 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2550-1_0_5_load_14 | 48 | 0.028986 | 0.0072645 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2550-1_0_5_load_16 | 50 | 0.013109 | 0.0032854 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2550-1_0_5_load_17 | 51 | 0.022111 | 0.0055416 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2550-1_0_5_load_18 | 52 | 0.013059 | 0.0032728 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2550-1_0_5_load_83 | 55 | 0.0030259 | 0.00075835 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2550-1_0_5_load_84 | 56 | 0.0044181 | 0.0011073 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2550-1_0_5_load_20 | 57 | 0.0082712 | 0.002073 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2550-1_0_5_load_22 | 58 | 0.0029694 | 0.00074421 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2550-1_0_5_load_99 | 59 | 0.0081137 | 0.0020335 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2550-1_0_5_load_156 | 61 | 0.00052948 | 0.0001327 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2550-1_0_5_load_86 | 63 | 0.0028139 | 0.00070524 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2550-1_0_5_load_141 | 65 | 0.0049853 | 0.0012494 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2550-1_0_5_load_57 | 66 | 0.0020914 | 0.00052416 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2550-1_0_5_load_32 | 67 | 0.0034247 | 0.0008583 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2550-1_0_5_load_33 | 68 | 0.0046635 | 0.0011688 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2550-1_0_5_load_34 | 69 | 0.00030218 | 7.5733e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2550-1_0_5_load_36 | 70 | 0.0057139 | 0.001432 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2550-1_0_5_load_89 | 72 | 0.0022354 | 0.00056026 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2550-1_0_5_load_75 | 73 | 0.0049169 | 0.0012323 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2550-1_0_5_load_74 | 76 | 0.0029454 | 0.00073819 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2550-1_0_5_load_82 | 78 | 0.0026644 | 0.00066777 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2550-1_0_5_load_37 | 79 | 0.005572 | 0.0013965 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2550-1_0_5_load_39 | 80 | 0.0021896 | 0.00054877 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2550-1_0_5_load_41 | 81 | 0.0022689 | 0.00056864 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2550-1_0_5_load_45 | 82 | 0.012225 | 0.0030638 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2550-1_0_5_load_46 | 83 | 0.0028315 | 0.00070965 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2550-1_0_5_load_62 | 84 | 0.0045963 | 0.0011519 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2550-1_0_5_load_63 | 85 | 0.0047659 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2550-1_0_5_load_91 | 86 | 0.0030844 | 0.00077303 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2550-1_0_5_load_90 | 87 | 0.0036395 | 0.00091215 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2550-1_0_5_load_49 | 88 | 0.0012626 | 0.00031643 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2550-1_0_5_load_50 | 89 | 0.0012413 | 0.00031111 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2550-1_0_5_load_53 | 92 | 0.0080207 | 0.0020102 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2550-1_0_5_load_54 | 93 | 0.0021216 | 0.00053172 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2550-1_0_5_load_55 | 94 | 0.01257 | 0.0031504 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2550-1_0_5_load_95 | 95 | 0.010584 | 0.0026526 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2550-1_0_5_load_96 | 96 | 0.0048533 | 0.0012164 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2550-1_0_5_load_117 | 97 | 0.00085868 | 0.00021521 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2550-1_0_5_load_124 | 98 | 0.0012981 | 0.00032533 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2550-1_0_5_load_61 | 101 | 0.0019558 | 0.00049017 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2550-1_0_5_load_69 | 102 | 0.0078594 | 0.0019698 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2550-1_0_5_load_64 | 104 | 0.0034118 | 0.00085508 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2550-1_0_5_load_115 | 105 | 0.010445 | 0.0026177 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2550-1_0_5_load_65 | 107 | 0.0080922 | 0.0020281 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2550-1_0_5_load_66 | 108 | 0.0083337 | 0.0020886 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2550-1_0_5_load_70 | 110 | 0.004579 | 0.0011476 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2550-1_0_5_load_97 | 111 | 0.0050254 | 0.0012595 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2550-1_0_5_load_112 | 113 | 0.0051151 | 0.001282 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2550-1_0_5_load_114 | 114 | 0.0028533 | 0.00071511 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2550-1_0_5_load_76 | 117 | 0.0023422 | 0.00058701 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2550-1_0_5_load_102 | 118 | 0.015537 | 0.003894 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2550-1_0_5_load_111 | 119 | 0.0039347 | 0.00098612 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2550-1_0_5_load_73 | 120 | 0.0036887 | 0.00092447 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2550-1_0_5_load_77 | 121 | 0.0021 | 0.0005263 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2550-1_0_5_load_104 | 122 | 0.0031814 | 0.00079735 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2550-1_0_5_load_139 | 123 | 0.0048652 | 0.0012193 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2550-1_0_5_load_136 | 124 | 0.0098401 | 0.0024662 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2550-1_0_5_load_85 | 125 | 0.0015358 | 0.0003849 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2550-1_0_5_load_110 | 126 | 0.0044121 | 0.0011058 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2550-1_0_5_load_87 | 127 | 0.00094337 | 0.00023643 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2550-1_0_5_load_125 | 128 | 0.0018978 | 0.00047564 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2550-1_0_5_load_116 | 130 | 0.0043577 | 0.0010921 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2550-1_0_5_load_158 | 132 | 0.001082 | 0.00027117 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2550-1_0_5_load_113 | 133 | 0.0044533 | 0.0011161 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2550-1_0_5_load_107 | 134 | 0.0038909 | 0.00097516 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2550-1_0_5_load_133 | 135 | 0.013841 | 0.003469 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2550-1_0_5_load_143 | 136 | 0.0053328 | 0.0013365 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2550-1_0_5_load_119 | 137 | 0.0023375 | 0.00058584 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2550-1_0_5_load_120 | 138 | 0.0011039 | 0.00027666 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2550-1_0_5_load_126 | 139 | 0.0022314 | 0.00055923 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2550-1_0_5_load_160 | 141 | 0.0016894 | 0.0004234 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2550-1_0_5_load_159 | 143 | 0.0031025 | 0.00077756 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2550-1_0_5_load_147 | 144 | 0.0079513 | 0.0019928 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2550-1_0_5_load_148 | 145 | 0.0022933 | 0.00057476 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2550-1_0_5_load_154 | 146 | 0.0035981 | 0.00090178 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2550-1_0_5_line_0 |  | 0 | 1 | 0.030396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2550-1_0_5_line_1 |  | 1 | 2 | 0.033143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2550-1_0_5_line_2 |  | 2 | 3 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2550-1_0_5_line_3 |  | 3 | 4 | 0.014318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2550-1_0_5_line_4 |  | 4 | 101 | 0.0043978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2550-1_0_5_line_5 |  | 5 | 6 | 0.022415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2550-1_0_5_line_6 |  | 6 | 134 | 0.0087966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2550-1_0_5_line_7 |  | 7 | 8 | 0.008354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2550-1_0_5_line_8 |  | 7 | 9 | 0.0045784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2550-1_0_5_line_9 |  | 8 | 10 | 0.051274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2550-1_0_5_line_10 |  | 8 | 11 | 0.03854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2550-1_0_5_line_11 |  | 9 | 12 | 0.01344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2550-1_0_5_line_12 |  | 10 | 13 | 0.04874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2550-1_0_5_line_13 |  | 10 | 14 | 0.030182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2550-1_0_5_line_14 |  | 11 | 18 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2550-1_0_5_line_15 |  | 12 | 19 | 0.013843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2550-1_0_5_line_16 |  | 13 | 20 | 0.034226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2550-1_0_5_line_17 |  | 13 | 21 | 0.0081507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2550-1_0_5_line_18 |  | 15 | 16 | 0.0368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2550-1_0_5_line_19 |  | 15 | 17 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2550-1_0_5_line_20 |  | 16 | 35 | 0.024946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2550-1_0_5_line_21 |  | 16 | 25 | 0.032624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2550-1_0_5_line_22 |  | 18 | 39 | 0.016611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2550-1_0_5_line_23 |  | 19 | 45 | 0.008229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2550-1_0_5_line_24 |  | 20 | 46 | 0.019844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2550-1_0_5_line_25 |  | 22 | 23 | 0.01186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2550-1_0_5_line_26 |  | 22 | 24 | 0.05878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2550-1_0_5_line_27 |  | 22 | 25 | 0.029029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2550-1_0_5_line_28 |  | 23 | 65 | 0.015694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2550-1_0_5_line_29 |  | 24 | 31 | 0.0052507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2550-1_0_5_line_30 |  | 24 | 29 | 0.021964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2550-1_0_5_line_31 |  | 25 | 34 | 0.017187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2550-1_0_5_line_32 |  | 26 | 27 | 0.013635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2550-1_0_5_line_33 |  | 26 | 28 | 0.030573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2550-1_0_5_line_34 |  | 27 | 60 | 0.033409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2550-1_0_5_line_35 |  | 28 | 57 | 0.0061899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2550-1_0_5_line_36 |  | 29 | 30 | 0.097429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2550-1_0_5_line_37 |  | 31 | 32 | 0.0031322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2550-1_0_5_line_38 |  | 32 | 33 | 0.091236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2550-1_0_5_line_39 |  | 33 | 61 | 0.035223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2550-1_0_5_line_40 |  | 34 | 54 | 0.012267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2550-1_0_5_line_41 |  | 35 | 66 | 0.007145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2550-1_0_5_line_42 |  | 36 | 37 | 0.017246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2550-1_0_5_line_43 |  | 36 | 38 | 0.022557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2550-1_0_5_line_44 |  | 37 | 43 | 0.012059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2550-1_0_5_line_45 |  | 38 | 123 | 0.012229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2550-1_0_5_line_46 |  | 39 | 79 | 0.0017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2550-1_0_5_line_47 |  | 40 | 41 | 0.017906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2550-1_0_5_line_48 |  | 40 | 42 | 0.037996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2550-1_0_5_line_49 |  | 41 | 53 | 0.026026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2550-1_0_5_line_50 |  | 42 | 135 | 0.0034427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2550-1_0_5_line_51 |  | 43 | 44 | 0.028544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2550-1_0_5_line_52 |  | 44 | 129 | 0.018541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2550-1_0_5_line_53 |  | 45 | 66 | 0.0052686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2550-1_0_5_line_54 |  | 46 | 64 | 0.015718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2550-1_0_5_line_55 |  | 47 | 48 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2550-1_0_5_line_56 |  | 47 | 49 | 0.012581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2550-1_0_5_line_57 |  | 48 | 50 | 0.021453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2550-1_0_5_line_58 |  | 49 | 51 | 0.034325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2550-1_0_5_line_59 |  | 49 | 52 | 0.018869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2550-1_0_5_line_60 |  | 50 | 53 | 0.011867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2550-1_0_5_line_61 |  | 51 | 54 | 0.036299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2550-1_0_5_line_62 |  | 52 | 55 | 0.025289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2550-1_0_5_line_63 |  | 55 | 56 | 0.0048334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2550-1_0_5_line_64 |  | 56 | 125 | 0.013715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2550-1_0_5_line_65 |  | 57 | 58 | 0.029956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2550-1_0_5_line_66 |  | 58 | 59 | 0.0068446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2550-1_0_5_line_67 |  | 59 | 62 | 0.018469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2550-1_0_5_line_68 |  | 60 | 63 | 0.022753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2550-1_0_5_line_69 |  | 62 | 134 | 0.016298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2550-1_0_5_line_70 |  | 62 | 126 | 0.021472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2550-1_0_5_line_71 |  | 63 | 127 | 0.031194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2550-1_0_5_line_72 |  | 64 | 146 | 0.021315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2550-1_0_5_line_73 |  | 65 | 120 | 0.0071197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2550-1_0_5_line_74 |  | 67 | 68 | 0.0042008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2550-1_0_5_line_75 |  | 67 | 69 | 0.03275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2550-1_0_5_line_76 |  | 69 | 70 | 0.0092404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2550-1_0_5_line_77 |  | 70 | 74 | 0.038333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2550-1_0_5_line_78 |  | 71 | 72 | 0.039218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2550-1_0_5_line_79 |  | 71 | 73 | 0.038575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2550-1_0_5_line_80 |  | 72 | 75 | 0.015303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2550-1_0_5_line_81 |  | 73 | 76 | 0.0013641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2550-1_0_5_line_82 |  | 74 | 77 | 0.024912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2550-1_0_5_line_83 |  | 74 | 78 | 0.016293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2550-1_0_5_line_84 |  | 75 | 128 | 0.0062646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2550-1_0_5_line_85 |  | 76 | 117 | 0.021926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2550-1_0_5_line_86 |  | 77 | 123 | 0.018873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2550-1_0_5_line_87 |  | 77 | 124 | 0.028573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2550-1_0_5_line_88 |  | 78 | 98 | 0.0057812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2550-1_0_5_line_89 |  | 79 | 80 | 0.020035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2550-1_0_5_line_90 |  | 80 | 81 | 0.00035941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2550-1_0_5_line_91 |  | 81 | 82 | 0.0035072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2550-1_0_5_line_92 |  | 82 | 83 | 0.0039513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2550-1_0_5_line_93 |  | 83 | 86 | 0.01036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2550-1_0_5_line_94 |  | 84 | 85 | 0.019426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2550-1_0_5_line_95 |  | 85 | 104 | 0.0068155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2550-1_0_5_line_96 |  | 86 | 87 | 0.012006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2550-1_0_5_line_97 |  | 87 | 129 | 0.0059011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2550-1_0_5_line_98 |  | 88 | 89 | 0.0099958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2550-1_0_5_line_99 |  | 88 | 90 | 0.021946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2550-1_0_5_line_100 |  | 89 | 91 | 0.016929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2550-1_0_5_line_101 |  | 90 | 92 | 0.021884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2550-1_0_5_line_102 |  | 90 | 93 | 0.017977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2550-1_0_5_line_103 |  | 90 | 94 | 0.025673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2550-1_0_5_line_104 |  | 91 | 95 | 0.025699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2550-1_0_5_line_105 |  | 91 | 96 | 0.012316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2550-1_0_5_line_106 |  | 92 | 97 | 0.017523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2550-1_0_5_line_107 |  | 93 | 98 | 0.027379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_2550-1_0_5_line_108 |  | 96 | 99 | 0.024551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2550-1_0_5_line_109 |  | 97 | 100 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2550-1_0_5_line_110 |  | 99 | 132 | 0.036978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2550-1_0_5_line_111 |  | 100 | 137 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2550-1_0_5_line_112 |  | 100 | 138 | 0.010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2550-1_0_5_line_113 |  | 101 | 102 | 0.012839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2550-1_0_5_line_114 |  | 102 | 103 | 0.018959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2550-1_0_5_line_115 |  | 103 | 110 | 0.015426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2550-1_0_5_line_116 |  | 103 | 107 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2550-1_0_5_line_117 |  | 104 | 105 | 0.0099276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2550-1_0_5_line_118 |  | 105 | 106 | 0.026194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2550-1_0_5_line_119 |  | 106 | 130 | 0.02383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2550-1_0_5_line_120 |  | 106 | 129 | 0.010814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2550-1_0_5_line_121 |  | 108 | 109 | 0.017141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2550-1_0_5_line_122 |  | 109 | 111 | 0.024136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2550-1_0_5_line_123 |  | 109 | 112 | 0.027023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2550-1_0_5_line_124 |  | 110 | 113 | 0.012849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2550-1_0_5_line_125 |  | 111 | 114 | 0.0089209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2550-1_0_5_line_126 |  | 112 | 118 | 0.0018167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2550-1_0_5_line_127 |  | 113 | 119 | 0.012451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2550-1_0_5_line_128 |  | 114 | 133 | 0.019427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2550-1_0_5_line_129 |  | 115 | 116 | 0.018074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2550-1_0_5_line_130 |  | 115 | 117 | 0.010008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2550-1_0_5_line_131 |  | 116 | 122 | 0.011363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2550-1_0_5_line_132 |  | 116 | 118 | 0.025705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2550-1_0_5_line_133 |  | 117 | 121 | 0.018487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2550-1_0_5_line_134 |  | 119 | 133 | 0.0098218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2550-1_0_5_line_135 |  | 122 | 135 | 0.037813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2550-1_0_5_line_136 |  | 125 | 126 | 0.0034411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2550-1_0_5_line_137 |  | 128 | 139 | 0.020157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2550-1_0_5_line_138 |  | 130 | 131 | 0.026811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2550-1_0_5_line_139 |  | 131 | 136 | 0.020017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2550-1_0_5_line_140 |  | 136 | 144 | 0.0086235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2550-1_0_5_line_141 |  | 139 | 140 | 0.0071537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2550-1_0_5_line_142 |  | 140 | 141 | 0.015027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2550-1_0_5_line_143 |  | 141 | 142 | 0.018328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2550-1_0_5_line_144 |  | 142 | 143 | 0.0091433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2550-1_0_5_line_145 |  | 144 | 145 | 0.0053945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2550-1_0_5_trafo_123 | 0.63 MVA 20/0.4 kV | 147 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2605906.1307 | 1229705.0107 | 2605909.0974 | 1229713.0017 | 2605917.4293 | 1229733.2251
1 | 2605917.4293 | 1229733.2251 | 2605930.0543 | 1229763.869
2 | 2605938.7436 | 1229784.9597 | 2605930.0543 | 1229763.869
3 | 2605944.1977 | 1229798.1981 | 2605938.7436 | 1229784.9597
4 | 2605944.1977 | 1229798.1981 | 2605945.5906 | 1229802.3695
5 | 2605842.3917 | 1229703.7537 | 2605849.1162 | 1229725.1367
6 | 2605851.7552 | 1229733.5281 | 2605849.1162 | 1229725.1367
7 | 2605748.7854 | 1229920.0585 | 2605744.648 | 1229912.801
8 | 2605742.3805 | 1229908.8235 | 2605744.648 | 1229912.801
9 | 2605748.7854 | 1229920.0585 | 2605707.9588 | 1229928.3579 | 2605698.398 | 1229930.3056
10 | 2605748.7854 | 1229920.0585 | 2605756.8992 | 1229918.4097 | 2605768.179 | 1229916.8974 | 2605770.5181 | 1229926.2496 | 2605772.6682 | 1229935.2348
11 | 2605742.3805 | 1229908.8235 | 2605741.3862 | 1229895.4199
12 | 2605690.301 | 1229882.2471 | 2605692.1914 | 1229893.6334 | 2605693.8999 | 1229905.1975 | 2605695.5123 | 1229914.2155 | 2605698.398 | 1229930.3056
13 | 2605698.398 | 1229930.3056 | 2605703.1087 | 1229960.1173
14 | 2605772.6682 | 1229935.2348 | 2605776.4408 | 1229952.0613
15 | 2605740.3039 | 1229881.6417 | 2605740.3689 | 1229881.7054 | 2605741.3862 | 1229895.4199
16 | 2605690.301 | 1229882.2471 | 2605687.2671 | 1229862.4991 | 2605687.4775 | 1229848.2575
17 | 2605690.301 | 1229882.2471 | 2605698.382 | 1229883.3109
18 | 2605753.9214 | 1229856.092 | 2605759.4205 | 1229856.1084 | 2605762.0281 | 1229877.8349 | 2605763.1553 | 1229887.186
19 | 2605763.1553 | 1229887.186 | 2605769.0555 | 1229887.503 | 2605787.402 | 1229888.4564
20 | 2605753.9214 | 1229856.092 | 2605739.3244 | 1229857.0231 | 2605734.2093 | 1229865.9851
21 | 2605753.9214 | 1229856.092 | 2605759.4205 | 1229856.1084 | 2605758.5971 | 1229837.9635 | 2605767.5577 | 1229838.0721
22 | 2605780.0751 | 1229968.2702 | 2605776.4408 | 1229952.0613
23 | 2605740.3039 | 1229881.6417 | 2605734.4289 | 1229875.8797
24 | 2605687.4775 | 1229848.2575 | 2605706.8313 | 1229843.873
25 | 2605765.6691 | 1229809.1086 | 2605775.7493 | 1229802.859
26 | 2605717.8533 | 1229798.5012 | 2605736.3466 | 1229802.5545 | 2605741.5189 | 1229803.6823 | 2605753.4839 | 1229798.7464 | 2605755.8817 | 1229810.2555 | 2605765.6691 | 1229809.1086
27 | 2605765.6691 | 1229809.1086 | 2605767.5577 | 1229838.0721
28 | 2605775.7493 | 1229802.859 | 2605775.7493 | 1229802.859 | 2605791.4289 | 1229802.1934
29 | 2605717.8533 | 1229798.5012 | 2605712.7113 | 1229797.4378
30 | 2605712.1906 | 1229779.2177 | 2605710.1481 | 1229784.4522 | 2605710.9181 | 1229787.1767 | 2605712.1034 | 1229791.347 | 2605717.8533 | 1229798.5012
31 | 2605767.5577 | 1229838.0721 | 2605784.66 | 1229836.3694
32 | 2605764.4667 | 1229743.8131 | 2605772.633 | 1229732.8943
33 | 2605764.4667 | 1229743.8131 | 2605779.3301 | 1229749.7642 | 2605793.892 | 1229749.9334
34 | 2605792.6429 | 1229706.14 | 2605772.633 | 1229732.8943
35 | 2605793.892 | 1229749.9334 | 2605800.0815 | 1229750.0053
36 | 2605712.1906 | 1229779.2177 | 2605715.0975 | 1229773.1057 | 2605735.5242 | 1229743.4964 | 2605738.5755 | 1229736.9287 | 2605738.5976 | 1229729.7022 | 2605736.196 | 1229722.1399 | 2605726.1004 | 1229712.7024 | 2605711.292 | 1229701.6689
37 | 2605709.644 | 1229796.8035 | 2605712.7113 | 1229797.4378
38 | 2605704.4713 | 1229732.1601 | 2605707.9308 | 1229726.3711 | 2605709.3495 | 1229724.0711 | 2605714.9574 | 1229729.2572 | 2605718.4265 | 1229737.3098 | 2605717.273 | 1229747.5592 | 2605709.7244 | 1229759.9816 | 2605706.5372 | 1229766.1601 | 2605704.6628 | 1229769.7938 | 2605701.942 | 1229779.3858 | 2605704.1743 | 1229789.7163 | 2605709.644 | 1229796.8035
39 | 2605704.4713 | 1229732.1601 | 2605709.7721 | 1229733.7328 | 2605712.0089 | 1229747.2096 | 2605703.3047 | 1229760.6732
40 | 2605796.8664 | 1229835.1541 | 2605784.66 | 1229836.3694
41 | 2605734.2093 | 1229865.9851 | 2605730.6675 | 1229872.1905 | 2605730.6675 | 1229872.1905
42 | 2605848.8439 | 1229997.8012 | 2605840.1019 | 1230006.8536 | 2605840.7942 | 1230011.4793
43 | 2605848.8439 | 1229997.8012 | 2605865.7352 | 1230012.8043
44 | 2605840.7942 | 1230011.4793 | 2605831.8417 | 1230011.1371 | 2605828.7735 | 1230011.7789
45 | 2605865.7352 | 1230012.8043 | 2605877.9332 | 1230013.6729
46 | 2605780.4485 | 1229969.9356 | 2605780.0751 | 1229968.2702
47 | 2605882.231 | 1229936.5084 | 2605879.5963 | 1229918.7969
48 | 2605882.231 | 1229936.5084 | 2605920.2225 | 1229937.1052
49 | 2605875.767 | 1229893.054 | 2605879.5963 | 1229918.7969
50 | 2605923.6647 | 1229937.1593 | 2605920.2225 | 1229937.1052
51 | 2605828.7735 | 1230011.7789 | 2605819.69 | 1230013.6601 | 2605802.0984 | 1230021.5193
52 | 2605784.329 | 1230025.8333 | 2605790.7293 | 1230025.7505 | 2605798.9805 | 1230022.9123 | 2605802.0984 | 1230021.5193
53 | 2605730.6675 | 1229872.1905 | 2605734.4289 | 1229875.8797
54 | 2605721.1642 | 1229837.4942 | 2605708.1983 | 1229843.5632 | 2605706.8313 | 1229843.873
55 | 2605869.2953 | 1229848.5954 | 2605870.9674 | 1229860.0819
56 | 2605867.483 | 1229836.1454 | 2605869.2953 | 1229848.5954
57 | 2605870.9674 | 1229860.0819 | 2605874.0576 | 1229881.3109
58 | 2605867.483 | 1229836.1454 | 2605833.1617 | 1229835.6636
59 | 2605867.483 | 1229836.1454 | 2605864.8684 | 1229817.4581
60 | 2605875.767 | 1229893.054 | 2605874.0576 | 1229881.3109
61 | 2605796.8664 | 1229835.1541 | 2605833.1617 | 1229835.6636
62 | 2605861.3644 | 1229792.4134 | 2605864.8684 | 1229817.4581
63 | 2605861.3644 | 1229792.4134 | 2605860.6947 | 1229787.6267
64 | 2605860.6947 | 1229787.6267 | 2605858.7943 | 1229774.0441
65 | 2605830.0335 | 1229749.8539 | 2605813.7717 | 1229750.1643 | 2605800.0815 | 1229750.0053
66 | 2605830.0335 | 1229749.8539 | 2605836.8769 | 1229749.7233
67 | 2605855.3422 | 1229749.3708 | 2605836.8769 | 1229749.7233
68 | 2605792.6429 | 1229706.14 | 2605773.7693 | 1229693.4319
69 | 2605855.3422 | 1229749.3708 | 2605854.1987 | 1229741.2982 | 2605851.7552 | 1229733.5281
70 | 2605855.3422 | 1229749.3708 | 2605858.3175 | 1229770.6361
71 | 2605773.7693 | 1229693.4319 | 2605758.3818 | 1229683.0712 | 2605749.0364 | 1229691.587
72 | 2605721.1642 | 1229837.4942 | 2605730.1922 | 1229846.3191 | 2605738.8359 | 1229845.0711
73 | 2605791.4289 | 1229802.1934 | 2605798.5422 | 1229801.8915
74 | 2605978.4723 | 1230030.2461 | 2605982.5271 | 1230029.1483
75 | 2605947.1465 | 1230036.4995 | 2605949.8231 | 1230038.0019 | 2605978.4723 | 1230030.2461
76 | 2605939.0887 | 1230031.9766 | 2605939.0887 | 1230031.9766 | 2605947.1465 | 1230036.4995
77 | 2605901.219 | 1230037.9207 | 2605939.0887 | 1230031.9766
78 | 2606005.2986 | 1229998.6892 | 2606015.5707 | 1229982.2786 | 2606018.2016 | 1229979.7019 | 2606021.7035 | 1229977.1928 | 2606024.5447 | 1229976.3173 | 2606027.3927 | 1229976.3202 | 2606033.351 | 1229977.3495
79 | 2606005.2986 | 1229998.6892 | 2605998.1253 | 1229968.7753 | 2605998.8446 | 1229960.9958
80 | 2606048.4306 | 1229979.9546 | 2606033.351 | 1229977.3495
81 | 2605998.9702 | 1229959.6375 | 2605998.8446 | 1229960.9958
82 | 2605901.219 | 1230037.9207 | 2605896.6378 | 1230013.4349
83 | 2605901.219 | 1230037.9207 | 2605904.3407 | 1230053.9122
84 | 2606048.4306 | 1229979.9546 | 2606054.6692 | 1229980.5254
85 | 2606000.989 | 1229937.8042 | 2605998.9702 | 1229959.6375
86 | 2605896.6378 | 1230013.4349 | 2605891.38 | 1230014.6305 | 2605877.9332 | 1230013.6729
87 | 2605896.6378 | 1230013.4349 | 2605891.3806 | 1229985.3497
88 | 2605904.3407 | 1230053.9122 | 2605905.1002 | 1230057.803 | 2605905.1532 | 1230059.6192
89 | 2605783.0561 | 1229989.795 | 2605782.7612 | 1229986.3082 | 2605780.5119 | 1229970.2187 | 2605780.4485 | 1229969.9356
90 | 2605783.0864 | 1229990.1531 | 2605783.0561 | 1229989.795
91 | 2605783.3819 | 1229993.6479 | 2605783.0864 | 1229990.1531
92 | 2605783.7148 | 1229997.5851 | 2605783.3819 | 1229993.6479
93 | 2605783.7148 | 1229997.5851 | 2605784.0493 | 1230001.5408 | 2605784.1735 | 1230007.9299
94 | 2605723.2889 | 1230025.3694 | 2605741.2383 | 1230032.7988
95 | 2605741.2383 | 1230032.7988 | 2605742.2012 | 1230033.1973 | 2605747.9551 | 1230033.6706
96 | 2605784.4068 | 1230019.9333 | 2605784.1735 | 1230007.9299
97 | 2605784.329 | 1230025.8333 | 2605784.4246 | 1230020.8526 | 2605784.4068 | 1230019.9333
98 | 2605884.7985 | 1230101.751 | 2605874.8898 | 1230100.434
99 | 2605906.5081 | 1230104.9546 | 2605892.8236 | 1230102.8177 | 2605884.7985 | 1230101.751
100 | 2605858.108 | 1230098.2033 | 2605874.8898 | 1230100.434
101 | 2605906.5081 | 1230104.9546 | 2605917.4281 | 1230107.011 | 2605922.3427 | 1230108.1388 | 2605927.8386 | 1230109.7581
102 | 2605906.5081 | 1230104.9546 | 2605906.1481 | 1230093.692 | 2605905.9523 | 1230086.9865
103 | 2605906.5081 | 1230104.9546 | 2605906.3907 | 1230108.8124 | 2605905.8541 | 1230115.338 | 2605904.2378 | 1230130.518
104 | 2605858.108 | 1230098.2033 | 2605853.3612 | 1230123.4597
105 | 2605858.108 | 1230098.2033 | 2605845.8997 | 1230096.577
106 | 2605944.1668 | 1230116.0544 | 2605942.0894 | 1230115.0179 | 2605935.8205 | 1230112.4213 | 2605929.271 | 1230110.1801 | 2605927.8386 | 1230109.7581
107 | 2605905.9523 | 1230086.9865 | 2605905.1532 | 1230059.6192
108 | 2605821.5747 | 1230093.2538 | 2605837.3421 | 1230095.437 | 2605845.8997 | 1230096.577
109 | 2605961.1135 | 1230124.9204 | 2605951.7796 | 1230119.8526 | 2605944.1668 | 1230116.0544
110 | 2605821.5747 | 1230093.2538 | 2605824.0948 | 1230056.3676
111 | 2605961.1135 | 1230124.9204 | 2605959.9662 | 1230128.5548 | 2605955.6454 | 1230140.6439
112 | 2605961.1135 | 1230124.9204 | 2605970.0773 | 1230130.5487
113 | 2605945.5906 | 1229802.3695 | 2605949.6571 | 1229814.5473
114 | 2605955.6619 | 1229832.5299 | 2605949.6571 | 1229814.5473
115 | 2605955.6619 | 1229832.5299 | 2605962.1547 | 1229831.1577 | 2605970.9215 | 1229830.5161
116 | 2605955.6619 | 1229832.5299 | 2605959.4344 | 1229843.824
117 | 2605757.8493 | 1230034.4845 | 2605747.9551 | 1230033.6706
118 | 2605783.955 | 1230036.6394 | 2605771.3297 | 1230035.5933 | 2605757.8493 | 1230034.4845
119 | 2605783.955 | 1230036.6394 | 2605783.3693 | 1230047.045 | 2605782.6141 | 1230060.4318
120 | 2605783.955 | 1230036.6394 | 2605784.329 | 1230025.8333
121 | 2605974.4289 | 1229888.7152 | 2605968.9984 | 1229872.4572
122 | 2605974.4289 | 1229888.7152 | 2605991.6556 | 1229886.3532 | 2605990.8443 | 1229879.654
123 | 2605969.9001 | 1229910.8017 | 2605970.784 | 1229897.8948 | 2605976.8757 | 1229896.0331 | 2605974.4289 | 1229888.7152
124 | 2605983.7362 | 1229829.5782 | 2605983.7362 | 1229829.5782 | 2605970.9215 | 1229830.5161
125 | 2605989.7718 | 1229870.7978 | 2605990.8443 | 1229879.654
126 | 2605969.9001 | 1229910.8017 | 2605969.8003 | 1229912.1801 | 2605969.888 | 1229912.6058
127 | 2605985.3311 | 1229841.9271 | 2605983.7362 | 1229829.5782
128 | 2605989.7718 | 1229870.7978 | 2605988.6205 | 1229861.2908 | 2605987.0134 | 1229854.9521 | 2605986.5892 | 1229851.668
129 | 2605990.9601 | 1229938.2167 | 2605972.8348 | 1229937.9318
130 | 2605990.9601 | 1229938.2167 | 2606000.989 | 1229937.8042
131 | 2605972.8348 | 1229937.9318 | 2605961.4729 | 1229937.7533
132 | 2605972.8348 | 1229937.9318 | 2605973.411 | 1229929.6942 | 2605969.888 | 1229912.6058
133 | 2606000.989 | 1229937.8042 | 2606019.4187 | 1229939.2539
134 | 2605985.3311 | 1229841.9271 | 2605986.5892 | 1229851.668
135 | 2605961.4729 | 1229937.7533 | 2605923.6647 | 1229937.1593
136 | 2605858.3175 | 1229770.6361 | 2605858.7943 | 1229774.0441
137 | 2606074.7071 | 1229982.6528 | 2606070.0535 | 1229981.9331 | 2606054.6692 | 1229980.5254
138 | 2605781.1039 | 1230087.2 | 2605782.6141 | 1230060.4318
139 | 2605781.1039 | 1230087.2 | 2605780.0379 | 1230100.8961 | 2605779.3111 | 1230107.1339
140 | 2605779.3111 | 1230107.1339 | 2605778.4188 | 1230114.7917 | 2605778.3003 | 1230115.6979
141 | 2606081.7767 | 1229983.746 | 2606074.7071 | 1229982.6528
142 | 2606081.7767 | 1229983.746 | 2606096.5701 | 1229986.3852
143 | 2606114.7047 | 1229989.027 | 2606099.2628 | 1229986.8656 | 2606096.5701 | 1229986.3852
144 | 2606114.7047 | 1229989.027 | 2606123.7008 | 1229990.6613
145 | 2605778.3003 | 1230115.6979 | 2605777.6004 | 1230121.0468

## bus_geodata
| x | y | coords
0 | 2605906.1307 | 1229705.0107
1 | 2605917.4293 | 1229733.2251
2 | 2605930.0543 | 1229763.869
3 | 2605938.7436 | 1229784.9597
4 | 2605944.1977 | 1229798.1981
5 | 2605842.3917 | 1229703.7537
6 | 2605849.1162 | 1229725.1367
7 | 2605744.648 | 1229912.801
8 | 2605748.7854 | 1229920.0585
9 | 2605742.3805 | 1229908.8235
10 | 2605698.398 | 1229930.3056
11 | 2605772.6682 | 1229935.2348
12 | 2605741.3862 | 1229895.4199
13 | 2605690.301 | 1229882.2471
14 | 2605703.1087 | 1229960.1173
15 | 2605763.1553 | 1229887.186
16 | 2605753.9214 | 1229856.092
17 | 2605787.402 | 1229888.4564
18 | 2605776.4408 | 1229952.0613
19 | 2605740.3039 | 1229881.6417
20 | 2605687.4775 | 1229848.2575
21 | 2605698.382 | 1229883.3109
22 | 2605765.6691 | 1229809.1086
23 | 2605775.7493 | 1229802.859
24 | 2605717.8533 | 1229798.5012
25 | 2605767.5577 | 1229838.0721
26 | 2605764.4667 | 1229743.8131
27 | 2605772.6331 | 1229732.8943
28 | 2605793.892 | 1229749.9334
29 | 2605712.1906 | 1229779.2177
30 | 2605711.292 | 1229701.6689
31 | 2605712.7113 | 1229797.4378
32 | 2605709.644 | 1229796.8035
33 | 2605704.4713 | 1229732.1601
34 | 2605784.66 | 1229836.3694
35 | 2605734.2093 | 1229865.9851
36 | 2605848.8439 | 1229997.8012
37 | 2605840.7942 | 1230011.4793
38 | 2605865.7352 | 1230012.8043
39 | 2605780.0751 | 1229968.2702
40 | 2605882.231 | 1229936.5084
41 | 2605879.5963 | 1229918.7969
42 | 2605920.2225 | 1229937.1052
43 | 2605828.7735 | 1230011.7789
44 | 2605802.0984 | 1230021.5193
45 | 2605734.4289 | 1229875.8797
46 | 2605706.8313 | 1229843.873
47 | 2605869.2953 | 1229848.5954
48 | 2605870.9674 | 1229860.0819
49 | 2605867.483 | 1229836.1454
50 | 2605874.0576 | 1229881.3109
51 | 2605833.1617 | 1229835.6636
52 | 2605864.8684 | 1229817.4581
53 | 2605875.767 | 1229893.054
54 | 2605796.8664 | 1229835.1541
55 | 2605861.3644 | 1229792.4134
56 | 2605860.6947 | 1229787.6267
57 | 2605800.0815 | 1229750.0053
58 | 2605830.0335 | 1229749.8539
59 | 2605836.8769 | 1229749.7233
60 | 2605792.6429 | 1229706.14
61 | 2605703.3047 | 1229760.6732
62 | 2605855.3422 | 1229749.3708
63 | 2605773.7693 | 1229693.4319
64 | 2605721.1642 | 1229837.4942
65 | 2605791.4289 | 1229802.1934
66 | 2605730.6675 | 1229872.1905
67 | 2605978.4723 | 1230030.2461
68 | 2605982.5271 | 1230029.1484
69 | 2605947.1465 | 1230036.4995
70 | 2605939.0887 | 1230031.9766
71 | 2606005.2986 | 1229998.6892
72 | 2606033.351 | 1229977.3495
73 | 2605998.8446 | 1229960.9958
74 | 2605901.219 | 1230037.9207
75 | 2606048.4306 | 1229979.9546
76 | 2605998.9702 | 1229959.6375
77 | 2605896.6378 | 1230013.4349
78 | 2605904.3407 | 1230053.9122
79 | 2605780.4485 | 1229969.9356
80 | 2605783.0561 | 1229989.795
81 | 2605783.0864 | 1229990.1531
82 | 2605783.3819 | 1229993.6479
83 | 2605783.7148 | 1229997.5851
84 | 2605723.2889 | 1230025.3694
85 | 2605741.2383 | 1230032.7988
86 | 2605784.1735 | 1230007.9299
87 | 2605784.4068 | 1230019.9333
88 | 2605884.7985 | 1230101.751
89 | 2605874.8898 | 1230100.434
90 | 2605906.5081 | 1230104.9546
91 | 2605858.1079 | 1230098.2033
92 | 2605927.8386 | 1230109.7581
93 | 2605905.9523 | 1230086.9865
94 | 2605904.2378 | 1230130.518
95 | 2605853.3612 | 1230123.4597
96 | 2605845.8997 | 1230096.577
97 | 2605944.1668 | 1230116.0544
98 | 2605905.1532 | 1230059.6192
99 | 2605821.5747 | 1230093.2538
100 | 2605961.1135 | 1230124.9204
101 | 2605945.5906 | 1229802.3695
102 | 2605949.6571 | 1229814.5473
103 | 2605955.6619 | 1229832.5299
104 | 2605747.9551 | 1230033.6706
105 | 2605757.8493 | 1230034.4845
106 | 2605783.955 | 1230036.6394
107 | 2605959.4344 | 1229843.824
108 | 2605968.9984 | 1229872.4572
109 | 2605974.4289 | 1229888.7152
110 | 2605970.9215 | 1229830.5161
111 | 2605990.8443 | 1229879.654
112 | 2605969.9001 | 1229910.8017
113 | 2605983.7362 | 1229829.5782
114 | 2605989.7718 | 1229870.7978
115 | 2605990.9601 | 1229938.2167
116 | 2605972.8348 | 1229937.9318
117 | 2606000.989 | 1229937.8042
118 | 2605969.888 | 1229912.6058
119 | 2605985.3311 | 1229841.9271
120 | 2605798.5422 | 1229801.8915
121 | 2606019.4187 | 1229939.2539
122 | 2605961.4729 | 1229937.7533
123 | 2605877.9332 | 1230013.6729
124 | 2605891.3806 | 1229985.3497
125 | 2605858.7943 | 1229774.0441
126 | 2605858.3175 | 1229770.6361
127 | 2605749.0364 | 1229691.587
128 | 2606054.6692 | 1229980.5254
129 | 2605784.329 | 1230025.8333
130 | 2605782.6141 | 1230060.4318
131 | 2605781.1039 | 1230087.2
132 | 2605824.0948 | 1230056.3676
133 | 2605986.5892 | 1229851.668
134 | 2605851.7552 | 1229733.5281
135 | 2605923.6647 | 1229937.1593
136 | 2605779.3111 | 1230107.1339
137 | 2605955.6454 | 1230140.6439
138 | 2605970.0773 | 1230130.5487
139 | 2606074.7071 | 1229982.6528
140 | 2606081.7767 | 1229983.746
141 | 2606096.5701 | 1229986.3852
142 | 2606114.7047 | 1229989.027
143 | 2606123.7008 | 1229990.6613
144 | 2605778.3003 | 1230115.6979
145 | 2605777.6004 | 1230121.0468
146 | 2605738.8359 | 1229845.0711
147 | 2605882.231 | 1229936.5084

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97956 | -0.3942 | 0.0025988 | 0.00065133
1 | 0.97963 | -0.39276 | 0.003515 | 0.00088095
2 | 0.97982 | -0.38908 | 0.0021515 | 0.00053921
3 | 0.98 | -0.38566 | 0.0025898 | 0.00064908
4 | 0.98014 | -0.38284 | 0 | 0
5 | 0.98679 | -0.25295 | 0.004019 | 0.0010073
6 | 0.98687 | -0.25134 | 0.0075594 | 0.0018946
7 | 0.98076 | -0.36856 | 0.0028519 | 0.00071476
8 | 0.98039 | -0.37584 | 0 | 0
9 | 0.98097 | -0.36451 | 0 | 0
10 | 0.97933 | -0.39664 | 0 | 0
11 | 0.97886 | -0.4056 | 0 | 0
12 | 0.98158 | -0.35264 | 0.0063024 | 0.0015795
13 | 0.97898 | -0.40347 | 0 | 0
14 | 0.97892 | -0.40467 | 0.014627 | 0.003666
15 | 0.984 | -0.30575 | 0 | 0
16 | 0.98448 | -0.29648 | 0 | 0
17 | 0.98369 | -0.31187 | 0.013999 | 0.0035086
18 | 0.97818 | -0.41894 | 0.0036923 | 0.00092537
19 | 0.98223 | -0.34003 | 0.006417 | 0.0016083
20 | 0.97877 | -0.40756 | 0 | 0
21 | 0.97897 | -0.40364 | 0.0011517 | 0.00028863
22 | 0.98561 | -0.27464 | 0 | 0
23 | 0.98548 | -0.27728 | 0.0037557 | 0.00094126
24 | 0.98509 | -0.28481 | 0 | 0
25 | 0.9862 | -0.26315 | 0 | 0
26 | 0.98533 | -0.28139 | 0 | 0
27 | 0.98522 | -0.28346 | 0.0046596 | 0.0011678
28 | 0.98557 | -0.27677 | 0.0093313 | 0.0023386
29 | 0.98507 | -0.2852 | 0 | 0
30 | 0.98498 | -0.28695 | 0.00099687 | 0.00024984
31 | 0.98505 | -0.28562 | 0.0081036 | 0.0020309
32 | 0.98505 | -0.28565 | 0 | 0
33 | 0.98501 | -0.28653 | 0 | 0
34 | 0.9872 | -0.24394 | 0.0080458 | 0.0020165
35 | 0.98324 | -0.32048 | 0.0014583 | 0.0003655
36 | 0.97412 | -0.49862 | 0 | 0
37 | 0.97444 | -0.49238 | 0.0048597 | 0.001218
38 | 0.97371 | -0.50679 | 0 | 0
39 | 0.97754 | -0.43153 | 0.0050339 | 0.0012616
40 | 0.99791 | -0.039684 | 0 | 0
41 | 1 | 0 | -0.55137 | -0.1411
42 | 0.99347 | -0.12444 | 0.0077873 | 0.0019517
43 | 0.97468 | -0.48775 | 0 | 0
44 | 0.97523 | -0.47679 | 0.002604 | 0.00065262
45 | 0.98263 | -0.33231 | 0.002156 | 0.00054034
46 | 0.97865 | -0.40992 | 0.0029581 | 0.00074138
47 | 0.99338 | -0.12556 | 0.01324 | 0.0033183
48 | 0.99438 | -0.1065 | 0.028986 | 0.0072645
49 | 0.99234 | -0.14552 | 0 | 0
50 | 0.99637 | -0.068653 | 0.013109 | 0.0032854
51 | 0.99011 | -0.18813 | 0.022111 | 0.0055416
52 | 0.99097 | -0.17195 | 0.013059 | 0.0032728
53 | 0.99751 | -0.047099 | 0 | 0
54 | 0.98793 | -0.22981 | 0 | 0
55 | 0.98943 | -0.20161 | 0.0030259 | 0.00075835
56 | 0.98915 | -0.20703 | 0.0044181 | 0.0011073
57 | 0.98567 | -0.2748 | 0.0082712 | 0.002073
58 | 0.98639 | -0.26083 | 0.0029694 | 0.00074421
59 | 0.98657 | -0.25727 | 0.0081137 | 0.0020335
60 | 0.98511 | -0.28571 | 0 | 0
61 | 0.98499 | -0.28686 | 0.00052948 | 0.0001327
62 | 0.9872 | -0.24501 | 0 | 0
63 | 0.98503 | -0.28725 | 0.0028139 | 0.00070524
64 | 0.9786 | -0.41095 | 0 | 0
65 | 0.98535 | -0.27973 | 0.0049853 | 0.0012494
66 | 0.98289 | -0.32731 | 0.0020914 | 0.00052416
67 | 0.97196 | -0.54128 | 0.0034247 | 0.0008583
68 | 0.97194 | -0.54164 | 0.0046635 | 0.0011688
69 | 0.97221 | -0.53639 | 0.00030218 | 7.5733e-05
70 | 0.97228 | -0.53496 | 0.0057139 | 0.001432
71 | 0.98695 | -0.25028 | 0 | 0
72 | 0.98654 | -0.25811 | 0.0022354 | 0.00056026
73 | 0.98734 | -0.24257 | 0.0049169 | 0.0012323
74 | 0.97279 | -0.52499 | 0 | 0
75 | 0.98642 | -0.26056 | 0 | 0
76 | 0.98736 | -0.24218 | 0.0029454 | 0.00073819
77 | 0.97316 | -0.51764 | 0 | 0
78 | 0.9726 | -0.52875 | 0.0026644 | 0.00066777
79 | 0.97747 | -0.43278 | 0.005572 | 0.0013965
80 | 0.97675 | -0.44702 | 0.0021896 | 0.00054877
81 | 0.97674 | -0.44727 | 0.0022689 | 0.00056864
82 | 0.97661 | -0.4497 | 0.012225 | 0.0030638
83 | 0.97648 | -0.45221 | 0.0028315 | 0.00070965
84 | 0.97435 | -0.49431 | 0.0045963 | 0.0011519
85 | 0.97443 | -0.49267 | 0.0047659 | 0.0011944
86 | 0.97616 | -0.45866 | 0.0030844 | 0.00077303
87 | 0.97578 | -0.46597 | 0.0036395 | 0.00091215
88 | 0.97196 | -0.54139 | 0.0012626 | 0.00031643
89 | 0.97187 | -0.54302 | 0.0012413 | 0.00031111
90 | 0.97205 | -0.53946 | 0 | 0
91 | 0.97161 | -0.54819 | 0 | 0
92 | 0.9718 | -0.54444 | 0.0080207 | 0.0020102
93 | 0.97224 | -0.53582 | 0.0021216 | 0.00053172
94 | 0.97175 | -0.54541 | 0.01257 | 0.0031504
95 | 0.97136 | -0.55321 | 0.010584 | 0.0026526
96 | 0.97155 | -0.54954 | 0.0048533 | 0.0012164
97 | 0.97173 | -0.54583 | 0.00085868 | 0.00021521
98 | 0.97253 | -0.53001 | 0.0012981 | 0.00032533
99 | 0.97152 | -0.55003 | 0 | 0
100 | 0.97167 | -0.54704 | 0 | 0
101 | 0.98018 | -0.38197 | 0.0019558 | 0.00049017
102 | 0.98034 | -0.37899 | 0.0078594 | 0.0019698
103 | 0.9807 | -0.37188 | 0 | 0
104 | 0.97449 | -0.4915 | 0.0034118 | 0.00085508
105 | 0.97461 | -0.48917 | 0.010445 | 0.0026177
106 | 0.97517 | -0.47802 | 0 | 0
107 | 0.98061 | -0.37363 | 0.0080922 | 0.0020281
108 | 0.98467 | -0.29428 | 0.0083337 | 0.0020886
109 | 0.9848 | -0.29171 | 0 | 0
110 | 0.98111 | -0.36384 | 0.004579 | 0.0011476
111 | 0.98358 | -0.31548 | 0.0050254 | 0.0012595
112 | 0.98638 | -0.26113 | 0 | 0
113 | 0.9815 | -0.35608 | 0.0051151 | 0.001282
114 | 0.98317 | -0.32347 | 0.0028533 | 0.00071511
115 | 0.98796 | -0.23053 | 0 | 0
116 | 0.98835 | -0.22296 | 0 | 0
117 | 0.98774 | -0.23473 | 0.0023422 | 0.00058701
118 | 0.98648 | -0.25908 | 0.015537 | 0.003894
119 | 0.98195 | -0.34742 | 0.0039347 | 0.00098612
120 | 0.98533 | -0.2802 | 0.0036887 | 0.00092447
121 | 0.98771 | -0.23542 | 0.0021 | 0.0005263
122 | 0.98942 | -0.20229 | 0.0031814 | 0.00079735
123 | 0.97348 | -0.51122 | 0.0048652 | 0.0012193
124 | 0.9729 | -0.52282 | 0.0098401 | 0.0024662
125 | 0.98842 | -0.22134 | 0.0015358 | 0.0003849
126 | 0.98824 | -0.22484 | 0.0044121 | 0.0011058
127 | 0.985 | -0.28778 | 0.00094337 | 0.00023643
128 | 0.98637 | -0.26156 | 0.0018978 | 0.00047564
129 | 0.97561 | -0.46946 | 0 | 0
130 | 0.97473 | -0.48673 | 0.0043577 | 0.0010921
131 | 0.97434 | -0.49439 | 0 | 0
132 | 0.97148 | -0.55077 | 0.001082 | 0.00027117
133 | 0.98233 | -0.3399 | 0.0044533 | 0.0011161
134 | 0.98697 | -0.24952 | 0.0038909 | 0.00097516
135 | 0.99309 | -0.13169 | 0.013841 | 0.003469
136 | 0.97405 | -0.50012 | 0.0053328 | 0.0013365
137 | 0.97163 | -0.54776 | 0.0023375 | 0.00058584
138 | 0.97166 | -0.54726 | 0.0011039 | 0.00027666
139 | 0.98624 | -0.26409 | 0.0022314 | 0.00055923
140 | 0.9862 | -0.26471 | 0 | 0
141 | 0.98614 | -0.266 | 0.0016894 | 0.0004234
142 | 0.98609 | -0.26702 | 0 | 0
143 | 0.98606 | -0.26753 | 0.0031025 | 0.00077756
144 | 0.97397 | -0.50174 | 0.0079513 | 0.0019928
145 | 0.97396 | -0.50197 | 0.0022933 | 0.00057476
146 | 0.97853 | -0.41235 | 0.0035981 | 0.00090178
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0025988 | -0.00065133 | 0.002599 | 0.00065106 | 1.7764e-07 | -2.6898e-07 | 0.0039478 | 0.0039477 | 0.0039478 | 0.97956 | -0.3942 | 0.97963 | -0.39276 | 1.0846
1 | -0.0061141 | -0.001532 | 0.0061151 | 0.0015323 | 1.0719e-06 | 2.6865e-07 | 0.0092868 | 0.0092867 | 0.0092868 | 0.97963 | -0.39276 | 0.97982 | -0.38908 | 2.5513
2 | -0.0082666 | -0.0020715 | 0.0082679 | 0.0020721 | 1.3481e-06 | 5.7545e-07 | 0.012554 | 0.012554 | 0.012554 | 0.97982 | -0.38908 | 0.98 | -0.38566 | 3.4489
3 | -0.010858 | -0.0027211 | 0.010859 | 0.0027219 | 1.4593e-06 | 7.5356e-07 | 0.016486 | 0.016486 | 0.016486 | 0.98 | -0.38566 | 0.98014 | -0.38284 | 4.5292
4 | -0.010859 | -0.0027219 | 0.01086 | 0.0027221 | 4.4825e-07 | 2.3145e-07 | 0.016486 | 0.016486 | 0.016486 | 0.98014 | -0.38284 | 0.98018 | -0.38197 | 4.5292
5 | -0.004019 | -0.0010073 | 0.0040193 | 0.0010072 | 3.0873e-07 | -8.8796e-08 | 0.0060604 | 0.0060603 | 0.0060604 | 0.98679 | -0.25295 | 0.98687 | -0.25134 | 1.6649
6 | -0.011579 | -0.0029017 | 0.01158 | 0.0029023 | 1.0054e-06 | 5.3107e-07 | 0.017458 | 0.017458 | 0.017458 | 0.98687 | -0.25134 | 0.98697 | -0.24952 | 4.7963
7 | 0.19343 | 0.048894 | -0.19337 | -0.048851 | 6.7524e-05 | 4.2794e-05 | 0.29363 | 0.29363 | 0.29363 | 0.98076 | -0.36856 | 0.98039 | -0.37584 | 20.1668
8 | -0.19629 | -0.049608 | 0.19632 | 0.049633 | 3.8106e-05 | 2.4156e-05 | 0.29795 | 0.29795 | 0.29795 | 0.98076 | -0.36856 | 0.98097 | -0.36451 | 20.4639
9 | 0.022368 | 0.0056158 | -0.022346 | -0.0056023 | 2.2167e-05 | 1.3541e-05 | 0.033953 | 0.033954 | 0.033954 | 0.98039 | -0.37584 | 0.97933 | -0.39664 | 9.3279
10 | 0.171 | 0.043235 | -0.17076 | -0.043081 | 0.00024363 | 0.00015399 | 0.25967 | 0.25968 | 0.25968 | 0.98039 | -0.37584 | 0.97886 | -0.4056 | 17.8349
11 | -0.19632 | -0.049633 | 0.19644 | 0.049703 | 0.00011186 | 7.0913e-05 | 0.29795 | 0.29795 | 0.29795 | 0.98097 | -0.36451 | 0.98158 | -0.35264 | 20.4639
12 | 0.0077129 | 0.0019331 | -0.0077104 | -0.0019321 | 2.5102e-06 | 9.935e-07 | 0.011719 | 0.011719 | 0.011719 | 0.97933 | -0.39664 | 0.97898 | -0.40347 | 3.2196
13 | 0.014633 | 0.0036692 | -0.014627 | -0.003666 | 5.5954e-06 | 3.2015e-06 | 0.022235 | 0.022235 | 0.022235 | 0.97933 | -0.39664 | 0.97892 | -0.40467 | 6.1084
14 | 0.17076 | 0.043081 | -0.17065 | -0.043012 | 0.00010901 | 6.8902e-05 | 0.25968 | 0.25968 | 0.25968 | 0.97886 | -0.4056 | 0.97818 | -0.41894 | 17.8349
15 | -0.20274 | -0.051283 | 0.20286 | 0.051361 | 0.00012272 | 7.7842e-05 | 0.30751 | 0.30751 | 0.30751 | 0.98158 | -0.35264 | 0.98223 | -0.34003 | 21.1201
16 | 0.0065587 | 0.0016436 | -0.0065574 | -0.0016432 | 1.2755e-06 | 3.8609e-07 | 0.0099689 | 0.0099691 | 0.0099691 | 0.97898 | -0.40347 | 0.97877 | -0.40756 | 2.7388
17 | 0.0011517 | 0.00028854 | -0.0011517 | -0.00028863 | 9.3657e-09 | -9.6488e-08 | 0.0017505 | 0.0017505 | 0.0017505 | 0.97898 | -0.40347 | 0.97897 | -0.40364 | 0.48091
18 | -0.014003 | -0.0035109 | 0.01401 | 0.0035144 | 6.1886e-06 | 3.493e-06 | 0.021177 | 0.021176 | 0.021177 | 0.984 | -0.30575 | 0.98448 | -0.29648 | 5.8177
19 | 0.014003 | 0.0035109 | -0.013999 | -0.0035086 | 4.0831e-06 | 2.3049e-06 | 0.021177 | 0.021177 | 0.021177 | 0.984 | -0.30575 | 0.98369 | -0.31187 | 5.8178
20 | 0.21543 | 0.054683 | -0.21518 | -0.054525 | 0.00024834 | 0.00015767 | 0.32587 | 0.32587 | 0.32587 | 0.98448 | -0.29648 | 0.98324 | -0.32048 | 22.381
21 | -0.22944 | -0.058197 | 0.22981 | 0.058431 | 0.00036836 | 0.00023409 | 0.34704 | 0.34704 | 0.34704 | 0.98448 | -0.29648 | 0.9862 | -0.26315 | 23.8354
22 | 0.16695 | 0.042087 | -0.16685 | -0.042023 | 0.00010052 | 6.3498e-05 | 0.25406 | 0.25406 | 0.25406 | 0.97818 | -0.41894 | 0.97754 | -0.43153 | 17.4491
23 | -0.20928 | -0.052969 | 0.20936 | 0.053018 | 7.7636e-05 | 4.927e-05 | 0.31723 | 0.31723 | 0.31723 | 0.98223 | -0.34003 | 0.98263 | -0.33231 | 21.7878
24 | 0.0065574 | 0.0016432 | -0.0065567 | -0.001643 | 7.3957e-07 | 2.2395e-07 | 0.0099691 | 0.0099692 | 0.0099692 | 0.97877 | -0.40756 | 0.97865 | -0.40992 | 2.7388
25 | 0.012432 | 0.0031164 | -0.012431 | -0.0031156 | 1.5669e-06 | 8.5169e-07 | 0.01877 | 0.01877 | 0.01877 | 0.98561 | -0.27464 | 0.98548 | -0.27728 | 5.1565
26 | 0.0096351 | 0.0024128 | -0.0096304 | -0.0024106 | 4.6638e-06 | 2.2361e-06 | 0.014546 | 0.014546 | 0.014546 | 0.98561 | -0.27464 | 0.98509 | -0.28481 | 3.9961
27 | -0.022067 | -0.0055292 | 0.022079 | 0.0055366 | 1.2082e-05 | 7.3625e-06 | 0.033315 | 0.033315 | 0.033315 | 0.98561 | -0.27464 | 0.9862 | -0.26315 | 9.1526
28 | 0.0086751 | 0.0021743 | -0.0086741 | -0.0021739 | 1.0098e-06 | 4.4633e-07 | 0.013099 | 0.013099 | 0.013099 | 0.98548 | -0.27728 | 0.98535 | -0.27973 | 3.5986
29 | 0.0086334 | 0.0021622 | -0.0086331 | -0.002162 | 3.3484e-07 | 1.4746e-07 | 0.013041 | 0.013041 | 0.013041 | 0.98509 | -0.28481 | 0.98505 | -0.28562 | 3.5826
30 | 0.00099697 | 0.00024838 | -0.00099695 | -0.00024865 | 1.8668e-08 | -2.6767e-07 | 0.0015054 | 0.0015055 | 0.0015055 | 0.98509 | -0.28481 | 0.98507 | -0.2852 | 0.41361
31 | -0.25189 | -0.063968 | 0.25212 | 0.064116 | 0.0002331 | 0.00014831 | 0.38036 | 0.38036 | 0.38036 | 0.9862 | -0.26315 | 0.9872 | -0.24394 | 26.1235
32 | 0.0084184 | 0.0021092 | -0.0084176 | -0.0021088 | 8.2637e-07 | 3.5523e-07 | 0.012713 | 0.012713 | 0.012713 | 0.98533 | -0.28139 | 0.98522 | -0.28346 | 3.4926
33 | -0.0084184 | -0.0021092 | 0.0084202 | 0.00211 | 1.8529e-06 | 7.9637e-07 | 0.012713 | 0.012713 | 0.012713 | 0.98533 | -0.28139 | 0.98557 | -0.27677 | 3.4926
34 | 0.003758 | 0.000941 | -0.0037576 | -0.00094117 | 4.0357e-07 | -1.6711e-07 | 0.0056755 | 0.0056757 | 0.0056757 | 0.98522 | -0.28346 | 0.98511 | -0.28571 | 1.5593
35 | -0.017752 | -0.0044486 | 0.017753 | 0.0044496 | 1.6673e-06 | 9.8821e-07 | 0.026801 | 0.026801 | 0.026801 | 0.98557 | -0.27677 | 0.98567 | -0.2748 | 7.363
36 | 0.00099695 | 0.00024865 | -0.00099687 | -0.00024984 | 8.2837e-08 | -1.1872e-06 | 0.0015055 | 0.001506 | 0.001506 | 0.98507 | -0.2852 | 0.98498 | -0.28695 | 0.41373
37 | 0.00052951 | 0.00013107 | -0.00052951 | -0.00013111 | 7.5043e-10 | -3.9393e-08 | 0.0007993 | 0.00079931 | 0.00079931 | 0.98505 | -0.28562 | 0.98505 | -0.28565 | 0.21959
38 | 0.00052951 | 0.00013111 | -0.00052949 | -0.00013226 | 2.187e-08 | -1.1474e-06 | 0.00079931 | 0.00079973 | 0.00079973 | 0.98505 | -0.28565 | 0.98501 | -0.28653 | 0.2197
39 | 0.00052949 | 0.00013226 | -0.00052948 | -0.0001327 | 8.4493e-09 | -4.4293e-07 | 0.00079973 | 0.00079989 | 0.00079989 | 0.98501 | -0.28653 | 0.98499 | -0.28686 | 0.21975
40 | -0.26017 | -0.066133 | 0.26034 | 0.066245 | 0.00017715 | 0.00011275 | 0.39248 | 0.39248 | 0.39248 | 0.9872 | -0.24394 | 0.98793 | -0.22981 | 26.9564
41 | 0.21372 | 0.05416 | -0.21365 | -0.054115 | 7.017e-05 | 4.4547e-05 | 0.32366 | 0.32366 | 0.32366 | 0.98324 | -0.32048 | 0.98289 | -0.32731 | 22.2294
42 | -0.078961 | -0.019837 | 0.078985 | 0.019851 | 2.3529e-05 | 1.4199e-05 | 0.12063 | 0.12063 | 0.12063 | 0.97412 | -0.49862 | 0.97444 | -0.49238 | 8.2853
43 | 0.078961 | 0.019837 | -0.078931 | -0.019818 | 3.0775e-05 | 1.8573e-05 | 0.12063 | 0.12063 | 0.12063 | 0.97412 | -0.49862 | 0.97371 | -0.50679 | 8.2853
44 | -0.083845 | -0.021069 | 0.083863 | 0.02108 | 1.8538e-05 | 1.1264e-05 | 0.12805 | 0.12805 | 0.12805 | 0.97444 | -0.49238 | 0.97468 | -0.48775 | 8.795
45 | 0.078931 | 0.019818 | -0.078914 | -0.019808 | 1.6684e-05 | 1.0069e-05 | 0.12063 | 0.12063 | 0.12063 | 0.97371 | -0.50679 | 0.97348 | -0.51122 | 8.2853
46 | 0.16182 | 0.040762 | -0.16181 | -0.040755 | 9.7139e-06 | 6.1313e-06 | 0.2464 | 0.2464 | 0.2464 | 0.97754 | -0.43153 | 0.97747 | -0.43278 | 16.9229
47 | -0.12835 | -0.032735 | 0.12859 | 0.032892 | 0.00024646 | 0.0001575 | 0.19158 | 0.19158 | 0.19158 | 0.99791 | -0.039684 | 1 | 0 | 52.6326
48 | 0.12835 | 0.032735 | -0.12782 | -0.0324 | 0.00052298 | 0.00033421 | 0.19158 | 0.19158 | 0.19158 | 0.99791 | -0.039684 | 0.99347 | -0.12444 | 52.6326
49 | 0.42112 | 0.10821 | -0.42016 | -0.10759 | 0.00096101 | 0.00061369 | 0.62759 | 0.62759 | 0.62759 | 1 | 0 | 0.99751 | -0.047099 | 43.1035
50 | 0.12004 | 0.030449 | -0.11999 | -0.030422 | 4.1791e-05 | 2.6702e-05 | 0.17992 | 0.17992 | 0.17992 | 0.99347 | -0.12444 | 0.99309 | -0.13169 | 49.4283
51 | -0.083863 | -0.02108 | 0.083907 | 0.021107 | 4.388e-05 | 2.6659e-05 | 0.12805 | 0.12805 | 0.12805 | 0.97468 | -0.48775 | 0.97523 | -0.47679 | 8.7949
52 | -0.086511 | -0.021759 | 0.086541 | 0.021778 | 3.03e-05 | 1.8466e-05 | 0.13203 | 0.13203 | 0.13203 | 0.97523 | -0.47679 | 0.97561 | -0.46946 | 9.0678
53 | -0.21151 | -0.053559 | 0.21156 | 0.053591 | 5.0735e-05 | 3.2204e-05 | 0.32049 | 0.32049 | 0.32049 | 0.98263 | -0.33231 | 0.98289 | -0.32731 | 22.012
54 | 0.0035985 | 0.00090158 | -0.0035984 | -0.00090166 | 1.7645e-07 | -8.4556e-08 | 0.0054714 | 0.0054715 | 0.0054715 | 0.97865 | -0.40992 | 0.9786 | -0.41095 | 1.5031
55 | -0.37654 | -0.096068 | 0.37689 | 0.096289 | 0.00034694 | 0.00022144 | 0.56464 | 0.56464 | 0.56464 | 0.99338 | -0.12556 | 0.99438 | -0.1065 | 38.78
56 | 0.3633 | 0.092749 | -0.36295 | -0.092526 | 0.00035008 | 0.0002234 | 0.5448 | 0.5448 | 0.5448 | 0.99338 | -0.12556 | 0.99234 | -0.14552 | 37.4178
57 | -0.40587 | -0.10355 | 0.40662 | 0.10403 | 0.00074349 | 0.00047472 | 0.60801 | 0.60801 | 0.60801 | 0.99438 | -0.1065 | 0.99637 | -0.068653 | 41.759
58 | 0.28356 | 0.072492 | -0.28298 | -0.072121 | 0.0005832 | 0.00037148 | 0.42571 | 0.42571 | 0.42571 | 0.99234 | -0.14552 | 0.99011 | -0.18813 | 29.2386
59 | 0.079387 | 0.020034 | -0.079287 | -0.01997 | 0.00010035 | 6.3983e-05 | 0.11909 | 0.11909 | 0.11909 | 0.99234 | -0.14552 | 0.99097 | -0.17195 | 32.7171
60 | -0.41973 | -0.10731 | 0.42016 | 0.10759 | 0.00043818 | 0.00027982 | 0.62759 | 0.62759 | 0.62759 | 0.99637 | -0.068653 | 0.99751 | -0.047099 | 43.1035
61 | 0.26087 | 0.066579 | -0.26034 | -0.066245 | 0.00052421 | 0.00033363 | 0.39248 | 0.39248 | 0.39248 | 0.99011 | -0.18813 | 0.98793 | -0.22981 | 26.9564
62 | 0.066228 | 0.016697 | -0.066134 | -0.016637 | 9.3852e-05 | 5.974e-05 | 0.099481 | 0.099482 | 0.099482 | 0.99097 | -0.17195 | 0.98943 | -0.20161 | 27.3301
63 | 0.063108 | 0.015879 | -0.063092 | -0.015869 | 1.6334e-05 | 1.0392e-05 | 0.094931 | 0.094931 | 0.094931 | 0.98943 | -0.20161 | 0.98915 | -0.20703 | 26.0799
64 | 0.058674 | 0.014761 | -0.058634 | -0.014736 | 4.0086e-05 | 2.5479e-05 | 0.088285 | 0.088285 | 0.088285 | 0.98915 | -0.20703 | 0.98842 | -0.22134 | 24.254
65 | -0.026024 | -0.0065225 | 0.026042 | 0.0065333 | 1.7339e-05 | 1.0715e-05 | 0.039288 | 0.039288 | 0.039288 | 0.98567 | -0.2748 | 0.98639 | -0.26083 | 10.7934
66 | -0.029011 | -0.0072775 | 0.029016 | 0.0072805 | 4.9168e-06 | 3.0594e-06 | 0.043767 | 0.043767 | 0.043767 | 0.98639 | -0.26083 | 0.98657 | -0.25727 | 12.024
67 | -0.03713 | -0.009314 | 0.037152 | 0.0093277 | 2.1723e-05 | 1.3667e-05 | 0.056005 | 0.056005 | 0.056005 | 0.98657 | -0.25727 | 0.9872 | -0.24501 | 15.386
68 | 0.0037576 | 0.00094117 | -0.0037573 | -0.00094128 | 2.7486e-07 | -1.1375e-07 | 0.0056757 | 0.0056758 | 0.0056758 | 0.98511 | -0.28571 | 0.98503 | -0.28725 | 1.5593
69 | 0.015474 | 0.0038793 | -0.015471 | -0.0038774 | 3.3251e-06 | 1.9197e-06 | 0.023325 | 0.023325 | 0.023325 | 0.9872 | -0.24501 | 0.98697 | -0.24952 | 6.4079
70 | -0.052625 | -0.013207 | 0.052676 | 0.013239 | 5.0673e-05 | 3.2156e-05 | 0.079329 | 0.079329 | 0.079329 | 0.9872 | -0.24501 | 0.98824 | -0.22484 | 21.7938
71 | 0.00094339 | 0.00023605 | -0.00094337 | -0.00023643 | 2.3755e-08 | -3.8187e-07 | 0.001425 | 0.0014251 | 0.0014251 | 0.98503 | -0.28725 | 0.985 | -0.28778 | 0.39152
72 | 0.0035984 | 0.00090166 | -0.0035981 | -0.00090178 | 2.3929e-07 | -1.1463e-07 | 0.0054715 | 0.0054716 | 0.0054716 | 0.9786 | -0.41095 | 0.97853 | -0.41235 | 1.5032
73 | 0.0036888 | 0.00092444 | -0.0036887 | -0.00092447 | 8.2849e-08 | -3.7664e-08 | 0.0055705 | 0.0055706 | 0.0055706 | 0.98535 | -0.27973 | 0.98533 | -0.2802 | 1.5304
74 | 0.0046636 | 0.0011688 | -0.0046635 | -0.0011688 | 8.0302e-08 | -6.708e-10 | 0.0071397 | 0.0071397 | 0.0071397 | 0.97196 | -0.54128 | 0.97194 | -0.54164 | 1.9615
75 | -0.0080883 | -0.0020271 | 0.0080902 | 0.0020279 | 1.883e-06 | 7.9915e-07 | 0.012383 | 0.012382 | 0.012383 | 0.97196 | -0.54128 | 0.97221 | -0.53639 | 3.4018
76 | -0.0083923 | -0.0021036 | 0.0083929 | 0.0021039 | 5.7173e-07 | 2.5131e-07 | 0.012845 | 0.012845 | 0.012845 | 0.97221 | -0.53639 | 0.97228 | -0.53496 | 3.5288
77 | -0.014107 | -0.0035359 | 0.014113 | 0.0035397 | 6.7003e-06 | 3.8126e-06 | 0.02159 | 0.021589 | 0.02159 | 0.97228 | -0.53496 | 0.97279 | -0.52499 | 5.9312
78 | 0.011164 | 0.002799 | -0.011159 | -0.0027968 | 4.1667e-06 | 2.1657e-06 | 0.016832 | 0.016832 | 0.016832 | 0.98695 | -0.25028 | 0.98654 | -0.25811 | 4.6242
79 | -0.011164 | -0.002799 | 0.011168 | 0.0028011 | 4.0982e-06 | 2.1297e-06 | 0.016832 | 0.016832 | 0.016832 | 0.98695 | -0.25028 | 0.98734 | -0.24257 | 4.6241
80 | 0.008924 | 0.0022366 | -0.008923 | -0.0022361 | 1.0397e-06 | 4.7005e-07 | 0.01346 | 0.01346 | 0.01346 | 0.98654 | -0.25811 | 0.98642 | -0.26056 | 3.6979
81 | -0.016085 | -0.0040334 | 0.016085 | 0.0040336 | 3.0062e-07 | 1.7495e-07 | 0.024242 | 0.024242 | 0.024242 | 0.98734 | -0.24257 | 0.98736 | -0.24218 | 6.6599
82 | -0.064161 | -0.016095 | 0.064183 | 0.016108 | 2.2498e-05 | 1.3161e-05 | 0.098148 | 0.098148 | 0.098148 | 0.97279 | -0.52499 | 0.97316 | -0.51764 | 6.741
83 | 0.050047 | 0.012555 | -0.050039 | -0.01255 | 8.9532e-06 | 4.9211e-06 | 0.076559 | 0.076559 | 0.076559 | 0.97279 | -0.52499 | 0.9726 | -0.52875 | 5.2582
84 | 0.008923 | 0.0022361 | -0.0089226 | -0.0022359 | 4.2563e-07 | 1.9244e-07 | 0.01346 | 0.01346 | 0.01346 | 0.98642 | -0.26056 | 0.98637 | -0.26156 | 3.6979
85 | -0.01903 | -0.0047718 | 0.019037 | 0.0047758 | 6.7636e-06 | 4.0482e-06 | 0.028681 | 0.028681 | 0.028681 | 0.98736 | -0.24218 | 0.98774 | -0.23473 | 7.8793
86 | -0.074026 | -0.018575 | 0.074049 | 0.018589 | 2.2672e-05 | 1.3572e-05 | 0.1132 | 0.1132 | 0.1132 | 0.97316 | -0.51764 | 0.97348 | -0.51122 | 7.7746
87 | 0.0098425 | 0.0024674 | -0.0098401 | -0.0024662 | 2.427e-06 | 1.1983e-06 | 0.01505 | 0.01505 | 0.01505 | 0.97316 | -0.51764 | 0.9729 | -0.52282 | 4.1346
88 | 0.047374 | 0.011882 | -0.047371 | -0.011881 | 2.8475e-06 | 1.5354e-06 | 0.072483 | 0.072483 | 0.072483 | 0.9726 | -0.52875 | 0.97253 | -0.53001 | 4.9782
89 | 0.15624 | 0.039359 | -0.15613 | -0.039292 | 0.00010632 | 6.704e-05 | 0.23791 | 0.23791 | 0.23791 | 0.97747 | -0.43278 | 0.97675 | -0.44702 | 16.3403
90 | 0.15394 | 0.038743 | -0.15394 | -0.038742 | 1.8541e-06 | 1.1687e-06 | 0.23458 | 0.23458 | 0.23458 | 0.97675 | -0.44702 | 0.97674 | -0.44727 | 16.1112
91 | 0.15167 | 0.038173 | -0.15165 | -0.038162 | 1.7564e-05 | 1.1065e-05 | 0.23112 | 0.23112 | 0.23112 | 0.97674 | -0.44727 | 0.97661 | -0.4497 | 15.8738
92 | 0.13943 | 0.035099 | -0.13941 | -0.035088 | 1.6727e-05 | 1.0507e-05 | 0.2125 | 0.2125 | 0.2125 | 0.97661 | -0.4497 | 0.97648 | -0.45221 | 14.5945
93 | 0.13658 | 0.034378 | -0.13654 | -0.034352 | 4.2094e-05 | 2.6422e-05 | 0.20818 | 0.20818 | 0.20818 | 0.97648 | -0.45221 | 0.97616 | -0.45866 | 14.2982
94 | -0.0045963 | -0.0011519 | 0.0045966 | 0.0011519 | 3.5893e-07 | -1.2253e-08 | 0.0070194 | 0.0070193 | 0.0070194 | 0.97435 | -0.49431 | 0.97443 | -0.49267 | 1.9284
95 | -0.0093625 | -0.0023464 | 0.009363 | 0.0023466 | 5.2243e-07 | 2.4945e-07 | 0.014297 | 0.014297 | 0.014297 | 0.97443 | -0.49267 | 0.97449 | -0.4915 | 3.9278
96 | 0.13345 | 0.033579 | -0.13341 | -0.03355 | 4.6602e-05 | 2.9225e-05 | 0.20348 | 0.20348 | 0.20348 | 0.97616 | -0.45866 | 0.97578 | -0.46597 | 13.9753
97 | 0.12977 | 0.032638 | -0.12975 | -0.032624 | 2.1673e-05 | 1.3576e-05 | 0.19793 | 0.19793 | 0.19793 | 0.97578 | -0.46597 | 0.97561 | -0.46946 | 13.5941
98 | 0.017769 | 0.0044549 | -0.017768 | -0.0044543 | 1.387e-06 | 6.3994e-07 | 0.027204 | 0.027204 | 0.027204 | 0.97196 | -0.54139 | 0.97187 | -0.54302 | 3.7368
99 | -0.019032 | -0.0047713 | 0.019033 | 0.0047714 | 1.7467e-06 | 2.9768e-08 | 0.029137 | 0.029136 | 0.029137 | 0.97196 | -0.54139 | 0.97205 | -0.53946 | 2.0012
100 | 0.016526 | 0.0041432 | -0.016522 | -0.0041408 | 4.0647e-06 | 2.3917e-06 | 0.025303 | 0.025303 | 0.025303 | 0.97187 | -0.54302 | 0.97161 | -0.54819 | 6.9515
101 | 0.012324 | 0.0030891 | -0.012321 | -0.0030875 | 2.9209e-06 | 1.5982e-06 | 0.018866 | 0.018866 | 0.018866 | 0.97205 | -0.53946 | 0.9718 | -0.54444 | 5.183
102 | -0.043931 | -0.011013 | 0.043939 | 0.011017 | 7.622e-06 | 3.9866e-06 | 0.067251 | 0.06725 | 0.067251 | 0.97205 | -0.53946 | 0.97224 | -0.53582 | 4.6189
103 | 0.012574 | 0.0031523 | -0.01257 | -0.0031504 | 3.5668e-06 | 1.9646e-06 | 0.019248 | 0.019248 | 0.019248 | 0.97205 | -0.53946 | 0.97175 | -0.54541 | 5.288
104 | 0.010586 | 0.0026539 | -0.010584 | -0.0026526 | 2.5333e-06 | 1.3031e-06 | 0.016213 | 0.016213 | 0.016213 | 0.97161 | -0.54819 | 0.97136 | -0.55321 | 4.4542
105 | 0.0059358 | 0.0014869 | -0.0059354 | -0.0014868 | 3.8165e-07 | 9.173e-08 | 0.0090903 | 0.0090903 | 0.0090903 | 0.97161 | -0.54819 | 0.97155 | -0.54954 | 2.4973
106 | 0.0043007 | 0.0010773 | -0.0043004 | -0.0010773 | 2.8493e-07 | -3.4732e-08 | 0.0065849 | 0.006585 | 0.006585 | 0.9718 | -0.54444 | 0.97173 | -0.54583 | 1.8091
107 | -0.04606 | -0.011548 | 0.046073 | 0.011555 | 1.2757e-05 | 6.8056e-06 | 0.070497 | 0.070497 | 0.070497 | 0.97224 | -0.53582 | 0.97253 | -0.53001 | 4.8419
108 | 0.001082 | 0.00027045 | -0.001082 | -0.00027073 | 2.5279e-08 | -2.8784e-07 | 0.001657 | 0.0016571 | 0.0016571 | 0.97155 | -0.54954 | 0.97152 | -0.55003 | 0.45524
109 | 0.0034417 | 0.00086211 | -0.0034415 | -0.00086222 | 1.9923e-07 | -1.0944e-07 | 0.0052701 | 0.0052702 | 0.0052702 | 0.97173 | -0.54583 | 0.97167 | -0.54704 | 1.4479
110 | 0.001082 | 0.00027073 | -0.001082 | -0.00027117 | 3.8081e-08 | -4.335e-07 | 0.0016571 | 0.0016573 | 0.0016573 | 0.97152 | -0.55003 | 0.97148 | -0.55077 | 0.45529
111 | 0.0023376 | 0.00058568 | -0.0023375 | -0.00058584 | 8.0008e-08 | -1.5501e-07 | 0.0035797 | 0.0035798 | 0.0035798 | 0.97167 | -0.54704 | 0.97163 | -0.54776 | 0.98346
112 | 0.0011039 | 0.00027654 | -0.0011039 | -0.00027666 | 1.1343e-08 | -1.2384e-07 | 0.0016905 | 0.0016905 | 0.0016905 | 0.97167 | -0.54704 | 0.97166 | -0.54726 | 0.46443
113 | -0.012816 | -0.0032123 | 0.012817 | 0.0032133 | 1.8224e-06 | 1.0045e-06 | 0.019455 | 0.019455 | 0.019455 | 0.98018 | -0.38197 | 0.98034 | -0.37899 | 5.3449
114 | -0.020677 | -0.0051831 | 0.020684 | 0.0051873 | 7.0029e-06 | 4.2427e-06 | 0.031385 | 0.031385 | 0.031385 | 0.98034 | -0.37899 | 0.9807 | -0.37188 | 8.6222
115 | -0.028777 | -0.0072157 | 0.028788 | 0.0072226 | 1.1029e-05 | 6.864e-06 | 0.043664 | 0.043664 | 0.043664 | 0.9807 | -0.37188 | 0.98111 | -0.36384 | 11.9957
116 | 0.0080929 | 0.0020284 | -0.0080922 | -0.0020281 | 6.7331e-07 | 2.8068e-07 | 0.012279 | 0.012279 | 0.012279 | 0.9807 | -0.37188 | 0.98061 | -0.37363 | 3.3735
117 | -0.012775 | -0.0032017 | 0.012776 | 0.0032025 | 1.4166e-06 | 7.8293e-07 | 0.019507 | 0.019507 | 0.019507 | 0.97449 | -0.4915 | 0.97461 | -0.48917 | 5.359
118 | -0.023221 | -0.0058201 | 0.023233 | 0.0058277 | 1.2347e-05 | 7.5754e-06 | 0.035454 | 0.035453 | 0.035454 | 0.97461 | -0.48917 | 0.97517 | -0.47802 | 9.74
119 | 0.019954 | 0.0050073 | -0.019946 | -0.0050023 | 8.286e-06 | 5.0059e-06 | 0.03045 | 0.03045 | 0.03045 | 0.97517 | -0.47802 | 0.97473 | -0.48673 | 8.3655
120 | -0.043187 | -0.010835 | 0.043205 | 0.010846 | 1.7613e-05 | 1.1137e-05 | 0.065904 | 0.065904 | 0.065904 | 0.97517 | -0.47802 | 0.97561 | -0.46946 | 18.1054
121 | -0.0083337 | -0.0020886 | 0.0083347 | 0.002089 | 1.0195e-06 | 4.3438e-07 | 0.012594 | 0.012594 | 0.012594 | 0.98467 | -0.29428 | 0.9848 | -0.29171 | 3.4598
122 | 0.05491 | 0.013831 | -0.054848 | -0.013792 | 6.2342e-05 | 3.9592e-05 | 0.082993 | 0.082993 | 0.082993 | 0.9848 | -0.29171 | 0.98358 | -0.31548 | 22.8002
123 | -0.063245 | -0.01592 | 0.063337 | 0.015979 | 9.2588e-05 | 5.8912e-05 | 0.095586 | 0.095586 | 0.095586 | 0.9848 | -0.29171 | 0.98638 | -0.26113 | 26.26
124 | -0.033367 | -0.0083702 | 0.033379 | 0.0083779 | 1.2341e-05 | 7.736e-06 | 0.050609 | 0.050609 | 0.050609 | 0.98111 | -0.36384 | 0.9815 | -0.35608 | 13.9036
125 | 0.049822 | 0.012532 | -0.049803 | -0.01252 | 1.9014e-05 | 1.2056e-05 | 0.07539 | 0.07539 | 0.07539 | 0.98358 | -0.31548 | 0.98317 | -0.32347 | 20.7116
126 | -0.063337 | -0.015979 | 0.063344 | 0.015983 | 6.2247e-06 | 3.9606e-06 | 0.095586 | 0.095586 | 0.095586 | 0.98638 | -0.26113 | 0.98648 | -0.25908 | 26.26
127 | -0.038494 | -0.0096599 | 0.03851 | 0.0096699 | 1.5905e-05 | 1.0022e-05 | 0.058364 | 0.058364 | 0.058364 | 0.9815 | -0.35608 | 0.98195 | -0.34742 | 16.034
128 | 0.04695 | 0.011805 | -0.046913 | -0.011782 | 3.6799e-05 | 2.3305e-05 | 0.071072 | 0.071072 | 0.071072 | 0.98317 | -0.32347 | 0.98233 | -0.3399 | 19.5252
129 | -0.023484 | -0.0058918 | 0.023493 | 0.005897 | 8.4805e-06 | 5.196e-06 | 0.035373 | 0.035373 | 0.035373 | 0.98796 | -0.23053 | 0.98835 | -0.22296 | 9.7178
130 | 0.023484 | 0.0058918 | -0.023479 | -0.0058889 | 4.6959e-06 | 2.8772e-06 | 0.035373 | 0.035373 | 0.035373 | 0.98796 | -0.23053 | 0.98774 | -0.23473 | 9.7178
131 | -0.10251 | -0.025861 | 0.10261 | 0.025926 | 0.00010158 | 6.4864e-05 | 0.1544 | 0.1544 | 0.1544 | 0.98835 | -0.22296 | 0.98942 | -0.20229 | 42.4162
132 | 0.079017 | 0.019964 | -0.078881 | -0.019877 | 0.00013656 | 8.7068e-05 | 0.11902 | 0.11902 | 0.11902 | 0.98835 | -0.22296 | 0.98648 | -0.25908 | 32.6985
133 | 0.0021 | 0.00052611 | -0.0021 | -0.0005263 | 6.9384e-08 | -1.9221e-07 | 0.0031636 | 0.0031637 | 0.0031637 | 0.98774 | -0.23473 | 0.98771 | -0.23542 | 0.86914
134 | -0.042445 | -0.010656 | 0.04246 | 0.010666 | 1.524e-05 | 9.6296e-06 | 0.064326 | 0.064326 | 0.064326 | 0.98195 | -0.34742 | 0.98233 | -0.3399 | 17.672
135 | -0.10579 | -0.026724 | 0.10615 | 0.026953 | 0.00035929 | 0.00022946 | 0.15918 | 0.15918 | 0.15918 | 0.98942 | -0.20229 | 0.99309 | -0.13169 | 43.7307
136 | 0.057098 | 0.014351 | -0.057088 | -0.014345 | 9.5379e-06 | 6.0602e-06 | 0.085973 | 0.085973 | 0.085973 | 0.98842 | -0.22134 | 0.98824 | -0.22484 | 23.6189
137 | 0.0070247 | 0.0017603 | -0.0070239 | -0.00176 | 8.4891e-07 | 2.8605e-07 | 0.010597 | 0.010597 | 0.010597 | 0.98637 | -0.26156 | 0.98624 | -0.26409 | 2.9114
138 | 0.015588 | 0.0039102 | -0.015582 | -0.0039069 | 5.6941e-06 | 3.3102e-06 | 0.023798 | 0.023798 | 0.023798 | 0.97473 | -0.48673 | 0.97434 | -0.49439 | 6.538
139 | 0.015582 | 0.0039069 | -0.015578 | -0.0039044 | 4.2514e-06 | 2.4717e-06 | 0.023798 | 0.023798 | 0.023798 | 0.97434 | -0.49439 | 0.97405 | -0.50012 | 6.538
140 | 0.010245 | 0.0025679 | -0.010245 | -0.0025675 | 7.9219e-07 | 3.9967e-07 | 0.015652 | 0.015652 | 0.015652 | 0.97405 | -0.50012 | 0.97397 | -0.50174 | 4.2999
141 | 0.0047925 | 0.0012007 | -0.0047924 | -0.0012007 | 1.4026e-07 | -1.5171e-09 | 0.0072308 | 0.0072308 | 0.0072308 | 0.98624 | -0.26409 | 0.9862 | -0.26471 | 1.9865
142 | 0.0047924 | 0.0012007 | -0.0047921 | -0.0012007 | 2.9463e-07 | -3.1651e-09 | 0.0072308 | 0.0072309 | 0.0072309 | 0.9862 | -0.26471 | 0.98614 | -0.266 | 1.9865
143 | 0.0031027 | 0.00077735 | -0.0031026 | -0.00077749 | 1.5065e-07 | -1.374e-07 | 0.0046817 | 0.0046818 | 0.0046818 | 0.98614 | -0.266 | 0.98609 | -0.26702 | 1.2862
144 | 0.0031026 | 0.00077749 | -0.0031025 | -0.00077756 | 7.5156e-08 | -6.8536e-08 | 0.0046818 | 0.0046818 | 0.0046818 | 0.98609 | -0.26702 | 0.98606 | -0.26753 | 1.2862
145 | 0.0022933 | 0.00057471 | -0.0022933 | -0.00057476 | 2.4834e-08 | -5.1241e-08 | 0.0035037 | 0.0035037 | 0.0035037 | 0.97397 | -0.50174 | 0.97396 | -0.50197 | 0.96256

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58109 | 0.14855

## res_load
| p_mw | q_mvar
0 | 0.0025988 | 0.00065133
1 | 0.003515 | 0.00088095
2 | 0.0021515 | 0.00053921
3 | 0.0025898 | 0.00064908
4 | 0.004019 | 0.0010073
5 | 0.0075594 | 0.0018946
6 | 0.0028519 | 0.00071476
7 | 0.0063024 | 0.0015795
8 | 0.014627 | 0.003666
9 | 0.013999 | 0.0035086
10 | 0.0036923 | 0.00092537
11 | 0.006417 | 0.0016083
12 | 0.0011517 | 0.00028863
13 | 0.0037557 | 0.00094126
14 | 0.0046596 | 0.0011678
15 | 0.0093313 | 0.0023386
16 | 0.00099687 | 0.00024984
17 | 0.0081036 | 0.0020309
18 | 0.0080458 | 0.0020165
19 | 0.0014583 | 0.0003655
20 | 0.0048597 | 0.001218
21 | 0.0050339 | 0.0012616
22 | 0.029727 | 0.0074503
23 | 0.0077873 | 0.0019517
24 | 0.002604 | 0.00065262
25 | 0.002156 | 0.00054034
26 | 0.0029581 | 0.00074138
27 | 0.01324 | 0.0033183
28 | 0.028986 | 0.0072645
29 | 0.013109 | 0.0032854
30 | 0.022111 | 0.0055416
31 | 0.013059 | 0.0032728
32 | 0.0030259 | 0.00075835
33 | 0.0044181 | 0.0011073
34 | 0.0082712 | 0.002073
35 | 0.0029694 | 0.00074421
36 | 0.0081137 | 0.0020335
37 | 0.00052948 | 0.0001327
38 | 0.0028139 | 0.00070524
39 | 0.0049853 | 0.0012494
40 | 0.0020914 | 0.00052416
41 | 0.0034247 | 0.0008583
42 | 0.0046635 | 0.0011688
43 | 0.00030218 | 7.5733e-05
44 | 0.0057139 | 0.001432
45 | 0.0022354 | 0.00056026
46 | 0.0049169 | 0.0012323
47 | 0.0029454 | 0.00073819
48 | 0.0026644 | 0.00066777
49 | 0.005572 | 0.0013965
50 | 0.0021896 | 0.00054877
51 | 0.0022689 | 0.00056864
52 | 0.012225 | 0.0030638
53 | 0.0028315 | 0.00070965
54 | 0.0045963 | 0.0011519
55 | 0.0047659 | 0.0011944
56 | 0.0030844 | 0.00077303
57 | 0.0036395 | 0.00091215
58 | 0.0012626 | 0.00031643
59 | 0.0012413 | 0.00031111
60 | 0.0080207 | 0.0020102
61 | 0.0021216 | 0.00053172
62 | 0.01257 | 0.0031504
63 | 0.010584 | 0.0026526
64 | 0.0048533 | 0.0012164
65 | 0.00085868 | 0.00021521
66 | 0.0012981 | 0.00032533
67 | 0.0019558 | 0.00049017
68 | 0.0078594 | 0.0019698
69 | 0.0034118 | 0.00085508
70 | 0.010445 | 0.0026177
71 | 0.0080922 | 0.0020281
72 | 0.0083337 | 0.0020886
73 | 0.004579 | 0.0011476
74 | 0.0050254 | 0.0012595
75 | 0.0051151 | 0.001282
76 | 0.0028533 | 0.00071511
77 | 0.0023422 | 0.00058701
78 | 0.015537 | 0.003894
79 | 0.0039347 | 0.00098612
80 | 0.0036887 | 0.00092447
81 | 0.0021 | 0.0005263
82 | 0.0031814 | 0.00079735
83 | 0.0048652 | 0.0012193
84 | 0.0098401 | 0.0024662
85 | 0.0015358 | 0.0003849
86 | 0.0044121 | 0.0011058
87 | 0.00094337 | 0.00023643
88 | 0.0018978 | 0.00047564
89 | 0.0043577 | 0.0010921
90 | 0.001082 | 0.00027117
91 | 0.0044533 | 0.0011161
92 | 0.0038909 | 0.00097516
93 | 0.013841 | 0.003469
94 | 0.0053328 | 0.0013365
95 | 0.0023375 | 0.00058584
96 | 0.0011039 | 0.00027666
97 | 0.0022314 | 0.00055923
98 | 0.0016894 | 0.0004234
99 | 0.0031025 | 0.00077756
100 | 0.0079513 | 0.0019928
101 | 0.0022933 | 0.00057476
102 | 0.0035981 | 0.00090178

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1