## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2550-4_1_4_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_2550-4_1_4_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_2550-4_1_4_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2550-4_1_4_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_2550-4_1_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_2550-4_1_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_2550-4_1_4_node_81 | 0.4 | n |  | TRUE
7 | bus_LV_2550-4_1_4_node_78 | 0.4 | n |  | TRUE
8 | bus_LV_2550-4_1_4_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_2550-4_1_4_node_146 | 0.4 | n |  | TRUE
10 | bus_LV_2550-4_1_4_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_2550-4_1_4_node_35 | 0.4 | n |  | TRUE
12 | bus_LV_2550-4_1_4_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_2550-4_1_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2550-4_1_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_2550-4_1_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2550-4_1_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2550-4_1_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2550-4_1_4_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_2550-4_1_4_node_106 | 0.4 | n |  | TRUE
20 | bus_LV_2550-4_1_4_node_104 | 0.4 | n |  | TRUE
21 | bus_LV_2550-4_1_4_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_2550-4_1_4_node_147 | 0.4 | n |  | TRUE
23 | bus_LV_2550-4_1_4_node_132 | 0.4 | n |  | TRUE
24 | bus_LV_2550-4_1_4_node_105 | 0.4 | n |  | TRUE
25 | bus_LV_2550-4_1_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2550-4_1_4_node_157 | 0.4 | n |  | TRUE
27 | bus_LV_2550-4_1_4_node_152 | 0.4 | n |  | TRUE
28 | bus_LV_2550-4_1_4_node_155 | 0.4 | n |  | TRUE
29 | bus_LV_2550-4_1_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_2550-4_1_4_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_2550-4_1_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2550-4_1_4_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_2550-4_1_4_node_206 | 0.4 | n |  | TRUE
34 | bus_LV_2550-4_1_4_node_153 | 0.4 | n |  | TRUE
35 | bus_LV_2550-4_1_4_node_204 | 0.4 | n |  | TRUE
36 | bus_LV_2550-4_1_4_node_115 | 0.4 | n |  | TRUE
37 | bus_LV_2550-4_1_4_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_2550-4_1_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_2550-4_1_4_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_2550-4_1_4_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_2550-4_1_4_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_2550-4_1_4_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_2550-4_1_4_node_74 | 0.4 | n |  | TRUE
44 | bus_LV_2550-4_1_4_node_166 | 0.4 | n |  | TRUE
45 | bus_LV_2550-4_1_4_node_80 | 0.4 | n |  | TRUE
46 | bus_LV_2550-4_1_4_node_119 | 0.4 | n |  | TRUE
47 | bus_LV_2550-4_1_4_node_172 | 0.4 | n |  | TRUE
48 | bus_LV_2550-4_1_4_node_209 | 0.4 | n |  | TRUE
49 | bus_LV_2550-4_1_4_node_212 | 0.4 | n |  | TRUE
50 | bus_LV_2550-4_1_4_node_213 | 0.4 | n |  | TRUE
51 | bus_LV_2550-4_1_4_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_2550-4_1_4_node_59 | 0.4 | n |  | TRUE
53 | bus_LV_2550-4_1_4_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_2550-4_1_4_node_61 | 0.4 | n |  | TRUE
55 | bus_LV_2550-4_1_4_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_2550-4_1_4_node_64 | 0.4 | n |  | TRUE
57 | bus_LV_2550-4_1_4_node_120 | 0.4 | n |  | TRUE
58 | bus_LV_2550-4_1_4_node_63 | 0.4 | n |  | TRUE
59 | bus_LV_2550-4_1_4_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_2550-4_1_4_node_65 | 0.4 | n |  | TRUE
61 | bus_LV_2550-4_1_4_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_2550-4_1_4_node_151 | 0.4 | n |  | TRUE
63 | bus_LV_2550-4_1_4_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_2550-4_1_4_node_199 | 0.4 | n |  | TRUE
65 | bus_LV_2550-4_1_4_node_118 | 0.4 | n |  | TRUE
66 | bus_LV_2550-4_1_4_node_92 | 0.4 | n |  | TRUE
67 | bus_LV_2550-4_1_4_node_93 | 0.4 | n |  | TRUE
68 | bus_LV_2550-4_1_4_node_94 | 0.4 | n |  | TRUE
69 | bus_LV_2550-4_1_4_node_95 | 0.4 | n |  | TRUE
70 | bus_LV_2550-4_1_4_node_96 | 0.4 | n |  | TRUE
71 | bus_LV_2550-4_1_4_node_109 | 0.4 | n |  | TRUE
72 | bus_LV_2550-4_1_4_node_187 | 0.4 | n |  | TRUE
73 | bus_LV_2550-4_1_4_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_2550-4_1_4_node_184 | 0.4 | n |  | TRUE
75 | bus_LV_2550-4_1_4_node_97 | 0.4 | n |  | TRUE
76 | bus_LV_2550-4_1_4_node_98 | 0.4 | n |  | TRUE
77 | bus_LV_2550-4_1_4_node_99 | 0.4 | n |  | TRUE
78 | bus_LV_2550-4_1_4_node_100 | 0.4 | n |  | TRUE
79 | bus_LV_2550-4_1_4_node_171 | 0.4 | n |  | TRUE
80 | bus_LV_2550-4_1_4_node_169 | 0.4 | n |  | TRUE
81 | bus_LV_2550-4_1_4_node_185 | 0.4 | n |  | TRUE
82 | bus_LV_2550-4_1_4_node_130 | 0.4 | n |  | TRUE
83 | bus_LV_2550-4_1_4_node_140 | 0.4 | n |  | TRUE
84 | bus_LV_2550-4_1_4_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_2550-4_1_4_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_2550-4_1_4_node_111 | 0.4 | n |  | TRUE
87 | bus_LV_2550-4_1_4_node_113 | 0.4 | n |  | TRUE
88 | bus_LV_2550-4_1_4_node_116 | 0.4 | n |  | TRUE
89 | bus_LV_2550-4_1_4_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_2550-4_1_4_node_162 | 0.4 | n |  | TRUE
91 | bus_LV_2550-4_1_4_node_128 | 0.4 | n |  | TRUE
92 | bus_LV_2550-4_1_4_node_129 | 0.4 | n |  | TRUE
93 | bus_LV_2550-4_1_4_node_131 | 0.4 | n |  | TRUE
94 | bus_LV_2550-4_1_4_node_220 | 0.4 | n |  | TRUE
95 | bus_LV_2550-4_1_4_node_190 | 0.4 | n |  | TRUE
96 | bus_LV_2550-4_1_4_node_191 | 0.4 | n |  | TRUE
97 | bus_LV_2550-4_1_4_node_189 | 0.4 | n |  | TRUE
98 | bus_LV_2550-4_1_4_node_141 | 0.4 | n |  | TRUE
99 | bus_LV_2550-4_1_4_node_182 | 0.4 | n |  | TRUE
100 | bus_LV_2550-4_1_4_node_186 | 0.4 | n |  | TRUE
101 | bus_LV_2550-4_1_4_node_154 | 0.4 | n |  | TRUE
102 | bus_LV_2550-4_1_4_node_156 | 0.4 | n |  | TRUE
103 | bus_LV_2550-4_1_4_node_158 | 0.4 | n |  | TRUE
104 | bus_LV_2550-4_1_4_node_207 | 0.4 | n |  | TRUE
105 | bus_LV_2550-4_1_4_node_183 | 0.4 | n |  | TRUE
106 | bus_LV_2550-4_1_4_node_159 | 0.4 | n |  | TRUE
107 | bus_LV_2550-4_1_4_node_160 | 0.4 | n |  | TRUE
108 | bus_LV_2550-4_1_4_node_161 | 0.4 | n |  | TRUE
109 | bus_LV_2550-4_1_4_node_163 | 0.4 | n |  | TRUE
110 | bus_LV_2550-4_1_4_node_170 | 0.4 | n |  | TRUE
111 | bus_LV_2550-4_1_4_node_210 | 0.4 | n |  | TRUE
112 | bus_LV_2550-4_1_4_node_167 | 0.4 | n |  | TRUE
113 | bus_LV_2550-4_1_4_node_168 | 0.4 | n |  | TRUE
114 | bus_LV_2550-4_1_4_node_202 | 0.4 | n |  | TRUE
115 | bus_LV_2550-4_1_4_node_203 | 0.4 | n |  | TRUE
116 | bus_LV_2550-4_1_4_node_205 | 0.4 | n |  | TRUE
117 | bus_LV_2550-4_1_4_node_211 | 0.4 | n |  | TRUE
118 | bus_MV_395_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2550-4_1_4_load_6 | 0 | 0.0035613 | 0.00089256 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2550-4_1_4_load_8 | 2 | 0.001251 | 0.00031354 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2550-4_1_4_load_10 | 4 | 0.0025395 | 0.00063646 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2550-4_1_4_load_11 | 5 | 0.0019485 | 0.00048834 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2550-4_1_4_load_81 | 6 | 0.0031884 | 0.00079909 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2550-4_1_4_load_78 | 7 | 0.0047964 | 0.0012021 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2550-4_1_4_load_146 | 9 | 0.0055654 | 0.0013948 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2550-4_1_4_load_77 | 10 | 0.0025044 | 0.00062767 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2550-4_1_4_load_35 | 11 | 0.0053674 | 0.0013452 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2550-4_1_4_load_46 | 12 | 0.0023736 | 0.00059489 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2550-4_1_4_load_12 | 13 | 0.0094632 | 0.0023717 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2550-4_1_4_load_13 | 14 | 0.0029534 | 0.00074019 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2550-4_1_4_load_85 | 18 | 0.0043793 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2550-4_1_4_load_104 | 20 | 0.0024077 | 0.00060342 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2550-4_1_4_load_66 | 21 | 0.0062335 | 0.0015623 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2550-4_1_4_load_147 | 22 | 0.0025471 | 0.00063836 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2550-4_1_4_load_132 | 23 | 0.0017299 | 0.00043355 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2550-4_1_4_load_105 | 24 | 0.0018005 | 0.00045125 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2550-4_1_4_load_30 | 25 | 0.00028658 | 7.1823e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2550-4_1_4_load_152 | 27 | 0.0033463 | 0.00083867 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2550-4_1_4_load_155 | 28 | 0.0027855 | 0.0006981 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2550-4_1_4_load_32 | 29 | 0.0059142 | 0.0014822 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2550-4_1_4_load_34 | 31 | 0.00080595 | 0.00020199 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2550-4_1_4_load_206 | 33 | 0.0013083 | 0.00032789 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2550-4_1_4_load_153 | 34 | 0.0014145 | 0.0003545 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2550-4_1_4_load_204 | 35 | 0.00090206 | 0.00022608 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2550-4_1_4_load_39 | 37 | 0.0027294 | 0.00068406 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2550-4_1_4_load_40 | 38 | 0.0020772 | 0.0005206 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2550-4_1_4_load_41 | 39 | 0.0019378 | 0.00048566 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2550-4_1_4_load_43 | 41 | 0.0019032 | 0.00047698 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2550-4_1_4_load_73 | 42 | 0.0015529 | 0.0003892 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2550-4_1_4_load_74 | 43 | 0.0020798 | 0.00052125 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2550-4_1_4_load_80 | 45 | 0.0043439 | 0.0010887 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2550-4_1_4_load_209 | 48 | 0.0036801 | 0.00092231 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2550-4_1_4_load_212 | 49 | 0.0023365 | 0.00058558 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2550-4_1_4_load_213 | 50 | 0.0019869 | 0.00049796 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2550-4_1_4_load_58 | 51 | 0.0010518 | 0.0002636 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2550-4_1_4_load_59 | 52 | 0.0019132 | 0.00047949 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2550-4_1_4_load_60 | 53 | 0.0018161 | 0.00045515 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2550-4_1_4_load_61 | 54 | 0.0017408 | 0.00043627 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2550-4_1_4_load_62 | 55 | 0.0011108 | 0.00027838 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2550-4_1_4_load_64 | 56 | 0.002207 | 0.00055312 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2550-4_1_4_load_120 | 57 | 0.0026198 | 0.00065658 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2550-4_1_4_load_63 | 58 | 0.001921 | 0.00048144 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2550-4_1_4_load_110 | 59 | 0.0011224 | 0.0002813 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2550-4_1_4_load_67 | 61 | 0.0027859 | 0.00069822 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2550-4_1_4_load_151 | 62 | 0.0053568 | 0.0013425 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2550-4_1_4_load_79 | 63 | 0.0023894 | 0.00059883 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2550-4_1_4_load_199 | 64 | 0.0031995 | 0.00080187 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2550-4_1_4_load_118 | 65 | 0.0010959 | 0.00027465 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2550-4_1_4_load_92 | 66 | 0.0037402 | 0.00093739 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2550-4_1_4_load_93 | 67 | 0.0019232 | 0.000482 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2550-4_1_4_load_94 | 68 | 0.0021239 | 0.00053231 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2550-4_1_4_load_95 | 69 | 0.0040191 | 0.0010073 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2550-4_1_4_load_109 | 71 | 0.0018262 | 0.0004577 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2550-4_1_4_load_187 | 72 | 0.0028031 | 0.00070253 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2550-4_1_4_load_107 | 73 | 0.0017987 | 0.00045081 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2550-4_1_4_load_184 | 74 | 0.0013685 | 0.00034299 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2550-4_1_4_load_97 | 75 | 0.0030029 | 0.00075261 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2550-4_1_4_load_98 | 76 | 0.0025106 | 0.00062922 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2550-4_1_4_load_99 | 77 | 0.0032726 | 0.00082019 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2550-4_1_4_load_100 | 78 | 0.0029258 | 0.00073328 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2550-4_1_4_load_169 | 80 | 0.0027257 | 0.00068313 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2550-4_1_4_load_185 | 81 | 0.0015626 | 0.00039162 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2550-4_1_4_load_130 | 82 | 0.0017032 | 0.00042687 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2550-4_1_4_load_140 | 83 | 0.0031415 | 0.00078734 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2550-4_1_4_load_139 | 84 | 0.0033909 | 0.00084983 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2550-4_1_4_load_108 | 85 | 0.0018979 | 0.00047565 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2550-4_1_4_load_111 | 86 | 0.0034479 | 0.00086414 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2550-4_1_4_load_113 | 87 | 0.0072892 | 0.0018268 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2550-4_1_4_load_116 | 88 | 0.0022306 | 0.00055903 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2550-4_1_4_load_117 | 89 | 0.0033934 | 0.00085046 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2550-4_1_4_load_162 | 90 | 0.002966 | 0.00074334 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2550-4_1_4_load_128 | 91 | 0.0019057 | 0.00047761 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2550-4_1_4_load_129 | 92 | 0.0012957 | 0.00032473 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2550-4_1_4_load_220 | 94 | 0.0015286 | 0.00038311 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2550-4_1_4_load_191 | 96 | 0.0026331 | 0.00065991 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2550-4_1_4_load_189 | 97 | 0.0027021 | 0.00067722 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2550-4_1_4_load_141 | 98 | 0.019878 | 0.0049819 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2550-4_1_4_load_182 | 99 | 0.0048418 | 0.0012135 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2550-4_1_4_load_186 | 100 | 0.0033041 | 0.00082809 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2550-4_1_4_load_154 | 101 | 0.0014044 | 0.00035197 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2550-4_1_4_load_156 | 102 | 0.0022086 | 0.00055352 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2550-4_1_4_load_158 | 103 | 0.0021873 | 0.00054818 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2550-4_1_4_load_207 | 104 | 0.0034912 | 0.00087497 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2550-4_1_4_load_159 | 106 | 0.00088542 | 0.00022191 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2550-4_1_4_load_160 | 107 | 0.0020223 | 0.00050684 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2550-4_1_4_load_163 | 109 | 0.0016117 | 0.00040392 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2550-4_1_4_load_170 | 110 | 0.0035505 | 0.00088985 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2550-4_1_4_load_210 | 111 | 0.0054125 | 0.0013565 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2550-4_1_4_load_167 | 112 | 0.0035652 | 0.00089354 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2550-4_1_4_load_168 | 113 | 0.0031267 | 0.00078363 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2550-4_1_4_load_202 | 114 | 0.0080491 | 0.0020173 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2550-4_1_4_load_203 | 115 | 0.0029406 | 0.00073699 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2550-4_1_4_load_205 | 116 | 0.0081546 | 0.0020437 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2550-4_1_4_load_211 | 117 | 0.0085255 | 0.0021367 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2550-4_1_4_line_0 |  | 0 | 1 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2550-4_1_4_line_1 |  | 0 | 2 | 0.015984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2550-4_1_4_line_2 |  | 1 | 3 | 0.038754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2550-4_1_4_line_3 |  | 1 | 4 | 0.02568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2550-4_1_4_line_4 |  | 1 | 5 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2550-4_1_4_line_5 |  | 3 | 6 | 0.011076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2550-4_1_4_line_6 |  | 3 | 7 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2550-4_1_4_line_7 |  | 4 | 8 | 0.0040658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2550-4_1_4_line_8 |  | 6 | 9 | 0.012115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2550-4_1_4_line_9 |  | 7 | 10 | 0.029122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2550-4_1_4_line_10 |  | 7 | 11 | 0.032562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2550-4_1_4_line_11 |  | 8 | 12 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2550-4_1_4_line_12 |  | 10 | 63 | 0.00011322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2550-4_1_4_line_13 |  | 11 | 30 | 0.014787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2550-4_1_4_line_14 |  | 12 | 49 | 0.010831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2550-4_1_4_line_15 |  | 13 | 14 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2550-4_1_4_line_16 |  | 13 | 15 | 0.0068447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2550-4_1_4_line_17 |  | 14 | 16 | 0.018585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2550-4_1_4_line_18 |  | 15 | 17 | 0.025878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2550-4_1_4_line_19 |  | 16 | 18 | 0.018253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2550-4_1_4_line_20 |  | 17 | 19 | 0.044243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2550-4_1_4_line_21 |  | 17 | 20 | 0.015342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2550-4_1_4_line_22 |  | 18 | 21 | 0.020342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2550-4_1_4_line_23 |  | 19 | 22 | 0.01967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2550-4_1_4_line_24 |  | 19 | 23 | 0.035088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2550-4_1_4_line_25 |  | 20 | 24 | 0.017361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2550-4_1_4_line_26 |  | 21 | 60 | 0.0040696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2550-4_1_4_line_27 |  | 22 | 81 | 0.0005753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2550-4_1_4_line_28 |  | 23 | 82 | 0.022127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2550-4_1_4_line_29 |  | 25 | 26 | 0.0096183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2550-4_1_4_line_30 |  | 26 | 27 | 0.019335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2550-4_1_4_line_31 |  | 26 | 28 | 0.0088834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2550-4_1_4_line_32 |  | 28 | 101 | 0.027099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2550-4_1_4_line_33 |  | 29 | 30 | 0.016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2550-4_1_4_line_34 |  | 29 | 31 | 0.0067622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2550-4_1_4_line_35 |  | 30 | 32 | 0.042945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2550-4_1_4_line_36 |  | 32 | 33 | 0.0087131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2550-4_1_4_line_37 |  | 32 | 34 | 0.0099349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2550-4_1_4_line_38 |  | 33 | 35 | 0.0058949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2550-4_1_4_line_39 |  | 34 | 36 | 0.034709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2550-4_1_4_line_40 |  | 35 | 115 | 0.013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2550-4_1_4_line_41 |  | 36 | 62 | 0.0094031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2550-4_1_4_line_42 |  | 36 | 87 | 0.014303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2550-4_1_4_line_43 |  | 37 | 38 | 0.0094691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2550-4_1_4_line_44 |  | 37 | 39 | 0.0056579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2550-4_1_4_line_45 |  | 38 | 40 | 0.011697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2550-4_1_4_line_46 |  | 39 | 41 | 0.0097437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2550-4_1_4_line_47 |  | 40 | 42 | 0.02984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2550-4_1_4_line_48 |  | 40 | 43 | 0.010328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2550-4_1_4_line_49 |  | 41 | 44 | 0.004361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2550-4_1_4_line_50 |  | 42 | 45 | 0.0086622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2550-4_1_4_line_51 |  | 43 | 46 | 0.03402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2550-4_1_4_line_52 |  | 44 | 47 | 0.031945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2550-4_1_4_line_53 |  | 44 | 48 | 0.015921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2550-4_1_4_line_54 |  | 45 | 63 | 0.024981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2550-4_1_4_line_55 |  | 46 | 64 | 0.0038374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2550-4_1_4_line_56 |  | 46 | 65 | 0.010128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2550-4_1_4_line_57 |  | 47 | 99 | 0.013263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2550-4_1_4_line_58 |  | 47 | 110 | 0.0026635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2550-4_1_4_line_59 |  | 48 | 111 | 0.011333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2550-4_1_4_line_60 |  | 49 | 50 | 0.011013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2550-4_1_4_line_61 |  | 51 | 52 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2550-4_1_4_line_62 |  | 51 | 53 | 0.0054274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2550-4_1_4_line_63 |  | 52 | 54 | 0.0038688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2550-4_1_4_line_64 |  | 53 | 55 | 0.019473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2550-4_1_4_line_65 |  | 54 | 56 | 0.020906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2550-4_1_4_line_66 |  | 55 | 57 | 0.0043754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2550-4_1_4_line_67 |  | 56 | 58 | 0.0023493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2550-4_1_4_line_68 |  | 57 | 59 | 0.01846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2550-4_1_4_line_69 |  | 58 | 60 | 0.035824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2550-4_1_4_line_70 |  | 59 | 85 | 0.0072563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2550-4_1_4_line_71 |  | 60 | 61 | 0.021084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2550-4_1_4_line_72 |  | 61 | 62 | 0.034172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2550-4_1_4_line_73 |  | 64 | 90 | 0.02175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2550-4_1_4_line_74 |  | 65 | 88 | 0.0015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2550-4_1_4_line_75 |  | 66 | 67 | 0.024046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2550-4_1_4_line_76 |  | 66 | 68 | 0.0060373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2550-4_1_4_line_77 |  | 67 | 69 | 0.013521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2550-4_1_4_line_78 |  | 68 | 70 | 0.016069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2550-4_1_4_line_79 |  | 69 | 71 | 0.012148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2550-4_1_4_line_80 |  | 70 | 72 | 0.033074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2550-4_1_4_line_81 |  | 71 | 73 | 0.0021728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2550-4_1_4_line_82 |  | 72 | 74 | 0.01794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2550-4_1_4_line_83 |  | 73 | 85 | 0.02171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2550-4_1_4_line_84 |  | 74 | 105 | 0.011654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2550-4_1_4_line_85 |  | 75 | 76 | 0.030514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2550-4_1_4_line_86 |  | 75 | 77 | 0.02456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2550-4_1_4_line_87 |  | 76 | 78 | 0.010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2550-4_1_4_line_88 |  | 78 | 79 | 0.020136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2550-4_1_4_line_89 |  | 79 | 80 | 0.0075303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2550-4_1_4_line_90 |  | 80 | 112 | 0.025932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2550-4_1_4_line_91 |  | 81 | 100 | 0.019848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2550-4_1_4_line_92 |  | 82 | 91 | 0.02187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2550-4_1_4_line_93 |  | 83 | 84 | 0.0055598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2550-4_1_4_line_94 |  | 84 | 98 | 0.00078206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2550-4_1_4_line_95 |  | 86 | 87 | 0.0072959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2550-4_1_4_line_96 |  | 88 | 89 | 0.012207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2550-4_1_4_line_97 |  | 90 | 107 | 0.0053185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2550-4_1_4_line_98 |  | 91 | 92 | 0.026333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2550-4_1_4_line_99 |  | 92 | 93 | 0.019178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2550-4_1_4_line_100 |  | 93 | 94 | 0.044123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2550-4_1_4_line_101 |  | 93 | 95 | 0.027931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2550-4_1_4_line_102 |  | 95 | 96 | 0.041582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2550-4_1_4_line_103 |  | 95 | 97 | 0.01109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2550-4_1_4_line_104 |  | 96 | 114 | 0.011399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2550-4_1_4_line_105 |  | 98 | 99 | 0.043992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2550-4_1_4_line_106 |  | 101 | 102 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2550-4_1_4_line_107 |  | 102 | 103 | 0.021351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2550-4_1_4_line_108 |  | 102 | 104 | 0.029588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2550-4_1_4_line_109 |  | 103 | 105 | 0.010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2550-4_1_4_line_110 |  | 106 | 107 | 0.010292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2550-4_1_4_line_111 |  | 106 | 108 | 0.0018507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2550-4_1_4_line_112 |  | 108 | 109 | 0.020125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2550-4_1_4_line_113 |  | 110 | 113 | 0.010896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2550-4_1_4_line_114 |  | 111 | 117 | 0.0043344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2550-4_1_4_line_115 |  | 112 | 113 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2550-4_1_4_line_116 |  | 115 | 116 | 0.0067805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2550-4_1_4_trafo_13 | 0.63 MVA 20/0.4 kV | 118 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2606039.2992 | 1230361.2058 | 2606019.6696 | 1230354.7809
1 | 2606004.4783 | 1230349.8086 | 2606019.6696 | 1230354.7809
2 | 2606039.2992 | 1230361.2058 | 2606042.0745 | 1230350.3688 | 2606044.1031 | 1230336.4959 | 2606044.3743 | 1230322.9548
3 | 2606039.2992 | 1230361.2058 | 2606031.0623 | 1230385.5287
4 | 2606039.2992 | 1230361.2058 | 2606054.34 | 1230366.7025
5 | 2606044.3743 | 1230322.9548 | 2606054.7776 | 1230326.7566
6 | 2606044.3743 | 1230322.9548 | 2606043.7105 | 1230312.6702 | 2606042.967 | 1230307.3869
7 | 2606029.7581 | 1230389.3797 | 2606031.0623 | 1230385.5287
8 | 2606066.1564 | 1230330.9148 | 2606054.7776 | 1230326.7566
9 | 2606034.2592 | 1230279.7076 | 2606037.0567 | 1230286.4368 | 2606040.1839 | 1230294.8005 | 2606042.4697 | 1230303.8526 | 2606042.967 | 1230307.3869
10 | 2606071.8512 | 1230292.353 | 2606042.967 | 1230307.3869
11 | 2606029.7581 | 1230389.3797 | 2606018.3689 | 1230386.4138
12 | 2606034.2158 | 1230279.6031 | 2606034.2592 | 1230279.7076
13 | 2606085.6323 | 1230297.7147 | 2606071.8512 | 1230292.353
14 | 2606018.3689 | 1230386.4138 | 2606007.8873 | 1230383.6843
15 | 2606079.7326 | 1230190.2585 | 2606093.4174 | 1230198.5766
16 | 2606073.8837 | 1230186.7034 | 2606079.7326 | 1230190.2585
17 | 2606109.5286 | 1230207.8298 | 2606100.9444 | 1230203.1517 | 2606093.4174 | 1230198.5766
18 | 2606073.8837 | 1230186.7034 | 2606079.3927 | 1230176.6251 | 2606084.091 | 1230166.7573 | 2606085.3895 | 1230163.5345
19 | 2606109.5286 | 1230207.8298 | 2606119.3015 | 1230213.0317 | 2606125.802 | 1230216.0849
20 | 2606101.8897 | 1230122.4712 | 2606085.3895 | 1230163.5345
21 | 2606085.3895 | 1230163.5345 | 2606099.5215 | 1230169.505
22 | 2606144.2123 | 1230224.7371 | 2606135.2902 | 1230220.5414 | 2606125.802 | 1230216.0849
23 | 2606101.8897 | 1230122.4712 | 2606119.8815 | 1230130.4202
24 | 2606101.8897 | 1230122.4712 | 2606114.9728 | 1230089.9133
25 | 2606115.514 | 1230176.2615 | 2606099.5215 | 1230169.505
26 | 2606147.895 | 1230226.4689 | 2606144.2123 | 1230224.7371
27 | 2606120.4077 | 1230130.6527 | 2606119.8815 | 1230130.4202
28 | 2606123.2232 | 1230069.3815 | 2606114.9728 | 1230089.9133
29 | 2606208.9854 | 1230235.626 | 2606218.6035 | 1230235.6799
30 | 2606201.0675 | 1230253.2728 | 2606206.1539 | 1230241.8602 | 2606208.9854 | 1230235.626
31 | 2606208.9854 | 1230235.626 | 2606212.6591 | 1230227.5379
32 | 2606223.8658 | 1230202.8645 | 2606212.6591 | 1230227.5379
33 | 2606085.6323 | 1230297.7147 | 2606100.749 | 1230303.5994
34 | 2606107.0506 | 1230306.0525 | 2606100.749 | 1230303.5994
35 | 2606101.298 | 1230257.7179 | 2606085.6323 | 1230297.7147
36 | 2606101.298 | 1230257.7179 | 2606093.1261 | 1230254.6948
37 | 2606101.298 | 1230257.7179 | 2606110.6158 | 1230261.1647
38 | 2606093.1261 | 1230254.6948 | 2606087.5975 | 1230252.6495
39 | 2606143.3567 | 1230272.3694 | 2606140.1456 | 1230272.0882 | 2606110.6158 | 1230261.1647
40 | 2606090.0794 | 1230241.1442 | 2606085.9891 | 1230252.0545 | 2606087.5975 | 1230252.6495
41 | 2606143.3567 | 1230272.3694 | 2606148.438 | 1230264.4575
42 | 2606143.3567 | 1230272.3694 | 2606146.7299 | 1230277.0312 | 2606148.0296 | 1230280.001 | 2606148.5497 | 1230282.4585 | 2606148.6485 | 1230285.2518
43 | 2605998.1381 | 1230213.988 | 2605997.1205 | 1230209.1174 | 2605996.7841 | 1230204.6367 | 2605996.7841 | 1230204.6367
44 | 2605996.6535 | 1230198.9803 | 2605996.7841 | 1230204.6367
45 | 2606002.1793 | 1230224.9653 | 2605998.1381 | 1230213.988
46 | 2605998.0264 | 1230189.351 | 2605997.1284 | 1230193.6193 | 2605996.6534 | 1230198.9776 | 2605996.6535 | 1230198.9803
47 | 2606002.1793 | 1230224.9653 | 2606018.3593 | 1230250.0384
48 | 2606002.1793 | 1230224.9653 | 2605998.2786 | 1230234.5284
49 | 2605999.2348 | 1230185.1608 | 2605998.0264 | 1230189.351
50 | 2606023.0561 | 1230257.3167 | 2606018.3593 | 1230250.0384
51 | 2605985.43 | 1230266.0286 | 2605998.2786 | 1230234.5284
52 | 2606010.6031 | 1230155.2988 | 2606009.1982 | 1230158.9885 | 2605999.2348 | 1230185.1608
53 | 2605999.2348 | 1230185.1608 | 2606014.3843 | 1230190.0581
54 | 2606034.2158 | 1230279.6031 | 2606031.2539 | 1230272.4782 | 2606026.4014 | 1230262.5007 | 2606023.0561 | 1230257.3167
55 | 2605985.43 | 1230266.0286 | 2605984.1234 | 1230269.6367
56 | 2605985.43 | 1230266.0286 | 2605975.9148 | 1230262.5602
57 | 2606010.6031 | 1230155.2988 | 2606022.6568 | 1230160.8327
58 | 2606010.6031 | 1230155.2988 | 2606008.288 | 1230153.9819
59 | 2606014.3843 | 1230190.0581 | 2606019.1407 | 1230191.5957 | 2606023.2137 | 1230193.4342 | 2606024.8337 | 1230194.3586
60 | 2605997.2293 | 1230380.9088 | 2606007.8873 | 1230383.6843
61 | 2606177.373 | 1230148.9653 | 2606172.8364 | 1230160.0104 | 2606170.0125 | 1230167.5352
62 | 2606179.4351 | 1230143.9449 | 2606177.373 | 1230148.9653
63 | 2606168.6531 | 1230171.1573 | 2606170.0125 | 1230167.5352
64 | 2606179.4351 | 1230143.9449 | 2606186.8333 | 1230125.9325
65 | 2606168.6531 | 1230171.1573 | 2606161.3076 | 1230190.7301
66 | 2606186.8333 | 1230125.9325 | 2606188.4956 | 1230121.8852
67 | 2606160.4821 | 1230192.9296 | 2606161.3076 | 1230190.7301
68 | 2606195.5093 | 1230104.809 | 2606188.4956 | 1230121.8852
69 | 2606147.895 | 1230226.4689 | 2606160.4821 | 1230192.9296
70 | 2606195.5093 | 1230104.809 | 2606198.2662 | 1230098.0969
71 | 2606166.904 | 1230235.705 | 2606147.895 | 1230226.4689
72 | 2606166.904 | 1230235.705 | 2606148.438 | 1230264.4575
73 | 2605976.7176 | 1230290.0868 | 2605984.1234 | 1230269.6367
74 | 2605975.9148 | 1230262.5602 | 2605974.4194 | 1230262.0151
75 | 2606249.1646 | 1230082.688 | 2606235.002 | 1230075.3019 | 2606227.485 | 1230072.3568
76 | 2606254.5177 | 1230085.4798 | 2606249.1646 | 1230082.688
77 | 2606214.747 | 1230067.9506 | 2606215.6573 | 1230068.0442 | 2606217.8457 | 1230068.5801 | 2606227.485 | 1230072.3568
78 | 2606268.0821 | 1230093.8585 | 2606267.3711 | 1230092.9016 | 2606265.9559 | 1230091.7661 | 2606263.39 | 1230090.1069 | 2606254.5177 | 1230085.4798
79 | 2606207.34 | 1230076.0051 | 2606209.489 | 1230070.7728 | 2606210.5207 | 1230069.2174 | 2606211.7639 | 1230068.2181 | 2606213.5822 | 1230067.8308 | 2606214.747 | 1230067.9506
80 | 2606268.0821 | 1230093.8585 | 2606268.361 | 1230095.1262 | 2606268.3221 | 1230096.1045 | 2606268.1089 | 1230097.1827 | 2606257.3818 | 1230124.8751
81 | 2606207.34 | 1230076.0051 | 2606206.5145 | 1230078.0149
82 | 2606250.9017 | 1230141.604 | 2606257.3818 | 1230124.8751
83 | 2606206.5145 | 1230078.0149 | 2606198.2662 | 1230098.0969
84 | 2606246.6921 | 1230152.4711 | 2606250.9017 | 1230141.604
85 | 2605940.5603 | 1230182.8508 | 2605950.83 | 1230154.1169
86 | 2605932.2945 | 1230205.9777 | 2605940.5603 | 1230182.8508
87 | 2605954.472 | 1230143.9272 | 2605950.83 | 1230154.1169
88 | 2605961.1135 | 1230124.9204 | 2605959.9662 | 1230128.5548 | 2605954.472 | 1230143.9272
89 | 2605961.1135 | 1230124.9204 | 2605967.4909 | 1230128.9247
90 | 2605967.4909 | 1230128.9247 | 2605989.4524 | 1230142.7143
91 | 2606138.5625 | 1230138.6738 | 2606120.4077 | 1230130.6527
92 | 2606123.2232 | 1230069.3815 | 2606131.3779 | 1230049.0882
93 | 2606059.8317 | 1230127.4348 | 2606057.0589 | 1230132.2539
94 | 2606057.0589 | 1230132.2539 | 2606056.6689 | 1230132.9317
95 | 2606148.6485 | 1230285.2518 | 2606148.6527 | 1230285.3715 | 2606147.7551 | 1230289.1283 | 2606146.5537 | 1230292.2163
96 | 2605974.4194 | 1230262.0151 | 2605962.951 | 1230257.8347
97 | 2605974.9067 | 1230295.0875 | 2605976.7176 | 1230290.0868
98 | 2606141.1963 | 1230024.6544 | 2606131.3779 | 1230049.0882
99 | 2606148.6043 | 1230006.9723 | 2606146.6004 | 1230011.2061 | 2606141.1963 | 1230024.6544
100 | 2606148.6043 | 1230006.9723 | 2606153.2056 | 1230010.7792 | 2606165.944 | 1230012.3821 | 2606175.2263 | 1230016.0939 | 2606187.1563 | 1230022.988 | 2606188.4805 | 1230023.7676
101 | 2606165.5028 | 1229984.6985 | 2606148.6043 | 1230006.9723
102 | 2606165.5028 | 1229984.6985 | 2606198.1975 | 1229959.0057
103 | 2606165.5028 | 1229984.6985 | 2606161.0754 | 1229974.5308
104 | 2606198.1975 | 1229959.0057 | 2606198.1975 | 1229959.0057 | 2606208.6042 | 1229954.3543
105 | 2606056.6689 | 1230132.9317 | 2606022.6568 | 1230160.8327
106 | 2606223.8658 | 1230202.8645 | 2606233.441 | 1230181.7829
107 | 2606242.2705 | 1230162.3434 | 2606233.441 | 1230181.7829
108 | 2606233.441 | 1230181.7829 | 2606262.1869 | 1230188.7932
109 | 2606246.6921 | 1230152.4711 | 2606244.6043 | 1230157.2051 | 2606242.2705 | 1230162.3434
110 | 2605974.9067 | 1230295.0875 | 2605971.4022 | 1230304.7647
111 | 2605970.772 | 1230306.5048 | 2605971.4022 | 1230304.7647
112 | 2605970.772 | 1230306.5048 | 2605963.921 | 1230325.4279
113 | 2606008.288 | 1230153.9819 | 2605998.8169 | 1230148.5942 | 2605998.8169 | 1230148.5942
114 | 2606025.9356 | 1230198.2509 | 2606026.0587 | 1230196.361 | 2606025.8324 | 1230195.3602 | 2606024.8337 | 1230194.3586
115 | 2605989.4524 | 1230142.7143 | 2605998.8169 | 1230148.5942
116 | 2606092.4596 | 1230234.7952 | 2606090.0794 | 1230241.1442

## bus_geodata
| x | y | coords
0 | 2606019.6696 | 1230354.7809
1 | 2606039.2992 | 1230361.2058
2 | 2606004.4783 | 1230349.8086
3 | 2606044.3743 | 1230322.9548
4 | 2606031.0623 | 1230385.5287
5 | 2606054.34 | 1230366.7025
6 | 2606054.7776 | 1230326.7566
7 | 2606042.967 | 1230307.3869
8 | 2606029.7581 | 1230389.3797
9 | 2606066.1564 | 1230330.9148
10 | 2606034.2592 | 1230279.7076
11 | 2606071.8512 | 1230292.353
12 | 2606018.3689 | 1230386.4138
13 | 2606079.7326 | 1230190.2585
14 | 2606093.4174 | 1230198.5765
15 | 2606073.8837 | 1230186.7034
16 | 2606109.5286 | 1230207.8298
17 | 2606085.3895 | 1230163.5345
18 | 2606125.802 | 1230216.0849
19 | 2606101.8897 | 1230122.4712
20 | 2606099.5215 | 1230169.505
21 | 2606144.2123 | 1230224.7371
22 | 2606119.8815 | 1230130.4202
23 | 2606114.9728 | 1230089.9133
24 | 2606115.514 | 1230176.2615
25 | 2606218.6035 | 1230235.6799
26 | 2606208.9854 | 1230235.626
27 | 2606201.0675 | 1230253.2728
28 | 2606212.6591 | 1230227.5379
29 | 2606100.749 | 1230303.5994
30 | 2606085.6323 | 1230297.7147
31 | 2606107.0506 | 1230306.0525
32 | 2606101.298 | 1230257.7179
33 | 2606093.1261 | 1230254.6948
34 | 2606110.6158 | 1230261.1647
35 | 2606087.5975 | 1230252.6495
36 | 2606143.3567 | 1230272.3694
37 | 2605996.7841 | 1230204.6367
38 | 2605998.1381 | 1230213.988
39 | 2605996.6535 | 1230198.9803
40 | 2606002.1793 | 1230224.9653
41 | 2605998.0264 | 1230189.351
42 | 2606018.3593 | 1230250.0384
43 | 2605998.2786 | 1230234.5284
44 | 2605999.2348 | 1230185.1608
45 | 2606023.0561 | 1230257.3167
46 | 2605985.43 | 1230266.0286
47 | 2606010.6031 | 1230155.2988
48 | 2606014.3843 | 1230190.0581
49 | 2606007.8873 | 1230383.6843
50 | 2605997.2293 | 1230380.9088
51 | 2606177.373 | 1230148.9653
52 | 2606170.0125 | 1230167.5352
53 | 2606179.4351 | 1230143.9449
54 | 2606168.6531 | 1230171.1573
55 | 2606186.8333 | 1230125.9325
56 | 2606161.3076 | 1230190.7301
57 | 2606188.4956 | 1230121.8852
58 | 2606160.4821 | 1230192.9296
59 | 2606195.5093 | 1230104.809
60 | 2606147.895 | 1230226.4689
61 | 2606166.904 | 1230235.705
62 | 2606148.438 | 1230264.4575
63 | 2606034.2158 | 1230279.6031
64 | 2605984.1234 | 1230269.6367
65 | 2605975.9148 | 1230262.5602
66 | 2606249.1646 | 1230082.688
67 | 2606227.485 | 1230072.3568
68 | 2606254.5177 | 1230085.4798
69 | 2606214.747 | 1230067.9506
70 | 2606268.0821 | 1230093.8585
71 | 2606207.34 | 1230076.0051
72 | 2606257.3818 | 1230124.8751
73 | 2606206.5145 | 1230078.0149
74 | 2606250.9017 | 1230141.604
75 | 2605940.5603 | 1230182.8508
76 | 2605950.83 | 1230154.1169
77 | 2605932.2945 | 1230205.9777
78 | 2605954.472 | 1230143.9272
79 | 2605961.1135 | 1230124.9204
80 | 2605967.4909 | 1230128.9247
81 | 2606120.4077 | 1230130.6527
82 | 2606123.2232 | 1230069.3815
83 | 2606059.8317 | 1230127.4348
84 | 2606057.0589 | 1230132.2539
85 | 2606198.2662 | 1230098.0969
86 | 2606146.5537 | 1230292.2163
87 | 2606148.6485 | 1230285.2518
88 | 2605974.4194 | 1230262.0151
89 | 2605962.951 | 1230257.8347
90 | 2605976.7176 | 1230290.0868
91 | 2606131.3779 | 1230049.0882
92 | 2606141.1963 | 1230024.6544
93 | 2606148.6043 | 1230006.9723
94 | 2606188.4805 | 1230023.7676
95 | 2606165.5028 | 1229984.6985
96 | 2606198.1975 | 1229959.0057
97 | 2606161.0754 | 1229974.5308
98 | 2606056.6689 | 1230132.9317
99 | 2606022.6568 | 1230160.8327
100 | 2606138.5625 | 1230138.6738
101 | 2606223.8658 | 1230202.8645
102 | 2606233.441 | 1230181.7829
103 | 2606242.2705 | 1230162.3434
104 | 2606262.1869 | 1230188.7932
105 | 2606246.6921 | 1230152.4711
106 | 2605971.4022 | 1230304.7647
107 | 2605974.9067 | 1230295.0875
108 | 2605970.772 | 1230306.5048
109 | 2605963.921 | 1230325.4279
110 | 2606008.288 | 1230153.9819
111 | 2606024.8337 | 1230194.3586
112 | 2605989.4524 | 1230142.7143
113 | 2605998.8169 | 1230148.5942
114 | 2606208.6042 | 1229954.3543
115 | 2606090.0794 | 1230241.1442
116 | 2606092.4596 | 1230234.7952
117 | 2606025.9356 | 1230198.2509
118 | 2606109.5286 | 1230207.8298

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98337 | -0.31784 | 0.0035613 | 0.00089256
1 | 0.98346 | -0.31604 | 0 | 0
2 | 0.98335 | -0.3182 | 0.001251 | 0.00031354
3 | 0.98403 | -0.30488 | 0 | 0
4 | 0.98324 | -0.32032 | 0.0025395 | 0.00063646
5 | 0.98343 | -0.31661 | 0.0019485 | 0.00048834
6 | 0.98395 | -0.30662 | 0.0031884 | 0.00079909
7 | 0.98439 | -0.29791 | 0.0047964 | 0.0012021
8 | 0.98322 | -0.32081 | 0 | 0
9 | 0.98388 | -0.30783 | 0.0055654 | 0.0013948
10 | 0.98286 | -0.32741 | 0.0025044 | 0.00062767
11 | 0.98654 | -0.2564 | 0.0053674 | 0.0013452
12 | 0.98315 | -0.32223 | 0.0023736 | 0.00059489
13 | 0.99938 | -0.011911 | 0.0094632 | 0.0023717
14 | 1 | 0 | -0.29975 | -0.076404
15 | 0.99917 | -0.015875 | 0 | 0
16 | 0.99856 | -0.027151 | 0 | 0
17 | 0.99839 | -0.030879 | 0 | 0
18 | 0.99715 | -0.053894 | 0.0043793 | 0.0010976
19 | 0.99722 | -0.053318 | 0 | 0
20 | 0.99833 | -0.032008 | 0.0024077 | 0.00060342
21 | 0.9956 | -0.083264 | 0.0062335 | 0.0015623
22 | 0.99709 | -0.055874 | 0.0025471 | 0.00063836
23 | 0.99653 | -0.066583 | 0.0017299 | 0.00043355
24 | 0.9983 | -0.032554 | 0.0018005 | 0.00045125
25 | 0.98521 | -0.28426 | 0.00028658 | 7.1823e-05
26 | 0.98521 | -0.28421 | 0 | 0
27 | 0.98515 | -0.28537 | 0.0033463 | 0.00083867
28 | 0.98524 | -0.28363 | 0.0027855 | 0.0006981
29 | 0.98712 | -0.24535 | 0.0059142 | 0.0014822
30 | 0.98722 | -0.2434 | 0 | 0
31 | 0.98711 | -0.24545 | 0.00080595 | 0.00020199
32 | 0.98927 | -0.20402 | 0 | 0
33 | 0.98916 | -0.20608 | 0.0013083 | 0.00032789
34 | 0.98978 | -0.19415 | 0.0014145 | 0.0003545
35 | 0.9891 | -0.20734 | 0.00090206 | 0.00022608
36 | 0.9916 | -0.15945 | 0 | 0
37 | 0.97508 | -0.47927 | 0.0027294 | 0.00068406
38 | 0.97579 | -0.46537 | 0.0020772 | 0.0005206
39 | 0.97467 | -0.4873 | 0.0019378 | 0.00048566
40 | 0.97668 | -0.44778 | 0 | 0
41 | 0.97398 | -0.5008 | 0.0019032 | 0.00047698
42 | 0.97951 | -0.39249 | 0.0015529 | 0.0003892
43 | 0.9765 | -0.45146 | 0.0020798 | 0.00052125
44 | 0.97368 | -0.50669 | 0 | 0
45 | 0.98035 | -0.37626 | 0.0043439 | 0.0010887
46 | 0.97595 | -0.46229 | 0 | 0
47 | 0.97201 | -0.5396 | 0 | 0
48 | 0.97342 | -0.51185 | 0.0036801 | 0.00092231
49 | 0.9831 | -0.32308 | 0.0023365 | 0.00058558
50 | 0.98308 | -0.32347 | 0.0019869 | 0.00049796
51 | 0.99153 | -0.16147 | 0.0010518 | 0.0002636
52 | 0.99236 | -0.14557 | 0.0019132 | 0.00047949
53 | 0.99131 | -0.1657 | 0.0018161 | 0.00045515
54 | 0.99252 | -0.14236 | 0.0017408 | 0.00043627
55 | 0.99056 | -0.18024 | 0.0011108 | 0.00027838
56 | 0.99346 | -0.1244 | 0.002207 | 0.00055312
57 | 0.9904 | -0.18342 | 0.0026198 | 0.00065658
58 | 0.99357 | -0.12229 | 0.001921 | 0.00048144
59 | 0.98975 | -0.19601 | 0.0011224 | 0.0002813
60 | 0.9953 | -0.089002 | 0 | 0
61 | 0.99407 | -0.11225 | 0.0027859 | 0.00069822
62 | 0.99212 | -0.14948 | 0.0053568 | 0.0013425
63 | 0.98285 | -0.32764 | 0.0023894 | 0.00059883
64 | 0.97591 | -0.46304 | 0.0031995 | 0.00080187
65 | 0.97588 | -0.46354 | 0.0010959 | 0.00027465
66 | 0.98746 | -0.24039 | 0.0037402 | 0.00093739
67 | 0.98803 | -0.22932 | 0.0019232 | 0.000482
68 | 0.98734 | -0.24276 | 0.0021239 | 0.00053231
69 | 0.98837 | -0.22264 | 0.0040191 | 0.0010073
70 | 0.98704 | -0.24848 | 0 | 0
71 | 0.98873 | -0.21578 | 0.0018262 | 0.0004577
72 | 0.98644 | -0.26025 | 0.0028031 | 0.00070253
73 | 0.98879 | -0.21448 | 0.0017987 | 0.00045081
74 | 0.98616 | -0.26574 | 0.0013685 | 0.00034299
75 | 0.97063 | -0.56695 | 0.0030029 | 0.00075261
76 | 0.97081 | -0.56341 | 0.0025106 | 0.00062922
77 | 0.97056 | -0.56844 | 0.0032726 | 0.00082019
78 | 0.9709 | -0.56165 | 0.0029258 | 0.00073328
79 | 0.97112 | -0.55729 | 0 | 0
80 | 0.9712 | -0.55566 | 0.0027257 | 0.00068313
81 | 0.99709 | -0.055924 | 0.0015626 | 0.00039162
82 | 0.99613 | -0.074285 | 0.0017032 | 0.00042687
83 | 0.97052 | -0.56914 | 0.0031415 | 0.00078734
84 | 0.97054 | -0.56882 | 0.0033909 | 0.00084983
85 | 0.9895 | -0.20082 | 0.0018979 | 0.00047565
86 | 0.99144 | -0.16262 | 0.0034479 | 0.00086414
87 | 0.99146 | -0.16218 | 0.0072892 | 0.0018268
88 | 0.97587 | -0.4637 | 0.0022306 | 0.00055903
89 | 0.97584 | -0.46446 | 0.0033934 | 0.00085046
90 | 0.97576 | -0.46602 | 0.002966 | 0.00074334
91 | 0.99577 | -0.081249 | 0.0019057 | 0.00047761
92 | 0.99538 | -0.088757 | 0.0012957 | 0.00032473
93 | 0.99512 | -0.093791 | 0 | 0
94 | 0.99506 | -0.094979 | 0.0015286 | 0.00038311
95 | 0.99478 | -0.10037 | 0 | 0
96 | 0.99438 | -0.1082 | 0.0026331 | 0.00065991
97 | 0.99476 | -0.1009 | 0.0027021 | 0.00067722
98 | 0.97054 | -0.56873 | 0.019878 | 0.0049819
99 | 0.97163 | -0.54725 | 0.0048418 | 0.0012135
100 | 0.99703 | -0.057073 | 0.0033041 | 0.00082809
101 | 0.9854 | -0.28051 | 0.0014044 | 0.00035197
102 | 0.98557 | -0.27725 | 0.0022086 | 0.00055352
103 | 0.98583 | -0.27207 | 0.0021873 | 0.00054818
104 | 0.98547 | -0.27911 | 0.0034912 | 0.00087497
105 | 0.98599 | -0.26903 | 0 | 0
106 | 0.97571 | -0.46693 | 0.00088542 | 0.00022191
107 | 0.97573 | -0.46646 | 0.0020223 | 0.00050684
108 | 0.97571 | -0.46699 | 0 | 0
109 | 0.97568 | -0.46758 | 0.0016117 | 0.00040392
110 | 0.97195 | -0.54082 | 0.0035505 | 0.00088985
111 | 0.97328 | -0.51476 | 0.0054125 | 0.0013565
112 | 0.97155 | -0.54874 | 0.0035652 | 0.00089354
113 | 0.97174 | -0.54506 | 0.0031267 | 0.00078363
114 | 0.99429 | -0.10982 | 0.0080491 | 0.0020173
115 | 0.98896 | -0.20999 | 0.0029406 | 0.00073699
116 | 0.98891 | -0.21097 | 0.0081546 | 0.0020437
117 | 0.97324 | -0.51544 | 0.0085255 | 0.0021367
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0048124 | -0.0012059 | 0.0048128 | 0.0012059 | 4.1071e-07 | 7.9509e-10 | 0.007282 | 0.0072819 | 0.007282 | 0.98337 | -0.31784 | 0.98346 | -0.31604 | 2.0005
1 | 0.0012511 | 0.00031335 | -0.001251 | -0.00031354 | 2.1481e-08 | -1.8904e-07 | 0.001893 | 0.0018931 | 0.0018931 | 0.98337 | -0.31784 | 0.98335 | -0.3182 | 0.52008
2 | -0.016001 | -0.0040099 | 0.016009 | 0.0040149 | 8.5175e-06 | 4.9592e-06 | 0.024209 | 0.024209 | 0.024209 | 0.98346 | -0.31604 | 0.98403 | -0.30488 | 6.6509
3 | 0.0092392 | 0.0023158 | -0.0092373 | -0.0023149 | 1.8819e-06 | 8.7865e-07 | 0.013979 | 0.013979 | 0.013979 | 0.98346 | -0.31604 | 0.98324 | -0.32032 | 3.8405
4 | 0.0019486 | 0.00048817 | -0.0019485 | -0.00048834 | 5.2197e-08 | -1.6979e-07 | 0.0029482 | 0.0029483 | 0.0029483 | 0.98346 | -0.31604 | 0.98343 | -0.31661 | 0.80996
5 | 0.0087548 | 0.0021943 | -0.0087541 | -0.002194 | 7.2798e-07 | 3.2521e-07 | 0.013239 | 0.013239 | 0.013239 | 0.98403 | -0.30488 | 0.98395 | -0.30662 | 3.637
6 | -0.024764 | -0.0062091 | 0.024772 | 0.0062142 | 8.2255e-06 | 5.0655e-06 | 0.037448 | 0.037448 | 0.037448 | 0.98403 | -0.30488 | 0.98439 | -0.29791 | 10.2879
7 | 0.0066978 | 0.0016785 | -0.0066977 | -0.0016784 | 1.5665e-07 | 4.8691e-08 | 0.010136 | 0.010136 | 0.010136 | 0.98324 | -0.32032 | 0.98322 | -0.32081 | 2.7847
8 | 0.0055657 | 0.0013949 | -0.0055654 | -0.0013948 | 3.2185e-07 | 5.2121e-08 | 0.0084169 | 0.008417 | 0.008417 | 0.98395 | -0.30662 | 0.98388 | -0.30783 | 2.3124
9 | 0.11363 | 0.028922 | -0.11347 | -0.028819 | 0.0001614 | 0.00010255 | 0.17192 | 0.17192 | 0.17192 | 0.98439 | -0.29791 | 0.98286 | -0.32741 | 23.6159
10 | -0.1432 | -0.036338 | 0.14349 | 0.036521 | 0.0002865 | 0.00018253 | 0.21662 | 0.21662 | 0.21662 | 0.98439 | -0.29791 | 0.98654 | -0.2564 | 29.7557
11 | 0.0066977 | 0.0016784 | -0.0066972 | -0.0016783 | 4.5346e-07 | 1.4096e-07 | 0.010136 | 0.010136 | 0.010136 | 0.98322 | -0.32081 | 0.98315 | -0.32223 | 2.7847
12 | 0.11096 | 0.028192 | -0.11096 | -0.028191 | 1.2002e-06 | 7.667e-07 | 0.16813 | 0.16813 | 0.16813 | 0.98286 | -0.32741 | 0.98285 | -0.32764 | 46.1902
13 | -0.14885 | -0.037866 | 0.14895 | 0.037925 | 9.3341e-05 | 5.9172e-05 | 0.22472 | 0.22472 | 0.22472 | 0.98654 | -0.2564 | 0.98722 | -0.2434 | 20.5785
14 | 0.0043236 | 0.0010834 | -0.0043234 | -0.0010834 | 1.7393e-07 | -2.6028e-08 | 0.0065438 | 0.0065439 | 0.0065439 | 0.98315 | -0.32223 | 0.9831 | -0.32308 | 1.7978
15 | -0.04274 | -0.010748 | 0.042765 | 0.010764 | 2.4331e-05 | 1.5362e-05 | 0.063651 | 0.063651 | 0.063651 | 0.99938 | -0.011911 | 1 | 0 | 17.4865
16 | 0.033277 | 0.0083767 | -0.033271 | -0.0083728 | 6.3047e-06 | 3.9453e-06 | 0.049561 | 0.049561 | 0.049561 | 0.99938 | -0.011911 | 0.99917 | -0.015875 | 13.6156
17 | 0.25533 | 0.06564 | -0.255 | -0.065426 | 0.00033638 | 0.00021455 | 0.38053 | 0.38053 | 0.38053 | 1 | 0 | 0.99856 | -0.027151 | 34.8467
18 | 0.033271 | 0.0083728 | -0.033247 | -0.0083579 | 2.3836e-05 | 1.4917e-05 | 0.049561 | 0.049561 | 0.049561 | 0.99917 | -0.015875 | 0.99839 | -0.030879 | 13.6156
19 | 0.255 | 0.065426 | -0.25467 | -0.065215 | 0.00033038 | 0.00021073 | 0.38053 | 0.38053 | 0.38053 | 0.99856 | -0.027151 | 0.99715 | -0.053894 | 34.8467
20 | 0.029039 | 0.0073035 | -0.029008 | -0.0072842 | 3.1091e-05 | 1.932e-05 | 0.043289 | 0.043289 | 0.043289 | 0.99839 | -0.030879 | 0.99722 | -0.053318 | 11.8926
21 | 0.0042084 | 0.0010544 | -0.0042082 | -0.0010545 | 2.2633e-07 | -5.5759e-08 | 0.0062722 | 0.0062723 | 0.0062723 | 0.99839 | -0.030879 | 0.99833 | -0.032008 | 1.7231
22 | 0.25029 | 0.064118 | -0.24993 | -0.063891 | 0.00035565 | 0.00022682 | 0.37399 | 0.37399 | 0.37399 | 0.99715 | -0.053894 | 0.9956 | -0.083264 | 34.2483
23 | 0.0074149 | 0.0018582 | -0.007414 | -0.0018579 | 9.0295e-07 | 3.213e-07 | 0.011064 | 0.011064 | 0.011064 | 0.99722 | -0.053318 | 0.99709 | -0.055874 | 3.0396
24 | 0.021593 | 0.0054259 | -0.021579 | -0.0054176 | 1.3664e-05 | 8.2875e-06 | 0.032225 | 0.032225 | 0.032225 | 0.99722 | -0.053318 | 0.99653 | -0.066583 | 8.853
25 | 0.0018005 | 0.00045105 | -0.0018005 | -0.00045125 | 4.6889e-08 | -1.9699e-07 | 0.0026836 | 0.0026837 | 0.0026837 | 0.99833 | -0.032008 | 0.9983 | -0.032554 | 0.73728
26 | 0.2437 | 0.062329 | -0.24363 | -0.062285 | 6.765e-05 | 4.3138e-05 | 0.36467 | 0.36467 | 0.36467 | 0.9956 | -0.083264 | 0.9953 | -0.089002 | 33.3951
27 | 0.0048669 | 0.0012196 | -0.0048669 | -0.0012196 | 1.1381e-08 | -2.1999e-10 | 0.0072631 | 0.0072631 | 0.0072631 | 0.99709 | -0.055874 | 0.99709 | -0.055924 | 1.9954
28 | 0.019849 | 0.0049841 | -0.019842 | -0.0049797 | 7.2908e-06 | 4.378e-06 | 0.029642 | 0.029642 | 0.029642 | 0.99653 | -0.066583 | 0.99613 | -0.074285 | 8.1434
29 | -0.00028658 | -7.1823e-05 | 0.00028658 | 7.1701e-05 | 6.7567e-10 | -1.2205e-07 | 0.00043284 | 0.00043279 | 0.00043284 | 0.98521 | -0.28426 | 0.98521 | -0.28421 | 0.11891
30 | 0.0033465 | 0.00083854 | -0.0033463 | -0.00083867 | 1.8523e-07 | -1.2765e-07 | 0.0050543 | 0.0050544 | 0.0050544 | 0.98521 | -0.28421 | 0.98515 | -0.28537 | 1.3886
31 | -0.0036331 | -0.00091024 | 0.0036332 | 0.00091019 | 1.003e-07 | -4.8933e-08 | 0.0054871 | 0.0054871 | 0.0054871 | 0.98521 | -0.28421 | 0.98524 | -0.28363 | 1.5075
32 | -0.0064186 | -0.0016083 | 0.0064196 | 0.0016086 | 9.5497e-07 | 2.6602e-07 | 0.009694 | 0.0096939 | 0.009694 | 0.98524 | -0.28363 | 0.9854 | -0.28051 | 2.6632
33 | -0.0067202 | -0.0016842 | 0.0067208 | 0.0016843 | 6.2426e-07 | 1.9213e-07 | 0.01013 | 0.01013 | 0.01013 | 0.98712 | -0.24535 | 0.98722 | -0.2434 | 2.783
34 | 0.00080596 | 0.00020191 | -0.00080595 | -0.00020199 | 3.7429e-09 | -8.4048e-08 | 0.0012149 | 0.0012149 | 0.0012149 | 0.98712 | -0.24535 | 0.98711 | -0.24545 | 0.33377
35 | -0.15567 | -0.039609 | 0.15596 | 0.039797 | 0.00029607 | 0.00018783 | 0.23485 | 0.23485 | 0.23485 | 0.98722 | -0.2434 | 0.98927 | -0.20402 | 21.5061
36 | 0.013309 | 0.0033367 | -0.013308 | -0.003336 | 1.3095e-06 | 7.2625e-07 | 0.02002 | 0.02002 | 0.02002 | 0.98927 | -0.20402 | 0.98916 | -0.20608 | 5.4999
37 | -0.16927 | -0.043134 | 0.16935 | 0.043185 | 8.0667e-05 | 5.1244e-05 | 0.25487 | 0.25487 | 0.25487 | 0.98927 | -0.20402 | 0.98978 | -0.19415 | 23.3394
38 | 0.012 | 0.0030081 | -0.011999 | -0.0030077 | 7.2034e-07 | 3.8536e-07 | 0.018052 | 0.018052 | 0.018052 | 0.98916 | -0.20608 | 0.9891 | -0.20734 | 4.9593
39 | -0.17077 | -0.04354 | 0.17105 | 0.043722 | 0.00028654 | 0.00018205 | 0.25699 | 0.25699 | 0.25699 | 0.98978 | -0.19415 | 0.9916 | -0.15945 | 23.5341
40 | 0.011097 | 0.0027816 | -0.011096 | -0.0027809 | 1.3971e-06 | 7.2258e-07 | 0.016695 | 0.016695 | 0.016695 | 0.9891 | -0.20734 | 0.98896 | -0.20999 | 4.5865
41 | -0.18179 | -0.046413 | 0.18188 | 0.046469 | 8.7668e-05 | 5.5744e-05 | 0.27311 | 0.27311 | 0.27311 | 0.9916 | -0.15945 | 0.99212 | -0.14948 | 25.0097
42 | 0.010739 | 0.0026916 | -0.010737 | -0.0026909 | 1.3928e-06 | 7.0694e-07 | 0.016115 | 0.016115 | 0.016115 | 0.9916 | -0.15945 | 0.99146 | -0.16218 | 4.4271
43 | -0.080372 | -0.020237 | 0.080426 | 0.020272 | 5.3448e-05 | 3.4089e-05 | 0.12269 | 0.12269 | 0.12269 | 0.97508 | -0.47927 | 0.97579 | -0.46537 | 33.7049
44 | 0.077643 | 0.019553 | -0.077613 | -0.019534 | 2.9804e-05 | 1.9004e-05 | 0.11852 | 0.11852 | 0.11852 | 0.97508 | -0.47927 | 0.97467 | -0.4873 | 32.5606
45 | -0.082503 | -0.020792 | 0.082572 | 0.020836 | 6.9479e-05 | 4.432e-05 | 0.12585 | 0.12585 | 0.12585 | 0.97579 | -0.46537 | 0.97668 | -0.44778 | 34.5751
46 | 0.075675 | 0.019049 | -0.075626 | -0.019018 | 4.8796e-05 | 3.1108e-05 | 0.11556 | 0.11556 | 0.11556 | 0.97467 | -0.4873 | 0.97398 | -0.5008 | 31.7479
47 | -0.10207 | -0.025727 | 0.10234 | 0.0259 | 0.0002708 | 0.00017294 | 0.15556 | 0.15556 | 0.15556 | 0.97668 | -0.44778 | 0.97951 | -0.39249 | 42.737
48 | 0.019499 | 0.004891 | -0.019496 | -0.0048889 | 3.4185e-06 | 2.0586e-06 | 0.029709 | 0.029709 | 0.029709 | 0.97668 | -0.44778 | 0.9765 | -0.45146 | 8.1619
49 | 0.073723 | 0.018541 | -0.073702 | -0.018527 | 2.0755e-05 | 1.3229e-05 | 0.11265 | 0.11265 | 0.11265 | 0.97398 | -0.5008 | 0.97368 | -0.50669 | 30.9491
50 | -0.1039 | -0.02629 | 0.10398 | 0.026341 | 8.1011e-05 | 5.1738e-05 | 0.15792 | 0.15792 | 0.15792 | 0.97951 | -0.39249 | 0.98035 | -0.37626 | 43.3851
51 | 0.017416 | 0.0043677 | -0.017407 | -0.0043624 | 8.986e-06 | 5.3257e-06 | 0.02654 | 0.02654 | 0.02654 | 0.9765 | -0.45146 | 0.97595 | -0.46229 | 7.2912
52 | 0.056078 | 0.014108 | -0.05599 | -0.014052 | 8.8023e-05 | 5.5938e-05 | 0.08572 | 0.08572 | 0.08572 | 0.97368 | -0.50669 | 0.97201 | -0.5396 | 23.5494
53 | 0.017625 | 0.0044193 | -0.01762 | -0.0044167 | 4.3316e-06 | 2.5743e-06 | 0.026935 | 0.026935 | 0.026935 | 0.97368 | -0.50669 | 0.97342 | -0.51185 | 7.3998
54 | -0.10832 | -0.02743 | 0.10857 | 0.027592 | 0.00025354 | 0.00016195 | 0.16451 | 0.16451 | 0.16451 | 0.98035 | -0.37626 | 0.98285 | -0.32764 | 45.1964
55 | 0.010687 | 0.0026782 | -0.010686 | -0.002678 | 3.8204e-07 | 1.9656e-07 | 0.016294 | 0.016294 | 0.016294 | 0.97595 | -0.46229 | 0.97591 | -0.46304 | 4.4763
56 | 0.0067204 | 0.0016842 | -0.00672 | -0.0016841 | 3.9874e-07 | 1.2865e-07 | 0.010246 | 0.010247 | 0.010247 | 0.97595 | -0.46229 | 0.97588 | -0.46354 | 2.815
57 | 0.031291 | 0.0078564 | -0.031279 | -0.0078493 | 1.1415e-05 | 7.1413e-06 | 0.047907 | 0.047907 | 0.047907 | 0.97201 | -0.5396 | 0.97163 | -0.54725 | 13.1612
58 | 0.024699 | 0.0061958 | -0.024698 | -0.0061949 | 1.4281e-06 | 8.8098e-07 | 0.037813 | 0.037813 | 0.037813 | 0.97201 | -0.5396 | 0.97195 | -0.54082 | 10.3882
59 | 0.01394 | 0.0034944 | -0.013938 | -0.0034933 | 1.9298e-06 | 1.0942e-06 | 0.02131 | 0.02131 | 0.02131 | 0.97342 | -0.51185 | 0.97328 | -0.51476 | 5.8543
60 | 0.0019869 | 0.00049785 | -0.0019869 | -0.00049796 | 3.7353e-08 | -1.1574e-07 | 0.0030073 | 0.0030074 | 0.0030074 | 0.9831 | -0.32308 | 0.98308 | -0.32347 | 0.82621
61 | -0.0451 | -0.011364 | 0.045135 | 0.011386 | 3.4341e-05 | 2.172e-05 | 0.067705 | 0.067705 | 0.067705 | 0.99153 | -0.16147 | 0.99236 | -0.14557 | 18.6002
62 | 0.044048 | 0.011101 | -0.04404 | -0.011095 | 8.8996e-06 | 5.6258e-06 | 0.066126 | 0.066126 | 0.066126 | 0.99153 | -0.16147 | 0.99131 | -0.1657 | 18.1665
63 | -0.047048 | -0.011865 | 0.047055 | 0.01187 | 7.2258e-06 | 4.5745e-06 | 0.070573 | 0.070573 | 0.070573 | 0.99236 | -0.14557 | 0.99252 | -0.14236 | 19.3883
64 | 0.042223 | 0.01064 | -0.042194 | -0.010621 | 2.9352e-05 | 1.8534e-05 | 0.0634 | 0.0634 | 0.0634 | 0.99131 | -0.1657 | 0.99056 | -0.18024 | 17.4176
65 | -0.048796 | -0.012306 | 0.048838 | 0.012333 | 4.1987e-05 | 2.6601e-05 | 0.073183 | 0.073183 | 0.073183 | 0.99252 | -0.14236 | 0.99346 | -0.1244 | 20.1052
66 | 0.041083 | 0.010343 | -0.041077 | -0.010339 | 6.2526e-06 | 3.9454e-06 | 0.061732 | 0.061732 | 0.061732 | 0.99056 | -0.18024 | 0.9904 | -0.18342 | 16.9592
67 | -0.051045 | -0.012886 | 0.05105 | 0.012889 | 5.1543e-06 | 3.2683e-06 | 0.076489 | 0.076489 | 0.076489 | 0.99346 | -0.1244 | 0.99357 | -0.12229 | 21.0133
68 | 0.038457 | 0.0096824 | -0.038434 | -0.0096678 | 2.3124e-05 | 1.4562e-05 | 0.057796 | 0.057796 | 0.057796 | 0.9904 | -0.18342 | 0.98975 | -0.19601 | 15.8779
69 | -0.052971 | -0.013371 | 0.053055 | 0.013424 | 8.4618e-05 | 5.3691e-05 | 0.079366 | 0.079365 | 0.079366 | 0.99357 | -0.12229 | 0.9953 | -0.089002 | 21.8037
70 | 0.037312 | 0.0093865 | -0.037303 | -0.0093811 | 8.5664e-06 | 5.3892e-06 | 0.056108 | 0.056108 | 0.056108 | 0.98975 | -0.19601 | 0.9895 | -0.20082 | 15.4143
71 | 0.19058 | 0.048861 | -0.19036 | -0.048725 | 0.00021453 | 0.00013648 | 0.28531 | 0.28531 | 0.28531 | 0.9953 | -0.089002 | 0.99407 | -0.11225 | 26.1273
72 | 0.18757 | 0.048026 | -0.18724 | -0.047812 | 0.00033761 | 0.00021475 | 0.28114 | 0.28114 | 0.28114 | 0.99407 | -0.11225 | 0.99212 | -0.14948 | 25.7455
73 | 0.0074867 | 0.0018761 | -0.0074856 | -0.0018757 | 1.0628e-06 | 4.0848e-07 | 0.011415 | 0.011415 | 0.011415 | 0.97591 | -0.46304 | 0.97576 | -0.46602 | 3.1361
74 | 0.0056241 | 0.0014094 | -0.0056241 | -0.0014094 | 4.3894e-08 | 8.2059e-09 | 0.0085755 | 0.0085755 | 0.0085755 | 0.97588 | -0.46354 | 0.97587 | -0.4637 | 2.3559
75 | -0.02578 | -0.0064715 | 0.025794 | 0.0064799 | 1.3611e-05 | 8.4035e-06 | 0.038852 | 0.038852 | 0.038852 | 0.98746 | -0.24039 | 0.98803 | -0.22932 | 10.6736
76 | 0.02204 | 0.0055341 | -0.022037 | -0.0055326 | 2.4978e-06 | 1.5214e-06 | 0.033216 | 0.033216 | 0.033216 | 0.98746 | -0.24039 | 0.98734 | -0.24276 | 9.1252
77 | -0.027717 | -0.0069619 | 0.027726 | 0.0069674 | 8.8371e-06 | 5.4825e-06 | 0.041748 | 0.041748 | 0.041748 | 0.98803 | -0.22932 | 0.98837 | -0.22264 | 11.4693
78 | 0.019913 | 0.0050003 | -0.019908 | -0.004997 | 5.4285e-06 | 3.2688e-06 | 0.030015 | 0.030015 | 0.030015 | 0.98734 | -0.24276 | 0.98704 | -0.24848 | 8.2458
79 | -0.031745 | -0.0079746 | 0.031755 | 0.0079812 | 1.0408e-05 | 6.5054e-06 | 0.047799 | 0.047799 | 0.047799 | 0.98837 | -0.22264 | 0.98873 | -0.21578 | 13.1316
80 | 0.019908 | 0.004997 | -0.019897 | -0.0049903 | 1.1173e-05 | 6.7286e-06 | 0.030015 | 0.030015 | 0.030015 | 0.98704 | -0.24848 | 0.98644 | -0.26025 | 8.2459
81 | -0.033581 | -0.0084389 | 0.033583 | 0.0084402 | 2.0818e-06 | 1.3045e-06 | 0.050547 | 0.050547 | 0.050547 | 0.98873 | -0.21578 | 0.98879 | -0.21448 | 13.8867
82 | 0.017094 | 0.0042877 | -0.017089 | -0.0042851 | 4.4735e-06 | 2.6341e-06 | 0.025787 | 0.025787 | 0.025787 | 0.98644 | -0.26025 | 0.98616 | -0.26574 | 7.0842
83 | -0.035382 | -0.008891 | 0.035405 | 0.0089055 | 2.3089e-05 | 1.4498e-05 | 0.053254 | 0.053254 | 0.053254 | 0.98879 | -0.21448 | 0.9895 | -0.20082 | 14.6303
84 | 0.015721 | 0.0039421 | -0.015718 | -0.0039407 | 2.4592e-06 | 1.4252e-06 | 0.023722 | 0.023722 | 0.023722 | 0.98616 | -0.26574 | 0.98599 | -0.26903 | 6.517
85 | -0.0062758 | -0.0015726 | 0.0062768 | 0.0015729 | 1.0591e-06 | 3.0063e-07 | 0.0096209 | 0.0096208 | 0.0096209 | 0.97063 | -0.56695 | 0.97081 | -0.56341 | 2.6431
86 | 0.0032728 | 0.00082003 | -0.0032726 | -0.00082019 | 2.3185e-07 | -1.5515e-07 | 0.0050173 | 0.0050174 | 0.0050174 | 0.97063 | -0.56695 | 0.97056 | -0.56844 | 1.3784
87 | -0.0087874 | -0.0022022 | 0.0087882 | 0.0022025 | 7.3615e-07 | 3.3733e-07 | 0.013469 | 0.013469 | 0.013469 | 0.97081 | -0.56341 | 0.9709 | -0.56165 | 3.7003
88 | -0.011714 | -0.0029358 | 0.011716 | 0.0029371 | 2.4338e-06 | 1.3085e-06 | 0.017953 | 0.017953 | 0.017953 | 0.9709 | -0.56165 | 0.97112 | -0.55729 | 4.9322
89 | -0.011716 | -0.0029371 | 0.011717 | 0.0029376 | 9.1016e-07 | 4.8932e-07 | 0.017953 | 0.017953 | 0.017953 | 0.97112 | -0.55729 | 0.9712 | -0.55566 | 4.9321
90 | -0.014443 | -0.0036207 | 0.014448 | 0.0036234 | 4.762e-06 | 2.7267e-06 | 0.022129 | 0.022129 | 0.022129 | 0.9712 | -0.55566 | 0.97155 | -0.54874 | 6.0794
91 | 0.0033043 | 0.00082795 | -0.0033041 | -0.00082809 | 1.8099e-07 | -1.4303e-07 | 0.0049312 | 0.0049312 | 0.0049312 | 0.99709 | -0.055924 | 0.99703 | -0.057073 | 1.3547
92 | 0.018139 | 0.0045528 | -0.018133 | -0.0045493 | 6.0222e-06 | 3.5696e-06 | 0.027098 | 0.027098 | 0.027098 | 0.99613 | -0.074285 | 0.99577 | -0.081249 | 7.4445
93 | -0.0031415 | -0.00078734 | 0.0031416 | 0.0007873 | 4.837e-08 | -3.7748e-08 | 0.0048166 | 0.0048166 | 0.0048166 | 0.97052 | -0.56914 | 0.97054 | -0.56882 | 1.3232
94 | -0.0065324 | -0.0016371 | 0.0065325 | 0.0016371 | 2.9418e-08 | 9.1631e-09 | 0.010015 | 0.010015 | 0.010015 | 0.97054 | -0.56882 | 0.97054 | -0.56873 | 2.7515
95 | -0.0034479 | -0.00086414 | 0.003448 | 0.00086409 | 7.3268e-08 | -4.7195e-08 | 0.0051749 | 0.0051749 | 0.0051749 | 0.99144 | -0.16262 | 0.99146 | -0.16218 | 1.4217
96 | 0.0033935 | 0.00085039 | -0.0033934 | -0.00085046 | 1.2256e-07 | -7.4064e-08 | 0.0051744 | 0.0051744 | 0.0051744 | 0.97587 | -0.4637 | 0.97584 | -0.46446 | 1.4215
97 | 0.0045196 | 0.0011323 | -0.0045195 | -0.0011323 | 9.4742e-08 | -5.7966e-09 | 0.0068922 | 0.0068923 | 0.0068923 | 0.97576 | -0.46602 | 0.97573 | -0.46646 | 1.8935
98 | 0.016227 | 0.0040716 | -0.016221 | -0.0040683 | 5.8071e-06 | 3.3741e-06 | 0.02425 | 0.02425 | 0.02425 | 0.99577 | -0.081249 | 0.99538 | -0.088757 | 6.6622
99 | 0.014925 | 0.0037435 | -0.014922 | -0.0037415 | 3.5806e-06 | 2.0424e-06 | 0.022313 | 0.022313 | 0.022313 | 0.99538 | -0.088757 | 0.99512 | -0.093791 | 6.1301
100 | 0.0015287 | 0.00038259 | -0.0015286 | -0.00038311 | 8.6451e-08 | -5.1787e-07 | 0.0022857 | 0.0022859 | 0.0022859 | 0.99512 | -0.093791 | 0.99506 | -0.094979 | 0.62799
101 | 0.013393 | 0.0033589 | -0.013389 | -0.0033566 | 4.2013e-06 | 2.3261e-06 | 0.020028 | 0.020028 | 0.020028 | 0.99512 | -0.093791 | 0.99478 | -0.10037 | 5.5022
102 | 0.010687 | 0.0026795 | -0.010683 | -0.0026775 | 3.9849e-06 | 2.0107e-06 | 0.015986 | 0.015986 | 0.015986 | 0.99478 | -0.10037 | 0.99438 | -0.1082 | 4.3918
103 | 0.0027022 | 0.00067711 | -0.0027021 | -0.00067722 | 6.7943e-08 | -1.0049e-07 | 0.0040419 | 0.004042 | 0.004042 | 0.99478 | -0.10037 | 0.99476 | -0.1009 | 1.1104
104 | 0.0080498 | 0.0020176 | -0.0080491 | -0.0020173 | 6.2027e-07 | 2.4911e-07 | 0.012046 | 0.012046 | 0.012046 | 0.99438 | -0.1082 | 0.99429 | -0.10982 | 3.3093
105 | -0.02641 | -0.006619 | 0.026437 | 0.0066358 | 2.7048e-05 | 1.6767e-05 | 0.040492 | 0.040492 | 0.040492 | 0.97054 | -0.56873 | 0.97163 | -0.54725 | 11.1242
106 | -0.007824 | -0.0019605 | 0.0078252 | 0.001961 | 1.212e-06 | 4.8065e-07 | 0.011815 | 0.011814 | 0.011815 | 0.9854 | -0.28051 | 0.98557 | -0.27725 | 3.2458
107 | -0.013525 | -0.0033893 | 0.013529 | 0.0033912 | 3.3386e-06 | 1.8646e-06 | 0.02042 | 0.02042 | 0.02042 | 0.98557 | -0.27725 | 0.98583 | -0.27207 | 5.61
108 | 0.0034915 | 0.00087479 | -0.0034912 | -0.00087497 | 3.0833e-07 | -1.7969e-07 | 0.0052714 | 0.0052715 | 0.0052715 | 0.98557 | -0.27725 | 0.98547 | -0.27911 | 1.4482
109 | -0.015716 | -0.0039394 | 0.015718 | 0.0039407 | 2.2827e-06 | 1.323e-06 | 0.023722 | 0.023722 | 0.023722 | 0.98583 | -0.27207 | 0.98599 | -0.26903 | 6.517
110 | -0.0024971 | -0.00062559 | 0.0024972 | 0.0006255 | 5.5972e-08 | -9.2727e-08 | 0.0038082 | 0.0038082 | 0.0038082 | 0.97571 | -0.46693 | 0.97573 | -0.46646 | 1.0462
111 | 0.0016117 | 0.00040368 | -0.0016117 | -0.0004037 | 4.1927e-09 | -2.0432e-08 | 0.0024579 | 0.0024579 | 0.0024579 | 0.97571 | -0.46693 | 0.97571 | -0.46699 | 0.67524
112 | 0.0016117 | 0.0004037 | -0.0016117 | -0.00040392 | 4.5594e-08 | -2.2217e-07 | 0.0024579 | 0.002458 | 0.002458 | 0.97571 | -0.46699 | 0.97568 | -0.46758 | 0.67527
113 | 0.021147 | 0.0053051 | -0.021143 | -0.0053025 | 4.2834e-06 | 2.6064e-06 | 0.032377 | 0.032377 | 0.032377 | 0.97195 | -0.54082 | 0.97174 | -0.54506 | 8.8949
114 | 0.0085257 | 0.0021368 | -0.0085255 | -0.0021367 | 2.7617e-07 | 1.2288e-07 | 0.013035 | 0.013035 | 0.013035 | 0.97328 | -0.51476 | 0.97324 | -0.51544 | 3.581
115 | -0.018013 | -0.004517 | 0.018016 | 0.0045189 | 3.1562e-06 | 1.883e-06 | 0.027589 | 0.027589 | 0.027589 | 0.97155 | -0.54874 | 0.97174 | -0.54506 | 7.5795
116 | 0.008155 | 0.0020439 | -0.0081546 | -0.0020437 | 3.8282e-07 | 1.5801e-07 | 0.01227 | 0.01227 | 0.01227 | 0.98896 | -0.20999 | 0.98891 | -0.21097 | 3.3709

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3027 | 0.077145

## res_load
| p_mw | q_mvar
0 | 0.0035613 | 0.00089256
1 | 0.001251 | 0.00031354
2 | 0.0025395 | 0.00063646
3 | 0.0019485 | 0.00048834
4 | 0.0031884 | 0.00079909
5 | 0.0047964 | 0.0012021
6 | 0.0055654 | 0.0013948
7 | 0.0025044 | 0.00062767
8 | 0.0053674 | 0.0013452
9 | 0.0023736 | 0.00059489
10 | 0.0094632 | 0.0023717
11 | 0.0029534 | 0.00074019
12 | 0.0043793 | 0.0010976
13 | 0.0024077 | 0.00060342
14 | 0.0062335 | 0.0015623
15 | 0.0025471 | 0.00063836
16 | 0.0017299 | 0.00043355
17 | 0.0018005 | 0.00045125
18 | 0.00028658 | 7.1823e-05
19 | 0.0033463 | 0.00083867
20 | 0.0027855 | 0.0006981
21 | 0.0059142 | 0.0014822
22 | 0.00080595 | 0.00020199
23 | 0.0013083 | 0.00032789
24 | 0.0014145 | 0.0003545
25 | 0.00090206 | 0.00022608
26 | 0.0027294 | 0.00068406
27 | 0.0020772 | 0.0005206
28 | 0.0019378 | 0.00048566
29 | 0.0019032 | 0.00047698
30 | 0.0015529 | 0.0003892
31 | 0.0020798 | 0.00052125
32 | 0.0043439 | 0.0010887
33 | 0.0036801 | 0.00092231
34 | 0.0023365 | 0.00058558
35 | 0.0019869 | 0.00049796
36 | 0.0010518 | 0.0002636
37 | 0.0019132 | 0.00047949
38 | 0.0018161 | 0.00045515
39 | 0.0017408 | 0.00043627
40 | 0.0011108 | 0.00027838
41 | 0.002207 | 0.00055312
42 | 0.0026198 | 0.00065658
43 | 0.001921 | 0.00048144
44 | 0.0011224 | 0.0002813
45 | 0.0027859 | 0.00069822
46 | 0.0053568 | 0.0013425
47 | 0.0023894 | 0.00059883
48 | 0.0031995 | 0.00080187
49 | 0.0010959 | 0.00027465
50 | 0.0037402 | 0.00093739
51 | 0.0019232 | 0.000482
52 | 0.0021239 | 0.00053231
53 | 0.0040191 | 0.0010073
54 | 0.0018262 | 0.0004577
55 | 0.0028031 | 0.00070253
56 | 0.0017987 | 0.00045081
57 | 0.0013685 | 0.00034299
58 | 0.0030029 | 0.00075261
59 | 0.0025106 | 0.00062922
60 | 0.0032726 | 0.00082019
61 | 0.0029258 | 0.00073328
62 | 0.0027257 | 0.00068313
63 | 0.0015626 | 0.00039162
64 | 0.0017032 | 0.00042687
65 | 0.0031415 | 0.00078734
66 | 0.0033909 | 0.00084983
67 | 0.0018979 | 0.00047565
68 | 0.0034479 | 0.00086414
69 | 0.0072892 | 0.0018268
70 | 0.0022306 | 0.00055903
71 | 0.0033934 | 0.00085046
72 | 0.002966 | 0.00074334
73 | 0.0019057 | 0.00047761
74 | 0.0012957 | 0.00032473
75 | 0.0015286 | 0.00038311
76 | 0.0026331 | 0.00065991
77 | 0.0027021 | 0.00067722
78 | 0.019878 | 0.0049819
79 | 0.0048418 | 0.0012135
80 | 0.0033041 | 0.00082809
81 | 0.0014044 | 0.00035197
82 | 0.0022086 | 0.00055352
83 | 0.0021873 | 0.00054818
84 | 0.0034912 | 0.00087497
85 | 0.00088542 | 0.00022191
86 | 0.0020223 | 0.00050684
87 | 0.0016117 | 0.00040392
88 | 0.0035505 | 0.00088985
89 | 0.0054125 | 0.0013565
90 | 0.0035652 | 0.00089354
91 | 0.0031267 | 0.00078363
92 | 0.0080491 | 0.0020173
93 | 0.0029406 | 0.00073699
94 | 0.0081546 | 0.0020437
95 | 0.0085255 | 0.0021367

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1