## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2572-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2572-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2572-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2572-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2572-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2572-6_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2572-6_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2572-6_0_4_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_2572-6_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2572-6_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2572-6_0_4_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_2572-6_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2572-6_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2572-6_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2572-6_0_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2572-6_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2572-6_0_4_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2572-6_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_2572-6_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2572-6_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2572-6_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2572-6_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2572-6_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2572-6_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2572-6_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2572-6_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2572-6_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2572-6_0_4_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_2572-6_0_4_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_2572-6_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2572-6_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2572-6_0_4_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_2572-6_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2572-6_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2572-6_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_2572-6_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_2572-6_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_2572-6_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_2572-6_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2572-6_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_MV_291_1_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2572-6_0_4_load_0 | 0 | 0.011475 | 0.0028758 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2572-6_0_4_load_1 | 1 | 0.092908 | 0.023285 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2572-6_0_4_load_2 | 2 | 0.015341 | 0.0038447 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2572-6_0_4_load_3 | 3 | 0.0096776 | 0.0024254 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2572-6_0_4_load_4 | 4 | 0.047634 | 0.011938 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2572-6_0_4_load_8 | 5 | 0.016752 | 0.0041985 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2572-6_0_4_load_39 | 7 | 0.029469 | 0.0073857 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2572-6_0_4_load_5 | 9 | 0.028415 | 0.0071216 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2572-6_0_4_load_37 | 10 | 0.025284 | 0.0063368 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2572-6_0_4_load_9 | 11 | 0.014177 | 0.0035531 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2572-6_0_4_load_24 | 14 | 0.0059365 | 0.0014878 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2572-6_0_4_load_12 | 15 | 0.0006628 | 0.00016611 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2572-6_0_4_load_22 | 16 | 0.00055534 | 0.00013918 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2572-6_0_4_load_16 | 19 | 0.0010627 | 0.00026633 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2572-6_0_4_load_13 | 20 | 0.0020458 | 0.00051274 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2572-6_0_4_load_18 | 23 | 0.007639 | 0.0019145 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2572-6_0_4_load_21 | 25 | 0.002007 | 0.00050301 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2572-6_0_4_load_19 | 26 | 0.0024497 | 0.00061394 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2572-6_0_4_load_40 | 27 | 0.00092922 | 0.00023289 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2572-6_0_4_load_38 | 28 | 0.0029594 | 0.00074169 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2572-6_0_4_load_25 | 29 | 0.0010405 | 0.00026078 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2572-6_0_4_load_27 | 32 | 0.0057882 | 0.0014507 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2572-6_0_4_load_28 | 33 | 0.057403 | 0.014387 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2572-6_0_4_load_31 | 36 | 0.0010669 | 0.0002674 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2572-6_0_4_load_34 | 37 | 0.0030771 | 0.0007712 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2572-6_0_4_load_32 | 38 | 0.00046248 | 0.00011591 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2572-6_0_4_load_36 | 39 | 0.0020935 | 0.00052467 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2572-6_0_4_line_0 |  | 0 | 1 | 0.023818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2572-6_0_4_line_1 |  | 0 | 2 | 0.013873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2572-6_0_4_line_2 |  | 1 | 3 | 0.0034955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2572-6_0_4_line_3 |  | 2 | 4 | 0.030134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2572-6_0_4_line_4 |  | 3 | 5 | 0.031622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2572-6_0_4_line_5 |  | 4 | 6 | 0.024781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2572-6_0_4_line_6 |  | 5 | 7 | 0.021436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2572-6_0_4_line_7 |  | 6 | 8 | 0.047672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2572-6_0_4_line_8 |  | 7 | 10 | 0.030257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2572-6_0_4_line_9 |  | 8 | 9 | 0.037304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2572-6_0_4_line_10 |  | 10 | 39 | 0.04885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2572-6_0_4_line_11 |  | 11 | 12 | 0.053827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2572-6_0_4_line_12 |  | 11 | 13 | 0.013626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2572-6_0_4_line_13 |  | 12 | 14 | 0.16438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2572-6_0_4_line_14 |  | 13 | 15 | 0.050956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2572-6_0_4_line_15 |  | 14 | 17 | 0.043977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2572-6_0_4_line_16 |  | 15 | 18 | 0.023016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2572-6_0_4_line_17 |  | 16 | 17 | 0.059501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2572-6_0_4_line_18 |  | 18 | 19 | 0.0018104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2572-6_0_4_line_19 |  | 18 | 20 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2572-6_0_4_line_20 |  | 20 | 21 | 0.045404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2572-6_0_4_line_21 |  | 21 | 22 | 0.026884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2572-6_0_4_line_22 |  | 21 | 23 | 0.019439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2572-6_0_4_line_23 |  | 22 | 27 | 0.028155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2572-6_0_4_line_24 |  | 23 | 26 | 0.073945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2572-6_0_4_line_25 |  | 24 | 25 | 0.02959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2572-6_0_4_line_26 |  | 24 | 26 | 0.035685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2572-6_0_4_line_27 |  | 25 | 29 | 0.0047948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2572-6_0_4_line_28 |  | 27 | 28 | 0.0030091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2572-6_0_4_line_29 |  | 28 | 39 | 0.019305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2572-6_0_4_line_30 |  | 29 | 30 | 0.023493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2572-6_0_4_line_31 |  | 30 | 31 | 0.012715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2572-6_0_4_line_32 |  | 31 | 38 | 0.024271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2572-6_0_4_line_33 |  | 32 | 33 | 0.055473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2572-6_0_4_line_34 |  | 32 | 34 | 0.040956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2572-6_0_4_line_35 |  | 34 | 35 | 0.025207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2572-6_0_4_line_36 |  | 34 | 36 | 0.023026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2572-6_0_4_line_37 |  | 35 | 37 | 0.023653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2572-6_0_4_line_38 |  | 36 | 38 | 0.0024772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2572-6_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 40 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2641057.4984 | 1245474.8557 | 2641053.8003 | 1245471.8051 | 2641043.2979 | 1245464.3054 | 2641038.2799 | 1245460.8044
1 | 2641057.4984 | 1245474.8557 | 2641063.0026 | 1245479.396 | 2641068.1155 | 1245483.7847
2 | 2641038.2799 | 1245460.8044 | 2641035.4132 | 1245458.8043
3 | 2641068.1155 | 1245483.7847 | 2641071.3991 | 1245486.6032 | 2641079.6041 | 1245494.1983 | 2641087.2993 | 1245502.3013 | 2641089.6168 | 1245504.8583
4 | 2641008.8209 | 1245441.7085 | 2641022.1982 | 1245449.9057 | 2641031.4033 | 1245456.0066 | 2641035.4132 | 1245458.8043
5 | 2641105.3109 | 1245524.0181 | 2641102.3992 | 1245520.1064 | 2641094.0022 | 1245509.697 | 2641089.6168 | 1245504.8583
6 | 2641008.8209 | 1245441.7085 | 2641005.7 | 1245439.7962 | 2640990.463 | 1245430.6408
7 | 2641136.4837 | 1245487.8769 | 2641105.3109 | 1245524.0181
8 | 2640990.463 | 1245430.6408 | 2640970.6015 | 1245418.7067 | 2640964.7427 | 1245414.7206
9 | 2641136.4837 | 1245487.8769 | 2641140.5943 | 1245477.9655 | 2641138.4916 | 1245470.6906 | 2641123.1479 | 1245459.4833
10 | 2640926.769 | 1245384.0244 | 2640946.604 | 1245400.4958 | 2640960.2995 | 1245411.6977 | 2640964.7427 | 1245414.7206
11 | 2640743.3209 | 1245416.9082 | 2640758.4976 | 1245390.7063 | 2640770.7866 | 1245370.6198
12 | 2640777.8978 | 1245358.9964 | 2640770.7866 | 1245370.6198
13 | 2640743.3209 | 1245416.9082 | 2640748.2818 | 1245581.2168
14 | 2640777.8978 | 1245358.9964 | 2640804.4912 | 1245315.5302
15 | 2640742.6562 | 1245624.8291 | 2640748.2818 | 1245581.2168
16 | 2640817.2825 | 1245296.4037 | 2640809.2018 | 1245308.0003 | 2640805.0004 | 1245314.698 | 2640804.4912 | 1245315.5302
17 | 2640742.6562 | 1245624.8291 | 2640751.0728 | 1245624.7423 | 2640794.7459 | 1245651.2428
18 | 2640817.2825 | 1245296.4037 | 2640815.6192 | 1245295.689
19 | 2640817.2825 | 1245296.4037 | 2640825.5282 | 1245300.3519 | 2640833.3188 | 1245304.5718
20 | 2640868.3049 | 1245333.3679 | 2640856.9996 | 1245322.8053 | 2640844.8978 | 1245312.7043 | 2640835.4038 | 1245305.7011 | 2640833.3188 | 1245304.5718
21 | 2640868.3049 | 1245333.3679 | 2640872.7543 | 1245337.8348 | 2640880.0209 | 1245344.6226 | 2640887.9423 | 1245351.7818
22 | 2640868.3049 | 1245333.3679 | 2640881.7741 | 1245319.3514
23 | 2640887.9423 | 1245351.7818 | 2640909.6025 | 1245369.769
24 | 2640881.7741 | 1245319.3514 | 2640888.6009 | 1245245.7227
25 | 2640873.761 | 1245219.1193 | 2640875.7001 | 1245219.4996 | 2640880.2681 | 1245218.8195 | 2640884.0455 | 1245217.7559 | 2640890.3706 | 1245212.0846 | 2640897.2832 | 1245204.0811
26 | 2640873.761 | 1245219.1193 | 2640870.443 | 1245228.069 | 2640871.7418 | 1245232.5587 | 2640875.7703 | 1245236.7225 | 2640888.6009 | 1245245.7227
27 | 2640900.4173 | 1245200.4523 | 2640897.2832 | 1245204.0811
28 | 2640909.6025 | 1245369.769 | 2640911.9175 | 1245371.6914
29 | 2640926.769 | 1245384.0244 | 2640911.9175 | 1245371.6914
30 | 2640914.801 | 1245181.8998 | 2640912.1029 | 1245185.3056 | 2640905.1001 | 1245195.0304 | 2640900.4173 | 1245200.4523
31 | 2640914.801 | 1245181.8998 | 2640925.1001 | 1245189.3979
32 | 2640925.1001 | 1245189.3979 | 2640930.3975 | 1245194.7046 | 2640935.8022 | 1245200.9014 | 2640940.2026 | 1245207.0025 | 2640940.6862 | 1245207.9097
33 | 2641008.0037 | 1245307.603 | 2640997.8011 | 1245299.3049 | 2640989.9042 | 1245291.9011 | 2640983.4001 | 1245285.1962 | 2640979.0987 | 1245280.0965 | 2640974.3995 | 1245273.5042 | 2640970.5362 | 1245267.2056
34 | 2640952.7038 | 1245230.404 | 2640955.9997 | 1245238.899 | 2640959.5036 | 1245246.8061 | 2640969.3042 | 1245265.1969 | 2640970.5362 | 1245267.2056
35 | 2640952.7038 | 1245230.404 | 2640971.3018 | 1245213.3322
36 | 2640952.7038 | 1245230.404 | 2640947.4003 | 1245220.5054 | 2640941.8515 | 1245210.0958
37 | 2640971.3018 | 1245213.3322 | 2640951.4414 | 1245200.4867
38 | 2640940.6862 | 1245207.9097 | 2640941.8515 | 1245210.0958

## bus_geodata
| x | y | coords
0 | 2641057.4984 | 1245474.8557
1 | 2641038.2799 | 1245460.8044
2 | 2641068.1155 | 1245483.7847
3 | 2641035.4132 | 1245458.8043
4 | 2641089.6168 | 1245504.8583
5 | 2641008.8209 | 1245441.7085
6 | 2641105.3109 | 1245524.0181
7 | 2640990.463 | 1245430.6408
8 | 2641136.4837 | 1245487.8769
9 | 2641123.1479 | 1245459.4833
10 | 2640964.7427 | 1245414.7206
11 | 2640770.7866 | 1245370.6198
12 | 2640743.3209 | 1245416.9082
13 | 2640777.8978 | 1245358.9964
14 | 2640748.2818 | 1245581.2168
15 | 2640804.4912 | 1245315.5302
16 | 2640794.7459 | 1245651.2428
17 | 2640742.6562 | 1245624.8291
18 | 2640817.2825 | 1245296.4037
19 | 2640815.6192 | 1245295.689
20 | 2640833.3188 | 1245304.5718
21 | 2640868.3049 | 1245333.3679
22 | 2640887.9423 | 1245351.7818
23 | 2640881.7741 | 1245319.3514
24 | 2640873.761 | 1245219.1193
25 | 2640897.2832 | 1245204.0811
26 | 2640888.6009 | 1245245.7227
27 | 2640909.6025 | 1245369.769
28 | 2640911.9175 | 1245371.6914
29 | 2640900.4173 | 1245200.4523
30 | 2640914.801 | 1245181.8998
31 | 2640925.1001 | 1245189.3979
32 | 2640970.5362 | 1245267.2056
33 | 2641008.0037 | 1245307.603
34 | 2640952.7038 | 1245230.404
35 | 2640971.3018 | 1245213.3322
36 | 2640941.8515 | 1245210.0958
37 | 2640951.4414 | 1245200.4867
38 | 2640940.6862 | 1245207.9097
39 | 2640926.769 | 1245384.0244
40 | 2640986.4951 | 1245428.2566

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99448 | -0.10587 | 0.011475 | 0.0028758
1 | 0.99672 | -0.062789 | 0.092908 | 0.023285
2 | 0.99332 | -0.12824 | 0.015341 | 0.0038447
3 | 0.99704 | -0.056787 | 0.0096776 | 0.0024254
4 | 0.99122 | -0.16881 | 0.047634 | 0.011938
5 | 1 | 0 | -0.37676 | -0.095373
6 | 0.99058 | -0.18131 | 0 | 0
7 | 0.99836 | -0.03109 | 0.029469 | 0.0073857
8 | 0.98933 | -0.20541 | 0 | 0
9 | 0.98836 | -0.2243 | 0.028415 | 0.0071216
10 | 0.99645 | -0.067319 | 0.025284 | 0.0063368
11 | 0.98703 | -0.24768 | 0.014177 | 0.0035531
12 | 0.98671 | -0.25394 | 0 | 0
13 | 0.98729 | -0.24264 | 0 | 0
14 | 0.98573 | -0.27308 | 0.0059365 | 0.0014878
15 | 0.98826 | -0.22381 | 0.0006628 | 0.00016611
16 | 0.98568 | -0.27411 | 0.00055534 | 0.00013918
17 | 0.98571 | -0.27352 | 0 | 0
18 | 0.98871 | -0.21505 | 0 | 0
19 | 0.98871 | -0.21508 | 0.0010627 | 0.00026633
20 | 0.98908 | -0.20786 | 0.0020458 | 0.00051274
21 | 0.9901 | -0.1881 | 0 | 0
22 | 0.99141 | -0.16294 | 0 | 0
23 | 0.98937 | -0.20209 | 0.007639 | 0.0019145
24 | 0.98448 | -0.29584 | 0 | 0
25 | 0.98252 | -0.33362 | 0.002007 | 0.00050301
26 | 0.98684 | -0.25048 | 0.0024497 | 0.00061394
27 | 0.99279 | -0.13666 | 0.00092922 | 0.00023289
28 | 0.99294 | -0.13383 | 0.0029594 | 0.00074169
29 | 0.98221 | -0.33958 | 0.0010405 | 0.00026078
30 | 0.98072 | -0.3684 | 0 | 0
31 | 0.97992 | -0.38404 | 0 | 0
32 | 0.97439 | -0.49222 | 0.0057882 | 0.0014507
33 | 0.97142 | -0.55086 | 0.057403 | 0.014387
34 | 0.9768 | -0.44483 | 0 | 0
35 | 0.97673 | -0.44625 | 0 | 0
36 | 0.97823 | -0.41699 | 0.0010669 | 0.0002674
37 | 0.97666 | -0.44758 | 0.0030771 | 0.0007712
38 | 0.97838 | -0.41395 | 0.00046248 | 0.00011591
39 | 0.99392 | -0.1152 | 0.0020935 | 0.00052467
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.10319 | -0.025984 | 0.1034 | 0.02612 | 0.00021303 | 0.00013603 | 0.15444 | 0.15444 | 0.15444 | 0.99448 | -0.10587 | 0.99672 | -0.062789 | 42.428
1 | 0.091711 | 0.023108 | -0.091613 | -0.023045 | 9.8029e-05 | 6.2558e-05 | 0.13727 | 0.13727 | 0.13727 | 0.99448 | -0.10587 | 0.99332 | -0.12824 | 37.7112
2 | -0.19631 | -0.049405 | 0.19636 | 0.049441 | 5.632e-05 | 3.5953e-05 | 0.29314 | 0.29314 | 0.29314 | 0.99672 | -0.062789 | 0.99704 | -0.056787 | 40.2667
3 | 0.076273 | 0.019201 | -0.076125 | -0.019107 | 0.0001476 | 9.4075e-05 | 0.11429 | 0.11429 | 0.11429 | 0.99332 | -0.12824 | 0.99122 | -0.16881 | 31.3979
4 | -0.20604 | -0.051866 | 0.2066 | 0.052224 | 0.00056094 | 0.00035817 | 0.30758 | 0.30758 | 0.30758 | 0.99704 | -0.056787 | 1 | 0 | 42.2506
5 | 0.028491 | 0.0071684 | -0.028474 | -0.0071578 | 1.7007e-05 | 1.0565e-05 | 0.04278 | 0.04278 | 0.04278 | 0.99122 | -0.16881 | 0.99058 | -0.18131 | 11.7528
6 | 0.16851 | 0.043148 | -0.16825 | -0.042986 | 0.00025335 | 0.00016158 | 0.25106 | 0.25106 | 0.25106 | 1 | 0 | 0.99836 | -0.03109 | 34.4869
7 | 0.028474 | 0.0071578 | -0.028441 | -0.0071375 | 3.2718e-05 | 2.0326e-05 | 0.04278 | 0.04278 | 0.04278 | 0.99058 | -0.18131 | 0.98933 | -0.20541 | 11.7529
8 | 0.13878 | 0.035601 | -0.13854 | -0.035446 | 0.00024343 | 0.000155 | 0.20714 | 0.20714 | 0.20714 | 0.99836 | -0.03109 | 0.99645 | -0.067319 | 28.4537
9 | 0.028441 | 0.0071375 | -0.028415 | -0.0071216 | 2.5602e-05 | 1.5907e-05 | 0.04278 | 0.042781 | 0.042781 | 0.98933 | -0.20541 | 0.98836 | -0.2243 | 11.7529
10 | 0.11326 | 0.029109 | -0.11299 | -0.028942 | 0.0002628 | 0.00016692 | 0.16939 | 0.16939 | 0.16939 | 0.99645 | -0.067319 | 0.99392 | -0.1152 | 23.2673
11 | 0.0064997 | 0.0016279 | -0.0064977 | -0.0016274 | 1.938e-06 | 5.5256e-07 | 0.0097984 | 0.0097986 | 0.0097986 | 0.98703 | -0.24768 | 0.98671 | -0.25394 | 2.6919
12 | -0.020677 | -0.005181 | 0.020682 | 0.005184 | 4.9649e-06 | 3.0033e-06 | 0.031171 | 0.031171 | 0.031171 | 0.98703 | -0.24768 | 0.98729 | -0.24264 | 8.5635
13 | 0.0064977 | 0.0016274 | -0.0064918 | -0.0016257 | 5.919e-06 | 1.6906e-06 | 0.0097986 | 0.0097993 | 0.0097993 | 0.98671 | -0.25394 | 0.98573 | -0.27308 | 2.6921
14 | -0.020682 | -0.005184 | 0.0207 | 0.0051952 | 1.8566e-05 | 1.123e-05 | 0.031171 | 0.031171 | 0.031171 | 0.98729 | -0.24264 | 0.98826 | -0.22381 | 8.5634
15 | 0.00055536 | 0.00013788 | -0.00055535 | -0.00013843 | 1.1581e-08 | -5.5317e-07 | 0.00083789 | 0.00083809 | 0.00083809 | 0.98573 | -0.27308 | 0.98571 | -0.27352 | 0.23024
16 | -0.021363 | -0.0053614 | 0.021372 | 0.0053668 | 8.9316e-06 | 5.4212e-06 | 0.032169 | 0.032169 | 0.032169 | 0.98826 | -0.22381 | 0.98871 | -0.21505 | 8.8376
17 | -0.00055534 | -0.00013918 | 0.00055535 | 0.00013843 | 1.5678e-08 | -7.484e-07 | 0.00083836 | 0.00083809 | 0.00083836 | 0.98568 | -0.27411 | 0.98571 | -0.27352 | 0.23032
18 | 0.0010627 | 0.00026631 | -0.0010627 | -0.00026633 | 1.7364e-09 | -2.2106e-08 | 0.0015993 | 0.0015993 | 0.0015993 | 0.98871 | -0.21505 | 0.98871 | -0.21508 | 0.43937
19 | -0.022435 | -0.0056331 | 0.022442 | 0.0056378 | 7.6978e-06 | 4.6956e-06 | 0.033768 | 0.033768 | 0.033768 | 0.98871 | -0.21505 | 0.98908 | -0.20786 | 9.2769
20 | -0.024488 | -0.0061505 | 0.024511 | 0.0061647 | 2.3115e-05 | 1.421e-05 | 0.036846 | 0.036845 | 0.036846 | 0.98908 | -0.20786 | 0.9901 | -0.1881 | 10.1224
21 | -0.10663 | -0.027201 | 0.10676 | 0.027284 | 0.00012973 | 8.2335e-05 | 0.16043 | 0.16042 | 0.16043 | 0.9901 | -0.1881 | 0.99141 | -0.16294 | 22.0364
22 | 0.082119 | 0.021036 | -0.082064 | -0.021001 | 5.5664e-05 | 3.5125e-05 | 0.12358 | 0.12358 | 0.12358 | 0.9901 | -0.1881 | 0.98937 | -0.20209 | 16.9753
23 | -0.10676 | -0.027284 | 0.1069 | 0.02737 | 0.00013586 | 8.6225e-05 | 0.16042 | 0.16042 | 0.16042 | 0.99141 | -0.16294 | 0.99279 | -0.13666 | 22.0364
24 | 0.074425 | 0.019087 | -0.074251 | -0.018977 | 0.0001742 | 0.0001096 | 0.11209 | 0.11209 | 0.11209 | 0.98937 | -0.20209 | 0.98684 | -0.25048 | 15.3972
25 | 0.071644 | 0.018263 | -0.071513 | -0.01818 | 0.00013038 | 8.3069e-05 | 0.1084 | 0.1084 | 0.1084 | 0.98448 | -0.29584 | 0.98252 | -0.33362 | 29.7798
26 | -0.071644 | -0.018263 | 0.071801 | 0.018363 | 0.00015724 | 0.00010018 | 0.1084 | 0.1084 | 0.1084 | 0.98448 | -0.29584 | 0.98684 | -0.25048 | 29.7798
27 | 0.069506 | 0.017677 | -0.069486 | -0.017664 | 1.9959e-05 | 1.2713e-05 | 0.10536 | 0.10536 | 0.10536 | 0.98252 | -0.33362 | 0.98221 | -0.33958 | 28.9448
28 | -0.10783 | -0.027603 | 0.10784 | 0.027612 | 1.4774e-05 | 9.3773e-06 | 0.16182 | 0.16182 | 0.16182 | 0.99279 | -0.13666 | 0.99294 | -0.13383 | 22.2277
29 | -0.1108 | -0.028354 | 0.1109 | 0.028417 | 0.00010005 | 6.3529e-05 | 0.16625 | 0.16625 | 0.16625 | 0.99294 | -0.13383 | 0.99392 | -0.1152 | 22.8368
30 | 0.068446 | 0.017404 | -0.068351 | -0.017343 | 9.489e-05 | 6.0433e-05 | 0.10378 | 0.10378 | 0.10378 | 0.98221 | -0.33958 | 0.98072 | -0.3684 | 28.5117
31 | 0.068351 | 0.017343 | -0.068299 | -0.01731 | 5.1357e-05 | 3.2708e-05 | 0.10378 | 0.10378 | 0.10378 | 0.98072 | -0.3684 | 0.97992 | -0.38404 | 28.5118
32 | 0.068299 | 0.01731 | -0.068201 | -0.017248 | 9.8034e-05 | 6.2436e-05 | 0.10378 | 0.10378 | 0.10378 | 0.97992 | -0.38404 | 0.97838 | -0.41395 | 28.5118
33 | 0.057564 | 0.014489 | -0.057403 | -0.014387 | 0.00016084 | 0.00010225 | 0.08793 | 0.08793 | 0.08793 | 0.97439 | -0.49222 | 0.97142 | -0.55086 | 24.1566
34 | -0.063352 | -0.015939 | 0.063496 | 0.016031 | 0.00014382 | 9.1534e-05 | 0.096769 | 0.096769 | 0.096769 | 0.97439 | -0.49222 | 0.9768 | -0.44483 | 26.5849
35 | 0.0030775 | 0.00077084 | -0.0030773 | -0.00077103 | 2.0775e-07 | -1.8255e-07 | 0.004688 | 0.0046881 | 0.0046881 | 0.9768 | -0.44483 | 0.97673 | -0.44625 | 1.2879
36 | -0.066573 | -0.016802 | 0.066662 | 0.016858 | 8.8881e-05 | 5.6595e-05 | 0.10146 | 0.10146 | 0.10146 | 0.9768 | -0.44483 | 0.97823 | -0.41699 | 27.8727
37 | 0.0030773 | 0.00077103 | -0.0030771 | -0.0007712 | 1.9494e-07 | -1.7125e-07 | 0.0046881 | 0.0046882 | 0.0046882 | 0.97673 | -0.44625 | 0.97666 | -0.44758 | 1.288
38 | -0.067729 | -0.017126 | 0.067739 | 0.017132 | 9.8705e-06 | 6.286e-06 | 0.10308 | 0.10308 | 0.10308 | 0.97823 | -0.41699 | 0.97838 | -0.41395 | 28.3185

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39351 | 0.099571

## res_load
| p_mw | q_mvar
0 | 0.011475 | 0.0028758
1 | 0.092908 | 0.023285
2 | 0.015341 | 0.0038447
3 | 0.0096776 | 0.0024254
4 | 0.047634 | 0.011938
5 | 0.016752 | 0.0041985
6 | 0.029469 | 0.0073857
7 | 0.028415 | 0.0071216
8 | 0.025284 | 0.0063368
9 | 0.014177 | 0.0035531
10 | 0.0059365 | 0.0014878
11 | 0.0006628 | 0.00016611
12 | 0.00055534 | 0.00013918
13 | 0.0010627 | 0.00026633
14 | 0.0020458 | 0.00051274
15 | 0.007639 | 0.0019145
16 | 0.002007 | 0.00050301
17 | 0.0024497 | 0.00061394
18 | 0.00092922 | 0.00023289
19 | 0.0029594 | 0.00074169
20 | 0.0010405 | 0.00026078
21 | 0.0057882 | 0.0014507
22 | 0.057403 | 0.014387
23 | 0.0010669 | 0.0002674
24 | 0.0030771 | 0.0007712
25 | 0.00046248 | 0.00011591
26 | 0.0020935 | 0.00052467

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1