## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2572-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2572-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2572-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2572-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2572-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2572-7_0_6_node_127 | 0.4 | n |  | TRUE
6 | bus_LV_2572-7_0_6_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_2572-7_0_6_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_2572-7_0_6_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2572-7_0_6_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_2572-7_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2572-7_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2572-7_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2572-7_0_6_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_2572-7_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2572-7_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2572-7_0_6_node_92 | 0.4 | n |  | TRUE
17 | bus_LV_2572-7_0_6_node_91 | 0.4 | n |  | TRUE
18 | bus_LV_2572-7_0_6_node_97 | 0.4 | n |  | TRUE
19 | bus_LV_2572-7_0_6_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_2572-7_0_6_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2572-7_0_6_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2572-7_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2572-7_0_6_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2572-7_0_6_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2572-7_0_6_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2572-7_0_6_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2572-7_0_6_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_2572-7_0_6_node_118 | 0.4 | n |  | TRUE
29 | bus_LV_2572-7_0_6_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_2572-7_0_6_node_53 | 0.4 | n |  | TRUE
31 | bus_LV_2572-7_0_6_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_2572-7_0_6_node_119 | 0.4 | n |  | TRUE
33 | bus_LV_2572-7_0_6_node_89 | 0.4 | n |  | TRUE
34 | bus_LV_2572-7_0_6_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2572-7_0_6_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2572-7_0_6_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2572-7_0_6_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2572-7_0_6_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2572-7_0_6_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2572-7_0_6_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2572-7_0_6_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_2572-7_0_6_node_122 | 0.4 | n |  | TRUE
43 | bus_LV_2572-7_0_6_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2572-7_0_6_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_2572-7_0_6_node_124 | 0.4 | n |  | TRUE
46 | bus_LV_2572-7_0_6_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_2572-7_0_6_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_2572-7_0_6_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_2572-7_0_6_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_2572-7_0_6_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_2572-7_0_6_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_2572-7_0_6_node_115 | 0.4 | n |  | TRUE
53 | bus_LV_2572-7_0_6_node_106 | 0.4 | n |  | TRUE
54 | bus_LV_2572-7_0_6_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_2572-7_0_6_node_113 | 0.4 | n |  | TRUE
56 | bus_LV_2572-7_0_6_node_94 | 0.4 | n |  | TRUE
57 | bus_LV_2572-7_0_6_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_2572-7_0_6_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_2572-7_0_6_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_2572-7_0_6_node_131 | 0.4 | n |  | TRUE
61 | bus_LV_2572-7_0_6_node_139 | 0.4 | n |  | TRUE
62 | bus_LV_2572-7_0_6_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_2572-7_0_6_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_2572-7_0_6_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_2572-7_0_6_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_2572-7_0_6_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_2572-7_0_6_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_2572-7_0_6_node_117 | 0.4 | n |  | TRUE
69 | bus_LV_2572-7_0_6_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_2572-7_0_6_node_112 | 0.4 | n |  | TRUE
71 | bus_LV_2572-7_0_6_node_96 | 0.4 | n |  | TRUE
72 | bus_LV_2572-7_0_6_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_2572-7_0_6_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_2572-7_0_6_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_2572-7_0_6_node_79 | 0.4 | n |  | TRUE
76 | bus_LV_2572-7_0_6_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_2572-7_0_6_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_2572-7_0_6_node_82 | 0.4 | n |  | TRUE
79 | bus_LV_2572-7_0_6_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_2572-7_0_6_node_125 | 0.4 | n |  | TRUE
81 | bus_LV_2572-7_0_6_node_108 | 0.4 | n |  | TRUE
82 | bus_LV_2572-7_0_6_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_2572-7_0_6_node_55 | 0.4 | n |  | TRUE
84 | bus_LV_2572-7_0_6_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_2572-7_0_6_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_2572-7_0_6_node_102 | 0.4 | n |  | TRUE
87 | bus_LV_2572-7_0_6_node_111 | 0.4 | n |  | TRUE
88 | bus_LV_2572-7_0_6_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2572-7_0_6_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_2572-7_0_6_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_2572-7_0_6_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_2572-7_0_6_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_2572-7_0_6_node_93 | 0.4 | n |  | TRUE
94 | bus_LV_2572-7_0_6_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_2572-7_0_6_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_2572-7_0_6_node_62 | 0.4 | n |  | TRUE
97 | bus_LV_2572-7_0_6_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_2572-7_0_6_node_65 | 0.4 | n |  | TRUE
99 | bus_LV_2572-7_0_6_node_129 | 0.4 | n |  | TRUE
100 | bus_LV_2572-7_0_6_node_130 | 0.4 | n |  | TRUE
101 | bus_LV_2572-7_0_6_node_133 | 0.4 | n |  | TRUE
102 | bus_LV_2572-7_0_6_node_132 | 0.4 | n |  | TRUE
103 | bus_LV_2572-7_0_6_node_135 | 0.4 | n |  | TRUE
104 | bus_LV_2572-7_0_6_node_134 | 0.4 | n |  | TRUE
105 | bus_LV_2572-7_0_6_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_2572-7_0_6_node_67 | 0.4 | n |  | TRUE
107 | bus_LV_2572-7_0_6_node_68 | 0.4 | n |  | TRUE
108 | bus_LV_2572-7_0_6_node_69 | 0.4 | n |  | TRUE
109 | bus_LV_2572-7_0_6_node_70 | 0.4 | n |  | TRUE
110 | bus_LV_2572-7_0_6_node_126 | 0.4 | n |  | TRUE
111 | bus_LV_2572-7_0_6_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_2572-7_0_6_node_71 | 0.4 | n |  | TRUE
113 | bus_LV_2572-7_0_6_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_2572-7_0_6_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_2572-7_0_6_node_76 | 0.4 | n |  | TRUE
116 | bus_LV_2572-7_0_6_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_2572-7_0_6_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_2572-7_0_6_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_2572-7_0_6_node_78 | 0.4 | n |  | TRUE
120 | bus_LV_2572-7_0_6_node_80 | 0.4 | n |  | TRUE
121 | bus_LV_2572-7_0_6_node_81 | 0.4 | n |  | TRUE
122 | bus_LV_2572-7_0_6_node_86 | 0.4 | n |  | TRUE
123 | bus_LV_2572-7_0_6_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_2572-7_0_6_node_136 | 0.4 | n |  | TRUE
125 | bus_LV_2572-7_0_6_node_137 | 0.4 | n |  | TRUE
126 | bus_LV_2572-7_0_6_node_84 | 0.4 | n |  | TRUE
127 | bus_LV_2572-7_0_6_node_85 | 0.4 | n |  | TRUE
128 | bus_LV_2572-7_0_6_node_138 | 0.4 | n |  | TRUE
129 | bus_LV_2572-7_0_6_node_103 | 0.4 | n |  | TRUE
130 | bus_LV_2572-7_0_6_node_104 | 0.4 | n |  | TRUE
131 | bus_LV_2572-7_0_6_node_98 | 0.4 | n |  | TRUE
132 | bus_LV_2572-7_0_6_node_99 | 0.4 | n |  | TRUE
133 | bus_LV_2572-7_0_6_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_2572-7_0_6_node_114 | 0.4 | n |  | TRUE
135 | bus_LV_2572-7_0_6_node_116 | 0.4 | n |  | TRUE
136 | bus_MV_291_1_node_203 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2572-7_0_6_load_0 | 0 | 0.0015516 | 0.00038887 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2572-7_0_6_load_1 | 1 | 0.001625 | 0.00040726 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2572-7_0_6_load_2 | 2 | 0.00050796 | 0.00012731 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2572-7_0_6_load_3 | 3 | 0.0086476 | 0.0021673 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2572-7_0_6_load_4 | 4 | 0.0042198 | 0.0010576 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2572-7_0_6_load_127 | 5 | 0.0073189 | 0.0018343 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2572-7_0_6_load_30 | 7 | 0.00079292 | 0.00019872 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2572-7_0_6_load_28 | 8 | 0.0024281 | 0.00060855 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2572-7_0_6_load_25 | 9 | 0.0033301 | 0.00083461 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2572-7_0_6_load_5 | 10 | 0.0013584 | 0.00034045 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2572-7_0_6_load_6 | 11 | 0.0013589 | 0.00034056 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2572-7_0_6_load_7 | 14 | 0.0027321 | 0.00068473 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2572-7_0_6_load_8 | 15 | 0.0020605 | 0.00051642 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2572-7_0_6_load_91 | 17 | 0.0023157 | 0.00058038 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2572-7_0_6_load_97 | 18 | 0.0056435 | 0.0014144 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2572-7_0_6_load_10 | 20 | 0.0020049 | 0.00050247 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2572-7_0_6_load_11 | 21 | 0.0019798 | 0.00049617 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2572-7_0_6_load_13 | 23 | 0.0026052 | 0.00065293 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2572-7_0_6_load_15 | 25 | 0.0059086 | 0.0014808 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2572-7_0_6_load_23 | 26 | 0.0020438 | 0.00051223 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2572-7_0_6_load_118 | 28 | 0.0051315 | 0.0012861 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2572-7_0_6_load_90 | 29 | 0.0020556 | 0.00051519 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2572-7_0_6_load_53 | 30 | 0.0019568 | 0.00049041 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2572-7_0_6_load_38 | 31 | 0.0020534 | 0.00051462 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2572-7_0_6_load_89 | 33 | 0.0020316 | 0.00050917 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2572-7_0_6_load_16 | 34 | 0.00083768 | 0.00020994 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2572-7_0_6_load_19 | 37 | 0.0020239 | 0.00050724 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2572-7_0_6_load_20 | 38 | 0.0024037 | 0.00060243 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2572-7_0_6_load_22 | 40 | 0.00079666 | 0.00019966 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2572-7_0_6_load_49 | 41 | 0.0022679 | 0.0005684 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2572-7_0_6_load_43 | 43 | 0.0012184 | 0.00030536 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2572-7_0_6_load_50 | 44 | 0.00046676 | 0.00011698 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2572-7_0_6_load_124 | 45 | 0.0011271 | 0.00028249 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2572-7_0_6_load_52 | 47 | 0.0032422 | 0.00081258 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2572-7_0_6_load_24 | 48 | 0.014169 | 0.003551 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2572-7_0_6_load_26 | 49 | 0.0043235 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2572-7_0_6_load_31 | 51 | 0.0025269 | 0.0006333 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2572-7_0_6_load_115 | 52 | 0.0024027 | 0.00060219 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2572-7_0_6_load_106 | 53 | 0.0050888 | 0.0012754 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2572-7_0_6_load_113 | 55 | 0.0011921 | 0.00029877 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2572-7_0_6_load_94 | 56 | 0.0076634 | 0.0019206 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2572-7_0_6_load_33 | 57 | 0.01297 | 0.0032505 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2572-7_0_6_load_131 | 60 | 0.015919 | 0.0039898 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2572-7_0_6_load_139 | 61 | 0.080254 | 0.020114 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2572-7_0_6_load_75 | 63 | 0.00071948 | 0.00018032 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2572-7_0_6_load_42 | 65 | 0.0021752 | 0.00054516 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2572-7_0_6_load_51 | 67 | 0.00037695 | 9.4472e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2572-7_0_6_load_117 | 68 | 0.0013725 | 0.00034397 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2572-7_0_6_load_105 | 69 | 0.00081524 | 0.00020432 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2572-7_0_6_load_112 | 70 | 0.002082 | 0.00052181 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2572-7_0_6_load_44 | 72 | 0.0064351 | 0.0016128 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2572-7_0_6_load_45 | 73 | 0.0017672 | 0.0004429 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2572-7_0_6_load_82 | 78 | 0.00080051 | 0.00020063 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2572-7_0_6_load_77 | 79 | 0.007388 | 0.0018516 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2572-7_0_6_load_125 | 80 | 0.0065121 | 0.0016321 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2572-7_0_6_load_55 | 83 | 0.0031125 | 0.00078006 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2572-7_0_6_load_56 | 84 | 0.010487 | 0.0026283 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2572-7_0_6_load_110 | 85 | 0.0058575 | 0.001468 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2572-7_0_6_load_111 | 87 | 0.005851 | 0.0014664 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2572-7_0_6_load_57 | 89 | 0.0013821 | 0.00034638 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2572-7_0_6_load_58 | 90 | 0.0013728 | 0.00034406 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2572-7_0_6_load_59 | 91 | 0.0067808 | 0.0016994 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2572-7_0_6_load_60 | 92 | 0.0037555 | 0.00094122 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2572-7_0_6_load_93 | 93 | 0.0060554 | 0.0015176 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2572-7_0_6_load_88 | 94 | 0.0068111 | 0.001707 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2572-7_0_6_load_87 | 95 | 0.0070421 | 0.0017649 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2572-7_0_6_load_62 | 96 | 0.00017525 | 4.3923e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2572-7_0_6_load_63 | 97 | 0.0029928 | 0.00075007 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2572-7_0_6_load_65 | 98 | 0.0024313 | 0.00060933 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2572-7_0_6_load_130 | 100 | 0.0053045 | 0.0013294 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2572-7_0_6_load_132 | 102 | 0.031976 | 0.0080138 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2572-7_0_6_load_135 | 103 | 0.0026554 | 0.0006655 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2572-7_0_6_load_67 | 106 | 0.00051032 | 0.0001279 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2572-7_0_6_load_68 | 107 | 0.002577 | 0.00064586 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2572-7_0_6_load_69 | 108 | 0.0029543 | 0.00074041 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2572-7_0_6_load_70 | 109 | 0.0010267 | 0.0002573 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2572-7_0_6_load_126 | 110 | 0.0031952 | 0.00080078 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2572-7_0_6_load_120 | 111 | 0.003839 | 0.00096214 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2572-7_0_6_load_71 | 112 | 0.002513 | 0.00062983 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2572-7_0_6_load_72 | 113 | 0.0012253 | 0.0003071 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2572-7_0_6_load_74 | 114 | 0.00056375 | 0.00014129 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2572-7_0_6_load_95 | 116 | 0.0011843 | 0.00029681 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2572-7_0_6_load_101 | 117 | 0.00056358 | 0.00014125 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2572-7_0_6_load_80 | 120 | 0.003602 | 0.00090274 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2572-7_0_6_load_83 | 123 | 0.0065866 | 0.0016508 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2572-7_0_6_load_137 | 125 | 0.012468 | 0.0031248 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2572-7_0_6_load_84 | 126 | 0.0061108 | 0.0015315 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2572-7_0_6_load_85 | 127 | 0.0021285 | 0.00053345 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2572-7_0_6_load_138 | 128 | 0.0018621 | 0.00046667 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2572-7_0_6_load_103 | 129 | 0.0008369 | 0.00020975 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2572-7_0_6_load_104 | 130 | 0.00065337 | 0.00016375 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2572-7_0_6_load_98 | 131 | 0.00040373 | 0.00010118 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2572-7_0_6_load_99 | 132 | 0.0010753 | 0.0002695 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2572-7_0_6_load_128 | 133 | 0.0069615 | 0.0017447 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2572-7_0_6_load_114 | 134 | 0.0014396 | 0.0003608 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2572-7_0_6_load_116 | 135 | 0.001191 | 0.00029848 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2572-7_0_6_line_0 |  | 0 | 1 | 0.028306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2572-7_0_6_line_1 |  | 0 | 2 | 0.019277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2572-7_0_6_line_2 |  | 1 | 3 | 0.008951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2572-7_0_6_line_3 |  | 2 | 4 | 0.0087674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2572-7_0_6_line_4 |  | 3 | 5 | 0.031389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2572-7_0_6_line_5 |  | 4 | 6 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2572-7_0_6_line_6 |  | 6 | 7 | 0.039299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_2572-7_0_6_line_7 |  | 6 | 8 | 0.033938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_2572-7_0_6_line_8 |  | 6 | 9 | 0.019134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2572-7_0_6_line_9 |  | 7 | 50 | 0.026295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_2572-7_0_6_line_10 |  | 8 | 19 | 0.018793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_2572-7_0_6_line_11 |  | 9 | 48 | 0.013341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2572-7_0_6_line_12 |  | 10 | 11 | 7.8927e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2572-7_0_6_line_13 |  | 11 | 12 | 0.069452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2572-7_0_6_line_14 |  | 12 | 13 | 0.062744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2572-7_0_6_line_15 |  | 13 | 18 | 0.019326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_2572-7_0_6_line_16 |  | 13 | 19 | 0.00454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2572-7_0_6_line_17 |  | 14 | 15 | 0.053809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2572-7_0_6_line_18 |  | 15 | 16 | 0.0195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2572-7_0_6_line_19 |  | 16 | 17 | 0.024161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2572-7_0_6_line_20 |  | 17 | 33 | 0.0034748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2572-7_0_6_line_21 |  | 18 | 56 | 0.019697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_2572-7_0_6_line_22 |  | 19 | 51 | 0.013197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2572-7_0_6_line_23 |  | 20 | 21 | 0.01673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_2572-7_0_6_line_24 |  | 20 | 22 | 0.024112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_2572-7_0_6_line_25 |  | 21 | 23 | 7.7921e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_2572-7_0_6_line_26 |  | 22 | 24 | 0.009701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_2572-7_0_6_line_27 |  | 22 | 25 | 0.015718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2572-7_0_6_line_28 |  | 23 | 26 | 0.015281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_2572-7_0_6_line_29 |  | 24 | 27 | 0.024336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_2572-7_0_6_line_30 |  | 24 | 28 | 0.0078436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2572-7_0_6_line_31 |  | 25 | 29 | 0.013533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2572-7_0_6_line_32 |  | 26 | 30 | 0.00035536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_2572-7_0_6_line_33 |  | 27 | 31 | 0.028636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_2572-7_0_6_line_34 |  | 28 | 32 | 0.046132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2572-7_0_6_line_35 |  | 29 | 33 | 0.012905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2572-7_0_6_line_36 |  | 30 | 47 | 0.015818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_2572-7_0_6_line_37 |  | 31 | 46 | 0.0077762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_2572-7_0_6_line_38 |  | 32 | 111 | 0.024323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2572-7_0_6_line_39 |  | 34 | 35 | 0.013527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_2572-7_0_6_line_40 |  | 34 | 36 | 0.053927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_2572-7_0_6_line_41 |  | 35 | 37 | 0.02353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2572-7_0_6_line_42 |  | 35 | 38 | 0.0024659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_2572-7_0_6_line_43 |  | 36 | 39 | 0.009246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_2572-7_0_6_line_44 |  | 36 | 40 | 0.018921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2572-7_0_6_line_45 |  | 38 | 41 | 0.0056851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_2572-7_0_6_line_46 |  | 39 | 42 | 0.019086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2572-7_0_6_line_47 |  | 39 | 43 | 0.026255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2572-7_0_6_line_48 |  | 41 | 44 | 0.010553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_2572-7_0_6_line_49 |  | 42 | 45 | 0.0027068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2572-7_0_6_line_50 |  | 43 | 46 | 0.049911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_2572-7_0_6_line_51 |  | 44 | 67 | 0.00077812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_2572-7_0_6_line_52 |  | 46 | 65 | 0.024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2572-7_0_6_line_53 |  | 47 | 82 | 0.013234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_2572-7_0_6_line_54 |  | 48 | 49 | 0.0063735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2572-7_0_6_line_55 |  | 50 | 53 | 0.044646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_2572-7_0_6_line_56 |  | 50 | 54 | 0.007639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2572-7_0_6_line_57 |  | 51 | 52 | 0.0021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2572-7_0_6_line_58 |  | 52 | 55 | 0.0237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2572-7_0_6_line_59 |  | 53 | 105 | 0.035857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_2572-7_0_6_line_60 |  | 54 | 96 | 0.032307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2572-7_0_6_line_61 |  | 55 | 134 | 0.0031326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2572-7_0_6_line_62 |  | 56 | 93 | 0.0051633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_2572-7_0_6_line_63 |  | 57 | 58 | 0.011738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2572-7_0_6_line_64 |  | 58 | 59 | 0.034901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2572-7_0_6_line_65 |  | 58 | 60 | 0.32849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2572-7_0_6_line_66 |  | 59 | 61 | 0.16261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2572-7_0_6_line_67 |  | 61 | 62 | 0.06625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2572-7_0_6_line_68 |  | 62 | 105 | 0.020206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2572-7_0_6_line_69 |  | 63 | 64 | 0.030243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2572-7_0_6_line_70 |  | 64 | 115 | 0.041248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2572-7_0_6_line_71 |  | 64 | 112 | 0.02513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2572-7_0_6_line_72 |  | 65 | 69 | 0.0057469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2572-7_0_6_line_73 |  | 66 | 67 | 0.013841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2572-7_0_6_line_74 |  | 66 | 68 | 0.018369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2572-7_0_6_line_75 |  | 68 | 70 | 0.03211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_2572-7_0_6_line_76 |  | 69 | 71 | 0.018902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2572-7_0_6_line_77 |  | 70 | 127 | 0.019803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_2572-7_0_6_line_78 |  | 71 | 129 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2572-7_0_6_line_79 |  | 71 | 116 | 0.0086423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2572-7_0_6_line_80 |  | 72 | 73 | 0.045405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2572-7_0_6_line_81 |  | 73 | 74 | 0.0323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2572-7_0_6_line_82 |  | 74 | 75 | 0.005912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2572-7_0_6_line_83 |  | 75 | 78 | 0.05105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_2572-7_0_6_line_84 |  | 75 | 79 | 0.0029935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2572-7_0_6_line_85 |  | 76 | 77 | 0.013676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_2572-7_0_6_line_86 |  | 76 | 78 | 0.011974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2572-7_0_6_line_87 |  | 77 | 80 | 0.03435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2572-7_0_6_line_88 |  | 77 | 81 | 0.026919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2572-7_0_6_line_89 |  | 79 | 119 | 0.054287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_2572-7_0_6_line_90 |  | 81 | 133 | 0.04094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2572-7_0_6_line_91 |  | 82 | 83 | 0.012963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2572-7_0_6_line_92 |  | 82 | 84 | 0.018988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_2572-7_0_6_line_93 |  | 83 | 85 | 0.0049742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2572-7_0_6_line_94 |  | 84 | 86 | 0.0032695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2572-7_0_6_line_95 |  | 85 | 87 | 0.028269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2572-7_0_6_line_96 |  | 86 | 88 | 0.023768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2572-7_0_6_line_97 |  | 88 | 94 | 0.046651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2572-7_0_6_line_98 |  | 88 | 91 | 0.017347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_2572-7_0_6_line_99 |  | 89 | 90 | 0.022348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2572-7_0_6_line_100 |  | 89 | 91 | 0.0055367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2572-7_0_6_line_101 |  | 90 | 92 | 0.00031162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_2572-7_0_6_line_102 |  | 92 | 93 | 0.027642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_2572-7_0_6_line_103 |  | 94 | 95 | 0.020136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2572-7_0_6_line_104 |  | 96 | 97 | 0.014238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2572-7_0_6_line_105 |  | 97 | 98 | 0.061321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2572-7_0_6_line_106 |  | 98 | 99 | 0.034012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2572-7_0_6_line_107 |  | 99 | 100 | 0.01436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2572-7_0_6_line_108 |  | 99 | 101 | 0.10138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2572-7_0_6_line_109 |  | 101 | 104 | 0.015259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2572-7_0_6_line_110 |  | 101 | 102 | 0.070179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2572-7_0_6_line_111 |  | 103 | 104 | 0.027938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2572-7_0_6_line_112 |  | 106 | 107 | 0.01375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2572-7_0_6_line_113 |  | 106 | 108 | 0.0064535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2572-7_0_6_line_114 |  | 107 | 109 | 4.2262e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2572-7_0_6_line_115 |  | 109 | 110 | 0.023418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2572-7_0_6_line_116 |  | 110 | 111 | 0.0091867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2572-7_0_6_line_117 |  | 112 | 113 | 0.0033737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2572-7_0_6_line_118 |  | 113 | 114 | 0.019838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2572-7_0_6_line_119 |  | 114 | 116 | 0.01913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2572-7_0_6_line_120 |  | 115 | 117 | 0.019896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2572-7_0_6_line_121 |  | 117 | 118 | 0.023329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2572-7_0_6_line_122 |  | 118 | 131 | 0.034945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2572-7_0_6_line_123 |  | 119 | 120 | 0.041749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2572-7_0_6_line_124 |  | 119 | 121 | 0.044491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_2572-7_0_6_line_125 |  | 121 | 122 | 0.034836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2572-7_0_6_line_126 |  | 121 | 123 | 0.021859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_2572-7_0_6_line_127 |  | 122 | 124 | 0.075751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2572-7_0_6_line_128 |  | 122 | 125 | 0.081699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2572-7_0_6_line_129 |  | 123 | 126 | 0.018833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_2572-7_0_6_line_130 |  | 124 | 128 | 0.043977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2572-7_0_6_line_131 |  | 126 | 127 | 0.036754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_2572-7_0_6_line_132 |  | 129 | 130 | 0.0082855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2572-7_0_6_line_133 |  | 131 | 132 | 0.014487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2572-7_0_6_line_134 |  | 134 | 135 | 0.021917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2572-7_0_6_trafo_107 | 0.63 MVA 20/0.4 kV | 136 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2640373.0282 | 1245278.893 | 2640365.1566 | 1245272.1748 | 2640351.9811 | 1245259.9741
1 | 2640373.0282 | 1245278.893 | 2640381.7947 | 1245286.375 | 2640387.9941 | 1245291.0285
2 | 2640351.9811 | 1245259.9741 | 2640348.0535 | 1245256.337 | 2640345.4798 | 1245253.8227
3 | 2640387.9941 | 1245291.0285 | 2640395.0059 | 1245296.2918
4 | 2640323.4075 | 1245231.53 | 2640323.9423 | 1245232.2463 | 2640328.3294 | 1245237.0682 | 2640345.4798 | 1245253.8227
5 | 2640407.923 | 1245305.9878 | 2640395.0059 | 1245296.2918
6 | 2640407.923 | 1245305.9878 | 2640387.6961 | 1245339.6818
7 | 2640407.923 | 1245305.9878 | 2640414.6017 | 1245294.9038 | 2640425.4966 | 1245276.954
8 | 2640407.923 | 1245305.9878 | 2640424.1059 | 1245316.1966
9 | 2640373.4095 | 1245361.7341 | 2640378.191 | 1245355.1956 | 2640383.3011 | 1245347.0028 | 2640387.6961 | 1245339.6818
10 | 2640435.2476 | 1245260.8887 | 2640425.4966 | 1245276.954
11 | 2640435.3895 | 1245323.3147 | 2640424.1059 | 1245316.1966
12 | 2640531.6909 | 1245237.4361 | 2640531.6216 | 1245237.3982
13 | 2640470.8443 | 1245203.7938 | 2640481.4027 | 1245209.9031 | 2640531.6216 | 1245237.3982
14 | 2640437.6011 | 1245257.0022 | 2640446.1982 | 1245242.6958 | 2640465.1524 | 1245213.0611 | 2640470.8443 | 1245203.7938
15 | 2640437.6011 | 1245257.0022 | 2640454.2876 | 1245266.7514
16 | 2640437.6011 | 1245257.0022 | 2640435.2476 | 1245260.8887
17 | 2640665.9755 | 1245311.4864 | 2640622.2989 | 1245287.5052 | 2640618.8263 | 1245285.5559
18 | 2640683.0172 | 1245320.9651 | 2640670.1998 | 1245313.8059 | 2640665.9755 | 1245311.4864
19 | 2640683.0172 | 1245320.9651 | 2640670.5405 | 1245341.6556
20 | 2640668.7462 | 1245344.6312 | 2640670.5405 | 1245341.6556
21 | 2640471.2825 | 1245276.7086 | 2640469.1017 | 1245275.4067 | 2640454.2876 | 1245266.7514
22 | 2640435.2476 | 1245260.8887 | 2640424.7567 | 1245252.8822
23 | 2640631.0703 | 1245371.5421 | 2640626.1992 | 1245367.7956 | 2640620.6 | 1245363.499 | 2640617.5899 | 1245361.6609
24 | 2640651.8414 | 1245383.1924 | 2640645.879 | 1245381.1947 | 2640641.8098 | 1245379.6658 | 2640638.7938 | 1245377.6772 | 2640633.0984 | 1245373.1019 | 2640631.0703 | 1245371.5421
25 | 2640617.5234 | 1245361.6203 | 2640617.5899 | 1245361.6609
26 | 2640651.8414 | 1245383.1924 | 2640648.8845 | 1245392.4337
27 | 2640651.8414 | 1245383.1924 | 2640654.2329 | 1245375.9818 | 2640657.4559 | 1245368.5274
28 | 2640604.3784 | 1245353.831 | 2640611.0977 | 1245357.6968 | 2640617.5234 | 1245361.6203
29 | 2640668.8028 | 1245406.3015 | 2640663.1028 | 1245401.3036 | 2640655.9969 | 1245396.3961 | 2640651.6039 | 1245393.5976 | 2640648.8845 | 1245392.4337
30 | 2640648.8845 | 1245392.4337 | 2640646.6121 | 1245399.9409
31 | 2640663.0025 | 1245356.1859 | 2640660.7658 | 1245360.8722 | 2640657.4559 | 1245368.5274
32 | 2640604.0704 | 1245353.6538 | 2640604.3784 | 1245353.831
33 | 2640668.8028 | 1245406.3015 | 2640675.5995 | 1245398.9988 | 2640682.2032 | 1245392.3063 | 2640684.8997 | 1245390.2012 | 2640689.4032 | 1245387.8972 | 2640690.121 | 1245387.5978
34 | 2640633.2469 | 1245444.0939 | 2640646.6121 | 1245399.9409
35 | 2640668.7462 | 1245344.6312 | 2640668.7419 | 1245344.6383 | 2640665.6638 | 1245350.6101 | 2640663.0025 | 1245356.1859
36 | 2640590.3398 | 1245345.8005 | 2640593.2021 | 1245347.401 | 2640604.0704 | 1245353.6538
37 | 2640697.2981 | 1245384.6047 | 2640690.121 | 1245387.5978
38 | 2640633.2469 | 1245444.0939 | 2640624.3985 | 1245440.998 | 2640620.6017 | 1245439.4043 | 2640617.1023 | 1245437.4013 | 2640611.3045 | 1245433.8494
39 | 2640743.3209 | 1245416.9082 | 2640750.1007 | 1245405.2031
40 | 2640777.8978 | 1245358.9964 | 2640758.4976 | 1245390.7063 | 2640750.1007 | 1245405.2031
41 | 2640743.3209 | 1245416.9082 | 2640723.2032 | 1245404.6065
42 | 2640743.3209 | 1245416.9082 | 2640742.0335 | 1245419.0113
43 | 2640777.8978 | 1245358.9964 | 2640775.8016 | 1245358.4039 | 2640773.704 | 1245358.0003 | 2640770.3042 | 1245357.9992 | 2640768.798 | 1245358.4002
44 | 2640777.8978 | 1245358.9964 | 2640787.7727 | 1245342.8562
45 | 2640739.0654 | 1245423.8601 | 2640742.0335 | 1245419.0113
46 | 2640768.798 | 1245358.4002 | 2640767.197 | 1245356.0988 | 2640765.1015 | 1245354.3055 | 2640753.4921 | 1245347.299
47 | 2640768.798 | 1245358.4002 | 2640766.3982 | 1245359.1064 | 2640744.0364 | 1245367.117
48 | 2640739.0654 | 1245423.8601 | 2640733.5556 | 1245432.861
49 | 2640753.4921 | 1245347.299 | 2640751.1792 | 1245345.8928
50 | 2640697.2981 | 1245384.6047 | 2640697.904 | 1245384.3976 | 2640715.6013 | 1245377.3032 | 2640744.0364 | 1245367.117
51 | 2640733.5556 | 1245432.861 | 2640733.1493 | 1245433.5246
52 | 2640697.2981 | 1245384.6047 | 2640697.3043 | 1245381.5027 | 2640697.9004 | 1245378.3047 | 2640700.4987 | 1245372.8967 | 2640707.2317 | 1245362.5399
53 | 2640578.7891 | 1245339.3417 | 2640590.3398 | 1245345.8005
54 | 2640440.7801 | 1245326.7153 | 2640435.3895 | 1245323.3147
55 | 2640373.4095 | 1245361.7341 | 2640408.7673 | 1245388.9933
56 | 2640373.4095 | 1245361.7341 | 2640367.3519 | 1245357.0565
57 | 2640423.0574 | 1245251.5852 | 2640424.7567 | 1245252.8822
58 | 2640404.217 | 1245237.2064 | 2640423.0574 | 1245251.5852
59 | 2640437.1796 | 1245410.8669 | 2640411.1379 | 1245390.8209 | 2640408.7673 | 1245388.9933
60 | 2640367.3519 | 1245357.0565 | 2640355.3855 | 1245348.0359 | 2640342.0461 | 1245336.9861
61 | 2640404.217 | 1245237.2064 | 2640401.7268 | 1245235.3059
62 | 2640471.2825 | 1245276.7086 | 2640475.7158 | 1245279.3553
63 | 2640251.4407 | 1245611.1252 | 2640260.7186 | 1245603.9357
64 | 2640251.4407 | 1245611.1252 | 2640278.5468 | 1245612.2987 | 2640285.4174 | 1245608.465
65 | 2640251.4407 | 1245611.1252 | 2639927.9179 | 1245554.2427
66 | 2640384.725 | 1245479.6995 | 2640285.4174 | 1245608.465
67 | 2640424.914 | 1245426.9495 | 2640384.725 | 1245479.6995
68 | 2640424.914 | 1245426.9495 | 2640437.1796 | 1245410.8669
69 | 2640757.8012 | 1245275.4036 | 2640761.4024 | 1245276.896 | 2640786.3889 | 1245285.2465
70 | 2640722.4821 | 1245254.2807 | 2640733.1107 | 1245262.2144 | 2640741.0005 | 1245267.4053 | 2640751.1032 | 1245272.7003 | 2640757.8012 | 1245275.4036
71 | 2640757.8012 | 1245275.4036 | 2640755.1006 | 1245280.2994 | 2640748.9981 | 1245290.9978 | 2640745.4068 | 1245297.2641
72 | 2640707.2317 | 1245362.5399 | 2640710.3641 | 1245357.7217
73 | 2640725.923 | 1245445.3297 | 2640733.1493 | 1245433.5246
74 | 2640725.923 | 1245445.3297 | 2640716.3582 | 1245461.0125
75 | 2640716.3582 | 1245461.0125 | 2640708.9601 | 1245473.1428 | 2640699.5074 | 1245488.3454
76 | 2640720.0552 | 1245341.4991 | 2640713.3724 | 1245353.0942 | 2640710.3641 | 1245357.7217
77 | 2640699.5074 | 1245488.3454 | 2640689.0508 | 1245505.1625
78 | 2640720.0552 | 1245341.4991 | 2640708.8741 | 1245334.9226
79 | 2640720.0552 | 1245341.4991 | 2640724.3525 | 1245334.0009
80 | 2640515.5749 | 1245548.9753 | 2640540.601 | 1245558.9472 | 2640547.2104 | 1245556.8909 | 2640551.34 | 1245546.1111
81 | 2640562.8947 | 1245515.949 | 2640551.34 | 1245546.1111
82 | 2640565.01 | 1245510.4265 | 2640562.8947 | 1245515.949
83 | 2640565.01 | 1245510.4265 | 2640524.984 | 1245478.7398
84 | 2640565.01 | 1245510.4265 | 2640567.3573 | 1245512.2842
85 | 2640515.5961 | 1245471.3078 | 2640504.7819 | 1245462.8952
86 | 2640515.5961 | 1245471.3078 | 2640524.984 | 1245478.7398
87 | 2640504.7819 | 1245462.8952 | 2640492.3579 | 1245494.9192
88 | 2640504.7819 | 1245462.8952 | 2640483.4078 | 1245446.4497
89 | 2640610.578 | 1245545.1163 | 2640587.5978 | 1245528.3037 | 2640567.3573 | 1245512.2842
90 | 2640483.4078 | 1245446.4497 | 2640506.315 | 1245412.5181
91 | 2640578.7891 | 1245339.3417 | 2640572.1017 | 1245350.4461
92 | 2640578.7891 | 1245339.3417 | 2640569.4038 | 1245334.0963 | 2640562.2604 | 1245329.9963
93 | 2640572.1017 | 1245350.4461 | 2640569.5355 | 1245354.7072
94 | 2640559.4248 | 1245328.3688 | 2640562.2604 | 1245329.9963
95 | 2640558.9559 | 1245380.3377 | 2640567.9432 | 1245365.3957 | 2640569.3667 | 1245354.9875 | 2640569.5355 | 1245354.7072
96 | 2640559.4248 | 1245328.3688 | 2640538.767 | 1245316.5088
97 | 2640538.767 | 1245316.5088 | 2640525.0805 | 1245337.0178 | 2640514.1858 | 1245356.125
98 | 2640538.767 | 1245316.5088 | 2640523.7222 | 1245307.8723
99 | 2640518.9204 | 1245305.1158 | 2640517.4995 | 1245304.3001 | 2640499.7177 | 1245293.6844
100 | 2640518.9204 | 1245305.1158 | 2640523.7222 | 1245307.8723
101 | 2640499.7177 | 1245293.6844 | 2640499.4501 | 1245293.5246
102 | 2640499.4501 | 1245293.5246 | 2640475.7158 | 1245279.3553
103 | 2640522.9042 | 1245368.5454 | 2640511.0106 | 1245361.6935 | 2640514.1858 | 1245356.125
104 | 2640342.0461 | 1245336.9861 | 2640337.6027 | 1245333.3054 | 2640331.1247 | 1245327.8516
105 | 2640331.1247 | 1245327.8516 | 2640322.3982 | 1245320.5048 | 2640305.0991 | 1245304.5992 | 2640289.9979 | 1245288.7974 | 2640286.8858 | 1245285.4689
106 | 2640264.3013 | 1245260.0599 | 2640272.7987 | 1245270.402 | 2640286.8858 | 1245285.4689
107 | 2640264.3013 | 1245260.0599 | 2640257.1152 | 1245251.3054 | 2640255.2796 | 1245248.8895
108 | 2640264.3013 | 1245260.0599 | 2640194.6794 | 1245333.7587
109 | 2640182.754 | 1245343.1842 | 2640187.0449 | 1245338.7881 | 2640194.6794 | 1245333.7587
110 | 2640194.6794 | 1245333.7587 | 2640194.8937 | 1245336.6954 | 2640195.8041 | 1245339.4812 | 2640197.3662 | 1245341.9823 | 2640228.7864 | 1245372.2927 | 2640232.9297 | 1245376.2901 | 2640224.6512 | 1245384.8953
111 | 2640182.754 | 1245343.1842 | 2640202.8275 | 1245362.6151
112 | 2640571.9745 | 1245409.2363 | 2640583.6153 | 1245416.5551
113 | 2640566.511 | 1245405.8014 | 2640571.9745 | 1245409.2363
114 | 2640583.6153 | 1245416.5551 | 2640583.6511 | 1245416.5776
115 | 2640603.4761 | 1245429.0419 | 2640583.6511 | 1245416.5776
116 | 2640603.4761 | 1245429.0419 | 2640604.1996 | 1245429.4968 | 2640611.3045 | 1245433.8494
117 | 2640745.4068 | 1245297.2641 | 2640743.7293 | 1245300.1912
118 | 2640733.8649 | 1245317.4031 | 2640743.7293 | 1245300.1912
119 | 2640733.8649 | 1245317.4031 | 2640724.3525 | 1245334.0009
120 | 2640722.4821 | 1245254.2807 | 2640711.8244 | 1245248.3704 | 2640705.0577 | 1245244.676
121 | 2640685.8135 | 1245231.5811 | 2640698.5015 | 1245241.0965 | 2640705.0577 | 1245244.676
122 | 2640685.8135 | 1245231.5811 | 2640667.6365 | 1245261.4263
123 | 2640610.578 | 1245545.1163 | 2640606.5481 | 1245570.9613 | 2640604.2042 | 1245586.3753
124 | 2640610.578 | 1245545.1163 | 2640629.3007 | 1245559.1981 | 2640642.5259 | 1245567.4051 | 2640647.1976 | 1245570.3056
125 | 2640647.1976 | 1245570.3056 | 2640677.2803 | 1245588.0233
126 | 2640647.1976 | 1245570.3056 | 2640659.5378 | 1245552.2632
127 | 2640742.6562 | 1245624.8291 | 2640741.2827 | 1245625.7202 | 2640677.2803 | 1245588.0233
128 | 2640674.7052 | 1245669.4147 | 2640672.4994 | 1245642.9489 | 2640677.2803 | 1245588.0233
129 | 2640659.5378 | 1245552.2632 | 2640662.0328 | 1245548.6152 | 2640669.6437 | 1245536.3748
130 | 2640742.6562 | 1245624.8291 | 2640748.2818 | 1245581.2168
131 | 2640669.6437 | 1245536.3748 | 2640689.0508 | 1245505.1625
132 | 2640701.7324 | 1245330.7219 | 2640708.8741 | 1245334.9226
133 | 2640660.1007 | 1245273.7994 | 2640667.6365 | 1245261.4263
134 | 2640401.7268 | 1245235.3059 | 2640392.7662 | 1245228.4672 | 2640384.7061 | 1245221.5144

## bus_geodata
| x | y | coords
0 | 2640373.0282 | 1245278.893
1 | 2640351.9811 | 1245259.9741
2 | 2640387.9941 | 1245291.0285
3 | 2640345.4798 | 1245253.8227
4 | 2640395.0059 | 1245296.2918
5 | 2640323.4075 | 1245231.53
6 | 2640407.923 | 1245305.9878
7 | 2640387.6961 | 1245339.6818
8 | 2640425.4966 | 1245276.954
9 | 2640424.1059 | 1245316.1966
10 | 2640531.6909 | 1245237.4361
11 | 2640531.6216 | 1245237.3982
12 | 2640470.8443 | 1245203.7938
13 | 2640437.6011 | 1245257.0022
14 | 2640618.8263 | 1245285.5559
15 | 2640665.9755 | 1245311.4864
16 | 2640683.0172 | 1245320.9651
17 | 2640670.5405 | 1245341.6556
18 | 2640454.2876 | 1245266.7514
19 | 2640435.2476 | 1245260.8887
20 | 2640631.0703 | 1245371.5421
21 | 2640617.5899 | 1245361.6609
22 | 2640651.8414 | 1245383.1924
23 | 2640617.5234 | 1245361.6203
24 | 2640648.8845 | 1245392.4337
25 | 2640657.4559 | 1245368.5274
26 | 2640604.3784 | 1245353.831
27 | 2640668.8028 | 1245406.3015
28 | 2640646.6121 | 1245399.9409
29 | 2640663.0025 | 1245356.1859
30 | 2640604.0703 | 1245353.6538
31 | 2640690.121 | 1245387.5978
32 | 2640633.2469 | 1245444.0939
33 | 2640668.7462 | 1245344.6312
34 | 2640750.1007 | 1245405.2031
35 | 2640743.3209 | 1245416.9082
36 | 2640777.8978 | 1245358.9964
37 | 2640723.2032 | 1245404.6065
38 | 2640742.0335 | 1245419.0113
39 | 2640768.798 | 1245358.4002
40 | 2640787.7727 | 1245342.8562
41 | 2640739.0654 | 1245423.8601
42 | 2640753.4921 | 1245347.299
43 | 2640744.0364 | 1245367.117
44 | 2640733.5556 | 1245432.861
45 | 2640751.1792 | 1245345.8928
46 | 2640697.2981 | 1245384.6047
47 | 2640590.3398 | 1245345.8005
48 | 2640435.3895 | 1245323.3147
49 | 2640440.7801 | 1245326.7153
50 | 2640373.4095 | 1245361.7341
51 | 2640424.7567 | 1245252.8822
52 | 2640423.0574 | 1245251.5852
53 | 2640408.7673 | 1245388.9933
54 | 2640367.3519 | 1245357.0565
55 | 2640404.217 | 1245237.2064
56 | 2640471.2825 | 1245276.7086
57 | 2640260.7186 | 1245603.9357
58 | 2640251.4407 | 1245611.1252
59 | 2640285.4174 | 1245608.465
60 | 2639927.9179 | 1245554.2427
61 | 2640384.725 | 1245479.6995
62 | 2640424.914 | 1245426.9495
63 | 2640786.3889 | 1245285.2465
64 | 2640757.8012 | 1245275.4036
65 | 2640707.2317 | 1245362.5399
66 | 2640725.923 | 1245445.3297
67 | 2640733.1493 | 1245433.5246
68 | 2640716.3582 | 1245461.0125
69 | 2640710.3641 | 1245357.7217
70 | 2640699.5074 | 1245488.3454
71 | 2640720.0552 | 1245341.4991
72 | 2640515.5749 | 1245548.9753
73 | 2640551.34 | 1245546.1111
74 | 2640562.8947 | 1245515.949
75 | 2640565.01 | 1245510.4265
76 | 2640515.5961 | 1245471.3078
77 | 2640504.7819 | 1245462.8952
78 | 2640524.984 | 1245478.7398
79 | 2640567.3573 | 1245512.2842
80 | 2640492.3579 | 1245494.9192
81 | 2640483.4078 | 1245446.4497
82 | 2640578.7891 | 1245339.3417
83 | 2640572.1017 | 1245350.4461
84 | 2640562.2604 | 1245329.9963
85 | 2640569.5355 | 1245354.7072
86 | 2640559.4248 | 1245328.3688
87 | 2640558.9559 | 1245380.3377
88 | 2640538.767 | 1245316.5088
89 | 2640518.9204 | 1245305.1158
90 | 2640499.7177 | 1245293.6844
91 | 2640523.7222 | 1245307.8723
92 | 2640499.4501 | 1245293.5246
93 | 2640475.7158 | 1245279.3553
94 | 2640514.1858 | 1245356.125
95 | 2640522.9042 | 1245368.5454
96 | 2640342.0461 | 1245336.9861
97 | 2640331.1247 | 1245327.8516
98 | 2640286.8858 | 1245285.4689
99 | 2640264.3013 | 1245260.0599
100 | 2640255.2796 | 1245248.8895
101 | 2640194.6794 | 1245333.7587
102 | 2640224.6512 | 1245384.8953
103 | 2640202.8275 | 1245362.6151
104 | 2640182.754 | 1245343.1842
105 | 2640437.1796 | 1245410.8669
106 | 2640571.9745 | 1245409.2363
107 | 2640583.6153 | 1245416.5551
108 | 2640566.511 | 1245405.8014
109 | 2640583.6511 | 1245416.5776
110 | 2640603.4761 | 1245429.0419
111 | 2640611.3045 | 1245433.8494
112 | 2640745.4068 | 1245297.2641
113 | 2640743.7293 | 1245300.1912
114 | 2640733.8649 | 1245317.4031
115 | 2640722.4821 | 1245254.2807
116 | 2640724.3525 | 1245334.0009
117 | 2640705.0577 | 1245244.676
118 | 2640685.8135 | 1245231.5811
119 | 2640610.578 | 1245545.1163
120 | 2640604.2042 | 1245586.3753
121 | 2640647.1976 | 1245570.3056
122 | 2640677.2803 | 1245588.0233
123 | 2640659.5378 | 1245552.2632
124 | 2640742.6562 | 1245624.8291
125 | 2640674.7052 | 1245669.4147
126 | 2640669.6437 | 1245536.3748
127 | 2640689.0508 | 1245505.1625
128 | 2640748.2818 | 1245581.2168
129 | 2640708.8741 | 1245334.9226
130 | 2640701.7324 | 1245330.7219
131 | 2640667.6365 | 1245261.4263
132 | 2640660.1007 | 1245273.7994
133 | 2640506.315 | 1245412.5181
134 | 2640401.7268 | 1245235.3059
135 | 2640384.7061 | 1245221.5144
136 | 2640424.914 | 1245426.9495

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99104 | -0.17103 | 0.0015516 | 0.00038887
1 | 0.99058 | -0.17987 | 0.001625 | 0.00040726
2 | 0.99137 | -0.16448 | 0.00050796 | 0.00012731
3 | 0.99045 | -0.18241 | 0.0086476 | 0.0021673
4 | 0.99153 | -0.16143 | 0.0042198 | 0.0010576
5 | 0.99024 | -0.18649 | 0.0073189 | 0.0018343
6 | 0.99188 | -0.15459 | 0 | 0
7 | 0.99387 | -0.11649 | 0.00079292 | 0.00019872
8 | 0.99045 | -0.1821 | 0.0024281 | 0.00060855
9 | 0.9915 | -0.16199 | 0.0033301 | 0.00083461
10 | 0.98915 | -0.20712 | 0.0013584 | 0.00034045
11 | 0.98915 | -0.20712 | 0.0013589 | 0.00034056
12 | 0.98933 | -0.20376 | 0 | 0
13 | 0.98948 | -0.20072 | 0 | 0
14 | 0.98081 | -0.369 | 0.0027321 | 0.00068473
15 | 0.98095 | -0.36634 | 0.0020605 | 0.00051642
16 | 0.98104 | -0.36464 | 0 | 0
17 | 0.98114 | -0.36255 | 0.0023157 | 0.00058038
18 | 0.98872 | -0.21549 | 0.0056435 | 0.0014144
19 | 0.98967 | -0.19721 | 0 | 0
20 | 0.98224 | -0.34112 | 0.0020049 | 0.00050247
21 | 0.98265 | -0.33322 | 0.0019798 | 0.00049617
22 | 0.98166 | -0.35235 | 0 | 0
23 | 0.98265 | -0.33318 | 0.0026052 | 0.00065293
24 | 0.98146 | -0.35628 | 0 | 0
25 | 0.98142 | -0.35722 | 0.0059086 | 0.0014808
26 | 0.98303 | -0.32571 | 0.0020438 | 0.00051223
27 | 0.98105 | -0.36443 | 0 | 0
28 | 0.98132 | -0.35901 | 0.0051315 | 0.0012861
29 | 0.98128 | -0.35996 | 0.0020556 | 0.00051519
30 | 0.98304 | -0.32553 | 0.0019568 | 0.00049041
31 | 0.98055 | -0.37402 | 0.0020534 | 0.00051462
32 | 0.98072 | -0.37079 | 0 | 0
33 | 0.98117 | -0.3621 | 0.0020316 | 0.00050917
34 | 0.97846 | -0.4151 | 0.00083768 | 0.00020994
35 | 0.97827 | -0.41873 | 0 | 0
36 | 0.9792 | -0.40047 | 0 | 0
37 | 0.97823 | -0.41959 | 0.0020239 | 0.00050724
38 | 0.97824 | -0.41937 | 0.0024037 | 0.00060243
39 | 0.97933 | -0.39794 | 0 | 0
40 | 0.97919 | -0.40075 | 0.00079666 | 0.00019966
41 | 0.97817 | -0.42081 | 0.0022679 | 0.0005684
42 | 0.97931 | -0.39833 | 0 | 0
43 | 0.9797 | -0.39065 | 0.0012184 | 0.00030536
44 | 0.97803 | -0.42338 | 0.00046676 | 0.00011698
45 | 0.97931 | -0.39839 | 0.0011271 | 0.00028249
46 | 0.98042 | -0.37657 | 0 | 0
47 | 0.98345 | -0.31758 | 0.0032422 | 0.00081258
48 | 0.99128 | -0.16637 | 0.014169 | 0.003551
49 | 0.99125 | -0.16686 | 0.0043235 | 0.0010836
50 | 0.99521 | -0.091015 | 0 | 0
51 | 0.98956 | -0.19926 | 0.0025269 | 0.0006333
52 | 0.98955 | -0.1995 | 0.0024027 | 0.00060219
53 | 0.99785 | -0.040786 | 0.0050888 | 0.0012754
54 | 0.99489 | -0.097139 | 0 | 0
55 | 0.98946 | -0.20111 | 0.0011921 | 0.00029877
56 | 0.98796 | -0.23018 | 0.0076634 | 0.0019206
57 | 0.98594 | -0.27044 | 0.01297 | 0.0032505
58 | 0.98608 | -0.26772 | 0 | 0
59 | 0.98701 | -0.24965 | 0 | 0
60 | 0.98125 | -0.36194 | 0.015919 | 0.0039898
61 | 0.99135 | -0.16593 | 0.080254 | 0.020114
62 | 0.99798 | -0.038523 | 0 | 0
63 | 0.9795 | -0.39481 | 0.00071948 | 0.00018032
64 | 0.97952 | -0.39441 | 0 | 0
65 | 0.98013 | -0.38228 | 0.0021752 | 0.00054516
66 | 0.97785 | -0.42691 | 0 | 0
67 | 0.97802 | -0.42357 | 0.00037695 | 9.4472e-05
68 | 0.97763 | -0.43134 | 0.0013725 | 0.00034397
69 | 0.98008 | -0.38338 | 0.00081524 | 0.00020432
70 | 0.97724 | -0.43893 | 0.002082 | 0.00052181
71 | 0.97991 | -0.38673 | 0 | 0
72 | 0.97506 | -0.4819 | 0.0064351 | 0.0016128
73 | 0.97533 | -0.47654 | 0.0017672 | 0.0004429
74 | 0.97558 | -0.47169 | 0 | 0
75 | 0.97562 | -0.4708 | 0 | 0
76 | 0.97546 | -0.47406 | 0 | 0
77 | 0.97542 | -0.47474 | 0 | 0
78 | 0.97549 | -0.47347 | 0.00080051 | 0.00020063
79 | 0.97564 | -0.47055 | 0.007388 | 0.0018516
80 | 0.97522 | -0.47884 | 0.0065121 | 0.0016321
81 | 0.97537 | -0.47588 | 0 | 0
82 | 0.9838 | -0.31078 | 0 | 0
83 | 0.98362 | -0.31424 | 0.0031125 | 0.00078006
84 | 0.98435 | -0.30001 | 0.010487 | 0.0026283
85 | 0.98357 | -0.31529 | 0.0058575 | 0.001468
86 | 0.98445 | -0.29803 | 0 | 0
87 | 0.98341 | -0.31827 | 0.005851 | 0.0014664
88 | 0.98519 | -0.28368 | 0 | 0
89 | 0.98597 | -0.26861 | 0.0013821 | 0.00034638
90 | 0.98676 | -0.2534 | 0.0013728 | 0.00034406
91 | 0.98578 | -0.27236 | 0.0067808 | 0.0016994
92 | 0.98677 | -0.25318 | 0.0037555 | 0.00094122
93 | 0.98776 | -0.23389 | 0.0060554 | 0.0015176
94 | 0.9846 | -0.2953 | 0.0068111 | 0.001707
95 | 0.98447 | -0.29785 | 0.0070421 | 0.0017649
96 | 0.99353 | -0.12309 | 0.00017525 | 4.3923e-05
97 | 0.99294 | -0.1345 | 0.0029928 | 0.00075007
98 | 0.99054 | -0.18055 | 0.0024313 | 0.00060933
99 | 0.98929 | -0.20471 | 0 | 0
100 | 0.98922 | -0.20607 | 0.0053045 | 0.0013294
101 | 0.98606 | -0.26745 | 0 | 0
102 | 0.98399 | -0.30777 | 0.031976 | 0.0080138
103 | 0.98595 | -0.26951 | 0.0026554 | 0.0006655
104 | 0.98602 | -0.26818 | 0 | 0
105 | 1 | 0 | -0.44224 | -0.11269
106 | 0.98012 | -0.38259 | 0.00051032 | 0.0001279
107 | 0.98016 | -0.38173 | 0.002577 | 0.00064586
108 | 0.9801 | -0.38294 | 0.0029543 | 0.00074041
109 | 0.98016 | -0.38172 | 0.0010267 | 0.0002573
110 | 0.98032 | -0.37872 | 0.0031952 | 0.00080078
111 | 0.9804 | -0.37701 | 0.003839 | 0.00096214
112 | 0.97958 | -0.39315 | 0.002513 | 0.00062983
113 | 0.9796 | -0.39282 | 0.0012253 | 0.0003071
114 | 0.97972 | -0.39048 | 0.00056375 | 0.00014129
115 | 0.97944 | -0.39594 | 0 | 0
116 | 0.97984 | -0.38802 | 0.0011843 | 0.00029681
117 | 0.9794 | -0.39668 | 0.00056358 | 0.00014125
118 | 0.97937 | -0.39731 | 0 | 0
119 | 0.97594 | -0.46461 | 0 | 0
120 | 0.9758 | -0.46737 | 0.003602 | 0.00090274
121 | 0.97621 | -0.45916 | 0 | 0
122 | 0.97575 | -0.4683 | 0 | 0
123 | 0.97641 | -0.45534 | 0.0065866 | 0.0016508
124 | 0.97562 | -0.47089 | 0 | 0
125 | 0.9748 | -0.48697 | 0.012468 | 0.0031248
126 | 0.9766 | -0.45159 | 0.0061108 | 0.0015315
127 | 0.97701 | -0.44346 | 0.0021285 | 0.00053345
128 | 0.97554 | -0.47239 | 0.0018621 | 0.00046667
129 | 0.97989 | -0.38708 | 0.0008369 | 0.00020975
130 | 0.97988 | -0.38718 | 0.00065337 | 0.00016375
131 | 0.97932 | -0.39825 | 0.00040373 | 0.00010118
132 | 0.97931 | -0.39853 | 0.0010753 | 0.0002695
133 | 0.9751 | -0.48111 | 0.0069615 | 0.0017447
134 | 0.98946 | -0.20126 | 0.0014396 | 0.0003608
135 | 0.98943 | -0.20173 | 0.001191 | 0.00029848
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.017602 | 0.0044149 | -0.017595 | -0.0044105 | 7.4151e-06 | 4.3811e-06 | 0.026431 | 0.026431 | 0.026431 | 0.99104 | -0.17103 | 0.99058 | -0.17987 | 7.2612
1 | -0.019154 | -0.0048037 | 0.01916 | 0.0048073 | 5.9793e-06 | 3.5783e-06 | 0.02876 | 0.02876 | 0.02876 | 0.99104 | -0.17103 | 0.99137 | -0.16448 | 7.9012
2 | 0.01597 | 0.0040032 | -0.015968 | -0.0040021 | 1.9318e-06 | 1.1211e-06 | 0.02399 | 0.02399 | 0.02399 | 0.99058 | -0.17987 | 0.99045 | -0.18241 | 6.5906
3 | -0.019668 | -0.0049346 | 0.019671 | 0.0049363 | 2.8656e-06 | 1.7209e-06 | 0.029523 | 0.029523 | 0.029523 | 0.99137 | -0.16448 | 0.99153 | -0.16143 | 8.1106
4 | 0.0073203 | 0.0018348 | -0.0073189 | -0.0018343 | 1.4237e-06 | 5.073e-07 | 0.010998 | 0.010998 | 0.010998 | 0.99045 | -0.18241 | 0.99024 | -0.18649 | 3.0214
5 | -0.02389 | -0.0059939 | 0.023898 | 0.0059987 | 7.7865e-06 | 4.775e-06 | 0.035855 | 0.035855 | 0.035855 | 0.99153 | -0.16143 | 0.99188 | -0.15459 | 9.8504
6 | -0.27625 | -0.070054 | 0.27676 | 0.070376 | 0.00050694 | 0.0003219 | 0.41472 | 0.41472 | 0.41472 | 0.99188 | -0.15459 | 0.99387 | -0.11649 | 22.787
7 | 0.23052 | 0.058579 | -0.23022 | -0.058386 | 0.00030492 | 0.00019296 | 0.34611 | 0.34611 | 0.34611 | 0.99188 | -0.15459 | 0.99045 | -0.1821 | 19.0172
8 | 0.021834 | 0.0054761 | -0.021826 | -0.0054714 | 7.6989e-06 | 4.6804e-06 | 0.032756 | 0.032757 | 0.032757 | 0.99188 | -0.15459 | 0.9915 | -0.16199 | 8.999
9 | -0.27755 | -0.070574 | 0.27789 | 0.070791 | 0.00034114 | 0.00021662 | 0.41591 | 0.41591 | 0.41591 | 0.99387 | -0.11649 | 0.99521 | -0.091015 | 22.8522
10 | 0.22779 | 0.057777 | -0.22762 | -0.057673 | 0.00016531 | 0.00010459 | 0.34247 | 0.34247 | 0.34247 | 0.99045 | -0.1821 | 0.98967 | -0.19721 | 18.8168
11 | 0.018496 | 0.0046368 | -0.018492 | -0.0046345 | 3.855e-06 | 2.2952e-06 | 0.027759 | 0.027759 | 0.027759 | 0.9915 | -0.16199 | 0.99128 | -0.16637 | 7.6261
12 | -0.0013584 | -0.00034045 | 0.0013584 | 0.00034045 | 1.2354e-10 | -9.3299e-10 | 0.0020435 | 0.0020435 | 0.0020435 | 0.98915 | -0.20712 | 0.98915 | -0.20712 | 0.56141
13 | -0.0027173 | -0.00068102 | 0.0027177 | 0.0006804 | 4.3515e-07 | -6.1316e-07 | 0.0040877 | 0.0040874 | 0.0040877 | 0.98915 | -0.20712 | 0.98933 | -0.20376 | 1.123
14 | -0.0027177 | -0.0006804 | 0.0027181 | 0.00067985 | 3.9307e-07 | -5.5425e-07 | 0.0040874 | 0.0040871 | 0.0040874 | 0.98933 | -0.20376 | 0.98948 | -0.20072 | 1.1229
15 | 0.21611 | 0.054776 | -0.21596 | -0.054679 | 0.0001533 | 9.6873e-05 | 0.32522 | 0.32522 | 0.32522 | 0.98948 | -0.20072 | 0.98872 | -0.21549 | 17.8691
16 | -0.21883 | -0.055456 | 0.21887 | 0.055479 | 3.6924e-05 | 2.334e-05 | 0.3293 | 0.3293 | 0.3293 | 0.98948 | -0.20072 | 0.98967 | -0.19721 | 18.0936
17 | -0.0027321 | -0.00068473 | 0.0027324 | 0.00068427 | 3.4665e-07 | -4.5735e-07 | 0.0041449 | 0.0041447 | 0.0041449 | 0.98081 | -0.369 | 0.98095 | -0.36634 | 1.1387
18 | -0.004793 | -0.0012007 | 0.0047934 | 0.0012007 | 3.8653e-07 | 1.1781e-09 | 0.0072703 | 0.0072703 | 0.0072703 | 0.98095 | -0.36634 | 0.98104 | -0.36464 | 1.9973
19 | -0.0047934 | -0.0012007 | 0.0047939 | 0.0012007 | 4.789e-07 | 1.3912e-09 | 0.0072703 | 0.0072701 | 0.0072703 | 0.98104 | -0.36464 | 0.98114 | -0.36255 | 1.9973
20 | -0.0071096 | -0.0017811 | 0.0071097 | 0.0017811 | 1.5149e-07 | 5.3066e-08 | 0.010782 | 0.010782 | 0.010782 | 0.98114 | -0.36255 | 0.98117 | -0.3621 | 2.9621
21 | 0.21032 | 0.053265 | -0.21017 | -0.053171 | 0.00014819 | 9.3581e-05 | 0.31672 | 0.31672 | 0.31672 | 0.98872 | -0.21549 | 0.98796 | -0.23018 | 17.4025
22 | 0.0087536 | 0.0021935 | -0.0087527 | -0.0021931 | 8.5726e-07 | 3.7909e-07 | 0.013161 | 0.013161 | 0.013161 | 0.98967 | -0.19721 | 0.98956 | -0.19926 | 3.6158
23 | -0.13125 | -0.033049 | 0.1313 | 0.03308 | 4.9635e-05 | 3.0707e-05 | 0.19889 | 0.19889 | 0.19889 | 0.98224 | -0.34112 | 0.98265 | -0.33322 | 10.9281
24 | 0.12925 | 0.032546 | -0.12918 | -0.032504 | 6.9368e-05 | 4.2871e-05 | 0.19585 | 0.19586 | 0.19586 | 0.98224 | -0.34112 | 0.98166 | -0.35235 | 10.7613
25 | -0.13328 | -0.033576 | 0.13328 | 0.033576 | 2.382e-07 | 1.4752e-07 | 0.20189 | 0.20189 | 0.20189 | 0.98265 | -0.33322 | 0.98265 | -0.33318 | 11.0928
26 | 0.11207 | 0.028214 | -0.11205 | -0.028201 | 2.1006e-05 | 1.2831e-05 | 0.16992 | 0.16992 | 0.16992 | 0.98166 | -0.35235 | 0.98146 | -0.35628 | 9.3361
27 | 0.017112 | 0.0042899 | -0.017108 | -0.0042875 | 3.9659e-06 | 2.3395e-06 | 0.025939 | 0.025939 | 0.025939 | 0.98166 | -0.35235 | 0.98142 | -0.35722 | 7.1261
28 | -0.13589 | -0.034229 | 0.13594 | 0.034259 | 4.8556e-05 | 3.0108e-05 | 0.20583 | 0.20583 | 0.20583 | 0.98265 | -0.33318 | 0.98303 | -0.32571 | 11.3096
29 | 0.092795 | 0.023371 | -0.092758 | -0.02335 | 3.6148e-05 | 2.1597e-05 | 0.14073 | 0.14073 | 0.14073 | 0.98146 | -0.35628 | 0.98105 | -0.36443 | 7.7324
30 | 0.019251 | 0.0048295 | -0.019248 | -0.004828 | 2.5058e-06 | 1.5046e-06 | 0.029188 | 0.029188 | 0.029188 | 0.98146 | -0.35628 | 0.98132 | -0.35901 | 8.0187
31 | 0.011199 | 0.0028067 | -0.011198 | -0.0028059 | 1.4632e-06 | 7.655e-07 | 0.01698 | 0.01698 | 0.01698 | 0.98142 | -0.35722 | 0.98128 | -0.35996 | 4.665
32 | -0.13798 | -0.034771 | 0.13798 | 0.034772 | 1.1634e-06 | 7.2205e-07 | 0.20893 | 0.20893 | 0.20893 | 0.98303 | -0.32571 | 0.98304 | -0.32553 | 11.4796
33 | 0.092758 | 0.02335 | -0.092716 | -0.023324 | 4.2534e-05 | 2.5415e-05 | 0.14073 | 0.14073 | 0.14073 | 0.98105 | -0.36443 | 0.98055 | -0.37402 | 7.7324
34 | 0.014117 | 0.0035419 | -0.014109 | -0.0035374 | 7.9275e-06 | 4.4912e-06 | 0.021407 | 0.021407 | 0.021407 | 0.98132 | -0.35901 | 0.98072 | -0.37079 | 5.8811
35 | 0.0091423 | 0.0022907 | -0.0091414 | -0.0022903 | 9.3009e-07 | 4.3225e-07 | 0.013863 | 0.013863 | 0.013863 | 0.98128 | -0.35996 | 0.98117 | -0.3621 | 3.8086
36 | -0.13994 | -0.035262 | 0.13999 | 0.035295 | 5.3264e-05 | 3.3086e-05 | 0.21189 | 0.21189 | 0.21189 | 0.98304 | -0.32553 | 0.98345 | -0.31758 | 11.6423
37 | 0.090663 | 0.02281 | -0.090651 | -0.022803 | 1.1045e-05 | 6.5783e-06 | 0.13761 | 0.13761 | 0.13761 | 0.98055 | -0.37402 | 0.98042 | -0.37657 | 7.5612
38 | 0.014109 | 0.0035374 | -0.014104 | -0.003535 | 4.18e-06 | 2.3684e-06 | 0.021407 | 0.021407 | 0.021407 | 0.98072 | -0.37079 | 0.9804 | -0.37701 | 5.8811
39 | 0.073794 | 0.018534 | -0.073781 | -0.018526 | 1.278e-05 | 7.33e-06 | 0.11224 | 0.11224 | 0.11224 | 0.97846 | -0.4151 | 0.97827 | -0.41873 | 6.1669
40 | -0.074631 | -0.018743 | 0.074683 | 0.018773 | 5.2113e-05 | 2.9963e-05 | 0.11351 | 0.11351 | 0.11351 | 0.97846 | -0.4151 | 0.9792 | -0.40047 | 6.2369
41 | 0.002024 | 0.000507 | -0.0020239 | -0.00050724 | 8.3629e-08 | -2.4189e-07 | 0.0030785 | 0.0030786 | 0.0030786 | 0.97827 | -0.41873 | 0.97823 | -0.41959 | 0.84578
42 | 0.071757 | 0.018019 | -0.071755 | -0.018018 | 2.2037e-06 | 1.2556e-06 | 0.10916 | 0.10916 | 0.10916 | 0.97827 | -0.41873 | 0.97824 | -0.41937 | 5.9978
43 | -0.07548 | -0.018973 | 0.075489 | 0.018978 | 9.1264e-06 | 5.2593e-06 | 0.11472 | 0.11472 | 0.11472 | 0.9792 | -0.40047 | 0.97933 | -0.39794 | 6.3034
44 | 0.00079667 | 0.00019943 | -0.00079666 | -0.00019966 | 1.0399e-08 | -2.3136e-07 | 0.0012106 | 0.0012106 | 0.0012106 | 0.9792 | -0.40047 | 0.97919 | -0.40075 | 0.33259
45 | 0.069351 | 0.017415 | -0.069346 | -0.017413 | 4.746e-06 | 2.6806e-06 | 0.1055 | 0.1055 | 0.1055 | 0.97824 | -0.41937 | 0.97817 | -0.42081 | 5.7969
46 | 0.0011272 | 0.00028223 | -0.0011271 | -0.00028246 | 2.0992e-08 | -2.2671e-07 | 0.0017126 | 0.0017126 | 0.0017126 | 0.97933 | -0.39794 | 0.97931 | -0.39833 | 0.4705
47 | -0.076616 | -0.01926 | 0.076643 | 0.019276 | 2.6695e-05 | 1.5432e-05 | 0.11643 | 0.11643 | 0.11643 | 0.97933 | -0.39794 | 0.9797 | -0.39065 | 6.3974
48 | 0.067078 | 0.016844 | -0.06707 | -0.01684 | 8.2435e-06 | 4.6135e-06 | 0.10205 | 0.10205 | 0.10205 | 0.97817 | -0.42081 | 0.97803 | -0.42338 | 5.6073
49 | 0.0011271 | 0.00028246 | -0.0011271 | -0.00028249 | 2.9773e-09 | -3.2152e-08 | 0.0017126 | 0.0017126 | 0.0017126 | 0.97931 | -0.39833 | 0.97931 | -0.39839 | 0.47051
50 | -0.077862 | -0.019581 | 0.077914 | 0.019611 | 5.2372e-05 | 3.0374e-05 | 0.11828 | 0.11828 | 0.11828 | 0.9797 | -0.39065 | 0.98042 | -0.37657 | 6.4991
51 | 0.066603 | 0.016723 | -0.066603 | -0.016722 | 5.9938e-07 | 3.3478e-07 | 0.10134 | 0.10134 | 0.10134 | 0.97803 | -0.42338 | 0.97802 | -0.42357 | 5.5683
52 | 0.012738 | 0.0031916 | -0.012734 | -0.0031897 | 3.4627e-06 | 1.9046e-06 | 0.019332 | 0.019332 | 0.019332 | 0.98042 | -0.37657 | 0.98013 | -0.38228 | 5.311
53 | -0.14323 | -0.036108 | 0.14328 | 0.036137 | 4.665e-05 | 2.9016e-05 | 0.2168 | 0.2168 | 0.2168 | 0.98345 | -0.31758 | 0.9838 | -0.31078 | 11.9118
54 | 0.0043236 | 0.0010836 | -0.0043235 | -0.0010836 | 1.0068e-07 | -1.7728e-08 | 0.0064902 | 0.0064902 | 0.0064902 | 0.99128 | -0.16637 | 0.99125 | -0.16686 | 1.783
55 | -0.32383 | -0.082456 | 0.32462 | 0.082956 | 0.00078649 | 0.00050045 | 0.48465 | 0.48465 | 0.48465 | 0.99521 | -0.091015 | 0.99785 | -0.040786 | 26.629
56 | 0.045938 | 0.011665 | -0.045924 | -0.011656 | 1.3535e-05 | 8.5635e-06 | 0.068739 | 0.068739 | 0.068739 | 0.99521 | -0.091015 | 0.99489 | -0.097139 | 18.8843
57 | 0.0062258 | 0.0015598 | -0.0062258 | -0.0015598 | 7.0258e-08 | 1.7502e-08 | 0.0093617 | 0.0093617 | 0.0093617 | 0.98956 | -0.19926 | 0.98955 | -0.1995 | 2.5719
58 | 0.003823 | 0.00095764 | -0.0038227 | -0.00095776 | 2.9371e-07 | -1.1647e-07 | 0.0057486 | 0.0057487 | 0.0057487 | 0.98955 | -0.1995 | 0.98946 | -0.20111 | 1.5793
59 | -0.32971 | -0.084232 | 0.33036 | 0.084646 | 0.0006516 | 0.00041468 | 0.49224 | 0.49223 | 0.49224 | 0.99785 | -0.040786 | 1 | 0 | 27.0459
60 | 0.045924 | 0.011656 | -0.045867 | -0.01162 | 5.7245e-05 | 3.6218e-05 | 0.068739 | 0.068739 | 0.068739 | 0.99489 | -0.097139 | 0.99353 | -0.12309 | 18.8844
61 | 0.0026306 | 0.00065899 | -0.0026306 | -0.00065902 | 1.8384e-08 | -2.847e-08 | 0.003956 | 0.003956 | 0.003956 | 0.98946 | -0.20111 | 0.98946 | -0.20126 | 1.0868
62 | 0.20251 | 0.051251 | -0.20247 | -0.051228 | 3.6067e-05 | 2.2752e-05 | 0.30518 | 0.30518 | 0.30518 | 0.98796 | -0.23018 | 0.98776 | -0.23389 | 16.7683
63 | -0.01297 | -0.0032505 | 0.012971 | 0.0032514 | 1.6865e-06 | 9.2962e-07 | 0.019574 | 0.019574 | 0.019574 | 0.98594 | -0.27044 | 0.98608 | -0.26772 | 5.3775
64 | -0.028962 | -0.007283 | 0.028987 | 0.0072985 | 2.5009e-05 | 1.556e-05 | 0.043713 | 0.043713 | 0.043713 | 0.98608 | -0.26772 | 0.98701 | -0.24965 | 12.0092
65 | 0.015991 | 0.0040315 | -0.015919 | -0.0039898 | 7.1783e-05 | 4.1771e-05 | 0.024139 | 0.024141 | 0.024141 | 0.98608 | -0.26772 | 0.98125 | -0.36194 | 6.6321
66 | -0.028987 | -0.0072985 | 0.029104 | 0.007371 | 0.00011652 | 7.2486e-05 | 0.043713 | 0.043713 | 0.043713 | 0.98701 | -0.24965 | 0.99135 | -0.16593 | 12.0091
67 | -0.10936 | -0.027485 | 0.11003 | 0.027912 | 0.00066962 | 0.0004277 | 0.16417 | 0.16417 | 0.16417 | 0.99135 | -0.16593 | 0.99798 | -0.038523 | 45.103
68 | -0.11003 | -0.027912 | 0.11023 | 0.028043 | 0.00020423 | 0.00013044 | 0.16417 | 0.16417 | 0.16417 | 0.99798 | -0.038523 | 1 | 0 | 45.1029
69 | -0.00071948 | -0.00018032 | 0.0007195 | 0.00017995 | 1.3547e-08 | -3.72e-07 | 0.001093 | 0.0010929 | 0.001093 | 0.9795 | -0.39481 | 0.97952 | -0.39441 | 0.30028
70 | 0.002043 | 0.00051047 | -0.0020428 | -0.00051089 | 1.4895e-07 | -4.2383e-07 | 0.003103 | 0.0031032 | 0.0031032 | 0.97952 | -0.39441 | 0.97944 | -0.39594 | 0.85253
71 | -0.0027625 | -0.00069042 | 0.0027627 | 0.00069021 | 1.6591e-07 | -2.1016e-07 | 0.0041959 | 0.0041958 | 0.0041959 | 0.97952 | -0.39441 | 0.97958 | -0.39315 | 1.1527
72 | 0.010559 | 0.0026446 | -0.010558 | -0.0026443 | 5.5374e-07 | 2.8197e-07 | 0.01603 | 0.01603 | 0.01603 | 0.98013 | -0.38228 | 0.98008 | -0.38338 | 4.4037
73 | -0.066215 | -0.016622 | 0.066226 | 0.016628 | 1.0541e-05 | 5.8782e-06 | 0.10077 | 0.10077 | 0.10077 | 0.97785 | -0.42691 | 0.97802 | -0.42357 | 5.5368
74 | 0.066215 | 0.016622 | -0.066201 | -0.016614 | 1.399e-05 | 7.8018e-06 | 0.10077 | 0.10077 | 0.10077 | 0.97785 | -0.42691 | 0.97763 | -0.43134 | 5.5369
75 | 0.064829 | 0.01627 | -0.064805 | -0.016257 | 2.3452e-05 | 1.2997e-05 | 0.098682 | 0.098683 | 0.098683 | 0.97763 | -0.43134 | 0.97724 | -0.43893 | 5.4221
76 | 0.0097431 | 0.00244 | -0.0097415 | -0.0024392 | 1.551e-06 | 7.5445e-07 | 0.014792 | 0.014792 | 0.014792 | 0.98008 | -0.38338 | 0.97991 | -0.38673 | 4.0637
77 | 0.062723 | 0.015736 | -0.06271 | -0.015728 | 1.3549e-05 | 7.4312e-06 | 0.095512 | 0.095513 | 0.095513 | 0.97724 | -0.43893 | 0.97701 | -0.44346 | 5.248
78 | 0.0014903 | 0.00037325 | -0.0014903 | -0.00037339 | 2.4911e-08 | -1.4746e-07 | 0.002263 | 0.002263 | 0.002263 | 0.97991 | -0.38673 | 0.97989 | -0.38708 | 0.62171
79 | 0.0082512 | 0.002066 | -0.0082507 | -0.0020657 | 5.0874e-07 | 2.1673e-07 | 0.012529 | 0.012529 | 0.012529 | 0.97991 | -0.38673 | 0.97984 | -0.38802 | 3.442
80 | -0.0064351 | -0.0016128 | 0.0064367 | 0.0016133 | 1.6421e-06 | 4.8442e-07 | 0.0098204 | 0.0098202 | 0.0098204 | 0.97506 | -0.4819 | 0.97533 | -0.47654 | 2.6979
81 | -0.0082039 | -0.0020562 | 0.0082058 | 0.002057 | 1.8975e-06 | 8.1118e-07 | 0.012516 | 0.012516 | 0.012516 | 0.97533 | -0.47654 | 0.97558 | -0.47169 | 3.4386
82 | -0.0082058 | -0.002057 | 0.0082062 | 0.0020571 | 3.473e-07 | 1.4845e-07 | 0.012516 | 0.012516 | 0.012516 | 0.97558 | -0.47169 | 0.97562 | -0.4708 | 3.4385
83 | 0.01428 | 0.0035746 | -0.014278 | -0.0035766 | 1.8161e-06 | -2.0247e-06 | 0.021778 | 0.02178 | 0.02178 | 0.97562 | -0.4708 | 0.97549 | -0.47347 | 1.1967
84 | -0.022486 | -0.0056317 | 0.022487 | 0.0056317 | 2.6405e-07 | -1.7915e-08 | 0.034295 | 0.034295 | 0.034295 | 0.97562 | -0.4708 | 0.97564 | -0.47055 | 1.8843
85 | 0.013477 | 0.0033765 | -0.013477 | -0.003377 | 4.3353e-07 | -5.7612e-07 | 0.020559 | 0.020559 | 0.020559 | 0.97546 | -0.47406 | 0.97542 | -0.47474 | 1.1296
86 | -0.013477 | -0.0033765 | 0.013478 | 0.003376 | 3.7955e-07 | -5.0446e-07 | 0.020559 | 0.020558 | 0.020559 | 0.97546 | -0.47406 | 0.97549 | -0.47347 | 1.1296
87 | 0.0065134 | 0.0016325 | -0.0065121 | -0.0016321 | 1.2718e-06 | 3.8525e-07 | 0.0099362 | 0.0099364 | 0.0099364 | 0.97542 | -0.47474 | 0.97522 | -0.47884 | 2.7298
88 | 0.0069636 | 0.0017446 | -0.0069633 | -0.0017453 | 3.7972e-07 | -7.6496e-07 | 0.010623 | 0.010623 | 0.010623 | 0.97542 | -0.47474 | 0.97537 | -0.47588 | 0.97282
89 | -0.029875 | -0.0074833 | 0.029883 | 0.0074853 | 8.452e-06 | 2.0186e-06 | 0.045563 | 0.045561 | 0.045563 | 0.97564 | -0.47055 | 0.97594 | -0.46461 | 2.5034
90 | 0.0069633 | 0.0017453 | -0.0069615 | -0.0017447 | 1.7326e-06 | 5.9803e-07 | 0.010623 | 0.010623 | 0.010623 | 0.97537 | -0.47588 | 0.9751 | -0.48111 | 2.9185
91 | 0.014825 | 0.0037164 | -0.014822 | -0.003715 | 2.4441e-06 | 1.3997e-06 | 0.022423 | 0.022423 | 0.022423 | 0.9838 | -0.31078 | 0.98362 | -0.31424 | 6.1602
92 | -0.1581 | -0.039853 | 0.15819 | 0.039904 | 8.1495e-05 | 5.095e-05 | 0.23922 | 0.23922 | 0.23922 | 0.9838 | -0.31078 | 0.98435 | -0.30001 | 13.1439
93 | 0.01171 | 0.0029349 | -0.011709 | -0.0029346 | 5.8536e-07 | 3.115e-07 | 0.017715 | 0.017715 | 0.017715 | 0.98362 | -0.31424 | 0.98357 | -0.31529 | 4.8667
94 | -0.16867 | -0.042533 | 0.16869 | 0.042543 | 1.5954e-05 | 1.0002e-05 | 0.25507 | 0.25507 | 0.25507 | 0.98435 | -0.30001 | 0.98445 | -0.29803 | 14.0149
95 | 0.0058518 | 0.0014666 | -0.005851 | -0.0014664 | 8.3087e-07 | 1.7303e-07 | 0.0088531 | 0.0088532 | 0.0088532 | 0.98357 | -0.31529 | 0.98341 | -0.31827 | 2.4322
96 | -0.16869 | -0.042543 | 0.1688 | 0.042615 | 0.00011598 | 7.2714e-05 | 0.25507 | 0.25507 | 0.25507 | 0.98445 | -0.29803 | 0.98519 | -0.28368 | 14.0149
97 | 0.013862 | 0.0034765 | -0.013854 | -0.0034722 | 7.6691e-06 | 4.3145e-06 | 0.020937 | 0.020938 | 0.020938 | 0.98519 | -0.28368 | 0.9846 | -0.2953 | 5.7521
98 | -0.18267 | -0.046092 | 0.18277 | 0.046154 | 9.9115e-05 | 6.2328e-05 | 0.27601 | 0.27601 | 0.27601 | 0.98519 | -0.28368 | 0.98578 | -0.27236 | 15.1652
99 | -0.19096 | -0.048221 | 0.1911 | 0.048309 | 0.00013934 | 8.7751e-05 | 0.28833 | 0.28833 | 0.28833 | 0.98597 | -0.26861 | 0.98676 | -0.2534 | 15.8422
100 | 0.18958 | 0.047875 | -0.18955 | -0.047854 | 3.4024e-05 | 2.1422e-05 | 0.28624 | 0.28624 | 0.28624 | 0.98597 | -0.26861 | 0.98578 | -0.27236 | 15.7276
101 | -0.19247 | -0.048653 | 0.19248 | 0.048654 | 1.9709e-06 | 1.2415e-06 | 0.2904 | 0.2904 | 0.2904 | 0.98676 | -0.2534 | 0.98677 | -0.25318 | 15.9559
102 | -0.19623 | -0.049596 | 0.19641 | 0.04971 | 0.00018172 | 0.00011453 | 0.29606 | 0.29606 | 0.29606 | 0.98677 | -0.25318 | 0.98776 | -0.23389 | 16.2671
103 | 0.007043 | 0.0017652 | -0.0070421 | -0.0017649 | 8.5551e-07 | 2.9146e-07 | 0.010644 | 0.010644 | 0.010644 | 0.9846 | -0.2953 | 0.98447 | -0.29785 | 2.9242
104 | 0.045691 | 0.011576 | -0.045666 | -0.01156 | 2.5036e-05 | 1.5839e-05 | 0.068477 | 0.068477 | 0.068477 | 0.99353 | -0.12309 | 0.99294 | -0.1345 | 18.8123
105 | 0.042674 | 0.01081 | -0.042579 | -0.010751 | 9.4166e-05 | 5.9475e-05 | 0.063992 | 0.063992 | 0.063992 | 0.99294 | -0.1345 | 0.99054 | -0.18055 | 17.5802
106 | 0.040148 | 0.010142 | -0.040102 | -0.010112 | 4.6438e-05 | 2.9283e-05 | 0.06034 | 0.06034 | 0.06034 | 0.99054 | -0.18055 | 0.98929 | -0.20471 | 16.5769
107 | 0.0053048 | 0.0013295 | -0.0053045 | -0.0013294 | 3.4285e-07 | 3.5052e-08 | 0.0079791 | 0.0079791 | 0.0079791 | 0.98929 | -0.20471 | 0.98922 | -0.20607 | 2.1921
108 | 0.034797 | 0.0087828 | -0.034693 | -0.0087174 | 0.00010424 | 6.5414e-05 | 0.052361 | 0.052361 | 0.052361 | 0.98929 | -0.20471 | 0.98606 | -0.26745 | 14.385
109 | 0.0026556 | 0.00066511 | -0.0026555 | -0.00066525 | 9.1892e-08 | -1.3583e-07 | 0.0040073 | 0.0040074 | 0.0040074 | 0.98606 | -0.26745 | 0.98602 | -0.26818 | 1.1009
110 | 0.032037 | 0.0080523 | -0.031976 | -0.0080138 | 6.1533e-05 | 3.8488e-05 | 0.048354 | 0.048354 | 0.048354 | 0.98606 | -0.26745 | 0.98399 | -0.30777 | 13.2842
111 | -0.0026554 | -0.0006655 | 0.0026555 | 0.00066525 | 1.6825e-07 | -2.4864e-07 | 0.0040075 | 0.0040074 | 0.0040075 | 0.98595 | -0.26951 | 0.98602 | -0.26818 | 1.101
112 | -0.0034646 | -0.00086826 | 0.0034648 | 0.00086818 | 1.4266e-07 | -8.1998e-08 | 0.00526 | 0.0052599 | 0.00526 | 0.98012 | -0.38259 | 0.98016 | -0.38173 | 1.4451
113 | 0.0029543 | 0.00074036 | -0.0029543 | -0.00074041 | 4.8685e-08 | -5.0173e-08 | 0.0044852 | 0.0044853 | 0.0044853 | 0.98012 | -0.38259 | 0.9801 | -0.38294 | 1.2322
114 | -0.0060418 | -0.001514 | 0.0060418 | 0.001514 | 1.3369e-09 | 3.2195e-10 | 0.0091722 | 0.0091722 | 0.0091722 | 0.98016 | -0.38173 | 0.98016 | -0.38172 | 2.5198
115 | -0.0070685 | -0.0017713 | 0.0070695 | 0.0017717 | 1.0112e-06 | 3.5196e-07 | 0.010731 | 0.010731 | 0.010731 | 0.98016 | -0.38172 | 0.98032 | -0.37872 | 2.948
116 | -0.010265 | -0.0025725 | 0.010265 | 0.0025729 | 8.3629e-07 | 4.1939e-07 | 0.015581 | 0.015581 | 0.015581 | 0.98032 | -0.37872 | 0.9804 | -0.37701 | 4.2804
117 | -0.0052757 | -0.00132 | 0.0052758 | 0.00132 | 8.1237e-08 | 9.5188e-09 | 0.0080132 | 0.0080132 | 0.0080132 | 0.97958 | -0.39315 | 0.9796 | -0.39282 | 2.2014
118 | -0.0065011 | -0.0016271 | 0.0065018 | 0.0016274 | 7.2537e-07 | 2.1445e-07 | 0.0098745 | 0.0098744 | 0.0098745 | 0.9796 | -0.39282 | 0.97972 | -0.39048 | 2.7128
119 | -0.0070656 | -0.0017686 | 0.0070664 | 0.0017689 | 8.2604e-07 | 2.8774e-07 | 0.010731 | 0.010731 | 0.010731 | 0.97972 | -0.39048 | 0.97984 | -0.38802 | 2.948
120 | 0.0020428 | 0.00051089 | -0.0020428 | -0.0005111 | 7.1852e-08 | -2.0441e-07 | 0.0031032 | 0.0031033 | 0.0031033 | 0.97944 | -0.39594 | 0.9794 | -0.39668 | 0.85255
121 | 0.0014792 | 0.00036985 | -0.0014791 | -0.00037012 | 4.4175e-08 | -2.653e-07 | 0.002247 | 0.0022471 | 0.0022471 | 0.9794 | -0.39668 | 0.97937 | -0.39731 | 0.61735
122 | 0.0014791 | 0.00037012 | -0.0014791 | -0.00037051 | 6.6177e-08 | -3.9735e-07 | 0.0022471 | 0.0022473 | 0.0022473 | 0.97937 | -0.39731 | 0.97932 | -0.39825 | 0.61739
123 | 0.0036025 | 0.00090252 | -0.003602 | -0.00090274 | 4.7232e-07 | -2.1931e-07 | 0.0054926 | 0.0054928 | 0.0054928 | 0.97594 | -0.46461 | 0.9758 | -0.46737 | 1.509
124 | -0.033486 | -0.0083878 | 0.033494 | 0.0083906 | 8.6972e-06 | 2.7858e-06 | 0.051054 | 0.051053 | 0.051054 | 0.97594 | -0.46461 | 0.97621 | -0.45916 | 2.8052
125 | 0.014348 | 0.0035998 | -0.014341 | -0.0035963 | 6.249e-06 | 3.564e-06 | 0.021871 | 0.021871 | 0.021871 | 0.97621 | -0.45916 | 0.97575 | -0.4683 | 6.0086
126 | -0.047842 | -0.01199 | 0.047851 | 0.011995 | 8.7182e-06 | 4.2129e-06 | 0.072924 | 0.072924 | 0.072924 | 0.97621 | -0.45916 | 0.97641 | -0.45534 | 4.0068
127 | 0.0018624 | 0.00046541 | -0.0018622 | -0.00046621 | 2.2909e-07 | -7.9944e-07 | 0.0028397 | 0.00284 | 0.00284 | 0.97575 | -0.4683 | 0.97562 | -0.47089 | 0.78023
128 | 0.012479 | 0.0031308 | -0.012468 | -0.0031248 | 1.1097e-05 | 6.0827e-06 | 0.019032 | 0.019032 | 0.019032 | 0.97575 | -0.4683 | 0.9748 | -0.48697 | 5.2286
129 | -0.054437 | -0.013645 | 0.054447 | 0.01365 | 9.7216e-06 | 5.0438e-06 | 0.082961 | 0.082961 | 0.082961 | 0.97641 | -0.45534 | 0.9766 | -0.45159 | 4.5583
130 | 0.0018622 | 0.00046621 | -0.0018621 | -0.00046667 | 1.3303e-07 | -4.6398e-07 | 0.00284 | 0.0028402 | 0.0028402 | 0.97562 | -0.47089 | 0.97554 | -0.47239 | 0.78028
131 | -0.060558 | -0.015182 | 0.060581 | 0.015195 | 2.3469e-05 | 1.272e-05 | 0.092272 | 0.092271 | 0.092272 | 0.9766 | -0.45159 | 0.97701 | -0.44346 | 5.0699
132 | 0.00065338 | 0.00016365 | -0.00065337 | -0.00016375 | 3.0586e-09 | -1.0241e-07 | 0.00099215 | 0.00099219 | 0.00099219 | 0.97989 | -0.38708 | 0.97988 | -0.38718 | 0.27258
133 | 0.0010753 | 0.00026933 | -0.0010753 | -0.0002695 | 1.4503e-08 | -1.73e-07 | 0.0016339 | 0.0016339 | 0.0016339 | 0.97932 | -0.39825 | 0.97931 | -0.39853 | 0.44888
134 | 0.001191 | 0.00029822 | -0.001191 | -0.00029848 | 2.6365e-08 | -2.6462e-07 | 0.001791 | 0.0017911 | 0.0017911 | 0.98946 | -0.20126 | 0.98943 | -0.20173 | 0.49206

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44224 | 0.11269

## res_load
| p_mw | q_mvar
0 | 0.0015516 | 0.00038887
1 | 0.001625 | 0.00040726
2 | 0.00050796 | 0.00012731
3 | 0.0086476 | 0.0021673
4 | 0.0042198 | 0.0010576
5 | 0.0073189 | 0.0018343
6 | 0.00079292 | 0.00019872
7 | 0.0024281 | 0.00060855
8 | 0.0033301 | 0.00083461
9 | 0.0013584 | 0.00034045
10 | 0.0013589 | 0.00034056
11 | 0.0027321 | 0.00068473
12 | 0.0020605 | 0.00051642
13 | 0.0023157 | 0.00058038
14 | 0.0056435 | 0.0014144
15 | 0.0020049 | 0.00050247
16 | 0.0019798 | 0.00049617
17 | 0.0026052 | 0.00065293
18 | 0.0059086 | 0.0014808
19 | 0.0020438 | 0.00051223
20 | 0.0051315 | 0.0012861
21 | 0.0020556 | 0.00051519
22 | 0.0019568 | 0.00049041
23 | 0.0020534 | 0.00051462
24 | 0.0020316 | 0.00050917
25 | 0.00083768 | 0.00020994
26 | 0.0020239 | 0.00050724
27 | 0.0024037 | 0.00060243
28 | 0.00079666 | 0.00019966
29 | 0.0022679 | 0.0005684
30 | 0.0012184 | 0.00030536
31 | 0.00046676 | 0.00011698
32 | 0.0011271 | 0.00028249
33 | 0.0032422 | 0.00081258
34 | 0.014169 | 0.003551
35 | 0.0043235 | 0.0010836
36 | 0.0025269 | 0.0006333
37 | 0.0024027 | 0.00060219
38 | 0.0050888 | 0.0012754
39 | 0.0011921 | 0.00029877
40 | 0.0076634 | 0.0019206
41 | 0.01297 | 0.0032505
42 | 0.015919 | 0.0039898
43 | 0.080254 | 0.020114
44 | 0.00071948 | 0.00018032
45 | 0.0021752 | 0.00054516
46 | 0.00037695 | 9.4472e-05
47 | 0.0013725 | 0.00034397
48 | 0.00081524 | 0.00020432
49 | 0.002082 | 0.00052181
50 | 0.0064351 | 0.0016128
51 | 0.0017672 | 0.0004429
52 | 0.00080051 | 0.00020063
53 | 0.007388 | 0.0018516
54 | 0.0065121 | 0.0016321
55 | 0.0031125 | 0.00078006
56 | 0.010487 | 0.0026283
57 | 0.0058575 | 0.001468
58 | 0.005851 | 0.0014664
59 | 0.0013821 | 0.00034638
60 | 0.0013728 | 0.00034406
61 | 0.0067808 | 0.0016994
62 | 0.0037555 | 0.00094122
63 | 0.0060554 | 0.0015176
64 | 0.0068111 | 0.001707
65 | 0.0070421 | 0.0017649
66 | 0.00017525 | 4.3923e-05
67 | 0.0029928 | 0.00075007
68 | 0.0024313 | 0.00060933
69 | 0.0053045 | 0.0013294
70 | 0.031976 | 0.0080138
71 | 0.0026554 | 0.0006655
72 | 0.00051032 | 0.0001279
73 | 0.002577 | 0.00064586
74 | 0.0029543 | 0.00074041
75 | 0.0010267 | 0.0002573
76 | 0.0031952 | 0.00080078
77 | 0.003839 | 0.00096214
78 | 0.002513 | 0.00062983
79 | 0.0012253 | 0.0003071
80 | 0.00056375 | 0.00014129
81 | 0.0011843 | 0.00029681
82 | 0.00056358 | 0.00014125
83 | 0.003602 | 0.00090274
84 | 0.0065866 | 0.0016508
85 | 0.012468 | 0.0031248
86 | 0.0061108 | 0.0015315
87 | 0.0021285 | 0.00053345
88 | 0.0018621 | 0.00046667
89 | 0.0008369 | 0.00020975
90 | 0.00065337 | 0.00016375
91 | 0.00040373 | 0.00010118
92 | 0.0010753 | 0.0002695
93 | 0.0069615 | 0.0017447
94 | 0.0014396 | 0.0003608
95 | 0.001191 | 0.00029848

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1