## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2573-2_1_3_node_53 | 0.4 | n |  | TRUE
1 | bus_LV_2573-2_1_3_node_54 | 0.4 | n |  | TRUE
2 | bus_LV_2573-2_1_3_node_55 | 0.4 | n |  | TRUE
3 | bus_LV_2573-2_1_3_node_56 | 0.4 | n |  | TRUE
4 | bus_LV_2573-2_1_3_node_57 | 0.4 | n |  | TRUE
5 | bus_LV_2573-2_1_3_node_133 | 0.4 | n |  | TRUE
6 | bus_LV_2573-2_1_3_node_158 | 0.4 | n |  | TRUE
7 | bus_LV_2573-2_1_3_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_2573-2_1_3_node_63 | 0.4 | n |  | TRUE
9 | bus_LV_2573-2_1_3_node_64 | 0.4 | n |  | TRUE
10 | bus_LV_2573-2_1_3_node_65 | 0.4 | n |  | TRUE
11 | bus_LV_2573-2_1_3_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_2573-2_1_3_node_174 | 0.4 | n |  | TRUE
13 | bus_LV_2573-2_1_3_node_74 | 0.4 | n |  | TRUE
14 | bus_LV_2573-2_1_3_node_76 | 0.4 | n |  | TRUE
15 | bus_LV_2573-2_1_3_node_198 | 0.4 | n |  | TRUE
16 | bus_LV_2573-2_1_3_node_94 | 0.4 | n |  | TRUE
17 | bus_LV_2573-2_1_3_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_2573-2_1_3_node_96 | 0.4 | n |  | TRUE
19 | bus_LV_2573-2_1_3_node_97 | 0.4 | n |  | TRUE
20 | bus_LV_2573-2_1_3_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_2573-2_1_3_node_196 | 0.4 | n |  | TRUE
22 | bus_LV_2573-2_1_3_node_202 | 0.4 | n |  | TRUE
23 | bus_LV_2573-2_1_3_node_119 | 0.4 | n |  | TRUE
24 | bus_LV_2573-2_1_3_node_120 | 0.4 | n |  | TRUE
25 | bus_LV_2573-2_1_3_node_121 | 0.4 | n |  | TRUE
26 | bus_LV_2573-2_1_3_node_122 | 0.4 | n |  | TRUE
27 | bus_LV_2573-2_1_3_node_123 | 0.4 | n |  | TRUE
28 | bus_LV_2573-2_1_3_node_249 | 0.4 | n |  | TRUE
29 | bus_LV_2573-2_1_3_node_235 | 0.4 | n |  | TRUE
30 | bus_LV_2573-2_1_3_node_130 | 0.4 | n |  | TRUE
31 | bus_LV_2573-2_1_3_node_131 | 0.4 | n |  | TRUE
32 | bus_LV_2573-2_1_3_node_132 | 0.4 | n |  | TRUE
33 | bus_LV_2573-2_1_3_node_134 | 0.4 | n |  | TRUE
34 | bus_LV_2573-2_1_3_node_135 | 0.4 | n |  | TRUE
35 | bus_LV_2573-2_1_3_node_175 | 0.4 | n |  | TRUE
36 | bus_LV_2573-2_1_3_node_172 | 0.4 | n |  | TRUE
37 | bus_LV_2573-2_1_3_node_145 | 0.4 | n |  | TRUE
38 | bus_LV_2573-2_1_3_node_140 | 0.4 | n |  | TRUE
39 | bus_LV_2573-2_1_3_node_141 | 0.4 | n |  | TRUE
40 | bus_LV_2573-2_1_3_node_143 | 0.4 | n |  | TRUE
41 | bus_LV_2573-2_1_3_node_144 | 0.4 | n |  | TRUE
42 | bus_LV_2573-2_1_3_node_240 | 0.4 | n |  | TRUE
43 | bus_LV_2573-2_1_3_node_234 | 0.4 | n |  | TRUE
44 | bus_LV_2573-2_1_3_node_146 | 0.4 | n |  | TRUE
45 | bus_LV_2573-2_1_3_node_147 | 0.4 | n |  | TRUE
46 | bus_LV_2573-2_1_3_node_148 | 0.4 | n |  | TRUE
47 | bus_LV_2573-2_1_3_node_149 | 0.4 | n |  | TRUE
48 | bus_LV_2573-2_1_3_node_150 | 0.4 | n |  | TRUE
49 | bus_LV_2573-2_1_3_node_151 | 0.4 | n |  | TRUE
50 | bus_LV_2573-2_1_3_node_226 | 0.4 | n |  | TRUE
51 | bus_LV_2573-2_1_3_node_161 | 0.4 | n |  | TRUE
52 | bus_LV_2573-2_1_3_node_162 | 0.4 | n |  | TRUE
53 | bus_LV_2573-2_1_3_node_163 | 0.4 | n |  | TRUE
54 | bus_LV_2573-2_1_3_node_164 | 0.4 | n |  | TRUE
55 | bus_LV_2573-2_1_3_node_165 | 0.4 | n |  | TRUE
56 | bus_LV_2573-2_1_3_node_236 | 0.4 | n |  | TRUE
57 | bus_LV_2573-2_1_3_node_212 | 0.4 | n |  | TRUE
58 | bus_LV_2573-2_1_3_node_178 | 0.4 | n |  | TRUE
59 | bus_LV_2573-2_1_3_node_173 | 0.4 | n |  | TRUE
60 | bus_LV_2573-2_1_3_node_220 | 0.4 | n |  | TRUE
61 | bus_LV_2573-2_1_3_node_231 | 0.4 | n |  | TRUE
62 | bus_LV_2573-2_1_3_node_179 | 0.4 | n |  | TRUE
63 | bus_LV_2573-2_1_3_node_241 | 0.4 | n |  | TRUE
64 | bus_LV_2573-2_1_3_node_197 | 0.4 | n |  | TRUE
65 | bus_LV_2573-2_1_3_node_228 | 0.4 | n |  | TRUE
66 | bus_LV_2573-2_1_3_node_208 | 0.4 | n |  | TRUE
67 | bus_LV_2573-2_1_3_node_209 | 0.4 | n |  | TRUE
68 | bus_LV_2573-2_1_3_node_210 | 0.4 | n |  | TRUE
69 | bus_LV_2573-2_1_3_node_211 | 0.4 | n |  | TRUE
70 | bus_LV_2573-2_1_3_node_227 | 0.4 | n |  | TRUE
71 | bus_LV_2573-2_1_3_node_232 | 0.4 | n |  | TRUE
72 | bus_LV_2573-2_1_3_node_233 | 0.4 | n |  | TRUE
73 | bus_LV_2573-2_1_3_node_242 | 0.4 | n |  | TRUE
74 | bus_LV_2573-2_1_3_node_247 | 0.4 | n |  | TRUE
75 | bus_LV_2573-2_1_3_node_248 | 0.4 | n |  | TRUE
76 | bus_MV_398_1_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2573-2_1_3_load_53 | 0 | 0.0013697 | 0.00034328 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2573-2_1_3_load_54 | 1 | 0.001265 | 0.00031703 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2573-2_1_3_load_55 | 2 | 0.0013353 | 0.00033466 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2573-2_1_3_load_56 | 3 | 0.0013525 | 0.00033897 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2573-2_1_3_load_57 | 4 | 0.0012969 | 0.00032503 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2573-2_1_3_load_158 | 6 | 0.0011769 | 0.00029496 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2573-2_1_3_load_62 | 7 | 0.0016467 | 0.0004127 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2573-2_1_3_load_63 | 8 | 0.0018128 | 0.00045432 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2573-2_1_3_load_65 | 10 | 0.00090266 | 0.00022623 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2573-2_1_3_load_66 | 11 | 0.0032498 | 0.00081449 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2573-2_1_3_load_174 | 12 | 0.0010461 | 0.00026217 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2573-2_1_3_load_74 | 13 | 0.0027565 | 0.00069085 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2573-2_1_3_load_76 | 14 | 0.0013137 | 0.00032924 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2573-2_1_3_load_198 | 15 | 0.0030665 | 0.00076854 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2573-2_1_3_load_94 | 16 | 0.002261 | 0.00056667 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2573-2_1_3_load_95 | 17 | 0.00187 | 0.00046867 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2573-2_1_3_load_96 | 18 | 0.0011415 | 0.00028608 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2573-2_1_3_load_97 | 19 | 0.0017486 | 0.00043825 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2573-2_1_3_load_98 | 20 | 0.0017762 | 0.00044516 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2573-2_1_3_load_196 | 21 | 0.0013364 | 0.00033493 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2573-2_1_3_load_202 | 22 | 0.00082485 | 0.00020673 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2573-2_1_3_load_119 | 23 | 0.0014692 | 0.00036821 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2573-2_1_3_load_120 | 24 | 0.0018269 | 0.00045786 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2573-2_1_3_load_121 | 25 | 0.0034711 | 0.00086995 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2573-2_1_3_load_122 | 26 | 0.001098 | 0.00027518 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2573-2_1_3_load_123 | 27 | 0.0035931 | 0.00090052 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2573-2_1_3_load_249 | 28 | 0.0015271 | 0.00038273 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2573-2_1_3_load_235 | 29 | 0.003809 | 0.00095462 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2573-2_1_3_load_130 | 30 | 0.0011041 | 0.0002767 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2573-2_1_3_load_131 | 31 | 0.0035347 | 0.00088589 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2573-2_1_3_load_134 | 33 | 0.0038627 | 0.00096808 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2573-2_1_3_load_135 | 34 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2573-2_1_3_load_175 | 35 | 0.0014371 | 0.00036017 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2573-2_1_3_load_172 | 36 | 0.00097186 | 0.00024357 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2573-2_1_3_load_145 | 37 | 0.0041507 | 0.0010403 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2573-2_1_3_load_140 | 38 | 0.005191 | 0.001301 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2573-2_1_3_load_143 | 40 | 0.0040788 | 0.0010222 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2573-2_1_3_load_144 | 41 | 0.0028167 | 0.00070593 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2573-2_1_3_load_240 | 42 | 0.0015953 | 0.00039981 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2573-2_1_3_load_146 | 44 | 0.0040852 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2573-2_1_3_load_147 | 45 | 0.0014005 | 0.00035101 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2573-2_1_3_load_148 | 46 | 0.0013048 | 0.00032701 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2573-2_1_3_load_149 | 47 | 0.0020829 | 0.00052203 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2573-2_1_3_load_150 | 48 | 0.0012517 | 0.0003137 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2573-2_1_3_load_151 | 49 | 0.0018358 | 0.00046009 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2573-2_1_3_load_226 | 50 | 0.001303 | 0.00032657 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2573-2_1_3_load_161 | 51 | 0.0036568 | 0.00091647 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2573-2_1_3_load_162 | 52 | 0.0025127 | 0.00062975 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2573-2_1_3_load_163 | 53 | 0.0015241 | 0.00038197 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2573-2_1_3_load_165 | 55 | 0.0011618 | 0.00029118 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2573-2_1_3_load_236 | 56 | 0.0024827 | 0.00062222 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2573-2_1_3_load_212 | 57 | 0.0021849 | 0.0005476 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2573-2_1_3_load_178 | 58 | 0.0031129 | 0.00078017 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2573-2_1_3_load_173 | 59 | 0.0051292 | 0.0012855 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2573-2_1_3_load_220 | 60 | 0.00088187 | 0.00022102 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2573-2_1_3_load_231 | 61 | 0.0091363 | 0.0022898 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2573-2_1_3_load_241 | 63 | 0.0010036 | 0.00025154 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2573-2_1_3_load_228 | 65 | 0.0018257 | 0.00045757 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2573-2_1_3_load_208 | 66 | 0.0009192 | 0.00023037 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2573-2_1_3_load_209 | 67 | 0.010692 | 0.0026796 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2573-2_1_3_load_210 | 68 | 0.0011536 | 0.00028911 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2573-2_1_3_load_211 | 69 | 0.011676 | 0.0029263 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2573-2_1_3_load_227 | 70 | 0.0017766 | 0.00044525 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2573-2_1_3_load_232 | 71 | 0.0026024 | 0.00065223 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2573-2_1_3_load_233 | 72 | 0.0081348 | 0.0020388 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2573-2_1_3_load_242 | 73 | 0.0018729 | 0.0004694 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2573-2_1_3_load_247 | 74 | 0.0022421 | 0.00056192 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2573-2_1_3_load_248 | 75 | 0.001728 | 0.00043308 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2573-2_1_3_line_0 |  | 0 | 1 | 0.018156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2573-2_1_3_line_1 |  | 0 | 2 | 0.019203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2573-2_1_3_line_2 |  | 1 | 3 | 0.0052846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2573-2_1_3_line_3 |  | 2 | 4 | 0.02496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2573-2_1_3_line_4 |  | 3 | 5 | 0.015771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2573-2_1_3_line_5 |  | 4 | 6 | 0.0177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2573-2_1_3_line_6 |  | 5 | 35 | 0.026927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2573-2_1_3_line_7 |  | 5 | 36 | 0.028276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2573-2_1_3_line_8 |  | 5 | 31 | 0.019181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2573-2_1_3_line_9 |  | 7 | 8 | 0.020315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2573-2_1_3_line_10 |  | 7 | 9 | 0.0054758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2573-2_1_3_line_11 |  | 8 | 10 | 0.0017083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2573-2_1_3_line_12 |  | 9 | 11 | 0.013389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2573-2_1_3_line_13 |  | 10 | 12 | 0.027746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2573-2_1_3_line_14 |  | 12 | 59 | 0.0015925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2573-2_1_3_line_15 |  | 13 | 14 | 0.005769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2573-2_1_3_line_16 |  | 14 | 15 | 0.0079363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2573-2_1_3_line_17 |  | 15 | 65 | 0.00041835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2573-2_1_3_line_18 |  | 16 | 17 | 0.019624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2573-2_1_3_line_19 |  | 16 | 18 | 0.0045163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2573-2_1_3_line_20 |  | 17 | 19 | 0.0079152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2573-2_1_3_line_21 |  | 18 | 20 | 0.0016226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2573-2_1_3_line_22 |  | 19 | 21 | 0.00045841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2573-2_1_3_line_23 |  | 20 | 22 | 0.00017075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2573-2_1_3_line_24 |  | 21 | 64 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2573-2_1_3_line_25 |  | 22 | 34 | 0.0241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2573-2_1_3_line_26 |  | 23 | 24 | 0.00050439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2573-2_1_3_line_27 |  | 23 | 25 | 0.019328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2573-2_1_3_line_28 |  | 24 | 26 | 0.0073261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2573-2_1_3_line_29 |  | 25 | 27 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2573-2_1_3_line_30 |  | 26 | 28 | 0.016469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2573-2_1_3_line_31 |  | 27 | 29 | 0.03341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2573-2_1_3_line_32 |  | 28 | 75 | 0.0056625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2573-2_1_3_line_33 |  | 29 | 64 | 0.010333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2573-2_1_3_line_34 |  | 30 | 31 | 0.031581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2573-2_1_3_line_35 |  | 30 | 32 | 0.041914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2573-2_1_3_line_36 |  | 32 | 33 | 0.020928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2573-2_1_3_line_37 |  | 32 | 34 | 0.010244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2573-2_1_3_line_38 |  | 33 | 37 | 0.0019552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2573-2_1_3_line_39 |  | 35 | 60 | 0.025529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2573-2_1_3_line_40 |  | 35 | 61 | 0.07152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2573-2_1_3_line_41 |  | 36 | 59 | 0.025505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2573-2_1_3_line_42 |  | 37 | 44 | 0.042742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2573-2_1_3_line_43 |  | 38 | 39 | 0.0054442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2573-2_1_3_line_44 |  | 39 | 40 | 0.04138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2573-2_1_3_line_45 |  | 39 | 41 | 0.012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2573-2_1_3_line_46 |  | 40 | 42 | 0.00231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2573-2_1_3_line_47 |  | 41 | 43 | 0.011838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2573-2_1_3_line_48 |  | 42 | 48 | 0.0034071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2573-2_1_3_line_49 |  | 43 | 69 | 0.00065816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2573-2_1_3_line_50 |  | 43 | 71 | 0.014581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2573-2_1_3_line_51 |  | 45 | 46 | 0.00069727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2573-2_1_3_line_52 |  | 45 | 47 | 0.0032939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2573-2_1_3_line_53 |  | 46 | 48 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2573-2_1_3_line_54 |  | 47 | 49 | 0.001332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2573-2_1_3_line_55 |  | 49 | 50 | 0.0018753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2573-2_1_3_line_56 |  | 50 | 70 | 0.0020745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2573-2_1_3_line_57 |  | 51 | 52 | 0.0049542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2573-2_1_3_line_58 |  | 51 | 53 | 0.020515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2573-2_1_3_line_59 |  | 52 | 54 | 0.010502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2573-2_1_3_line_60 |  | 53 | 55 | 0.004284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2573-2_1_3_line_61 |  | 54 | 56 | 0.020811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2573-2_1_3_line_62 |  | 54 | 57 | 0.044395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2573-2_1_3_line_63 |  | 55 | 58 | 0.014274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2573-2_1_3_line_64 |  | 56 | 64 | 0.013814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2573-2_1_3_line_65 |  | 57 | 68 | 0.026297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2573-2_1_3_line_66 |  | 58 | 62 | 0.0033874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2573-2_1_3_line_67 |  | 62 | 63 | 0.046479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2573-2_1_3_line_68 |  | 63 | 73 | 0.025242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2573-2_1_3_line_69 |  | 65 | 70 | 0.026027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2573-2_1_3_line_70 |  | 66 | 67 | 0.0011932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2573-2_1_3_line_71 |  | 66 | 68 | 0.0021653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2573-2_1_3_line_72 |  | 67 | 69 | 0.035634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2573-2_1_3_line_73 |  | 71 | 72 | 0.01825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2573-2_1_3_line_74 |  | 74 | 75 | 0.032406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2573-2_1_3_trafo_235 | 0.63 MVA 20/0.4 kV | 76 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2638271.2906 | 1243877.9526 | 2638281.5178 | 1243892.9537
1 | 2638271.2906 | 1243877.9526 | 2638270.5021 | 1243876.7961 | 2638260.1909 | 1243862.2825
2 | 2638284.4947 | 1243897.3201 | 2638281.5178 | 1243892.9537
3 | 2638245.7348 | 1243841.9347 | 2638260.1909 | 1243862.2825
4 | 2638294.7013 | 1243909.3066 | 2638286.5973 | 1243900.4041 | 2638284.4947 | 1243897.3201
5 | 2638235.4834 | 1243827.5053 | 2638245.7348 | 1243841.9347
6 | 2638294.7013 | 1243909.3066 | 2638296.802 | 1243906.9964 | 2638300.3037 | 1243904.206 | 2638302.8979 | 1243902.6996 | 2638305.8988 | 1243901.3958 | 2638308.1987 | 1243900.9993 | 2638310.2013 | 1243901.0011 | 2638311.9979 | 1243901.3018 | 2638314.4008 | 1243902.4958 | 2638317.517 | 1243905.3322
7 | 2638294.7013 | 1243909.3066 | 2638297.0983 | 1243912.6019 | 2638313.134 | 1243930.7274
8 | 2638294.7013 | 1243909.3066 | 2638293.4984 | 1243910.6997 | 2638291.5999 | 1243913.3003 | 2638290.2009 | 1243915.804 | 2638289.6981 | 1243917.6019 | 2638289.2975 | 1243925.8047 | 2638289.3441 | 1243926.9768
9 | 2638365.5988 | 1243986.7033 | 2638365.5988 | 1243986.7033 | 2638359.8029 | 1243981.9961 | 2638354.7978 | 1243977.7054 | 2638350.4449 | 1243973.2127
10 | 2638370.3037 | 1243989.5022 | 2638368.3996 | 1243988.3002 | 2638365.5988 | 1243986.7033
11 | 2638349.2562 | 1243971.9859 | 2638350.4449 | 1243973.2127
12 | 2638370.3037 | 1243989.5022 | 2638370.3998 | 1243991.0038 | 2638371.1022 | 1243996.901 | 2638372.3695 | 1244002.71
13 | 2638349.2562 | 1243971.9859 | 2638348.5972 | 1243971.3057 | 2638333.4038 | 1243954.3966 | 2638330.7733 | 1243951.2955
14 | 2638329.7432 | 1243950.0811 | 2638330.7733 | 1243951.2955
15 | 2638054.6399 | 1244052.7496 | 2638054.4039 | 1244052.3996 | 2638051.5902 | 1244047.853
16 | 2638054.6399 | 1244052.7496 | 2638059.0761 | 1244059.3303
17 | 2638059.3099 | 1244059.6771 | 2638059.0761 | 1244059.3303
18 | 2638268.4636 | 1244018.4566 | 2638256.0976 | 1244028.2017 | 2638253.0184 | 1244030.5615
19 | 2638271.9924 | 1244015.6385 | 2638271.1972 | 1244016.3024 | 2638268.4636 | 1244018.4566
20 | 2638246.7359 | 1244035.376 | 2638253.0184 | 1244030.5615
21 | 2638273.238 | 1244014.5986 | 2638271.9924 | 1244015.6385
22 | 2638246.3721 | 1244035.6549 | 2638246.7359 | 1244035.376
23 | 2638273.238 | 1244014.5986 | 2638273.3691 | 1244014.4892
24 | 2638237.1987 | 1244042.2002 | 2638240.2008 | 1244040.6964 | 2638244.0987 | 1244037.3971 | 2638246.3721 | 1244035.6549
25 | 2638292.0209 | 1243999.238 | 2638288.801 | 1244001.6063 | 2638273.3691 | 1244014.4892
26 | 2638195.1891 | 1243980.9487 | 2638195.5353 | 1243981.3156
27 | 2638208.7036 | 1243995.4635 | 2638199.1024 | 1243985.0958 | 2638195.5353 | 1243981.3156
28 | 2638195.1891 | 1243980.9487 | 2638190.1612 | 1243975.6204
29 | 2638208.7036 | 1243995.4635 | 2638216.5774 | 1244003.9659
30 | 2638178.534 | 1243963.9629 | 2638185.8024 | 1243971.0011 | 2638190.1612 | 1243975.6204
31 | 2638216.5774 | 1244003.9659 | 2638216.7007 | 1244004.0991 | 2638221.9 | 1244011.1038 | 2638225.201 | 1244016.006 | 2638228.1028 | 1244020.7055 | 2638231.0989 | 1244026.006 | 2638233.5024 | 1244031.803 | 2638233.7536 | 1244032.4643
32 | 2638178.534 | 1243963.9629 | 2638176.197 | 1243961.7 | 2638174.8016 | 1243959.7358
33 | 2638237.1987 | 1244042.2002 | 2638236.1998 | 1244038.9028 | 2638233.7536 | 1244032.4643
34 | 2638295.4747 | 1243957.6503 | 2638293.2021 | 1243953.1031 | 2638290.6986 | 1243942.9026 | 2638289.6031 | 1243933.5005 | 2638289.3441 | 1243926.9768
35 | 2638301.8995 | 1243997.6993 | 2638303.7978 | 1243991.5965 | 2638304.2002 | 1243987.7966 | 2638304.0968 | 1243983.9045 | 2638303.3998 | 1243979.4972 | 2638302.0997 | 1243973.6961 | 2638299.2004 | 1243965.1052 | 2638295.4747 | 1243957.6503
36 | 2638301.8995 | 1243997.6993 | 2638303.5978 | 1243997.9993 | 2638306.9995 | 1243998.9997 | 2638310.9009 | 1244001.004 | 2638316.8003 | 1244004.9001 | 2638320.155 | 1244007.4305
37 | 2638301.8995 | 1243997.6993 | 2638300.2011 | 1243997.3993 | 2638297.6015 | 1243997.4047 | 2638294.9988 | 1243997.8994 | 2638292.2026 | 1243999.1044 | 2638292.0209 | 1243999.238
38 | 2638321.7159 | 1244008.6078 | 2638320.155 | 1244007.4305
39 | 2638336.5699 | 1243922.3029 | 2638333.3999 | 1243919.8964 | 2638319.9002 | 1243907.5012 | 2638317.517 | 1243905.3322
40 | 2638317.517 | 1243905.3322 | 2638361.8771 | 1243849.2313
41 | 2638329.7432 | 1243950.0811 | 2638317.8043 | 1243936.0062 | 2638313.134 | 1243930.7274
42 | 2638321.7159 | 1244008.6078 | 2638327.8023 | 1244013.1987 | 2638335.897 | 1244019.9998 | 2638344.101 | 1244028.6028 | 2638352.6561 | 1244037.9315
43 | 2638119.9998 | 1244138.9098 | 2638114.6412 | 1244139.8712
44 | 2638119.9998 | 1244138.9098 | 2638118.4016 | 1244134.7968 | 2638116.698 | 1244130.6054 | 2638114.0985 | 1244125.8968 | 2638109.1033 | 1244117.7038 | 2638105.8999 | 1244112.9024 | 2638101.1985 | 1244107.2019 | 2638098.3772 | 1244103.9463
45 | 2638119.9998 | 1244138.9098 | 2638126.8237 | 1244137.6972 | 2638131.7708 | 1244136.3196
46 | 2638098.3772 | 1244103.9463 | 2638096.8643 | 1244102.2006
47 | 2638143.1752 | 1244133.1437 | 2638131.7708 | 1244136.3196
48 | 2638094.633 | 1244099.6259 | 2638096.8643 | 1244102.2006
49 | 2638143.793 | 1244132.9166 | 2638143.1752 | 1244133.1437
50 | 2638143.1752 | 1244133.1437 | 2638148.2029 | 1244139.8025 | 2638151.8381 | 1244144.8714
51 | 2638081.7621 | 1244086.6785 | 2638081.2628 | 1244086.1918
52 | 2638078.904 | 1244083.8927 | 2638081.2628 | 1244086.1918
53 | 2638094.633 | 1244099.6259 | 2638090.8019 | 1244095.2052 | 2638086.099 | 1244090.9055 | 2638081.7621 | 1244086.6785
54 | 2638078.904 | 1244083.8927 | 2638078.1988 | 1244083.2054 | 2638077.9444 | 1244082.969
55 | 2638077.9444 | 1244082.969 | 2638076.5706 | 1244081.6926
56 | 2638076.5706 | 1244081.6926 | 2638075.0508 | 1244080.2806
57 | 2638243.6663 | 1244088.5264 | 2638241.0451 | 1244084.3224
58 | 2638254.5179 | 1244105.9364 | 2638248.929 | 1244096.9669 | 2638243.6663 | 1244088.5264
59 | 2638234.3026 | 1244076.5039 | 2638236.3051 | 1244077.6842 | 2638238.5999 | 1244080.4008 | 2638241.0451 | 1244084.3224
60 | 2638254.5179 | 1244105.9364 | 2638256.7835 | 1244109.5723
61 | 2638234.3026 | 1244076.5039 | 2638236.1012 | 1244067.0983 | 2638237.1023 | 1244059.4998 | 2638237.2824 | 1244055.934
62 | 2638234.3026 | 1244076.5039 | 2638232.003 | 1244075.6997 | 2638224.4009 | 1244075.7063 | 2638216.5039 | 1244078.1015 | 2638207.1931 | 1244084.1233 | 2638195.201 | 1244093.1604
63 | 2638264.3324 | 1244121.6873 | 2638256.7835 | 1244109.5723
64 | 2638237.1987 | 1244042.2002 | 2638237.3995 | 1244042.7019 | 2638237.8039 | 1244045.6064 | 2638237.2824 | 1244055.934
65 | 2638175.3306 | 1244110.3795 | 2638194.0563 | 1244094.023 | 2638195.201 | 1244093.1604
66 | 2638266.1239 | 1244124.5623 | 2638264.3324 | 1244121.6873
67 | 2638266.1239 | 1244124.5623 | 2638303.4705 | 1244096.8938
68 | 2638303.4705 | 1244096.8938 | 2638323.7526 | 1244081.8676
69 | 2638059.3099 | 1244059.6771 | 2638066.4031 | 1244070.1991 | 2638071.1977 | 1244076.7008 | 2638075.0508 | 1244080.2806
70 | 2638173.6998 | 1244111.8039 | 2638172.8012 | 1244112.5889
71 | 2638175.3306 | 1244110.3795 | 2638173.6998 | 1244111.8039
72 | 2638143.793 | 1244132.9166 | 2638147.0988 | 1244131.7013 | 2638161.7971 | 1244122.2006 | 2638172.8012 | 1244112.5889
73 | 2638162.4041 | 1244159.7515 | 2638159.6019 | 1244155.6972 | 2638151.8381 | 1244144.8714
74 | 2638174.4043 | 1243928.2255 | 2638173.2996 | 1243941.0346 | 2638172.0533 | 1243947.9978 | 2638171.8396 | 1243953.0219 | 2638172.9992 | 1243957.1987 | 2638174.8016 | 1243959.7358

## bus_geodata
| x | y | coords
0 | 2638271.2906 | 1243877.9526
1 | 2638281.5178 | 1243892.9537
2 | 2638260.1909 | 1243862.2825
3 | 2638284.4947 | 1243897.3201
4 | 2638245.7348 | 1243841.9347
5 | 2638294.7013 | 1243909.3066
6 | 2638235.4834 | 1243827.5053
7 | 2638365.5988 | 1243986.7033
8 | 2638350.4449 | 1243973.2127
9 | 2638370.3037 | 1243989.5022
10 | 2638349.2562 | 1243971.9859
11 | 2638372.3695 | 1244002.71
12 | 2638330.7733 | 1243951.2955
13 | 2638051.5902 | 1244047.853
14 | 2638054.6399 | 1244052.7496
15 | 2638059.0761 | 1244059.3303
16 | 2638268.4636 | 1244018.4566
17 | 2638253.0184 | 1244030.5615
18 | 2638271.9924 | 1244015.6385
19 | 2638246.7359 | 1244035.376
20 | 2638273.238 | 1244014.5986
21 | 2638246.3721 | 1244035.6549
22 | 2638273.3691 | 1244014.4892
23 | 2638195.5353 | 1243981.3156
24 | 2638195.1892 | 1243980.9487
25 | 2638208.7036 | 1243995.4635
26 | 2638190.1612 | 1243975.6204
27 | 2638216.5774 | 1244003.9659
28 | 2638178.534 | 1243963.9629
29 | 2638233.7536 | 1244032.4643
30 | 2638295.4747 | 1243957.6503
31 | 2638289.3441 | 1243926.9768
32 | 2638301.8995 | 1243997.6993
33 | 2638320.155 | 1244007.4305
34 | 2638292.0209 | 1243999.238
35 | 2638317.517 | 1243905.3322
36 | 2638313.134 | 1243930.7274
37 | 2638321.7159 | 1244008.6078
38 | 2638114.6412 | 1244139.8712
39 | 2638119.9998 | 1244138.9098
40 | 2638098.3772 | 1244103.9463
41 | 2638131.7708 | 1244136.3196
42 | 2638096.8643 | 1244102.2006
43 | 2638143.1752 | 1244133.1437
44 | 2638352.6561 | 1244037.9315
45 | 2638081.2628 | 1244086.1918
46 | 2638081.7621 | 1244086.6785
47 | 2638078.904 | 1244083.8927
48 | 2638094.633 | 1244099.6259
49 | 2638077.9444 | 1244082.969
50 | 2638076.5706 | 1244081.6926
51 | 2638243.6663 | 1244088.5264
52 | 2638241.0451 | 1244084.3224
53 | 2638254.5179 | 1244105.9364
54 | 2638234.3026 | 1244076.5039
55 | 2638256.7835 | 1244109.5723
56 | 2638237.2824 | 1244055.934
57 | 2638195.201 | 1244093.1604
58 | 2638264.3324 | 1244121.6873
59 | 2638329.7432 | 1243950.0811
60 | 2638336.5699 | 1243922.3029
61 | 2638361.8771 | 1243849.2313
62 | 2638266.1239 | 1244124.5623
63 | 2638303.4705 | 1244096.8938
64 | 2638237.1987 | 1244042.2002
65 | 2638059.3099 | 1244059.6771
66 | 2638173.6998 | 1244111.8039
67 | 2638172.8012 | 1244112.5889
68 | 2638175.3306 | 1244110.3795
69 | 2638143.793 | 1244132.9166
70 | 2638075.0508 | 1244080.2806
71 | 2638151.8381 | 1244144.8714
72 | 2638162.4041 | 1244159.7515
73 | 2638323.7526 | 1244081.8676
74 | 2638174.4043 | 1243928.2255
75 | 2638174.8016 | 1243959.7358
76 | 2638237.1987 | 1244042.2002

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99176 | -0.15853 | 0.0013697 | 0.00034328
1 | 0.99184 | -0.15686 | 0.001265 | 0.00031703
2 | 0.99169 | -0.15982 | 0.0013353 | 0.00033466
3 | 0.99187 | -0.15626 | 0.0013525 | 0.00033897
4 | 0.99163 | -0.16092 | 0.0012969 | 0.00032503
5 | 0.99199 | -0.15408 | 0 | 0
6 | 0.99162 | -0.16129 | 0.0011769 | 0.00029496
7 | 0.99098 | -0.17367 | 0.0016467 | 0.0004127
8 | 0.99107 | -0.17191 | 0.0018128 | 0.00045432
9 | 0.99096 | -0.17399 | 0 | 0
10 | 0.99108 | -0.1717 | 0.00090266 | 0.00022623
11 | 0.99092 | -0.17476 | 0.0032498 | 0.00081449
12 | 0.99127 | -0.16795 | 0.0010461 | 0.00026217
13 | 0.98744 | -0.24185 | 0.0027565 | 0.00069085
14 | 0.98746 | -0.24156 | 0.0013137 | 0.00032924
15 | 0.98749 | -0.24099 | 0.0030665 | 0.00076854
16 | 0.99711 | -0.055345 | 0.002261 | 0.00056667
17 | 0.99816 | -0.035172 | 0.00187 | 0.00046867
18 | 0.99688 | -0.059815 | 0.0011415 | 0.00028608
19 | 0.9986 | -0.026789 | 0.0017486 | 0.00043825
20 | 0.99679 | -0.061389 | 0.0017762 | 0.00044516
21 | 0.99862 | -0.026289 | 0.0013364 | 0.00033493
22 | 0.99678 | -0.061549 | 0.00082485 | 0.00020673
23 | 0.99917 | -0.015921 | 0.0014692 | 0.00036821
24 | 0.99917 | -0.015995 | 0.0018269 | 0.00045786
25 | 0.99935 | -0.012583 | 0.0034711 | 0.00086995
26 | 0.99912 | -0.016839 | 0.001098 | 0.00027518
27 | 0.99949 | -0.0098806 | 0.0035931 | 0.00090052
28 | 0.99904 | -0.01842 | 0.0015271 | 0.00038273
29 | 1 | 0 | -0.17168 | -0.043047
30 | 0.99367 | -0.12156 | 0.0011041 | 0.0002767
31 | 0.99258 | -0.14253 | 0.0035347 | 0.00088589
32 | 0.99515 | -0.093001 | 0 | 0
33 | 0.99492 | -0.097459 | 0.0038627 | 0.00096808
34 | 0.99562 | -0.083853 | 0.0019312 | 0.000484
35 | 0.9917 | -0.15954 | 0.0014371 | 0.00036017
36 | 0.99161 | -0.16147 | 0.00097186 | 0.00024357
37 | 0.9949 | -0.097742 | 0.0041507 | 0.0010403
38 | 0.98919 | -0.20791 | 0.005191 | 0.001301
39 | 0.98921 | -0.2074 | 0 | 0
40 | 0.98824 | -0.22629 | 0.0040788 | 0.0010222
41 | 0.98955 | -0.20079 | 0.0028167 | 0.00070593
42 | 0.9882 | -0.22717 | 0.0015953 | 0.00039981
43 | 0.98992 | -0.19371 | 0 | 0
44 | 0.99474 | -0.10082 | 0.0040852 | 0.0010238
45 | 0.98781 | -0.23469 | 0.0014005 | 0.00035101
46 | 0.98782 | -0.23448 | 0.0013048 | 0.00032701
47 | 0.98776 | -0.23563 | 0.0020829 | 0.00052203
48 | 0.98813 | -0.22838 | 0.0012517 | 0.0003137
49 | 0.98774 | -0.23596 | 0.0018358 | 0.00046009
50 | 0.98772 | -0.23637 | 0.001303 | 0.00032657
51 | 0.99633 | -0.070114 | 0.0036568 | 0.00091647
52 | 0.99639 | -0.069041 | 0.0025127 | 0.00062975
53 | 0.99617 | -0.07324 | 0.0015241 | 0.00038197
54 | 0.99653 | -0.066303 | 0 | 0
55 | 0.99614 | -0.073779 | 0.0011618 | 0.00029118
56 | 0.99817 | -0.035009 | 0.0024827 | 0.00062222
57 | 0.99364 | -0.12176 | 0.0021849 | 0.0005476
58 | 0.99606 | -0.075281 | 0.0031129 | 0.00078017
59 | 0.99128 | -0.16771 | 0.0051292 | 0.0012855
60 | 0.99168 | -0.15994 | 0.00088187 | 0.00022102
61 | 0.99111 | -0.17113 | 0.0091363 | 0.0022898
62 | 0.99606 | -0.075453 | 0 | 0
63 | 0.99593 | -0.077803 | 0.0010036 | 0.00025154
64 | 0.99928 | -0.013694 | 0 | 0
65 | 0.98749 | -0.24093 | 0.0018257 | 0.00045757
66 | 0.99185 | -0.15634 | 0.0009192 | 0.00023037
67 | 0.99178 | -0.15775 | 0.010692 | 0.0026796
68 | 0.99198 | -0.15375 | 0.0011536 | 0.00028911
69 | 0.98995 | -0.19319 | 0.011676 | 0.0029263
70 | 0.9877 | -0.23676 | 0.0017766 | 0.00044525
71 | 0.98978 | -0.19649 | 0.0026024 | 0.00065223
72 | 0.98964 | -0.19914 | 0.0081348 | 0.0020388
73 | 0.99589 | -0.078634 | 0.0018729 | 0.0004694
74 | 0.99896 | -0.020082 | 0.0022421 | 0.00056192
75 | 0.99902 | -0.018813 | 0.001728 | 0.00043308
76 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0051792 | -0.0012974 | 0.0051796 | 0.0012974 | 4.111e-07 | 2.8803e-08 | 0.0077706 | 0.0077705 | 0.0077706 | 0.99176 | -0.15853 | 0.99184 | -0.15686 | 2.1348
1 | 0.0038095 | 0.0009541 | -0.0038093 | -0.0009542 | 2.3524e-07 | -9.7224e-08 | 0.0057155 | 0.0057156 | 0.0057156 | 0.99176 | -0.15853 | 0.99169 | -0.15982 | 1.5702
2 | -0.0064446 | -0.0016144 | 0.0064448 | 0.0016145 | 1.8524e-07 | 5.0349e-08 | 0.0096683 | 0.0096682 | 0.0096683 | 0.99184 | -0.15686 | 0.99187 | -0.15626 | 2.6561
3 | 0.0024739 | 0.00061954 | -0.0024738 | -0.00061978 | 1.2897e-07 | -2.3948e-07 | 0.0037119 | 0.0037121 | 0.0037121 | 0.99169 | -0.15982 | 0.99163 | -0.16092 | 1.0198
4 | -0.0077973 | -0.0019535 | 0.0077981 | 0.0019538 | 8.0921e-07 | 3.1431e-07 | 0.011697 | 0.011697 | 0.011697 | 0.99187 | -0.15626 | 0.99199 | -0.15408 | 3.2135
5 | 0.0011769 | 0.00029475 | -0.0011769 | -0.00029496 | 2.0702e-08 | -2.1509e-07 | 0.001766 | 0.0017661 | 0.0017661 | 0.99163 | -0.16092 | 0.99162 | -0.16129 | 0.48518
6 | 0.011463 | 0.0028745 | -0.01146 | -0.002873 | 2.9859e-06 | 1.5634e-06 | 0.017196 | 0.017196 | 0.017196 | 0.99199 | -0.15408 | 0.9917 | -0.15954 | 4.7242
7 | 0.014771 | 0.0037047 | -0.014765 | -0.0037017 | 5.2057e-06 | 2.9668e-06 | 0.022157 | 0.022157 | 0.022157 | 0.99199 | -0.15408 | 0.99161 | -0.16147 | 6.0872
8 | -0.034032 | -0.008533 | 0.034051 | 0.0085447 | 1.8746e-05 | 1.1749e-05 | 0.05105 | 0.05105 | 0.05105 | 0.99199 | -0.15408 | 0.99258 | -0.14253 | 14.0249
9 | -0.0048967 | -0.0012271 | 0.0048971 | 0.0012271 | 4.1184e-07 | 1.827e-09 | 0.0073527 | 0.0073526 | 0.0073527 | 0.99098 | -0.17367 | 0.99107 | -0.17191 | 2.02
10 | 0.00325 | 0.00081435 | -0.00325 | -0.00081439 | 4.8902e-08 | -3.925e-08 | 0.00488 | 0.0048801 | 0.0048801 | 0.99098 | -0.17367 | 0.99096 | -0.17399 | 1.3407
11 | -0.0067099 | -0.0016814 | 0.00671 | 0.0016814 | 6.5017e-08 | 1.9598e-08 | 0.010074 | 0.010074 | 0.010074 | 0.99107 | -0.17191 | 0.99108 | -0.1717 | 2.7677
12 | 0.00325 | 0.00081439 | -0.0032498 | -0.00081449 | 1.1958e-07 | -9.596e-08 | 0.0048801 | 0.0048801 | 0.0048801 | 0.99096 | -0.17399 | 0.99092 | -0.17476 | 1.3407
13 | -0.0076126 | -0.0019076 | 0.007614 | 0.0019081 | 1.3592e-06 | 5.1228e-07 | 0.01143 | 0.011429 | 0.01143 | 0.99108 | -0.1717 | 0.99127 | -0.16795 | 3.14
14 | -0.00866 | -0.0021703 | 0.0086601 | 0.0021704 | 1.0092e-07 | 4.4058e-08 | 0.013 | 0.013 | 0.013 | 0.99127 | -0.16795 | 0.99128 | -0.16771 | 3.5714
15 | -0.0027565 | -0.00069085 | 0.0027565 | 0.0006908 | 3.7328e-08 | -4.9907e-08 | 0.0041539 | 0.0041539 | 0.0041539 | 0.98744 | -0.24185 | 0.98746 | -0.24156 | 1.1412
16 | -0.0040702 | -0.00102 | 0.0040703 | 0.00102 | 1.1196e-07 | -2.9872e-08 | 0.0061335 | 0.0061334 | 0.0061335 | 0.98746 | -0.24156 | 0.98749 | -0.24099 | 1.685
17 | -0.0071368 | -0.0017885 | 0.0071369 | 0.0017885 | 1.8144e-08 | 6.2604e-09 | 0.010754 | 0.010754 | 0.010754 | 0.98749 | -0.24099 | 0.98749 | -0.24093 | 2.9545
18 | -0.058912 | -0.014847 | 0.058969 | 0.014883 | 5.6916e-05 | 3.617e-05 | 0.087945 | 0.087945 | 0.087945 | 0.99711 | -0.055345 | 0.99816 | -0.035172 | 24.1607
19 | 0.056651 | 0.01428 | -0.056639 | -0.014272 | 1.2113e-05 | 7.6935e-06 | 0.084571 | 0.084571 | 0.084571 | 0.99711 | -0.055345 | 0.99688 | -0.059815 | 23.2337
20 | -0.060839 | -0.015352 | 0.060863 | 0.015367 | 2.4435e-05 | 1.5535e-05 | 0.090733 | 0.090733 | 0.090733 | 0.99816 | -0.035172 | 0.9986 | -0.026789 | 24.9266
21 | 0.055497 | 0.013986 | -0.055493 | -0.013984 | 4.1784e-06 | 2.653e-06 | 0.082867 | 0.082867 | 0.082867 | 0.99688 | -0.059815 | 0.99679 | -0.061389 | 22.7657
22 | -0.062612 | -0.015805 | 0.062613 | 0.015806 | 1.4976e-06 | 9.5249e-07 | 0.093338 | 0.093338 | 0.093338 | 0.9986 | -0.026789 | 0.99862 | -0.026289 | 25.6424
23 | 0.053717 | 0.013539 | -0.053716 | -0.013538 | 4.1201e-07 | 2.6146e-07 | 0.080216 | 0.080216 | 0.080216 | 0.99679 | -0.061389 | 0.99678 | -0.061549 | 22.0372
24 | -0.06395 | -0.016141 | 0.063988 | 0.016166 | 3.8607e-05 | 2.456e-05 | 0.09533 | 0.09533 | 0.09533 | 0.99862 | -0.026289 | 0.99928 | -0.013694 | 26.1894
25 | 0.052892 | 0.013332 | -0.052835 | -0.013296 | 5.638e-05 | 3.5769e-05 | 0.078984 | 0.078984 | 0.078984 | 0.99678 | -0.061549 | 0.99562 | -0.083853 | 21.699
26 | 0.008423 | 0.0021105 | -0.0084229 | -0.0021105 | 2.9761e-08 | 1.2441e-08 | 0.012544 | 0.012544 | 0.012544 | 0.99917 | -0.015921 | 0.99917 | -0.015995 | 3.4461
27 | -0.0098921 | -0.0024787 | 0.0098937 | 0.0024795 | 1.573e-06 | 7.5351e-07 | 0.014732 | 0.014732 | 0.014732 | 0.99917 | -0.015921 | 0.99935 | -0.012583 | 4.0472
28 | 0.0065961 | 0.0016527 | -0.0065958 | -0.0016526 | 2.6509e-07 | 7.3711e-08 | 0.0098231 | 0.0098231 | 0.0098231 | 0.99917 | -0.015995 | 0.99912 | -0.016839 | 2.6987
29 | -0.013365 | -0.0033494 | 0.013367 | 0.0033504 | 1.7209e-06 | 9.4953e-07 | 0.0199 | 0.0199 | 0.0199 | 0.99935 | -0.012583 | 0.99949 | -0.0098806 | 5.4671
30 | 0.0054978 | 0.0013774 | -0.0054974 | -0.0013774 | 4.1404e-07 | 4.9321e-08 | 0.0081879 | 0.008188 | 0.008188 | 0.99912 | -0.016839 | 0.99904 | -0.01842 | 2.2494
31 | -0.01696 | -0.0042509 | 0.016968 | 0.0042556 | 7.9874e-06 | 4.6738e-06 | 0.025249 | 0.025249 | 0.025249 | 0.99949 | -0.0098806 | 1 | 0 | 6.9366
32 | 0.0039703 | 0.00099464 | -0.0039702 | -0.00099466 | 7.4253e-08 | -2.6622e-08 | 0.0059134 | 0.0059134 | 0.0059134 | 0.99904 | -0.01842 | 0.99902 | -0.018813 | 1.6246
33 | 0.15307 | 0.038792 | -0.15297 | -0.038728 | 0.00010064 | 6.414e-05 | 0.22792 | 0.22792 | 0.22792 | 1 | 0 | 0.99928 | -0.013694 | 31.3073
34 | 0.037623 | 0.0094543 | -0.037585 | -0.0094306 | 3.7604e-05 | 2.3658e-05 | 0.056349 | 0.056349 | 0.056349 | 0.99367 | -0.12156 | 0.99258 | -0.14253 | 15.4806
35 | -0.038727 | -0.009731 | 0.03878 | 0.0097643 | 5.2879e-05 | 3.3299e-05 | 0.058003 | 0.058002 | 0.058003 | 0.99367 | -0.12156 | 0.99515 | -0.093001 | 15.9348
36 | 0.012102 | 0.0030334 | -0.012099 | -0.0030321 | 2.5699e-06 | 1.3729e-06 | 0.018096 | 0.018096 | 0.018096 | 0.99515 | -0.093001 | 0.99492 | -0.097459 | 4.9714
37 | -0.050882 | -0.012798 | 0.050904 | 0.012812 | 2.2246e-05 | 1.4104e-05 | 0.076098 | 0.076098 | 0.076098 | 0.99515 | -0.093001 | 0.99562 | -0.083853 | 20.9061
38 | 0.0082366 | 0.002064 | -0.0082365 | -0.0020639 | 1.1126e-07 | 4.5817e-08 | 0.012319 | 0.012319 | 0.012319 | 0.99492 | -0.097459 | 0.9949 | -0.097742 | 3.3843
39 | 0.00088189 | 0.0002207 | -0.00088187 | -0.00022102 | 1.6762e-08 | -3.1866e-07 | 0.0013231 | 0.0013232 | 0.0013232 | 0.9917 | -0.15954 | 0.99168 | -0.15994 | 0.36353
40 | 0.0091414 | 0.0022921 | -0.0091363 | -0.0022898 | 5.0462e-06 | 2.3073e-06 | 0.013717 | 0.013717 | 0.013717 | 0.9917 | -0.15954 | 0.99111 | -0.17113 | 3.7684
41 | 0.013793 | 0.0034581 | -0.013789 | -0.0034559 | 4.0978e-06 | 2.2937e-06 | 0.020699 | 0.020699 | 0.020699 | 0.99161 | -0.16147 | 0.99128 | -0.16771 | 5.6866
42 | 0.0040858 | 0.0010237 | -0.0040852 | -0.0010238 | 5.9853e-07 | -1.7189e-07 | 0.0061107 | 0.0061109 | 0.0061109 | 0.9949 | -0.097742 | 0.99474 | -0.10082 | 1.6788
43 | -0.005191 | -0.001301 | 0.0051911 | 0.001301 | 1.2449e-07 | 9.7821e-09 | 0.0078087 | 0.0078087 | 0.0078087 | 0.98919 | -0.20791 | 0.98921 | -0.2074 | 2.1453
44 | 0.025626 | 0.0064342 | -0.025603 | -0.00642 | 2.3063e-05 | 1.4229e-05 | 0.038552 | 0.038552 | 0.038552 | 0.98921 | -0.2074 | 0.98824 | -0.22629 | 10.5912
45 | -0.030817 | -0.0077352 | 0.030827 | 0.0077413 | 9.7251e-06 | 6.0691e-06 | 0.04636 | 0.04636 | 0.04636 | 0.98921 | -0.2074 | 0.98955 | -0.20079 | 12.7364
46 | 0.021524 | 0.0053978 | -0.021523 | -0.0053972 | 9.0993e-07 | 5.5276e-07 | 0.03241 | 0.03241 | 0.03241 | 0.98824 | -0.22629 | 0.9882 | -0.22717 | 8.9039
47 | -0.033643 | -0.0084472 | 0.033655 | 0.0084544 | 1.1365e-05 | 7.1212e-06 | 0.050596 | 0.050596 | 0.050596 | 0.98955 | -0.20079 | 0.98992 | -0.19371 | 13.9
48 | 0.019928 | 0.0049974 | -0.019927 | -0.0049967 | 1.1505e-06 | 6.9269e-07 | 0.030008 | 0.030008 | 0.030008 | 0.9882 | -0.22717 | 0.98813 | -0.22838 | 8.244
49 | -0.044394 | -0.011147 | 0.044396 | 0.011147 | 1.0993e-06 | 6.9511e-07 | 0.06674 | 0.06674 | 0.06674 | 0.98992 | -0.19371 | 0.98995 | -0.19319 | 18.335
50 | 0.01074 | 0.0026922 | -0.010738 | -0.0026914 | 1.4251e-06 | 7.2462e-07 | 0.016144 | 0.016144 | 0.016144 | 0.98992 | -0.19371 | 0.98978 | -0.19649 | 4.4351
51 | -0.017365 | -0.0043526 | 0.017365 | 0.0043528 | 1.7891e-07 | 1.0558e-07 | 0.026158 | 0.026158 | 0.026158 | 0.98781 | -0.23469 | 0.98782 | -0.23448 | 7.1862
52 | 0.015964 | 0.0040016 | -0.015963 | -0.0040012 | 7.1434e-07 | 4.1501e-07 | 0.024048 | 0.024048 | 0.024048 | 0.98781 | -0.23469 | 0.98776 | -0.23563 | 6.6066
53 | -0.01867 | -0.0046798 | 0.018675 | 0.004683 | 5.4212e-06 | 3.2355e-06 | 0.028123 | 0.028123 | 0.028123 | 0.98782 | -0.23448 | 0.98813 | -0.22838 | 7.7262
54 | 0.01388 | 0.0034792 | -0.01388 | -0.0034791 | 2.1841e-07 | 1.2273e-07 | 0.02091 | 0.02091 | 0.02091 | 0.98776 | -0.23563 | 0.98774 | -0.23596 | 5.7446
55 | 0.012044 | 0.003019 | -0.012044 | -0.0030188 | 2.3152e-07 | 1.2417e-07 | 0.018145 | 0.018145 | 0.018145 | 0.98774 | -0.23596 | 0.98772 | -0.23637 | 4.9848
56 | 0.010741 | 0.0026923 | -0.010741 | -0.0026922 | 2.037e-07 | 1.0382e-07 | 0.016182 | 0.016182 | 0.016182 | 0.98772 | -0.23637 | 0.9877 | -0.23676 | 4.4455
57 | -0.012334 | -0.0030907 | 0.012335 | 0.0030911 | 6.3044e-07 | 3.3896e-07 | 0.018421 | 0.018421 | 0.018421 | 0.99633 | -0.070114 | 0.99639 | -0.069041 | 5.0608
58 | 0.0086777 | 0.0021742 | -0.0086764 | -0.0021737 | 1.2921e-06 | 5.5983e-07 | 0.01296 | 0.01296 | 0.01296 | 0.99633 | -0.070114 | 0.99617 | -0.07324 | 3.5604
59 | -0.014848 | -0.0037208 | 0.01485 | 0.0037219 | 1.9363e-06 | 1.1025e-06 | 0.022174 | 0.022174 | 0.022174 | 0.99639 | -0.069041 | 0.99653 | -0.066303 | 6.0917
60 | 0.0071523 | 0.0017917 | -0.0071521 | -0.0017917 | 1.8336e-07 | 6.1577e-08 | 0.010683 | 0.010683 | 0.010683 | 0.99617 | -0.07324 | 0.99614 | -0.073779 | 2.935
61 | -0.086274 | -0.021799 | 0.086404 | 0.021881 | 0.00012964 | 8.2696e-05 | 0.12889 | 0.12889 | 0.12889 | 0.99653 | -0.066303 | 0.99817 | -0.035009 | 35.4084
62 | 0.071424 | 0.018077 | -0.071235 | -0.017956 | 0.00018958 | 0.00012076 | 0.10671 | 0.10671 | 0.10671 | 0.99653 | -0.066303 | 0.99364 | -0.12176 | 29.3168
63 | 0.0059903 | 0.0015005 | -0.0059899 | -0.0015004 | 4.2859e-07 | 8.8481e-08 | 0.0089479 | 0.008948 | 0.008948 | 0.99614 | -0.073779 | 0.99606 | -0.075281 | 2.4582
64 | -0.088886 | -0.022504 | 0.088977 | 0.022562 | 9.1063e-05 | 5.81e-05 | 0.13259 | 0.13259 | 0.13259 | 0.99817 | -0.035009 | 0.99928 | -0.013694 | 36.4251
65 | 0.06905 | 0.017408 | -0.068944 | -0.017341 | 0.00010552 | 6.719e-05 | 0.10344 | 0.10344 | 0.10344 | 0.99364 | -0.12176 | 0.99198 | -0.15375 | 28.4179
66 | 0.002877 | 0.00072023 | -0.002877 | -0.00072026 | 2.3462e-08 | -2.9076e-08 | 0.0042976 | 0.0042977 | 0.0042977 | 0.99606 | -0.075281 | 0.99606 | -0.075453 | 1.1807
67 | 0.002877 | 0.00072026 | -0.0028766 | -0.00072066 | 3.2194e-07 | -3.9886e-07 | 0.0042977 | 0.0042979 | 0.0042979 | 0.99606 | -0.075453 | 0.99593 | -0.077803 | 1.1807
68 | 0.001873 | 0.00046912 | -0.0018729 | -0.0004694 | 7.4126e-08 | -2.8101e-07 | 0.0027983 | 0.0027984 | 0.0027984 | 0.99593 | -0.077803 | 0.99589 | -0.078634 | 0.7688
69 | -0.0089626 | -0.0022461 | 0.0089644 | 0.0022469 | 1.7802e-06 | 8.0629e-07 | 0.013505 | 0.013505 | 0.013505 | 0.98749 | -0.24093 | 0.9877 | -0.23676 | 3.7103
70 | 0.066863 | 0.016816 | -0.066859 | -0.016813 | 4.5042e-06 | 2.8673e-06 | 0.10033 | 0.10033 | 0.10033 | 0.99185 | -0.15634 | 0.99178 | -0.15775 | 27.5637
71 | -0.067782 | -0.017047 | 0.067791 | 0.017052 | 8.4e-06 | 5.348e-06 | 0.10171 | 0.10171 | 0.10171 | 0.99185 | -0.15634 | 0.99198 | -0.15375 | 27.9425
72 | 0.056167 | 0.014134 | -0.056072 | -0.014074 | 9.4941e-05 | 6.0304e-05 | 0.08429 | 0.08429 | 0.08429 | 0.99178 | -0.15775 | 0.98995 | -0.19319 | 23.1567
73 | 0.0081359 | 0.0020392 | -0.0081348 | -0.0020388 | 1.0239e-06 | 4.2077e-07 | 0.012231 | 0.012231 | 0.012231 | 0.98978 | -0.19649 | 0.98964 | -0.19914 | 3.3603
74 | -0.0022421 | -0.00056192 | 0.0022422 | 0.00056158 | 1.3554e-07 | -3.3754e-07 | 0.0033397 | 0.0033396 | 0.0033397 | 0.99896 | -0.020082 | 0.99902 | -0.018813 | 0.91751

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.17549 | 0.044002

## res_load
| p_mw | q_mvar
0 | 0.0013697 | 0.00034328
1 | 0.001265 | 0.00031703
2 | 0.0013353 | 0.00033466
3 | 0.0013525 | 0.00033897
4 | 0.0012969 | 0.00032503
5 | 0.0011769 | 0.00029496
6 | 0.0016467 | 0.0004127
7 | 0.0018128 | 0.00045432
8 | 0.00090266 | 0.00022623
9 | 0.0032498 | 0.00081449
10 | 0.0010461 | 0.00026217
11 | 0.0027565 | 0.00069085
12 | 0.0013137 | 0.00032924
13 | 0.0030665 | 0.00076854
14 | 0.002261 | 0.00056667
15 | 0.00187 | 0.00046867
16 | 0.0011415 | 0.00028608
17 | 0.0017486 | 0.00043825
18 | 0.0017762 | 0.00044516
19 | 0.0013364 | 0.00033493
20 | 0.00082485 | 0.00020673
21 | 0.0014692 | 0.00036821
22 | 0.0018269 | 0.00045786
23 | 0.0034711 | 0.00086995
24 | 0.001098 | 0.00027518
25 | 0.0035931 | 0.00090052
26 | 0.0015271 | 0.00038273
27 | 0.003809 | 0.00095462
28 | 0.0011041 | 0.0002767
29 | 0.0035347 | 0.00088589
30 | 0.0038627 | 0.00096808
31 | 0.0019312 | 0.000484
32 | 0.0014371 | 0.00036017
33 | 0.00097186 | 0.00024357
34 | 0.0041507 | 0.0010403
35 | 0.005191 | 0.001301
36 | 0.0040788 | 0.0010222
37 | 0.0028167 | 0.00070593
38 | 0.0015953 | 0.00039981
39 | 0.0040852 | 0.0010238
40 | 0.0014005 | 0.00035101
41 | 0.0013048 | 0.00032701
42 | 0.0020829 | 0.00052203
43 | 0.0012517 | 0.0003137
44 | 0.0018358 | 0.00046009
45 | 0.001303 | 0.00032657
46 | 0.0036568 | 0.00091647
47 | 0.0025127 | 0.00062975
48 | 0.0015241 | 0.00038197
49 | 0.0011618 | 0.00029118
50 | 0.0024827 | 0.00062222
51 | 0.0021849 | 0.0005476
52 | 0.0031129 | 0.00078017
53 | 0.0051292 | 0.0012855
54 | 0.00088187 | 0.00022102
55 | 0.0091363 | 0.0022898
56 | 0.0010036 | 0.00025154
57 | 0.0018257 | 0.00045757
58 | 0.0009192 | 0.00023037
59 | 0.010692 | 0.0026796
60 | 0.0011536 | 0.00028911
61 | 0.011676 | 0.0029263
62 | 0.0017766 | 0.00044525
63 | 0.0026024 | 0.00065223
64 | 0.0081348 | 0.0020388
65 | 0.0018729 | 0.0004694
66 | 0.0022421 | 0.00056192
67 | 0.001728 | 0.00043308

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1