## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2573-6_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2573-6_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2573-6_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2573-6_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2573-6_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2573-6_0_8_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2573-6_0_8_node_101 | 0.4 | n |  | TRUE
7 | bus_LV_2573-6_0_8_node_71 | 0.4 | n |  | TRUE
8 | bus_LV_2573-6_0_8_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2573-6_0_8_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2573-6_0_8_node_98 | 0.4 | n |  | TRUE
11 | bus_LV_2573-6_0_8_node_128 | 0.4 | n |  | TRUE
12 | bus_LV_2573-6_0_8_node_92 | 0.4 | n |  | TRUE
13 | bus_LV_2573-6_0_8_node_130 | 0.4 | n |  | TRUE
14 | bus_LV_2573-6_0_8_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_2573-6_0_8_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_2573-6_0_8_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2573-6_0_8_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2573-6_0_8_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2573-6_0_8_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_2573-6_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2573-6_0_8_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2573-6_0_8_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_2573-6_0_8_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_2573-6_0_8_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2573-6_0_8_node_84 | 0.4 | n |  | TRUE
26 | bus_LV_2573-6_0_8_node_85 | 0.4 | n |  | TRUE
27 | bus_LV_2573-6_0_8_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_2573-6_0_8_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2573-6_0_8_node_82 | 0.4 | n |  | TRUE
30 | bus_LV_2573-6_0_8_node_83 | 0.4 | n |  | TRUE
31 | bus_LV_2573-6_0_8_node_75 | 0.4 | n |  | TRUE
32 | bus_LV_2573-6_0_8_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2573-6_0_8_node_86 | 0.4 | n |  | TRUE
34 | bus_LV_2573-6_0_8_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_2573-6_0_8_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_2573-6_0_8_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_2573-6_0_8_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2573-6_0_8_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2573-6_0_8_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_2573-6_0_8_node_72 | 0.4 | n |  | TRUE
41 | bus_LV_2573-6_0_8_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_2573-6_0_8_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2573-6_0_8_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2573-6_0_8_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2573-6_0_8_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_2573-6_0_8_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_2573-6_0_8_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2573-6_0_8_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_2573-6_0_8_node_99 | 0.4 | n |  | TRUE
50 | bus_LV_2573-6_0_8_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_2573-6_0_8_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_2573-6_0_8_node_100 | 0.4 | n |  | TRUE
53 | bus_LV_2573-6_0_8_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_2573-6_0_8_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2573-6_0_8_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_2573-6_0_8_node_70 | 0.4 | n |  | TRUE
57 | bus_LV_2573-6_0_8_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_2573-6_0_8_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2573-6_0_8_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_2573-6_0_8_node_43 | 0.4 | n |  | TRUE
61 | bus_LV_2573-6_0_8_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_2573-6_0_8_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_2573-6_0_8_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2573-6_0_8_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2573-6_0_8_node_88 | 0.4 | n |  | TRUE
66 | bus_LV_2573-6_0_8_node_69 | 0.4 | n |  | TRUE
67 | bus_LV_2573-6_0_8_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_2573-6_0_8_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_2573-6_0_8_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_2573-6_0_8_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_2573-6_0_8_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_2573-6_0_8_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_2573-6_0_8_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_2573-6_0_8_node_120 | 0.4 | n |  | TRUE
75 | bus_LV_2573-6_0_8_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_2573-6_0_8_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_2573-6_0_8_node_104 | 0.4 | n |  | TRUE
78 | bus_LV_2573-6_0_8_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_2573-6_0_8_node_87 | 0.4 | n |  | TRUE
80 | bus_LV_2573-6_0_8_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_2573-6_0_8_node_90 | 0.4 | n |  | TRUE
82 | bus_LV_2573-6_0_8_node_91 | 0.4 | n |  | TRUE
83 | bus_LV_2573-6_0_8_node_105 | 0.4 | n |  | TRUE
84 | bus_LV_2573-6_0_8_node_106 | 0.4 | n |  | TRUE
85 | bus_LV_2573-6_0_8_node_126 | 0.4 | n |  | TRUE
86 | bus_LV_2573-6_0_8_node_121 | 0.4 | n |  | TRUE
87 | bus_LV_2573-6_0_8_node_129 | 0.4 | n |  | TRUE
88 | bus_LV_2573-6_0_8_node_131 | 0.4 | n |  | TRUE
89 | bus_LV_2573-6_0_8_node_33 | 0.4 | n |  | TRUE
90 | bus_LV_2573-6_0_8_node_95 | 0.4 | n |  | TRUE
91 | bus_LV_2573-6_0_8_node_96 | 0.4 | n |  | TRUE
92 | bus_LV_2573-6_0_8_node_93 | 0.4 | n |  | TRUE
93 | bus_LV_2573-6_0_8_node_97 | 0.4 | n |  | TRUE
94 | bus_LV_2573-6_0_8_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_2573-6_0_8_node_36 | 0.4 | n |  | TRUE
96 | bus_LV_2573-6_0_8_node_37 | 0.4 | n |  | TRUE
97 | bus_LV_2573-6_0_8_node_114 | 0.4 | n |  | TRUE
98 | bus_LV_2573-6_0_8_node_115 | 0.4 | n |  | TRUE
99 | bus_LV_2573-6_0_8_node_38 | 0.4 | n |  | TRUE
100 | bus_LV_2573-6_0_8_node_39 | 0.4 | n |  | TRUE
101 | bus_LV_2573-6_0_8_node_41 | 0.4 | n |  | TRUE
102 | bus_LV_2573-6_0_8_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_2573-6_0_8_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_2573-6_0_8_node_64 | 0.4 | n |  | TRUE
105 | bus_LV_2573-6_0_8_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2573-6_0_8_node_127 | 0.4 | n |  | TRUE
107 | bus_LV_2573-6_0_8_node_124 | 0.4 | n |  | TRUE
108 | bus_LV_2573-6_0_8_node_76 | 0.4 | n |  | TRUE
109 | bus_LV_2573-6_0_8_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_2573-6_0_8_node_79 | 0.4 | n |  | TRUE
111 | bus_LV_2573-6_0_8_node_80 | 0.4 | n |  | TRUE
112 | bus_LV_2573-6_0_8_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_2573-6_0_8_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_2573-6_0_8_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_2573-6_0_8_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_2573-6_0_8_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_2573-6_0_8_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_2573-6_0_8_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_2573-6_0_8_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_2573-6_0_8_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_2573-6_0_8_node_125 | 0.4 | n |  | TRUE
122 | bus_LV_2573-6_0_8_node_119 | 0.4 | n |  | TRUE
123 | bus_LV_2573-6_0_8_node_118 | 0.4 | n |  | TRUE
124 | bus_LV_2573-6_0_8_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_2573-6_0_8_node_123 | 0.4 | n |  | TRUE
126 | bus_MV_398_1_node_75 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2573-6_0_8_load_0 | 0 | 0.0019052 | 0.00047748 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2573-6_0_8_load_1 | 1 | 0.0018978 | 0.00047563 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2573-6_0_8_load_2 | 2 | 0.0043196 | 0.0010826 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2573-6_0_8_load_3 | 3 | 0.0027002 | 0.00067674 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2573-6_0_8_load_4 | 4 | 0.0023166 | 0.00058059 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2573-6_0_8_load_31 | 5 | 0.0014426 | 0.00036156 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2573-6_0_8_load_71 | 7 | 0.0059178 | 0.0014832 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2573-6_0_8_load_5 | 8 | 0.0018834 | 0.00047203 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2573-6_0_8_load_6 | 9 | 0.0023166 | 0.00058059 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2573-6_0_8_load_98 | 10 | 0.003361 | 0.00084234 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2573-6_0_8_load_128 | 11 | 0.0016596 | 0.00041594 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2573-6_0_8_load_92 | 12 | 0.0017008 | 0.00042625 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2573-6_0_8_load_130 | 13 | 0.0016584 | 0.00041564 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2573-6_0_8_load_7 | 14 | 0.00256 | 0.0006416 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2573-6_0_8_load_8 | 15 | 0.0030493 | 0.00076423 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2573-6_0_8_load_10 | 17 | 0.0046839 | 0.0011739 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2573-6_0_8_load_11 | 18 | 0.026963 | 0.0067576 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2573-6_0_8_load_12 | 19 | 0.010618 | 0.002661 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2573-6_0_8_load_74 | 23 | 0.057421 | 0.014391 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2573-6_0_8_load_85 | 26 | 0.0014419 | 0.00036136 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2573-6_0_8_load_53 | 27 | 0.0069249 | 0.0017355 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2573-6_0_8_load_20 | 28 | 0.0086246 | 0.0021615 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2573-6_0_8_load_83 | 30 | 0.0063969 | 0.0016032 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2573-6_0_8_load_22 | 32 | 0.0087594 | 0.0021953 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2573-6_0_8_load_86 | 33 | 0.0011781 | 0.00029527 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2573-6_0_8_load_16 | 35 | 0.0086198 | 0.0021603 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2573-6_0_8_load_17 | 36 | 0.0086192 | 0.0021602 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2573-6_0_8_load_19 | 37 | 0.0087708 | 0.0021982 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2573-6_0_8_load_21 | 38 | 0.0016343 | 0.00040961 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2573-6_0_8_load_23 | 39 | 0.0016073 | 0.00040283 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2573-6_0_8_load_24 | 42 | 0.0012845 | 0.00032192 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2573-6_0_8_load_25 | 43 | 0.00079537 | 0.00019934 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2573-6_0_8_load_26 | 44 | 0.0011959 | 0.00029973 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2573-6_0_8_load_27 | 45 | 0.0012454 | 0.00031213 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2573-6_0_8_load_28 | 46 | 0.0012709 | 0.00031851 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2573-6_0_8_load_29 | 47 | 0.0013005 | 0.00032593 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2573-6_0_8_load_30 | 48 | 0.0012008 | 0.00030096 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2573-6_0_8_load_99 | 49 | 0.0020466 | 0.00051293 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2573-6_0_8_load_34 | 50 | 0.0012556 | 0.00031467 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2573-6_0_8_load_35 | 51 | 0.0011742 | 0.00029429 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2573-6_0_8_load_100 | 52 | 0.0024928 | 0.00062474 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2573-6_0_8_load_42 | 53 | 0.0021043 | 0.00052738 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2573-6_0_8_load_45 | 54 | 0.00095011 | 0.00023812 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2573-6_0_8_load_70 | 56 | 0.0024593 | 0.00061637 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2573-6_0_8_load_52 | 58 | 0.0015764 | 0.00039507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2573-6_0_8_load_49 | 59 | 0.0016013 | 0.00040131 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2573-6_0_8_load_43 | 60 | 0.0024867 | 0.00062322 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2573-6_0_8_load_47 | 61 | 0.0025353 | 0.0006354 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2573-6_0_8_load_48 | 62 | 0.0012348 | 0.00030947 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2573-6_0_8_load_50 | 63 | 0.0012361 | 0.00030979 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2573-6_0_8_load_88 | 65 | 0.0012524 | 0.00031388 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2573-6_0_8_load_69 | 66 | 0.00091911 | 0.00023035 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2573-6_0_8_load_55 | 67 | 0.0018305 | 0.00045876 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2573-6_0_8_load_57 | 69 | 0.0020359 | 0.00051024 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2573-6_0_8_load_58 | 70 | 0.0016302 | 0.00040857 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2573-6_0_8_load_59 | 71 | 0.0029245 | 0.00073295 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2573-6_0_8_load_60 | 72 | 0.0020354 | 0.00051012 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2573-6_0_8_load_61 | 73 | 0.0027415 | 0.00068707 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2573-6_0_8_load_120 | 74 | 0.0020358 | 0.00051022 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2573-6_0_8_load_62 | 75 | 0.0040626 | 0.0010182 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2573-6_0_8_load_63 | 76 | 0.0018461 | 0.00046267 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2573-6_0_8_load_67 | 78 | 0.0017328 | 0.00043428 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2573-6_0_8_load_87 | 79 | 0.0012357 | 0.00030969 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2573-6_0_8_load_89 | 80 | 0.001234 | 0.00030926 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2573-6_0_8_load_90 | 81 | 0.0012365 | 0.0003099 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2573-6_0_8_load_91 | 82 | 0.0018804 | 0.00047128 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2573-6_0_8_load_105 | 83 | 0.0020565 | 0.00051541 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2573-6_0_8_load_106 | 84 | 0.0012311 | 0.00030855 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2573-6_0_8_load_126 | 85 | 0.0014415 | 0.00036128 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2573-6_0_8_load_121 | 86 | 0.0020358 | 0.00051022 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2573-6_0_8_load_129 | 87 | 0.0023165 | 0.00058057 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2573-6_0_8_load_131 | 88 | 0.0023179 | 0.00058092 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2573-6_0_8_load_95 | 90 | 0.0023281 | 0.00058349 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2573-6_0_8_load_96 | 91 | 0.094897 | 0.023783 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2573-6_0_8_load_93 | 92 | 0.012763 | 0.0031988 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2573-6_0_8_load_81 | 94 | 0.012824 | 0.0032139 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2573-6_0_8_load_36 | 95 | 0.0015375 | 0.00038532 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2573-6_0_8_load_37 | 96 | 0.0014425 | 0.00036153 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2573-6_0_8_load_114 | 97 | 0.0019234 | 0.00048205 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2573-6_0_8_load_115 | 98 | 0.0011814 | 0.00029609 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2573-6_0_8_load_38 | 99 | 0.0015745 | 0.0003946 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2573-6_0_8_load_39 | 100 | 0.0012163 | 0.00030483 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2573-6_0_8_load_41 | 101 | 0.0009588 | 0.0002403 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2573-6_0_8_load_94 | 102 | 0.011517 | 0.0028864 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2573-6_0_8_load_103 | 103 | 0.0024963 | 0.00062564 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2573-6_0_8_load_64 | 104 | 0.0012243 | 0.00030683 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2573-6_0_8_load_65 | 105 | 0.0016023 | 0.00040156 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2573-6_0_8_load_127 | 106 | 0.00094972 | 0.00023802 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2573-6_0_8_load_124 | 107 | 0.0017144 | 0.00042968 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2573-6_0_8_load_77 | 109 | 0.018355 | 0.0046001 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2573-6_0_8_load_79 | 110 | 0.108 | 0.027068 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2573-6_0_8_load_80 | 111 | 0.0013695 | 0.00034324 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2573-6_0_8_load_107 | 112 | 0.00063943 | 0.00016026 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2573-6_0_8_load_102 | 113 | 0.0063839 | 0.0016 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2573-6_0_8_load_116 | 115 | 0.0011965 | 0.00029988 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2573-6_0_8_load_117 | 116 | 0.0012348 | 0.00030948 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2573-6_0_8_load_112 | 117 | 0.0013383 | 0.00033542 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2573-6_0_8_load_110 | 119 | 0.027794 | 0.0069658 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2573-6_0_8_load_111 | 120 | 0.0011257 | 0.00028214 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2573-6_0_8_load_125 | 121 | 0.0012019 | 0.00030123 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2573-6_0_8_load_119 | 122 | 0.0064016 | 0.0016044 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2573-6_0_8_load_118 | 123 | 0.0012331 | 0.00030906 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2573-6_0_8_load_122 | 124 | 0.00074844 | 0.00018758 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2573-6_0_8_load_123 | 125 | 0.00074579 | 0.00018691 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2573-6_0_8_line_0 |  | 0 | 1 | 0.0058302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2573-6_0_8_line_1 |  | 0 | 2 | 0.0061023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2573-6_0_8_line_2 |  | 1 | 3 | 0.021496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2573-6_0_8_line_3 |  | 2 | 4 | 0.0030653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2573-6_0_8_line_4 |  | 3 | 8 | 0.0061762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2573-6_0_8_line_5 |  | 4 | 9 | 0.01751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2573-6_0_8_line_6 |  | 5 | 6 | 0.03595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2573-6_0_8_line_7 |  | 5 | 7 | 0.049315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2573-6_0_8_line_8 |  | 6 | 52 | 0.065833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2573-6_0_8_line_9 |  | 7 | 56 | 0.0017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2573-6_0_8_line_10 |  | 8 | 10 | 0.01758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2573-6_0_8_line_11 |  | 9 | 11 | 0.011683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2573-6_0_8_line_12 |  | 10 | 12 | 0.00056615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2573-6_0_8_line_13 |  | 11 | 13 | 0.005874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2573-6_0_8_line_14 |  | 12 | 81 | 0.0071812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2573-6_0_8_line_15 |  | 13 | 88 | 0.00021666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2573-6_0_8_line_16 |  | 14 | 15 | 0.010733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2573-6_0_8_line_17 |  | 14 | 16 | 0.018404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2573-6_0_8_line_18 |  | 15 | 17 | 0.010199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2573-6_0_8_line_19 |  | 16 | 18 | 0.024893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2573-6_0_8_line_20 |  | 16 | 19 | 0.0098705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2573-6_0_8_line_21 |  | 17 | 20 | 0.031312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2573-6_0_8_line_22 |  | 19 | 21 | 0.030803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2573-6_0_8_line_23 |  | 20 | 22 | 0.026452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2573-6_0_8_line_24 |  | 20 | 23 | 0.10928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2573-6_0_8_line_25 |  | 21 | 27 | 0.043321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2573-6_0_8_line_26 |  | 21 | 28 | 0.034635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2573-6_0_8_line_27 |  | 22 | 29 | 0.028342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2573-6_0_8_line_28 |  | 22 | 30 | 0.06593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2573-6_0_8_line_29 |  | 23 | 31 | 0.035563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2573-6_0_8_line_30 |  | 24 | 25 | 0.022154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2573-6_0_8_line_31 |  | 24 | 26 | 0.026962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2573-6_0_8_line_32 |  | 25 | 32 | 0.033627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2573-6_0_8_line_33 |  | 26 | 33 | 0.0012623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2573-6_0_8_line_34 |  | 28 | 34 | 0.04823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2573-6_0_8_line_35 |  | 29 | 113 | 0.017413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2573-6_0_8_line_36 |  | 29 | 103 | 0.025827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2573-6_0_8_line_37 |  | 30 | 52 | 0.00019732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2573-6_0_8_line_38 |  | 31 | 108 | 0.00699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2573-6_0_8_line_39 |  | 31 | 109 | 0.0073573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2573-6_0_8_line_40 |  | 32 | 37 | 0.015113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2573-6_0_8_line_41 |  | 33 | 115 | 3.5772e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2573-6_0_8_line_42 |  | 34 | 38 | 0.016959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2573-6_0_8_line_43 |  | 34 | 35 | 0.048631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2573-6_0_8_line_44 |  | 35 | 36 | 0.00012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2573-6_0_8_line_45 |  | 36 | 37 | 0.036011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2573-6_0_8_line_46 |  | 38 | 39 | 0.0011592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2573-6_0_8_line_47 |  | 39 | 40 | 0.055983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2573-6_0_8_line_48 |  | 40 | 41 | 0.083265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2573-6_0_8_line_49 |  | 41 | 107 | 0.049393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2573-6_0_8_line_50 |  | 42 | 43 | 0.0044001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2573-6_0_8_line_51 |  | 42 | 44 | 0.0003834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2573-6_0_8_line_52 |  | 43 | 45 | 0.00038134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2573-6_0_8_line_53 |  | 44 | 46 | 0.0065922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2573-6_0_8_line_54 |  | 45 | 47 | 0.0068647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2573-6_0_8_line_55 |  | 46 | 48 | 0.00043228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2573-6_0_8_line_56 |  | 47 | 49 | 0.00034709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2573-6_0_8_line_57 |  | 48 | 50 | 0.0043346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2573-6_0_8_line_58 |  | 50 | 51 | 0.00043526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2573-6_0_8_line_59 |  | 51 | 95 | 0.0054172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2573-6_0_8_line_60 |  | 53 | 54 | 0.0022142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2573-6_0_8_line_61 |  | 53 | 55 | 0.036217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2573-6_0_8_line_62 |  | 54 | 56 | 0.017105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2573-6_0_8_line_63 |  | 55 | 60 | 0.020503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2573-6_0_8_line_64 |  | 55 | 99 | 0.018263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2573-6_0_8_line_65 |  | 57 | 58 | 0.012866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2573-6_0_8_line_66 |  | 57 | 59 | 0.0017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2573-6_0_8_line_67 |  | 57 | 60 | 0.022345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2573-6_0_8_line_68 |  | 58 | 66 | 0.0048099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2573-6_0_8_line_69 |  | 59 | 61 | 0.0031217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2573-6_0_8_line_70 |  | 61 | 62 | 0.032774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2573-6_0_8_line_71 |  | 62 | 63 | 0.00077513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2573-6_0_8_line_72 |  | 63 | 64 | 0.017435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2573-6_0_8_line_73 |  | 64 | 65 | 0.0093833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2573-6_0_8_line_74 |  | 65 | 79 | 0.008171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2573-6_0_8_line_75 |  | 66 | 78 | 0.00861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2573-6_0_8_line_76 |  | 67 | 68 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2573-6_0_8_line_77 |  | 68 | 69 | 0.032464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2573-6_0_8_line_78 |  | 68 | 70 | 0.015626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2573-6_0_8_line_79 |  | 69 | 71 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2573-6_0_8_line_80 |  | 70 | 72 | 0.011343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2573-6_0_8_line_81 |  | 71 | 73 | 0.026422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2573-6_0_8_line_82 |  | 72 | 74 | 0.015049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2573-6_0_8_line_83 |  | 73 | 75 | 0.021989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2573-6_0_8_line_84 |  | 74 | 86 | 0.007649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2573-6_0_8_line_85 |  | 75 | 76 | 0.026612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2573-6_0_8_line_86 |  | 76 | 77 | 0.01751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2573-6_0_8_line_87 |  | 77 | 83 | 0.031898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2573-6_0_8_line_88 |  | 78 | 105 | 0.024167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2573-6_0_8_line_89 |  | 79 | 80 | 0.0058342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2573-6_0_8_line_90 |  | 80 | 81 | 0.022246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2573-6_0_8_line_91 |  | 82 | 83 | 0.02012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2573-6_0_8_line_92 |  | 83 | 84 | 0.024227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2573-6_0_8_line_93 |  | 84 | 85 | 0.017113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2573-6_0_8_line_94 |  | 85 | 106 | 0.0020093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2573-6_0_8_line_95 |  | 86 | 87 | 0.010048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2573-6_0_8_line_96 |  | 87 | 88 | 0.016434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2573-6_0_8_line_97 |  | 89 | 90 | 0.059334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2573-6_0_8_line_98 |  | 89 | 91 | 0.036084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2573-6_0_8_line_99 |  | 89 | 92 | 0.053905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2573-6_0_8_line_100 |  | 90 | 93 | 0.083959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2573-6_0_8_line_101 |  | 91 | 94 | 0.036444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2573-6_0_8_line_102 |  | 93 | 117 | 0.072006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2573-6_0_8_line_103 |  | 94 | 109 | 0.05451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2573-6_0_8_line_104 |  | 95 | 96 | 0.00042084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2573-6_0_8_line_105 |  | 96 | 97 | 0.014487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2573-6_0_8_line_106 |  | 97 | 98 | 0.0057638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2573-6_0_8_line_107 |  | 98 | 121 | 0.0047801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2573-6_0_8_line_108 |  | 99 | 100 | 0.027589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2573-6_0_8_line_109 |  | 100 | 101 | 0.024954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2573-6_0_8_line_110 |  | 101 | 102 | 0.04978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2573-6_0_8_line_111 |  | 104 | 105 | 0.031317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2573-6_0_8_line_112 |  | 108 | 110 | 0.045159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2573-6_0_8_line_113 |  | 111 | 112 | 0.014499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2573-6_0_8_line_114 |  | 112 | 114 | 0.032748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2573-6_0_8_line_115 |  | 114 | 118 | 0.017844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2573-6_0_8_line_116 |  | 114 | 119 | 0.077191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_2573-6_0_8_line_117 |  | 115 | 116 | 6.8555e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2573-6_0_8_line_118 |  | 116 | 123 | 3.3385e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2573-6_0_8_line_119 |  | 117 | 118 | 0.080978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2573-6_0_8_line_120 |  | 118 | 120 | 0.058171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2573-6_0_8_line_121 |  | 121 | 122 | 0.0091357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2573-6_0_8_line_122 |  | 122 | 124 | 0.25151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2573-6_0_8_line_123 |  | 122 | 123 | 0.022372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2573-6_0_8_line_124 |  | 124 | 125 | 0.029201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2573-6_0_8_trafo_83 | 0.63 MVA 20/0.4 kV | 126 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2639038.8342 | 1244656.4065 | 2639036.1565 | 1244661.5853
1 | 2639038.8342 | 1244656.4065 | 2639041.637 | 1244650.9859 | 2639041.637 | 1244650.9859
2 | 2639036.1565 | 1244661.5853 | 2639026.2836 | 1244680.6797
3 | 2639043.2699 | 1244653.5801 | 2639041.637 | 1244650.9859
4 | 2639026.2836 | 1244680.6797 | 2639023.447 | 1244686.1659
5 | 2639043.2699 | 1244653.5801 | 2639052.5979 | 1244668.3985
6 | 2638977.4681 | 1244568.6885 | 2638970.6506 | 1244603.9864
7 | 2638970.6506 | 1244603.9864 | 2638950.5023 | 1244648.9973
8 | 2638977.4681 | 1244568.6885 | 2638997.6611 | 1244554.4118 | 2638969.6997 | 1244524.2848
9 | 2638950.5023 | 1244648.9973 | 2638949.1388 | 1244650.1048
10 | 2639023.447 | 1244686.1659 | 2639015.8377 | 1244700.8823 | 2639015.3748 | 1244701.7832
11 | 2639058.8218 | 1244678.2858 | 2639052.5979 | 1244668.3985
12 | 2639015.116 | 1244702.2867 | 2639015.3748 | 1244701.7832
13 | 2639058.8218 | 1244678.2858 | 2639061.951 | 1244683.2569
14 | 2639011.8337 | 1244708.6739 | 2639015.116 | 1244702.2867
15 | 2639061.951 | 1244683.2569 | 2639062.0664 | 1244683.4402
16 | 2638865.5682 | 1244534.6694 | 2638868.2976 | 1244531.8045 | 2638873.1781 | 1244527.1037
17 | 2638853.1007 | 1244548.2047 | 2638860.2023 | 1244540.3015 | 2638865.5682 | 1244534.6694
18 | 2638880.5455 | 1244520.0507 | 2638876.4036 | 1244523.9969 | 2638873.1781 | 1244527.1037
19 | 2638853.1007 | 1244548.2047 | 2638849.1012 | 1244545.0987 | 2638845.8044 | 1244541.9973 | 2638841.9982 | 1244538.2033 | 2638836.4033 | 1244531.7959 | 2638835.5023 | 1244530.6952
20 | 2638853.1007 | 1244548.2047 | 2638846.5777 | 1244555.6126
21 | 2638903.9042 | 1244499.2053 | 2638893.5985 | 1244508.2993 | 2638885.0033 | 1244515.8034 | 2638880.5455 | 1244520.0507
22 | 2638827.3702 | 1244579.6902 | 2638834.5991 | 1244570.7984 | 2638845.8001 | 1244556.4956 | 2638846.5777 | 1244555.6126
23 | 2638923.5622 | 1244516.9679 | 2638903.9042 | 1244499.2053
24 | 2638903.9042 | 1244499.2053 | 2638917.5023 | 1244489.299 | 2638933.903 | 1244477.1986 | 2638991.5537 | 1244433.9428
25 | 2638827.3702 | 1244579.6902 | 2638846.2173 | 1244588.586 | 2638862.7604 | 1244603.8072
26 | 2638827.3702 | 1244579.6902 | 2638824.5975 | 1244583.0966 | 2638815.7979 | 1244593.0011 | 2638806.4041 | 1244602.5014 | 2638803.8346 | 1244605.0707
27 | 2638923.5622 | 1244516.9679 | 2638917.8809 | 1244523.7462 | 2638928.9357 | 1244539.8403
28 | 2638923.5622 | 1244516.9679 | 2638944.3369 | 1244496.9577 | 2638969.5655 | 1244524.1402
29 | 2639019.9998 | 1244412.5994 | 2638991.5537 | 1244433.9428
30 | 2638763.0279 | 1244496.7714 | 2638744.1369 | 1244508.4335
31 | 2638763.0279 | 1244496.7714 | 2638749.1318 | 1244473.6659
32 | 2638744.1369 | 1244508.4335 | 2638744.7274 | 1244542.0552
33 | 2638749.1318 | 1244473.6659 | 2638748.4812 | 1244472.5842
34 | 2638767.2091 | 1244636.3342 | 2638777.3152 | 1244628.8175 | 2638783.7036 | 1244622.4995 | 2638790.7988 | 1244616.6976 | 2638799.2015 | 1244609.7035 | 2638803.8346 | 1244605.0707
35 | 2638928.9357 | 1244539.8403 | 2638938.808 | 1244554.2032
36 | 2638928.9357 | 1244539.8403 | 2638913.641 | 1244546.9335 | 2638906.795 | 1244552.7258
37 | 2638969.5655 | 1244524.1402 | 2638969.6997 | 1244524.2848
38 | 2639019.9998 | 1244412.5994 | 2639025.604 | 1244408.4001
39 | 2639019.9998 | 1244412.5994 | 2639022.0006 | 1244414.0023 | 2639023.5986 | 1244414.6021 | 2639024.8976 | 1244414.6996 | 2639026.8018 | 1244414.701
40 | 2638744.7274 | 1244542.0552 | 2638744.9929 | 1244557.1662
41 | 2638748.4812 | 1244472.5842 | 2638748.4628 | 1244472.5535
42 | 2638767.2091 | 1244636.3342 | 2638752.7865 | 1244645.2563
43 | 2638767.2091 | 1244636.3342 | 2638751.3822 | 1244612.7488 | 2638751.151 | 1244592.5228
44 | 2638751.1495 | 1244592.3941 | 2638751.151 | 1244592.5228
45 | 2638744.9929 | 1244557.1662 | 2638745.0789 | 1244562.0635 | 2638751.06 | 1244584.5617 | 2638751.1495 | 1244592.3941
46 | 2638752.7865 | 1244645.2563 | 2638752.0207 | 1244645.7301 | 2638751.7956 | 1244645.8574
47 | 2638705.0855 | 1244676.6219 | 2638714.1142 | 1244670.9215 | 2638723.8131 | 1244664.4249 | 2638733.0046 | 1244658.1141 | 2638741.7975 | 1244651.5116 | 2638751.7956 | 1244645.8574
48 | 2638659.4163 | 1244607.2014 | 2638676.0033 | 1244631.314 | 2638683.6979 | 1244642.5047 | 2638698.8989 | 1244663.6064 | 2638705.0855 | 1244676.6219
49 | 2638659.4163 | 1244607.2014 | 2638693.4824 | 1244571.4363
50 | 2638692.0597 | 1244480.0182 | 2638688.2804 | 1244482.2715
51 | 2638692.389 | 1244479.8218 | 2638692.0597 | 1244480.0182
52 | 2638688.2804 | 1244482.2715 | 2638687.9528 | 1244482.4668
53 | 2638692.389 | 1244479.8218 | 2638698.0511 | 1244476.4459
54 | 2638687.9528 | 1244482.4668 | 2638682.0566 | 1244485.9823
55 | 2638698.4224 | 1244476.2245 | 2638698.0511 | 1244476.4459
56 | 2638682.0566 | 1244485.9823 | 2638681.7585 | 1244486.1601
57 | 2638702.1454 | 1244474.0047 | 2638698.4224 | 1244476.2245
58 | 2638702.5193 | 1244473.7818 | 2638702.1454 | 1244474.0047
59 | 2638707.1721 | 1244471.0076 | 2638702.5193 | 1244473.7818
60 | 2638934.9981 | 1244663.1853 | 2638936.4819 | 1244661.5418
61 | 2638911.6996 | 1244690.9036 | 2638913.901 | 1244688.2052 | 2638929.2028 | 1244669.6044 | 2638934.9981 | 1244663.1853
62 | 2638936.4819 | 1244661.5418 | 2638940.399 | 1244657.2031 | 2638949.1388 | 1244650.1048
63 | 2638911.6996 | 1244690.9036 | 2638919.298 | 1244697.1019 | 2638927.4451 | 1244704.0335
64 | 2638911.6996 | 1244690.9036 | 2638906.0013 | 1244698.0043 | 2638901.1994 | 1244703.1984 | 2638899.6774 | 1244704.6234
65 | 2638944.7974 | 1244718.105 | 2638936.6999 | 1244728.1029 | 2638936.6999 | 1244728.1029
66 | 2638944.7974 | 1244718.105 | 2638946.2003 | 1244719.2319
67 | 2638944.7974 | 1244718.105 | 2638934.1005 | 1244709.696 | 2638927.4451 | 1244704.0335
68 | 2638933.4494 | 1244731.6483 | 2638936.6999 | 1244728.1029
69 | 2638946.2003 | 1244719.2319 | 2638948.3977 | 1244720.9972 | 2638948.6401 | 1244721.179
70 | 2638948.6401 | 1244721.179 | 2638958.3978 | 1244728.501 | 2638969.6984 | 1244737.0029 | 2638974.9021 | 1244740.7845
71 | 2638975.5291 | 1244741.2402 | 2638974.9021 | 1244740.7845
72 | 2638990.8353 | 1244749.1829 | 2638982.4974 | 1244746.3041 | 2638975.5291 | 1244741.2402
73 | 2638990.8353 | 1244749.1829 | 2638991.8356 | 1244747.5885 | 2638995.2641 | 1244740.9169
74 | 2638998.9988 | 1244733.6493 | 2638995.2641 | 1244740.9169
75 | 2638927.6355 | 1244737.9988 | 2638927.8034 | 1244737.8064 | 2638933.4494 | 1244731.6483
76 | 2639102.6326 | 1244747.8838 | 2639121.3438 | 1244739.8214
77 | 2639102.6326 | 1244747.8838 | 2639087.0759 | 1244755.7866 | 2639075.3001 | 1244762.1021 | 2639073.8408 | 1244762.8776
78 | 2639102.6326 | 1244747.8838 | 2639094.3082 | 1244734.6597
79 | 2639057.6371 | 1244771.8225 | 2639060.9998 | 1244769.7019 | 2639073.8408 | 1244762.8776
80 | 2639094.3082 | 1244734.6597 | 2639088.2654 | 1244725.0601
81 | 2639057.6371 | 1244771.8225 | 2639046.0984 | 1244779.0989 | 2639035.1614 | 1244785.7123
82 | 2639080.2487 | 1244712.3246 | 2639088.2654 | 1244725.0601
83 | 2639017.3461 | 1244798.5809 | 2639021.397 | 1244795.4027 | 2639033.2022 | 1244786.897 | 2639035.1614 | 1244785.7123
84 | 2639076.1739 | 1244705.8514 | 2639080.2487 | 1244712.3246
85 | 2638996.225 | 1244814.768 | 2639008.9033 | 1244805.2048 | 2639017.3461 | 1244798.5809
86 | 2638982.7975 | 1244826.0025 | 2638994.5973 | 1244815.9957 | 2638996.225 | 1244814.768
87 | 2638982.7975 | 1244826.0025 | 2638975.2006 | 1244817.3025 | 2638968.1994 | 1244811.097 | 2638963.8036 | 1244807.3991 | 2638961.0375 | 1244802.8891
88 | 2638910.8571 | 1244755.3565 | 2638916.3039 | 1244750.406 | 2638922.3982 | 1244743.9973 | 2638927.6355 | 1244737.9988
89 | 2638998.9988 | 1244733.6493 | 2639001.6655 | 1244728.4603
90 | 2639011.8337 | 1244708.6739 | 2639001.6655 | 1244728.4603
91 | 2638961.0375 | 1244802.8891 | 2638970.9323 | 1244785.3708
92 | 2638961.0375 | 1244802.8891 | 2638960.036 | 1244804.6837 | 2638955.8347 | 1244810.4821 | 2638954.2348 | 1244812.4841 | 2638948.3331 | 1244817.1817 | 2638944.5829 | 1244820.3433
93 | 2638931.3676 | 1244831.2096 | 2638935.037 | 1244828.3908 | 2638944.5829 | 1244820.3433
94 | 2638931.3676 | 1244831.2096 | 2638929.7742 | 1244832.4337
95 | 2639076.1739 | 1244705.8514 | 2639070.8213 | 1244697.3482
96 | 2639070.8213 | 1244697.3482 | 2639062.0664 | 1244683.4402
97 | 2639100.7817 | 1244505.847 | 2639140.8219 | 1244488.6551 | 2639155.7315 | 1244483.5496
98 | 2639100.7817 | 1244505.847 | 2639082.4039 | 1244474.7932
99 | 2639100.7817 | 1244505.847 | 2639054.5476 | 1244533.5626
100 | 2639235.7107 | 1244458.0502 | 2639188.8593 | 1244472.2056 | 2639155.7315 | 1244483.5496
101 | 2639082.4039 | 1244474.7932 | 2639068.7971 | 1244451.8013 | 2639064.0068 | 1244443.3352
102 | 2639235.7107 | 1244458.0502 | 2639233.4999 | 1244452.999 | 2639229.2993 | 1244444.8993 | 2639220.9023 | 1244429.2002 | 2639209.4977 | 1244407.7999 | 2639202.3635 | 1244394.2481
103 | 2639064.0068 | 1244443.3352 | 2639057.1972 | 1244431.3005 | 2639049.9006 | 1244419.4003 | 2639047.6038 | 1244415.9052 | 2639045.6008 | 1244413.7017 | 2639043.697 | 1244412.4995 | 2639041.8037 | 1244411.9978 | 2639039.1974 | 1244411.9028 | 2639034.2043 | 1244412.8039 | 2639029.1991 | 1244414.4054 | 2639026.8018 | 1244414.701
104 | 2638707.5336 | 1244470.7921 | 2638707.1721 | 1244471.0076
105 | 2638707.5336 | 1244470.7921 | 2638719.9771 | 1244463.3729
106 | 2638724.9277 | 1244460.4212 | 2638719.9771 | 1244463.3729
107 | 2638724.9277 | 1244460.4212 | 2638729.0334 | 1244457.9732
108 | 2638877.266 | 1244720.5887 | 2638880.9036 | 1244718.2976 | 2638895.1022 | 1244708.9066 | 2638899.6774 | 1244704.6234
109 | 2638855.7978 | 1244733.2931 | 2638867.3984 | 1244726.8036 | 2638877.266 | 1244720.5887
110 | 2638855.7978 | 1244733.2931 | 2638834.9471 | 1244688.0907
111 | 2638884.3736 | 1244771.9327 | 2638890.5017 | 1244768.7044 | 2638902.0003 | 1244761.9976 | 2638909.5997 | 1244756.4993 | 2638910.8571 | 1244755.3565
112 | 2639025.604 | 1244408.4001 | 2639021.7007 | 1244403.3045 | 2639016.1009 | 1244396.4966 | 2638998.8041 | 1244379.3051 | 2638995 | 1244375.1997
113 | 2639104.9486 | 1244347.1194 | 2639116.4238 | 1244338.2566
114 | 2639141.6037 | 1244317.4042 | 2639138.5978 | 1244320.5976 | 2639136.4001 | 1244322.7067 | 2639133.2018 | 1244325.2984 | 2639116.4238 | 1244338.2566
115 | 2639141.6037 | 1244317.4042 | 2639146.9006 | 1244321.9976 | 2639154.8997 | 1244329.344
116 | 2639141.6037 | 1244317.4042 | 2639133.8043 | 1244310.704 | 2639119.0995 | 1244298.0989 | 2639107.6043 | 1244291.4966 | 2639096.6035 | 1244286.6989 | 2639082.7993 | 1244281.9049 | 2639075.4296 | 1244279.7801
117 | 2638748.4628 | 1244472.5535 | 2638748.4274 | 1244472.4948
118 | 2638748.4274 | 1244472.4948 | 2638748.4102 | 1244472.4662
119 | 2639154.8997 | 1244329.344 | 2639159.0983 | 1244333.1965 | 2639168.3011 | 1244342.4965 | 2639177.4039 | 1244353.1969 | 2639182.7989 | 1244360.1037 | 2639187.3035 | 1244366.8044 | 2639194.6022 | 1244379.5053 | 2639202.3635 | 1244394.2481
120 | 2639154.8997 | 1244329.344 | 2639189.4781 | 1244331.5736 | 2639212.6019 | 1244335.8755
121 | 2638736.8802 | 1244453.2947 | 2638729.0334 | 1244457.9732
122 | 2638736.8802 | 1244453.2947 | 2638664.1707 | 1244212.5262
123 | 2638736.8802 | 1244453.2947 | 2638736.8802 | 1244453.2947 | 2638748.4102 | 1244472.4662
124 | 2638664.1707 | 1244212.5262 | 2638666.8969 | 1244210.5027 | 2638675.4021 | 1244206.3999 | 2638680.5969 | 1244204.6993 | 2638687.1041 | 1244203.3964 | 2638691.3165 | 1244202.757

## bus_geodata
| x | y | coords
0 | 2639038.8342 | 1244656.4065
1 | 2639036.1565 | 1244661.5853
2 | 2639041.637 | 1244650.9859
3 | 2639026.2836 | 1244680.6797
4 | 2639043.2699 | 1244653.5801
5 | 2638970.6506 | 1244603.9864
6 | 2638977.4681 | 1244568.6885
7 | 2638950.5023 | 1244648.9973
8 | 2639023.447 | 1244686.1659
9 | 2639052.5979 | 1244668.3985
10 | 2639015.3748 | 1244701.7832
11 | 2639058.8218 | 1244678.2858
12 | 2639015.116 | 1244702.2867
13 | 2639061.951 | 1244683.2569
14 | 2638865.5682 | 1244534.6694
15 | 2638873.1781 | 1244527.1037
16 | 2638853.1007 | 1244548.2047
17 | 2638880.5455 | 1244520.0507
18 | 2638835.5023 | 1244530.6952
19 | 2638846.5777 | 1244555.6126
20 | 2638903.9042 | 1244499.2053
21 | 2638827.3702 | 1244579.6902
22 | 2638923.5622 | 1244516.9679
23 | 2638991.5537 | 1244433.9428
24 | 2638763.0279 | 1244496.7714
25 | 2638744.1369 | 1244508.4335
26 | 2638749.1318 | 1244473.6659
27 | 2638862.7604 | 1244603.8072
28 | 2638803.8346 | 1244605.0707
29 | 2638928.9357 | 1244539.8403
30 | 2638969.5655 | 1244524.1402
31 | 2639019.9998 | 1244412.5994
32 | 2638744.7274 | 1244542.0552
33 | 2638748.4812 | 1244472.5842
34 | 2638767.2091 | 1244636.3342
35 | 2638751.151 | 1244592.5228
36 | 2638751.1495 | 1244592.3941
37 | 2638744.9929 | 1244557.1662
38 | 2638752.7865 | 1244645.2563
39 | 2638751.7956 | 1244645.8574
40 | 2638705.0855 | 1244676.6219
41 | 2638659.4163 | 1244607.2014
42 | 2638692.0597 | 1244480.0182
43 | 2638688.2804 | 1244482.2715
44 | 2638692.389 | 1244479.8218
45 | 2638687.9528 | 1244482.4668
46 | 2638698.0511 | 1244476.4459
47 | 2638682.0566 | 1244485.9823
48 | 2638698.4224 | 1244476.2245
49 | 2638681.7585 | 1244486.1601
50 | 2638702.1454 | 1244474.0047
51 | 2638702.5193 | 1244473.7818
52 | 2638969.6997 | 1244524.2848
53 | 2638934.9981 | 1244663.1853
54 | 2638936.4819 | 1244661.5418
55 | 2638911.6996 | 1244690.9036
56 | 2638949.1388 | 1244650.1048
57 | 2638944.7974 | 1244718.105
58 | 2638936.6999 | 1244728.1029
59 | 2638946.2003 | 1244719.232
60 | 2638927.4451 | 1244704.0335
61 | 2638948.6401 | 1244721.179
62 | 2638974.9021 | 1244740.7845
63 | 2638975.5291 | 1244741.2402
64 | 2638990.8353 | 1244749.1829
65 | 2638995.2641 | 1244740.9169
66 | 2638933.4494 | 1244731.6482
67 | 2639121.3438 | 1244739.8214
68 | 2639102.6326 | 1244747.8838
69 | 2639073.8408 | 1244762.8776
70 | 2639094.3082 | 1244734.6597
71 | 2639057.6371 | 1244771.8225
72 | 2639088.2654 | 1244725.0601
73 | 2639035.1614 | 1244785.7123
74 | 2639080.2487 | 1244712.3246
75 | 2639017.3461 | 1244798.5809
76 | 2638996.225 | 1244814.768
77 | 2638982.7975 | 1244826.0025
78 | 2638927.6355 | 1244737.9988
79 | 2638998.9988 | 1244733.6493
80 | 2639001.6655 | 1244728.4603
81 | 2639011.8337 | 1244708.6739
82 | 2638970.9323 | 1244785.3708
83 | 2638961.0375 | 1244802.8891
84 | 2638944.5829 | 1244820.3433
85 | 2638931.3676 | 1244831.2096
86 | 2639076.1739 | 1244705.8514
87 | 2639070.8213 | 1244697.3482
88 | 2639062.0664 | 1244683.4402
89 | 2639100.7817 | 1244505.847
90 | 2639155.7315 | 1244483.5496
91 | 2639082.4039 | 1244474.7932
92 | 2639054.5476 | 1244533.5626
93 | 2639235.7107 | 1244458.0502
94 | 2639064.0068 | 1244443.3352
95 | 2638707.1721 | 1244471.0076
96 | 2638707.5336 | 1244470.7921
97 | 2638719.9771 | 1244463.3729
98 | 2638724.9277 | 1244460.4212
99 | 2638899.6774 | 1244704.6234
100 | 2638877.266 | 1244720.5887
101 | 2638855.7978 | 1244733.2931
102 | 2638834.9471 | 1244688.0907
103 | 2638906.795 | 1244552.7258
104 | 2638884.3736 | 1244771.9327
105 | 2638910.8571 | 1244755.3565
106 | 2638929.7742 | 1244832.4337
107 | 2638693.4824 | 1244571.4363
108 | 2639025.604 | 1244408.4001
109 | 2639026.8018 | 1244414.701
110 | 2638995 | 1244375.1997
111 | 2639104.9486 | 1244347.1194
112 | 2639116.4238 | 1244338.2566
113 | 2638938.808 | 1244554.2032
114 | 2639141.6037 | 1244317.4042
115 | 2638748.4628 | 1244472.5535
116 | 2638748.4274 | 1244472.4948
117 | 2639202.3635 | 1244394.2481
118 | 2639154.8997 | 1244329.344
119 | 2639075.4296 | 1244279.7801
120 | 2639212.6019 | 1244335.8755
121 | 2638729.0334 | 1244457.9732
122 | 2638736.8802 | 1244453.2947
123 | 2638748.4102 | 1244472.4662
124 | 2638664.1707 | 1244212.5262
125 | 2638691.3165 | 1244202.757
126 | 2638951.0982 | 1244543.3877

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97693 | -0.44329 | 0.0019052 | 0.00047748
1 | 0.9772 | -0.43801 | 0.0018978 | 0.00047563
2 | 0.97666 | -0.4486 | 0.0043196 | 0.0010826
3 | 0.97823 | -0.41785 | 0.0027002 | 0.00067674
4 | 0.97654 | -0.45103 | 0.0023166 | 0.00058059
5 | 0.99709 | -0.054973 | 0.0014426 | 0.00036156
6 | 0.99831 | -0.031814 | 0 | 0
7 | 0.9946 | -0.10218 | 0.0059178 | 0.0014832
8 | 0.97854 | -0.41176 | 0.0018834 | 0.00047203
9 | 0.97587 | -0.46416 | 0.0023166 | 0.00058059
10 | 0.97946 | -0.39384 | 0.003361 | 0.00084234
11 | 0.97545 | -0.47244 | 0.0016596 | 0.00041594
12 | 0.97949 | -0.39323 | 0.0017008 | 0.00042625
13 | 0.97525 | -0.47643 | 0.0016584 | 0.00041564
14 | 0.988 | -0.22776 | 0.00256 | 0.0006416
15 | 0.98833 | -0.22155 | 0.0030493 | 0.00076423
16 | 0.98746 | -0.23821 | 0 | 0
17 | 0.98864 | -0.21551 | 0.0046839 | 0.0011739
18 | 0.98685 | -0.25022 | 0.026963 | 0.0067576
19 | 0.98723 | -0.24263 | 0.010618 | 0.002661
20 | 0.98964 | -0.19635 | 0 | 0
21 | 0.98595 | -0.26733 | 0 | 0
22 | 0.99256 | -0.14045 | 0 | 0
23 | 0.98102 | -0.36259 | 0.057421 | 0.014391
24 | 0.9727 | -0.52574 | 0 | 0
25 | 0.97341 | -0.51178 | 0 | 0
26 | 0.97184 | -0.54277 | 0.0014419 | 0.00036136
27 | 0.98567 | -0.27271 | 0.0069249 | 0.0017355
28 | 0.98329 | -0.31877 | 0.0086246 | 0.0021615
29 | 0.99233 | -0.14491 | 0 | 0
30 | 1 | 0 | -0.61207 | -0.15776
31 | 0.97869 | -0.40802 | 0 | 0
32 | 0.97448 | -0.49061 | 0.0087594 | 0.0021953
33 | 0.9718 | -0.54353 | 0.0011781 | 0.00029527
34 | 0.97996 | -0.38331 | 0 | 0
35 | 0.97684 | -0.44443 | 0.0086198 | 0.0021603
36 | 0.97683 | -0.44457 | 0.0086192 | 0.0021602
37 | 0.97509 | -0.47869 | 0.0087708 | 0.0021982
38 | 0.97989 | -0.38484 | 0.0016343 | 0.00040961
39 | 0.97988 | -0.38491 | 0.0016073 | 0.00040283
40 | 0.97979 | -0.38666 | 0 | 0
41 | 0.97966 | -0.38925 | 0 | 0
42 | 0.97048 | -0.56972 | 0.0012845 | 0.00032192
43 | 0.97046 | -0.57015 | 0.00079537 | 0.00019934
44 | 0.97048 | -0.56967 | 0.0011959 | 0.00029973
45 | 0.97045 | -0.57019 | 0.0012454 | 0.00031213
46 | 0.97053 | -0.56871 | 0.0012709 | 0.00031851
47 | 0.97043 | -0.57061 | 0.0013005 | 0.00032593
48 | 0.97053 | -0.56864 | 0.0012008 | 0.00030096
49 | 0.97043 | -0.57063 | 0.0020466 | 0.00051293
50 | 0.97057 | -0.56781 | 0.0012556 | 0.00031467
51 | 0.97058 | -0.56771 | 0.0011742 | 0.00029429
52 | 0.99999 | -9.705e-05 | 0.0024928 | 0.00062474
53 | 0.99264 | -0.13963 | 0.0021043 | 0.00052738
54 | 0.99284 | -0.13573 | 0.00095011 | 0.00023812
55 | 0.98936 | -0.20229 | 0 | 0
56 | 0.99443 | -0.10536 | 0.0024593 | 0.00061637
57 | 0.98614 | -0.26423 | 0 | 0
58 | 0.98606 | -0.26586 | 0.0015764 | 0.00039507
59 | 0.98602 | -0.26657 | 0.0016013 | 0.00040131
60 | 0.9878 | -0.23235 | 0.0024867 | 0.00062322
61 | 0.98581 | -0.27055 | 0.0025353 | 0.0006354
62 | 0.98372 | -0.31092 | 0.0012348 | 0.00030947
63 | 0.98368 | -0.31186 | 0.0012361 | 0.00030979
64 | 0.9826 | -0.33263 | 0 | 0
65 | 0.98203 | -0.34383 | 0.0012524 | 0.00031388
66 | 0.98603 | -0.26633 | 0.00091911 | 0.00023035
67 | 0.97323 | -0.51605 | 0.0018305 | 0.00045876
68 | 0.97327 | -0.51536 | 0 | 0
69 | 0.97263 | -0.52802 | 0.0020359 | 0.00051024
70 | 0.9736 | -0.50875 | 0.0016302 | 0.00040857
71 | 0.9723 | -0.53455 | 0.0029245 | 0.00073295
72 | 0.97386 | -0.50361 | 0.0020354 | 0.00051012
73 | 0.9719 | -0.54245 | 0.0027415 | 0.00068707
74 | 0.97424 | -0.49623 | 0.0020358 | 0.00051022
75 | 0.97162 | -0.54792 | 0.0040626 | 0.0010182
76 | 0.97139 | -0.55254 | 0.0018461 | 0.00046267
77 | 0.97126 | -0.55499 | 0 | 0
78 | 0.986 | -0.26703 | 0.0017328 | 0.00043428
79 | 0.98154 | -0.35341 | 0.0012357 | 0.00030969
80 | 0.98119 | -0.36012 | 0.001234 | 0.00030926
81 | 0.9799 | -0.38526 | 0.0012365 | 0.0003099
82 | 0.971 | -0.56015 | 0.0018804 | 0.00047128
83 | 0.97104 | -0.55945 | 0.0020565 | 0.00051541
84 | 0.97096 | -0.56107 | 0.0012311 | 0.00030855
85 | 0.97092 | -0.56183 | 0.0014415 | 0.00036128
86 | 0.97444 | -0.4922 | 0.0020358 | 0.00051022
87 | 0.97473 | -0.48653 | 0.0023165 | 0.00058057
88 | 0.97524 | -0.47657 | 0.0023179 | 0.00058092
89 | 0.97483 | -0.48398 | 0 | 0
90 | 0.97435 | -0.49341 | 0.0023281 | 0.00058349
91 | 0.97522 | -0.47614 | 0.094897 | 0.023783
92 | 0.97419 | -0.4966 | 0.012763 | 0.0031988
93 | 0.97372 | -0.50586 | 0 | 0
94 | 0.97643 | -0.4524 | 0.012824 | 0.0032139
95 | 0.97064 | -0.56643 | 0.0015375 | 0.00038532
96 | 0.97065 | -0.56632 | 0.0014425 | 0.00036153
97 | 0.97086 | -0.5621 | 0.0019234 | 0.00048205
98 | 0.97096 | -0.56022 | 0.0011814 | 0.00029609
99 | 0.98911 | -0.20726 | 0.0015745 | 0.0003946
100 | 0.98876 | -0.21399 | 0.0012163 | 0.00030483
101 | 0.98847 | -0.21954 | 0.0009588 | 0.0002403
102 | 0.98795 | -0.22977 | 0.011517 | 0.0028864
103 | 0.99228 | -0.14605 | 0.0024963 | 0.00062564
104 | 0.9859 | -0.26895 | 0.0012243 | 0.00030683
105 | 0.98594 | -0.26826 | 0.0016023 | 0.00040156
106 | 0.97092 | -0.56186 | 0.00094972 | 0.00023802
107 | 0.97958 | -0.39079 | 0.0017144 | 0.00042968
108 | 0.97799 | -0.42177 | 0 | 0
109 | 0.9784 | -0.41383 | 0.018355 | 0.0046001
110 | 0.97345 | -0.51106 | 0.108 | 0.027068
111 | 0.97239 | -0.53212 | 0.0013695 | 0.00034324
112 | 0.9724 | -0.53175 | 0.00063943 | 0.00016026
113 | 0.99223 | -0.14687 | 0.0063839 | 0.0016
114 | 0.97247 | -0.53054 | 0 | 0
115 | 0.9718 | -0.54356 | 0.0011965 | 0.00029988
116 | 0.9718 | -0.54359 | 0.0012348 | 0.00030948
117 | 0.97317 | -0.51655 | 0.0013383 | 0.00033542
118 | 0.97259 | -0.52809 | 0 | 0
119 | 0.97146 | -0.55033 | 0.027794 | 0.0069658
120 | 0.97253 | -0.5293 | 0.0011257 | 0.00028214
121 | 0.97104 | -0.55855 | 0.0012019 | 0.00030123
122 | 0.97121 | -0.55516 | 0.0064016 | 0.0016044
123 | 0.9718 | -0.54361 | 0.0012331 | 0.00030906
124 | 0.97086 | -0.56213 | 0.00074844 | 0.00018758
125 | 0.97084 | -0.56254 | 0.00074579 | 0.00018691
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.049699 | -0.01251 | 0.049712 | 0.012518 | 1.2535e-05 | 7.9493e-06 | 0.075719 | 0.075719 | 0.075719 | 0.97693 | -0.44329 | 0.9772 | -0.43801 | 20.802
1 | 0.047794 | 0.012033 | -0.047782 | -0.012025 | 1.2134e-05 | 7.6891e-06 | 0.072817 | 0.072817 | 0.072817 | 0.97693 | -0.44329 | 0.97666 | -0.4486 | 20.0048
2 | -0.05161 | -0.012994 | 0.051659 | 0.013025 | 4.9811e-05 | 3.161e-05 | 0.078609 | 0.078609 | 0.078609 | 0.9772 | -0.43801 | 0.97823 | -0.41785 | 21.5959
3 | 0.043462 | 0.010942 | -0.043457 | -0.010939 | 5.0431e-06 | 3.1892e-06 | 0.066236 | 0.066236 | 0.066236 | 0.97666 | -0.4486 | 0.97654 | -0.45103 | 18.1967
4 | -0.05436 | -0.013702 | 0.054376 | 0.013712 | 1.5846e-05 | 1.0064e-05 | 0.082716 | 0.082716 | 0.082716 | 0.97823 | -0.41785 | 0.97854 | -0.41176 | 22.7242
5 | 0.041141 | 0.010359 | -0.041115 | -0.010342 | 2.5819e-05 | 1.6305e-05 | 0.062706 | 0.062706 | 0.062706 | 0.97654 | -0.45103 | 0.97587 | -0.46416 | 17.227
6 | -0.11203 | -0.028722 | 0.11215 | 0.028801 | 0.00012595 | 7.92e-05 | 0.16741 | 0.16741 | 0.16741 | 0.99709 | -0.054973 | 0.99831 | -0.031814 | 15.331
7 | 0.11058 | 0.02836 | -0.11033 | -0.0282 | 0.00025254 | 0.00016034 | 0.16526 | 0.16526 | 0.16526 | 0.99709 | -0.054973 | 0.9946 | -0.10218 | 22.7009
8 | -0.11215 | -0.028801 | 0.11233 | 0.028909 | 0.00017298 | 0.00010726 | 0.16741 | 0.16741 | 0.16741 | 0.99831 | -0.031814 | 0.99999 | -9.705e-05 | 11.4982
9 | 0.10441 | 0.026717 | -0.1044 | -0.026707 | 1.6115e-05 | 1.0291e-05 | 0.15641 | 0.15641 | 0.15641 | 0.9946 | -0.10218 | 0.99443 | -0.10536 | 42.9695
10 | -0.056259 | -0.014184 | 0.056307 | 0.014215 | 4.8283e-05 | 3.068e-05 | 0.08558 | 0.08558 | 0.08558 | 0.97854 | -0.41176 | 0.97946 | -0.39384 | 23.511
11 | 0.038798 | 0.0097616 | -0.038783 | -0.009752 | 1.5341e-05 | 9.6723e-06 | 0.059174 | 0.059174 | 0.059174 | 0.97587 | -0.46416 | 0.97545 | -0.47244 | 16.2566
12 | -0.059668 | -0.015057 | 0.05967 | 0.015058 | 1.746e-06 | 1.1103e-06 | 0.090686 | 0.090686 | 0.090686 | 0.97946 | -0.39384 | 0.97949 | -0.39323 | 24.9138
13 | 0.037123 | 0.009336 | -0.037116 | -0.0093316 | 7.0672e-06 | 4.4497e-06 | 0.056642 | 0.056642 | 0.056642 | 0.97545 | -0.47244 | 0.97525 | -0.47643 | 15.5611
14 | -0.061371 | -0.015484 | 0.061394 | 0.015499 | 2.3427e-05 | 1.4903e-05 | 0.09327 | 0.09327 | 0.09327 | 0.97949 | -0.39323 | 0.9799 | -0.38526 | 25.6236
15 | 0.035458 | 0.0089159 | -0.035458 | -0.0089158 | 2.379e-07 | 1.4955e-07 | 0.054112 | 0.054112 | 0.054112 | 0.97525 | -0.47643 | 0.97524 | -0.47657 | 14.8659
16 | -0.13073 | -0.033169 | 0.13077 | 0.033193 | 3.9064e-05 | 2.4451e-05 | 0.19703 | 0.19703 | 0.19703 | 0.988 | -0.22776 | 0.98833 | -0.22155 | 13.5324
17 | 0.12817 | 0.032527 | -0.1281 | -0.032487 | 6.4387e-05 | 4.0265e-05 | 0.19318 | 0.19318 | 0.19318 | 0.988 | -0.22776 | 0.98746 | -0.23821 | 13.2676
18 | -0.13382 | -0.033957 | 0.13386 | 0.033982 | 3.887e-05 | 2.4354e-05 | 0.20162 | 0.20162 | 0.20162 | 0.98833 | -0.22155 | 0.98864 | -0.21551 | 13.8477
19 | 0.026979 | 0.0067672 | -0.026963 | -0.0067576 | 1.543e-05 | 9.5571e-06 | 0.040656 | 0.040657 | 0.040657 | 0.98746 | -0.23821 | 0.98685 | -0.25022 | 11.1694
20 | 0.10113 | 0.02572 | -0.1011 | -0.025706 | 2.1526e-05 | 1.3272e-05 | 0.15252 | 0.15252 | 0.15252 | 0.98746 | -0.23821 | 0.98723 | -0.24263 | 10.4753
21 | -0.13854 | -0.035156 | 0.13867 | 0.035236 | 0.00012782 | 8.0199e-05 | 0.20867 | 0.20867 | 0.20867 | 0.98864 | -0.21551 | 0.98964 | -0.19635 | 14.3319
22 | 0.090486 | 0.023045 | -0.090378 | -0.022977 | 0.00010764 | 6.8102e-05 | 0.13652 | 0.13652 | 0.13652 | 0.98723 | -0.24263 | 0.98595 | -0.26733 | 18.7524
23 | -0.48203 | -0.12301 | 0.48334 | 0.12385 | 0.0013055 | 0.00083418 | 0.72557 | 0.72557 | 0.72557 | 0.98964 | -0.19635 | 0.99256 | -0.14045 | 49.8332
24 | 0.34337 | 0.087776 | -0.34063 | -0.086029 | 0.0027373 | 0.0017463 | 0.5169 | 0.5169 | 0.5169 | 0.98964 | -0.19635 | 0.98102 | -0.36259 | 35.5015
25 | 0.0069266 | 0.0017361 | -0.0069249 | -0.0017355 | 1.7754e-06 | 5.8392e-07 | 0.010454 | 0.010454 | 0.010454 | 0.98595 | -0.26733 | 0.98567 | -0.27271 | 2.872
26 | 0.083452 | 0.021241 | -0.083245 | -0.02111 | 0.00020641 | 0.00013166 | 0.12606 | 0.12606 | 0.12606 | 0.98595 | -0.26733 | 0.98329 | -0.31877 | 34.633
27 | 0.0088829 | 0.0022264 | -0.008881 | -0.0022255 | 1.8848e-06 | 8.4007e-07 | 0.013317 | 0.013317 | 0.013317 | 0.99256 | -0.14045 | 0.99233 | -0.14491 | 3.6585
28 | -0.49222 | -0.12607 | 0.4956 | 0.12823 | 0.0033745 | 0.0021563 | 0.73889 | 0.73889 | 0.73889 | 0.99256 | -0.14045 | 1 | 0 | 50.7478
29 | 0.28321 | 0.071638 | -0.28259 | -0.071246 | 0.00061591 | 0.00039239 | 0.42981 | 0.42981 | 0.42981 | 0.98102 | -0.36259 | 0.97869 | -0.40802 | 29.5197
30 | -0.034293 | -0.0086118 | 0.034316 | 0.0086261 | 2.287e-05 | 1.4361e-05 | 0.052467 | 0.052467 | 0.052467 | 0.9727 | -0.52574 | 0.97341 | -0.51178 | 14.414
31 | 0.034293 | 0.0086118 | -0.034265 | -0.0085943 | 2.7833e-05 | 1.7479e-05 | 0.052467 | 0.052467 | 0.052467 | 0.9727 | -0.52574 | 0.97184 | -0.54277 | 14.4141
32 | -0.034316 | -0.0086261 | 0.034351 | 0.0086479 | 3.4713e-05 | 2.1798e-05 | 0.052467 | 0.052467 | 0.052467 | 0.97341 | -0.51178 | 0.97448 | -0.49061 | 14.414
33 | 0.032823 | 0.0082329 | -0.032822 | -0.0082322 | 1.1958e-06 | 7.4965e-07 | 0.05026 | 0.05026 | 0.05026 | 0.97184 | -0.54277 | 0.9718 | -0.54353 | 13.8076
34 | 0.074621 | 0.018948 | -0.07439 | -0.018801 | 0.00023099 | 0.00014723 | 0.11301 | 0.11301 | 0.11301 | 0.98329 | -0.31877 | 0.97996 | -0.38331 | 31.0474
35 | 0.0063845 | 0.0016001 | -0.0063839 | -0.0016 | 5.9851e-07 | 1.5811e-07 | 0.0095737 | 0.0095738 | 0.0095738 | 0.99233 | -0.14491 | 0.99223 | -0.14687 | 2.6302
36 | 0.0024965 | 0.0006254 | -0.0024963 | -0.00062564 | 1.3572e-07 | -2.4678e-07 | 0.0037434 | 0.0037435 | 0.0037435 | 0.99233 | -0.14491 | 0.99228 | -0.14605 | 1.0284
37 | 0.11482 | 0.029534 | -0.11482 | -0.029533 | 5.417e-07 | 3.3633e-07 | 0.17112 | 0.17112 | 0.17112 | 1 | 0 | 0.99999 | -9.705e-05 | 11.7529
38 | 0.10854 | 0.027409 | -0.10847 | -0.027363 | 7.1447e-05 | 4.5638e-05 | 0.1651 | 0.1651 | 0.1651 | 0.97869 | -0.40802 | 0.97799 | -0.42177 | 45.356
39 | 0.17405 | 0.043837 | -0.17401 | -0.043807 | 4.8332e-05 | 3.0563e-05 | 0.26471 | 0.26471 | 0.26471 | 0.97869 | -0.40802 | 0.9784 | -0.41383 | 18.1807
40 | -0.04311 | -0.010843 | 0.043135 | 0.010859 | 2.457e-05 | 1.5536e-05 | 0.065842 | 0.065842 | 0.065842 | 0.97448 | -0.49061 | 0.97509 | -0.47869 | 18.0885
41 | 0.031644 | 0.0079369 | -0.031644 | -0.0079369 | 3.1499e-08 | 1.9714e-08 | 0.048456 | 0.048456 | 0.048456 | 0.9718 | -0.54353 | 0.9718 | -0.54356 | 13.312
42 | 0.0049569 | 0.0012401 | -0.0049566 | -0.00124 | 3.6022e-07 | 1.6892e-08 | 0.007526 | 0.0075261 | 0.0075261 | 0.97996 | -0.38331 | 0.97989 | -0.38484 | 2.0676
43 | 0.069433 | 0.017561 | -0.06923 | -0.017432 | 0.00020293 | 0.00012926 | 0.10549 | 0.10549 | 0.10549 | 0.97996 | -0.38331 | 0.97684 | -0.44443 | 28.9799
44 | 0.06061 | 0.015271 | -0.06061 | -0.015271 | 4.1149e-07 | 2.6174e-07 | 0.092356 | 0.092356 | 0.092356 | 0.97684 | -0.44443 | 0.97683 | -0.44457 | 25.3726
45 | 0.05199 | 0.013111 | -0.051906 | -0.013057 | 8.4763e-05 | 5.3798e-05 | 0.079227 | 0.079227 | 0.079227 | 0.97683 | -0.44457 | 0.97509 | -0.47869 | 21.7656
46 | 0.0033222 | 0.00083043 | -0.0033222 | -0.00083044 | 1.1061e-08 | -7.5235e-09 | 0.0050442 | 0.0050442 | 0.0050442 | 0.97989 | -0.38484 | 0.97988 | -0.38491 | 1.3858
47 | 0.0017149 | 0.00042761 | -0.0017148 | -0.00042822 | 1.423e-07 | -6.1406e-07 | 0.0026034 | 0.0026037 | 0.0026037 | 0.97988 | -0.38491 | 0.97979 | -0.38666 | 0.7153
48 | 0.0017148 | 0.00042822 | -0.0017146 | -0.00042914 | 2.1171e-07 | -9.1305e-07 | 0.0026037 | 0.0026041 | 0.0026041 | 0.97979 | -0.38666 | 0.97966 | -0.38925 | 0.7154
49 | 0.0017146 | 0.00042914 | -0.0017144 | -0.00042968 | 1.2561e-07 | -5.4147e-07 | 0.0026041 | 0.0026043 | 0.0026043 | 0.97966 | -0.38925 | 0.97958 | -0.39079 | 0.71546
50 | 0.005388 | 0.0013503 | -0.0053879 | -0.0013503 | 1.1262e-07 | 1.7707e-08 | 0.0082614 | 0.0082614 | 0.0082614 | 0.97048 | -0.56972 | 0.97046 | -0.57015 | 2.2696
51 | -0.0066725 | -0.0016722 | 0.0066725 | 0.0016722 | 1.505e-08 | 4.8939e-09 | 0.010231 | 0.010231 | 0.010231 | 0.97048 | -0.56972 | 0.97048 | -0.56967 | 2.8107
52 | 0.0045926 | 0.0011509 | -0.0045925 | -0.0011509 | 7.091e-09 | -1.7293e-10 | 0.0070418 | 0.0070418 | 0.0070418 | 0.97046 | -0.57015 | 0.97045 | -0.57019 | 1.9346
53 | -0.0078684 | -0.0019719 | 0.0078688 | 0.0019721 | 3.5981e-07 | 1.4882e-07 | 0.012064 | 0.012064 | 0.012064 | 0.97048 | -0.56967 | 0.97053 | -0.56871 | 3.3144
54 | 0.0033471 | 0.00083881 | -0.0033471 | -0.00083885 | 6.7806e-08 | -4.1419e-08 | 0.0051322 | 0.0051323 | 0.0051323 | 0.97045 | -0.57019 | 0.97043 | -0.57061 | 1.41
55 | -0.0091397 | -0.0022906 | 0.0091397 | 0.0022906 | 3.1831e-08 | 1.503e-08 | 0.014013 | 0.014013 | 0.014013 | 0.97053 | -0.56871 | 0.97053 | -0.56864 | 3.8497
56 | 0.0020466 | 0.00051293 | -0.0020466 | -0.00051293 | 1.2819e-09 | -3.4677e-09 | 0.0031382 | 0.0031382 | 0.0031382 | 0.97043 | -0.57061 | 0.97043 | -0.57063 | 0.86214
57 | -0.010341 | -0.0025916 | 0.010341 | 0.0025918 | 4.0856e-07 | 2.0791e-07 | 0.015854 | 0.015854 | 0.015854 | 0.97053 | -0.56864 | 0.97057 | -0.56781 | 4.3555
58 | -0.011597 | -0.0029065 | 0.011597 | 0.0029065 | 5.1593e-08 | 2.7641e-08 | 0.017779 | 0.017779 | 0.017779 | 0.97057 | -0.56781 | 0.97058 | -0.56771 | 4.8843
59 | -0.012771 | -0.0032008 | 0.012772 | 0.0032012 | 7.7874e-07 | 4.3144e-07 | 0.019579 | 0.019579 | 0.019579 | 0.97058 | -0.56771 | 0.97064 | -0.56643 | 5.3789
60 | -0.10082 | -0.025745 | 0.10084 | 0.025757 | 1.9009e-05 | 1.2137e-05 | 0.1513 | 0.1513 | 0.1513 | 0.99264 | -0.13963 | 0.99284 | -0.13573 | 41.5673
61 | 0.098716 | 0.025217 | -0.098418 | -0.025027 | 0.00029809 | 0.00019031 | 0.14815 | 0.14815 | 0.14815 | 0.99264 | -0.13963 | 0.98936 | -0.20229 | 40.7008
62 | -0.10179 | -0.025995 | 0.10194 | 0.02609 | 0.00014962 | 9.5534e-05 | 0.15273 | 0.15273 | 0.15273 | 0.99284 | -0.13573 | 0.99443 | -0.10536 | 41.9585
63 | 0.083134 | 0.021191 | -0.083014 | -0.021115 | 0.00012045 | 7.6822e-05 | 0.12516 | 0.12516 | 0.12516 | 0.98936 | -0.20229 | 0.9878 | -0.23235 | 34.3853
64 | 0.015284 | 0.0038355 | -0.01528 | -0.0038334 | 3.6193e-06 | 2.0819e-06 | 0.022989 | 0.022989 | 0.022989 | 0.98936 | -0.20229 | 0.98911 | -0.20726 | 6.3155
65 | 0.0070558 | 0.0017677 | -0.0070553 | -0.0017675 | 5.4686e-07 | 1.8586e-07 | 0.010646 | 0.010647 | 0.010647 | 0.98614 | -0.26423 | 0.98606 | -0.26586 | 2.9249
66 | 0.073348 | 0.018645 | -0.073339 | -0.01864 | 8.2798e-06 | 5.2761e-06 | 0.11077 | 0.11077 | 0.11077 | 0.98614 | -0.26423 | 0.98602 | -0.26657 | 30.4314
67 | -0.080404 | -0.020413 | 0.080527 | 0.020491 | 0.00012353 | 7.8772e-05 | 0.12142 | 0.12142 | 0.12142 | 0.98614 | -0.26423 | 0.9878 | -0.23235 | 33.3562
68 | 0.0054789 | 0.0013725 | -0.0054788 | -0.0013724 | 1.2329e-07 | 1.7554e-08 | 0.0082677 | 0.0082677 | 0.0082677 | 0.98606 | -0.26586 | 0.98603 | -0.26633 | 2.2714
69 | 0.071738 | 0.018238 | -0.071724 | -0.01823 | 1.3744e-05 | 8.7562e-06 | 0.10835 | 0.10835 | 0.10835 | 0.98602 | -0.26657 | 0.98581 | -0.27055 | 29.7675
70 | 0.069189 | 0.017594 | -0.069055 | -0.017509 | 0.00013428 | 8.5523e-05 | 0.10453 | 0.10453 | 0.10453 | 0.98581 | -0.27055 | 0.98372 | -0.31092 | 28.7163
71 | 0.06782 | 0.017199 | -0.067817 | -0.017197 | 3.0634e-06 | 1.9507e-06 | 0.10266 | 0.10266 | 0.10266 | 0.98372 | -0.31092 | 0.98368 | -0.31186 | 28.2031
72 | 0.066581 | 0.016887 | -0.066515 | -0.016845 | 6.6417e-05 | 4.2286e-05 | 0.10079 | 0.10079 | 0.10079 | 0.98368 | -0.31186 | 0.9826 | -0.33263 | 27.6895
73 | 0.066515 | 0.016845 | -0.066479 | -0.016822 | 3.5745e-05 | 2.2758e-05 | 0.10079 | 0.10079 | 0.10079 | 0.9826 | -0.33263 | 0.98203 | -0.34383 | 27.6895
74 | 0.065226 | 0.016508 | -0.065196 | -0.016489 | 2.9966e-05 | 1.9075e-05 | 0.098892 | 0.098892 | 0.098892 | 0.98203 | -0.34383 | 0.98154 | -0.35341 | 27.1681
75 | 0.0045597 | 0.0011421 | -0.0045595 | -0.0011421 | 1.5286e-07 | -1.1987e-08 | 0.0068807 | 0.0068808 | 0.0068808 | 0.98603 | -0.26633 | 0.986 | -0.26703 | 1.8903
76 | -0.0018305 | -0.00045876 | 0.0018305 | 0.00045855 | 5.9843e-08 | -2.1489e-07 | 0.0027987 | 0.0027986 | 0.0027987 | 0.97323 | -0.51605 | 0.97327 | -0.51536 | 0.76887
77 | 0.021203 | 0.0053241 | -0.02119 | -0.0053163 | 1.2796e-05 | 7.7865e-06 | 0.032421 | 0.032421 | 0.032421 | 0.97327 | -0.51536 | 0.97263 | -0.52802 | 8.9069
78 | -0.023034 | -0.0057826 | 0.023041 | 0.0057871 | 7.2685e-06 | 4.4576e-06 | 0.03522 | 0.035219 | 0.03522 | 0.97327 | -0.51536 | 0.9736 | -0.50875 | 9.6757
79 | 0.019155 | 0.004806 | -0.019149 | -0.0048025 | 5.964e-06 | 3.5872e-06 | 0.029306 | 0.029306 | 0.029306 | 0.97263 | -0.52802 | 0.9723 | -0.53455 | 8.0512
80 | -0.024671 | -0.0061956 | 0.024677 | 0.0061994 | 6.0493e-06 | 3.7304e-06 | 0.037711 | 0.037711 | 0.037711 | 0.9736 | -0.50875 | 0.97386 | -0.50361 | 10.3602
81 | 0.016224 | 0.0040695 | -0.016218 | -0.0040659 | 6.1092e-06 | 3.5823e-06 | 0.024831 | 0.024831 | 0.024831 | 0.9723 | -0.53455 | 0.9719 | -0.54245 | 6.8217
82 | -0.026713 | -0.0067095 | 0.026722 | 0.0067153 | 9.4036e-06 | 5.831e-06 | 0.040821 | 0.040821 | 0.040821 | 0.97386 | -0.50361 | 0.97424 | -0.49623 | 11.2145
83 | 0.013477 | 0.0033788 | -0.013473 | -0.0033769 | 3.5106e-06 | 1.9744e-06 | 0.020634 | 0.020634 | 0.020634 | 0.9719 | -0.54245 | 0.97162 | -0.54792 | 5.6686
84 | -0.028758 | -0.0072255 | 0.028763 | 0.007229 | 5.5356e-06 | 3.4475e-06 | 0.04393 | 0.04393 | 0.04393 | 0.97424 | -0.49623 | 0.97444 | -0.4922 | 12.0688
85 | 0.0094104 | 0.0023587 | -0.0094083 | -0.0023577 | 2.0728e-06 | 9.9705e-07 | 0.014412 | 0.014412 | 0.014412 | 0.97162 | -0.54792 | 0.97139 | -0.55254 | 3.9593
86 | 0.0075622 | 0.001895 | -0.0075613 | -0.0018947 | 8.8116e-07 | 3.472e-07 | 0.011584 | 0.011584 | 0.011584 | 0.97139 | -0.55254 | 0.97126 | -0.55499 | 3.1825
87 | 0.0075613 | 0.0018947 | -0.0075597 | -0.001894 | 1.6052e-06 | 6.3265e-07 | 0.011584 | 0.011584 | 0.011584 | 0.97126 | -0.55499 | 0.97104 | -0.55945 | 3.1825
88 | 0.0028267 | 0.00070782 | -0.0028266 | -0.00070802 | 1.6492e-07 | -2.0268e-07 | 0.0042657 | 0.0042659 | 0.0042659 | 0.986 | -0.26703 | 0.98594 | -0.26826 | 1.1719
89 | 0.063961 | 0.01618 | -0.06394 | -0.016167 | 2.0593e-05 | 1.3106e-05 | 0.097019 | 0.097019 | 0.097019 | 0.98154 | -0.35341 | 0.98119 | -0.36012 | 26.6535
90 | 0.062706 | 0.015857 | -0.062631 | -0.015809 | 7.5523e-05 | 4.8054e-05 | 0.095147 | 0.095148 | 0.095148 | 0.98119 | -0.36012 | 0.9799 | -0.38526 | 26.1394
91 | -0.0018804 | -0.00047128 | 0.0018805 | 0.00047107 | 6.2651e-08 | -2.0878e-07 | 0.0028817 | 0.0028816 | 0.0028817 | 0.971 | -0.56015 | 0.97104 | -0.55945 | 0.79167
92 | 0.0036227 | 0.00090755 | -0.0036225 | -0.00090767 | 2.7998e-07 | -1.2048e-07 | 0.0055513 | 0.0055515 | 0.0055515 | 0.97104 | -0.55945 | 0.97096 | -0.56107 | 1.5251
93 | 0.0023913 | 0.00059912 | -0.0023912 | -0.00059928 | 8.6185e-08 | -1.5649e-07 | 0.0036647 | 0.0036648 | 0.0036648 | 0.97096 | -0.56107 | 0.97092 | -0.56183 | 1.0068
94 | 0.00094972 | 0.000238 | -0.00094972 | -0.00023802 | 1.5963e-09 | -2.3828e-08 | 0.0014555 | 0.0014555 | 0.0014555 | 0.97092 | -0.56183 | 0.97092 | -0.56186 | 0.39987
95 | -0.030799 | -0.0077392 | 0.030808 | 0.0077444 | 8.337e-06 | 5.2105e-06 | 0.047039 | 0.047039 | 0.047039 | 0.97444 | -0.4922 | 0.97473 | -0.48653 | 12.9228
96 | -0.033124 | -0.008325 | 0.03314 | 0.0083349 | 1.5764e-05 | 9.8837e-06 | 0.050575 | 0.050575 | 0.050575 | 0.97473 | -0.48653 | 0.97524 | -0.47657 | 13.8943
97 | 0.034694 | 0.0087144 | -0.034678 | -0.0087074 | 1.5605e-05 | 7.0296e-06 | 0.052965 | 0.052966 | 0.052966 | 0.97483 | -0.48398 | 0.97435 | -0.49341 | 3.6378
98 | -0.047464 | -0.011917 | 0.047482 | 0.011927 | 1.7761e-05 | 9.5671e-06 | 0.07246 | 0.072459 | 0.07246 | 0.97483 | -0.48398 | 0.97522 | -0.47614 | 4.9766
99 | 0.012771 | 0.003203 | -0.012763 | -0.0031988 | 7.6826e-06 | 4.2453e-06 | 0.019495 | 0.019495 | 0.019495 | 0.97483 | -0.48398 | 0.97419 | -0.4966 | 5.3558
100 | 0.03235 | 0.0081239 | -0.032331 | -0.0081158 | 1.9217e-05 | 8.1188e-06 | 0.04941 | 0.049412 | 0.049412 | 0.97435 | -0.49341 | 0.97372 | -0.50586 | 3.3937
101 | -0.14238 | -0.03571 | 0.14254 | 0.035812 | 0.00016126 | 0.00010139 | 0.21725 | 0.21725 | 0.21725 | 0.97522 | -0.47614 | 0.97643 | -0.4524 | 14.9213
102 | 0.032331 | 0.0081158 | -0.032314 | -0.0081088 | 1.6482e-05 | 6.9679e-06 | 0.049412 | 0.049413 | 0.049413 | 0.97372 | -0.50586 | 0.97317 | -0.51655 | 3.3937
103 | -0.15536 | -0.039026 | 0.15565 | 0.039206 | 0.00028654 | 0.00018066 | 0.2368 | 0.2368 | 0.2368 | 0.97643 | -0.4524 | 0.9784 | -0.41383 | 16.2635
104 | -0.014309 | -0.0035865 | 0.014309 | 0.0035866 | 7.594e-08 | 4.34e-08 | 0.021936 | 0.021936 | 0.021936 | 0.97064 | -0.56643 | 0.97065 | -0.56632 | 6.0264
105 | -0.015752 | -0.0039481 | 0.015755 | 0.0039499 | 3.1679e-06 | 1.8483e-06 | 0.024148 | 0.024147 | 0.024148 | 0.97065 | -0.56632 | 0.97086 | -0.5621 | 6.6339
106 | -0.017678 | -0.004432 | 0.01768 | 0.0044329 | 1.5868e-06 | 9.4429e-07 | 0.027095 | 0.027095 | 0.027095 | 0.97086 | -0.5621 | 0.97096 | -0.56022 | 7.4438
107 | -0.018861 | -0.004729 | 0.018863 | 0.0047299 | 1.4978e-06 | 8.9943e-07 | 0.028906 | 0.028906 | 0.028906 | 0.97096 | -0.56022 | 0.97104 | -0.55855 | 7.9412
108 | 0.013705 | 0.0034388 | -0.013701 | -0.0034363 | 4.399e-06 | 2.4614e-06 | 0.02062 | 0.02062 | 0.02062 | 0.98911 | -0.20726 | 0.98876 | -0.21399 | 5.6649
109 | 0.012485 | 0.0031315 | -0.012481 | -0.0031297 | 3.3038e-06 | 1.7945e-06 | 0.01879 | 0.01879 | 0.01879 | 0.98876 | -0.21399 | 0.98847 | -0.21954 | 5.162
110 | 0.011523 | 0.0028894 | -0.011517 | -0.0028864 | 5.617e-06 | 2.9571e-06 | 0.017346 | 0.017347 | 0.017347 | 0.98847 | -0.21954 | 0.98795 | -0.22977 | 4.7656
111 | -0.0012243 | -0.00030683 | 0.0012243 | 0.00030646 | 4.0095e-08 | -3.7371e-07 | 0.0018478 | 0.0018477 | 0.0018478 | 0.9859 | -0.26895 | 0.98594 | -0.26826 | 0.50764
112 | 0.10847 | 0.027363 | -0.108 | -0.027068 | 0.00046158 | 0.00029485 | 0.1651 | 0.1651 | 0.1651 | 0.97799 | -0.42177 | 0.97345 | -0.51106 | 45.3561
113 | -0.0013695 | -0.00034324 | 0.0013696 | 0.00034308 | 2.3881e-08 | -1.6458e-07 | 0.0020958 | 0.0020957 | 0.0020958 | 0.97239 | -0.53212 | 0.9724 | -0.53175 | 0.57577
114 | -0.002009 | -0.00050333 | 0.0020091 | 0.000503 | 1.1605e-07 | -3.3199e-07 | 0.0030742 | 0.0030741 | 0.0030742 | 0.9724 | -0.53175 | 0.97247 | -0.53054 | 0.84456
115 | -0.029829 | -0.0074837 | 0.029833 | 0.0074851 | 3.4855e-06 | 1.3451e-06 | 0.045646 | 0.045646 | 0.045646 | 0.97247 | -0.53054 | 0.97259 | -0.52809 | 3.135
116 | 0.02782 | 0.0069807 | -0.027794 | -0.0069658 | 2.6232e-05 | 1.4875e-05 | 0.042572 | 0.042573 | 0.042573 | 0.97247 | -0.53054 | 0.97146 | -0.55033 | 5.8479
117 | 0.030448 | 0.007637 | -0.030448 | -0.007637 | 5.5884e-08 | 3.4915e-08 | 0.046623 | 0.046623 | 0.046623 | 0.9718 | -0.54356 | 0.9718 | -0.54359 | 12.8087
118 | 0.029213 | 0.0073275 | -0.029213 | -0.0073275 | 2.5051e-08 | 1.5623e-08 | 0.044733 | 0.044733 | 0.044733 | 0.9718 | -0.54359 | 0.9718 | -0.54361 | 12.2892
119 | 0.030976 | 0.0077734 | -0.030959 | -0.0077665 | 1.7033e-05 | 6.8791e-06 | 0.047367 | 0.047368 | 0.047368 | 0.97317 | -0.51655 | 0.97259 | -0.52809 | 3.2533
120 | 0.0011258 | 0.00028145 | -0.0011257 | -0.00028214 | 6.4707e-08 | -6.8044e-07 | 0.0017222 | 0.0017224 | 0.0017224 | 0.97259 | -0.52809 | 0.97253 | -0.5293 | 0.47319
121 | -0.020065 | -0.0050312 | 0.020068 | 0.0050331 | 3.2389e-06 | 1.9599e-06 | 0.030748 | 0.030748 | 0.030748 | 0.97104 | -0.55855 | 0.97121 | -0.55516 | 8.4472
122 | 0.0014947 | 0.00037134 | -0.0014942 | -0.00037414 | 4.9439e-07 | -2.7948e-06 | 0.002289 | 0.0022901 | 0.0022901 | 0.97121 | -0.55516 | 0.97086 | -0.56213 | 0.62914
123 | -0.027964 | -0.0070088 | 0.02798 | 0.0070184 | 1.54e-05 | 9.579e-06 | 0.042845 | 0.042845 | 0.042845 | 0.97121 | -0.55516 | 0.9718 | -0.54361 | 11.7705
124 | 0.00074581 | 0.00018656 | -0.00074579 | -0.00018691 | 1.4307e-08 | -3.5193e-07 | 0.001143 | 0.0011431 | 0.0011431 | 0.97086 | -0.56213 | 0.97084 | -0.56254 | 0.31403

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61846 | 0.15937

## res_load
| p_mw | q_mvar
0 | 0.0019052 | 0.00047748
1 | 0.0018978 | 0.00047563
2 | 0.0043196 | 0.0010826
3 | 0.0027002 | 0.00067674
4 | 0.0023166 | 0.00058059
5 | 0.0014426 | 0.00036156
6 | 0.0059178 | 0.0014832
7 | 0.0018834 | 0.00047203
8 | 0.0023166 | 0.00058059
9 | 0.003361 | 0.00084234
10 | 0.0016596 | 0.00041594
11 | 0.0017008 | 0.00042625
12 | 0.0016584 | 0.00041564
13 | 0.00256 | 0.0006416
14 | 0.0030493 | 0.00076423
15 | 0.0046839 | 0.0011739
16 | 0.026963 | 0.0067576
17 | 0.010618 | 0.002661
18 | 0.057421 | 0.014391
19 | 0.0014419 | 0.00036136
20 | 0.0069249 | 0.0017355
21 | 0.0086246 | 0.0021615
22 | 0.0063969 | 0.0016032
23 | 0.0087594 | 0.0021953
24 | 0.0011781 | 0.00029527
25 | 0.0086198 | 0.0021603
26 | 0.0086192 | 0.0021602
27 | 0.0087708 | 0.0021982
28 | 0.0016343 | 0.00040961
29 | 0.0016073 | 0.00040283
30 | 0.0012845 | 0.00032192
31 | 0.00079537 | 0.00019934
32 | 0.0011959 | 0.00029973
33 | 0.0012454 | 0.00031213
34 | 0.0012709 | 0.00031851
35 | 0.0013005 | 0.00032593
36 | 0.0012008 | 0.00030096
37 | 0.0020466 | 0.00051293
38 | 0.0012556 | 0.00031467
39 | 0.0011742 | 0.00029429
40 | 0.0024928 | 0.00062474
41 | 0.0021043 | 0.00052738
42 | 0.00095011 | 0.00023812
43 | 0.0024593 | 0.00061637
44 | 0.0015764 | 0.00039507
45 | 0.0016013 | 0.00040131
46 | 0.0024867 | 0.00062322
47 | 0.0025353 | 0.0006354
48 | 0.0012348 | 0.00030947
49 | 0.0012361 | 0.00030979
50 | 0.0012524 | 0.00031388
51 | 0.00091911 | 0.00023035
52 | 0.0018305 | 0.00045876
53 | 0.0020359 | 0.00051024
54 | 0.0016302 | 0.00040857
55 | 0.0029245 | 0.00073295
56 | 0.0020354 | 0.00051012
57 | 0.0027415 | 0.00068707
58 | 0.0020358 | 0.00051022
59 | 0.0040626 | 0.0010182
60 | 0.0018461 | 0.00046267
61 | 0.0017328 | 0.00043428
62 | 0.0012357 | 0.00030969
63 | 0.001234 | 0.00030926
64 | 0.0012365 | 0.0003099
65 | 0.0018804 | 0.00047128
66 | 0.0020565 | 0.00051541
67 | 0.0012311 | 0.00030855
68 | 0.0014415 | 0.00036128
69 | 0.0020358 | 0.00051022
70 | 0.0023165 | 0.00058057
71 | 0.0023179 | 0.00058092
72 | 0.0023281 | 0.00058349
73 | 0.094897 | 0.023783
74 | 0.012763 | 0.0031988
75 | 0.012824 | 0.0032139
76 | 0.0015375 | 0.00038532
77 | 0.0014425 | 0.00036153
78 | 0.0019234 | 0.00048205
79 | 0.0011814 | 0.00029609
80 | 0.0015745 | 0.0003946
81 | 0.0012163 | 0.00030483
82 | 0.0009588 | 0.0002403
83 | 0.011517 | 0.0028864
84 | 0.0024963 | 0.00062564
85 | 0.0012243 | 0.00030683
86 | 0.0016023 | 0.00040156
87 | 0.00094972 | 0.00023802
88 | 0.0017144 | 0.00042968
89 | 0.018355 | 0.0046001
90 | 0.108 | 0.027068
91 | 0.0013695 | 0.00034324
92 | 0.00063943 | 0.00016026
93 | 0.0063839 | 0.0016
94 | 0.0011965 | 0.00029988
95 | 0.0012348 | 0.00030948
96 | 0.0013383 | 0.00033542
97 | 0.027794 | 0.0069658
98 | 0.0011257 | 0.00028214
99 | 0.0012019 | 0.00030123
100 | 0.0064016 | 0.0016044
101 | 0.0012331 | 0.00030906
102 | 0.00074844 | 0.00018758
103 | 0.00074579 | 0.00018691

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1