## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2574-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2574-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2574-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2574-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2574-1_0_6_node_47 | 0.4 | n |  | TRUE
5 | bus_LV_2574-1_0_6_node_75 | 0.4 | n |  | TRUE
6 | bus_LV_2574-1_0_6_node_76 | 0.4 | n |  | TRUE
7 | bus_LV_2574-1_0_6_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2574-1_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2574-1_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2574-1_0_6_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2574-1_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2574-1_0_6_node_133 | 0.4 | n |  | TRUE
13 | bus_LV_2574-1_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2574-1_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2574-1_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2574-1_0_6_node_166 | 0.4 | n |  | TRUE
17 | bus_LV_2574-1_0_6_node_165 | 0.4 | n |  | TRUE
18 | bus_LV_2574-1_0_6_node_79 | 0.4 | n |  | TRUE
19 | bus_LV_2574-1_0_6_node_77 | 0.4 | n |  | TRUE
20 | bus_LV_2574-1_0_6_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2574-1_0_6_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2574-1_0_6_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2574-1_0_6_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2574-1_0_6_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_2574-1_0_6_node_80 | 0.4 | n |  | TRUE
26 | bus_LV_2574-1_0_6_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_2574-1_0_6_node_60 | 0.4 | n |  | TRUE
28 | bus_LV_2574-1_0_6_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_2574-1_0_6_node_158 | 0.4 | n |  | TRUE
30 | bus_LV_2574-1_0_6_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_2574-1_0_6_node_167 | 0.4 | n |  | TRUE
32 | bus_LV_2574-1_0_6_node_147 | 0.4 | n |  | TRUE
33 | bus_LV_2574-1_0_6_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_2574-1_0_6_node_184 | 0.4 | n |  | TRUE
35 | bus_LV_2574-1_0_6_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_2574-1_0_6_node_141 | 0.4 | n |  | TRUE
37 | bus_LV_2574-1_0_6_node_182 | 0.4 | n |  | TRUE
38 | bus_LV_2574-1_0_6_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_2574-1_0_6_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_2574-1_0_6_node_72 | 0.4 | n |  | TRUE
41 | bus_LV_2574-1_0_6_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2574-1_0_6_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2574-1_0_6_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_2574-1_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2574-1_0_6_node_110 | 0.4 | n |  | TRUE
46 | bus_LV_2574-1_0_6_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_2574-1_0_6_node_111 | 0.4 | n |  | TRUE
48 | bus_LV_2574-1_0_6_node_146 | 0.4 | n |  | TRUE
49 | bus_LV_2574-1_0_6_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_2574-1_0_6_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_2574-1_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2574-1_0_6_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_2574-1_0_6_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_2574-1_0_6_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_2574-1_0_6_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_2574-1_0_6_node_65 | 0.4 | n |  | TRUE
57 | bus_LV_2574-1_0_6_node_121 | 0.4 | n |  | TRUE
58 | bus_LV_2574-1_0_6_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_2574-1_0_6_node_180 | 0.4 | n |  | TRUE
60 | bus_LV_2574-1_0_6_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_2574-1_0_6_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_2574-1_0_6_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_2574-1_0_6_node_179 | 0.4 | n |  | TRUE
64 | bus_LV_2574-1_0_6_node_112 | 0.4 | n |  | TRUE
65 | bus_LV_2574-1_0_6_node_124 | 0.4 | n |  | TRUE
66 | bus_LV_2574-1_0_6_node_126 | 0.4 | n |  | TRUE
67 | bus_LV_2574-1_0_6_node_123 | 0.4 | n |  | TRUE
68 | bus_LV_2574-1_0_6_node_181 | 0.4 | n |  | TRUE
69 | bus_LV_2574-1_0_6_node_129 | 0.4 | n |  | TRUE
70 | bus_LV_2574-1_0_6_node_130 | 0.4 | n |  | TRUE
71 | bus_LV_2574-1_0_6_node_145 | 0.4 | n |  | TRUE
72 | bus_LV_2574-1_0_6_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_2574-1_0_6_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_2574-1_0_6_node_103 | 0.4 | n |  | TRUE
75 | bus_LV_2574-1_0_6_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_2574-1_0_6_node_148 | 0.4 | n |  | TRUE
77 | bus_LV_2574-1_0_6_node_183 | 0.4 | n |  | TRUE
78 | bus_LV_2574-1_0_6_node_168 | 0.4 | n |  | TRUE
79 | bus_LV_2574-1_0_6_node_156 | 0.4 | n |  | TRUE
80 | bus_LV_2574-1_0_6_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_2574-1_0_6_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_2574-1_0_6_node_83 | 0.4 | n |  | TRUE
83 | bus_LV_2574-1_0_6_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_2574-1_0_6_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_2574-1_0_6_node_150 | 0.4 | n |  | TRUE
86 | bus_LV_2574-1_0_6_node_102 | 0.4 | n |  | TRUE
87 | bus_LV_2574-1_0_6_node_169 | 0.4 | n |  | TRUE
88 | bus_LV_2574-1_0_6_node_91 | 0.4 | n |  | TRUE
89 | bus_LV_2574-1_0_6_node_92 | 0.4 | n |  | TRUE
90 | bus_LV_2574-1_0_6_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_2574-1_0_6_node_94 | 0.4 | n |  | TRUE
92 | bus_LV_2574-1_0_6_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_2574-1_0_6_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_2574-1_0_6_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_2574-1_0_6_node_143 | 0.4 | n |  | TRUE
96 | bus_LV_2574-1_0_6_node_105 | 0.4 | n |  | TRUE
97 | bus_LV_2574-1_0_6_node_144 | 0.4 | n |  | TRUE
98 | bus_LV_2574-1_0_6_node_106 | 0.4 | n |  | TRUE
99 | bus_LV_2574-1_0_6_node_108 | 0.4 | n |  | TRUE
100 | bus_LV_2574-1_0_6_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_2574-1_0_6_node_132 | 0.4 | n |  | TRUE
102 | bus_LV_2574-1_0_6_node_142 | 0.4 | n |  | TRUE
103 | bus_LV_2574-1_0_6_node_185 | 0.4 | n |  | TRUE
104 | bus_LV_2574-1_0_6_node_125 | 0.4 | n |  | TRUE
105 | bus_LV_2574-1_0_6_node_127 | 0.4 | n |  | TRUE
106 | bus_LV_2574-1_0_6_node_128 | 0.4 | n |  | TRUE
107 | bus_LV_2574-1_0_6_node_173 | 0.4 | n |  | TRUE
108 | bus_LV_2574-1_0_6_node_138 | 0.4 | n |  | TRUE
109 | bus_LV_2574-1_0_6_node_139 | 0.4 | n |  | TRUE
110 | bus_LV_2574-1_0_6_node_134 | 0.4 | n |  | TRUE
111 | bus_LV_2574-1_0_6_node_140 | 0.4 | n |  | TRUE
112 | bus_LV_2574-1_0_6_node_155 | 0.4 | n |  | TRUE
113 | bus_LV_2574-1_0_6_node_157 | 0.4 | n |  | TRUE
114 | bus_LV_2574-1_0_6_node_159 | 0.4 | n |  | TRUE
115 | bus_MV_522_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2574-1_0_6_load_0 | 0 | 0.0016187 | 0.00040569 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2574-1_0_6_load_1 | 1 | 0.00071592 | 0.00017943 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2574-1_0_6_load_2 | 2 | 0.00034158 | 8.5609e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2574-1_0_6_load_3 | 3 | 0.0004 | 0.00010025 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2574-1_0_6_load_76 | 6 | 0.00071671 | 0.00017962 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2574-1_0_6_load_4 | 7 | 0.0018527 | 0.00046434 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2574-1_0_6_load_5 | 8 | 0.00070063 | 0.0001756 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2574-1_0_6_load_11 | 10 | 0.0033276 | 0.00083397 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2574-1_0_6_load_8 | 11 | 0.00060933 | 0.00015271 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2574-1_0_6_load_7 | 13 | 0.00033773 | 8.4643e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2574-1_0_6_load_9 | 14 | 0.0018768 | 0.00047037 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2574-1_0_6_load_10 | 15 | 0.0053319 | 0.0013363 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2574-1_0_6_load_166 | 16 | 0.0023107 | 0.00057912 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2574-1_0_6_load_165 | 17 | 0.001262 | 0.00031629 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2574-1_0_6_load_24 | 20 | 0.0015127 | 0.00037911 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2574-1_0_6_load_25 | 21 | 0.0015133 | 0.00037927 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2574-1_0_6_load_26 | 22 | 0.0042632 | 0.0010685 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2574-1_0_6_load_36 | 26 | 0.0024344 | 0.00061013 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2574-1_0_6_load_38 | 28 | 0.0019643 | 0.0004923 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2574-1_0_6_load_158 | 29 | 0.006694 | 0.0016777 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2574-1_0_6_load_35 | 30 | 0.0022425 | 0.00056201 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2574-1_0_6_load_167 | 31 | 0.00041007 | 0.00010277 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2574-1_0_6_load_147 | 32 | 0.0017382 | 0.00043564 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2574-1_0_6_load_184 | 34 | 0.0014107 | 0.00035357 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2574-1_0_6_load_141 | 36 | 9.2477e-05 | 2.3177e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2574-1_0_6_load_182 | 37 | 0.00077028 | 0.00019305 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2574-1_0_6_load_37 | 38 | 0.0017996 | 0.00045102 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2574-1_0_6_load_40 | 39 | 0.0020731 | 0.00051957 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2574-1_0_6_load_31 | 41 | 0.0018905 | 0.00047381 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2574-1_0_6_load_33 | 43 | 0.0012998 | 0.00032575 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2574-1_0_6_load_34 | 44 | 0.0012769 | 0.00032002 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2574-1_0_6_load_146 | 48 | 0.00057222 | 0.00014341 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2574-1_0_6_load_39 | 51 | 0.0041411 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2574-1_0_6_load_53 | 52 | 0.0070216 | 0.0017598 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2574-1_0_6_load_56 | 54 | 0.035096 | 0.0087958 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2574-1_0_6_load_121 | 57 | 0.0030191 | 0.00075665 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2574-1_0_6_load_180 | 59 | 0.028551 | 0.0071555 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2574-1_0_6_load_64 | 60 | 0.0032791 | 0.00082182 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2574-1_0_6_load_68 | 61 | 0.00049627 | 0.00012438 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2574-1_0_6_load_67 | 62 | 0.011445 | 0.0028685 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2574-1_0_6_load_179 | 63 | 0.049779 | 0.012476 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2574-1_0_6_load_126 | 66 | 0.0010656 | 0.00026707 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2574-1_0_6_load_123 | 67 | 0.00085962 | 0.00021544 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2574-1_0_6_load_181 | 68 | 0.00077028 | 0.00019305 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2574-1_0_6_load_129 | 69 | 0.00092369 | 0.0002315 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2574-1_0_6_load_130 | 70 | 0.0010541 | 0.00026417 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2574-1_0_6_load_145 | 71 | 0.0014211 | 0.00035616 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2574-1_0_6_load_71 | 72 | 0.0042964 | 0.0010768 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2574-1_0_6_load_74 | 73 | 0.0014159 | 0.00035486 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2574-1_0_6_load_103 | 74 | 0.0090611 | 0.0022709 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2574-1_0_6_load_101 | 75 | 0.0060377 | 0.0015132 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2574-1_0_6_load_148 | 76 | 0.0010164 | 0.00025473 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2574-1_0_6_load_183 | 77 | 0.0014749 | 0.00036964 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2574-1_0_6_load_168 | 78 | 0.0011938 | 0.00029919 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2574-1_0_6_load_81 | 80 | 0.0015779 | 0.00039547 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2574-1_0_6_load_82 | 81 | 0.0010692 | 0.00026797 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2574-1_0_6_load_84 | 83 | 0.001026 | 0.00025715 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2574-1_0_6_load_85 | 84 | 0.0033327 | 0.00083525 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2574-1_0_6_load_150 | 85 | 0.0035251 | 0.00088347 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2574-1_0_6_load_102 | 86 | 0.00099908 | 0.00025039 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2574-1_0_6_load_91 | 88 | 0.044124 | 0.011059 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2574-1_0_6_load_92 | 89 | 0.020883 | 0.0052339 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2574-1_0_6_load_93 | 90 | 0.0061266 | 0.0015355 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2574-1_0_6_load_95 | 92 | 0.0023329 | 0.00058467 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2574-1_0_6_load_122 | 93 | 0.046442 | 0.011639 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2574-1_0_6_load_143 | 95 | 0.0018339 | 0.00045961 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2574-1_0_6_load_105 | 96 | 0.0038498 | 0.00096486 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2574-1_0_6_load_144 | 97 | 0.002004 | 0.00050226 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2574-1_0_6_load_106 | 98 | 0.0075234 | 0.0018855 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2574-1_0_6_load_131 | 100 | 0.013924 | 0.0034896 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2574-1_0_6_load_132 | 101 | 0.0040869 | 0.0010243 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2574-1_0_6_load_185 | 103 | 0.0018832 | 0.00047198 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2574-1_0_6_load_127 | 105 | 0.0017986 | 0.00045076 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2574-1_0_6_load_128 | 106 | 0.0033003 | 0.00082713 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2574-1_0_6_load_173 | 107 | 0.0012093 | 0.00030307 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2574-1_0_6_load_138 | 108 | 0.0010718 | 0.00026861 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2574-1_0_6_load_139 | 109 | 0.00097352 | 0.00024399 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2574-1_0_6_load_134 | 110 | 0.00094179 | 0.00023604 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2574-1_0_6_load_140 | 111 | 0.00095799 | 0.0002401 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2574-1_0_6_load_155 | 112 | 0.00089043 | 0.00022316 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2574-1_0_6_load_159 | 114 | 0.0010704 | 0.00026827 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 92 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2574-1_0_6_line_0 |  | 0 | 1 | 0.30631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2574-1_0_6_line_1 |  | 0 | 2 | 0.070476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2574-1_0_6_line_2 |  | 1 | 3 | 0.025979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2574-1_0_6_line_3 |  | 3 | 4 | 0.099756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2574-1_0_6_line_4 |  | 4 | 5 | 0.030349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2574-1_0_6_line_5 |  | 4 | 6 | 0.014336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2574-1_0_6_line_6 |  | 5 | 39 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2574-1_0_6_line_7 |  | 5 | 40 | 0.006604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2574-1_0_6_line_8 |  | 7 | 8 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2574-1_0_6_line_9 |  | 8 | 9 | 0.075163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2574-1_0_6_line_10 |  | 9 | 10 | 0.041143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2574-1_0_6_line_11 |  | 9 | 11 | 0.034709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2574-1_0_6_line_12 |  | 10 | 12 | 0.013569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2574-1_0_6_line_13 |  | 11 | 13 | 0.0057972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2574-1_0_6_line_14 |  | 12 | 18 | 0.011621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2574-1_0_6_line_15 |  | 12 | 19 | 0.083795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2574-1_0_6_line_16 |  | 13 | 14 | 0.019984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2574-1_0_6_line_17 |  | 14 | 15 | 0.0015409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2574-1_0_6_line_18 |  | 15 | 16 | 0.0074178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2574-1_0_6_line_19 |  | 16 | 17 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2574-1_0_6_line_20 |  | 17 | 110 | 0.034935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2574-1_0_6_line_21 |  | 18 | 31 | 0.013553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2574-1_0_6_line_22 |  | 19 | 32 | 0.017468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2574-1_0_6_line_23 |  | 20 | 21 | 0.01595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2574-1_0_6_line_24 |  | 20 | 22 | 0.034027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2574-1_0_6_line_25 |  | 21 | 23 | 0.011368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2574-1_0_6_line_26 |  | 22 | 24 | 0.041631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2574-1_0_6_line_27 |  | 23 | 25 | 0.004794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2574-1_0_6_line_28 |  | 23 | 26 | 0.076829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2574-1_0_6_line_29 |  | 24 | 27 | 0.3046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2574-1_0_6_line_30 |  | 24 | 28 | 0.0083171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2574-1_0_6_line_31 |  | 25 | 29 | 0.031245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2574-1_0_6_line_32 |  | 26 | 30 | 0.021223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2574-1_0_6_line_33 |  | 27 | 37 | 0.13943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2574-1_0_6_line_34 |  | 27 | 35 | 0.21454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2574-1_0_6_line_35 |  | 28 | 38 | 0.010043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2574-1_0_6_line_36 |  | 29 | 79 | 0.027767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2574-1_0_6_line_37 |  | 31 | 78 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2574-1_0_6_line_38 |  | 32 | 76 | 0.070578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2574-1_0_6_line_39 |  | 33 | 34 | 0.061038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2574-1_0_6_line_40 |  | 33 | 35 | 0.007382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2574-1_0_6_line_41 |  | 34 | 77 | 0.01212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2574-1_0_6_line_42 |  | 35 | 36 | 0.099811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2574-1_0_6_line_43 |  | 36 | 64 | 0.054123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2574-1_0_6_line_44 |  | 37 | 68 | 0.00028331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2574-1_0_6_line_45 |  | 38 | 51 | 0.024091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2574-1_0_6_line_46 |  | 39 | 51 | 0.031347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2574-1_0_6_line_47 |  | 40 | 73 | 0.015111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2574-1_0_6_line_48 |  | 40 | 72 | 0.011005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2574-1_0_6_line_49 |  | 41 | 42 | 0.02593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2574-1_0_6_line_50 |  | 42 | 43 | 0.0093279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2574-1_0_6_line_51 |  | 42 | 44 | 0.030356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2574-1_0_6_line_52 |  | 43 | 45 | 0.056192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2574-1_0_6_line_53 |  | 44 | 46 | 0.020908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2574-1_0_6_line_54 |  | 45 | 47 | 0.19031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2574-1_0_6_line_55 |  | 46 | 48 | 0.016973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2574-1_0_6_line_56 |  | 46 | 49 | 0.052849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2574-1_0_6_line_57 |  | 46 | 50 | 0.049627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2574-1_0_6_line_58 |  | 47 | 103 | 0.034752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2574-1_0_6_line_59 |  | 48 | 71 | 0.057563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2574-1_0_6_line_60 |  | 49 | 58 | 0.017101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2574-1_0_6_line_61 |  | 49 | 59 | 0.07483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2574-1_0_6_line_62 |  | 50 | 61 | 0.010313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2574-1_0_6_line_63 |  | 50 | 60 | 0.060916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2574-1_0_6_line_64 |  | 52 | 53 | 0.056709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2574-1_0_6_line_65 |  | 53 | 54 | 0.038057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2574-1_0_6_line_66 |  | 53 | 55 | 0.082331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2574-1_0_6_line_67 |  | 55 | 56 | 0.028142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2574-1_0_6_line_68 |  | 55 | 57 | 0.027567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2574-1_0_6_line_69 |  | 56 | 60 | 0.022059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2574-1_0_6_line_70 |  | 58 | 62 | 0.036906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2574-1_0_6_line_71 |  | 59 | 63 | 0.044849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2574-1_0_6_line_72 |  | 61 | 69 | 0.012657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2574-1_0_6_line_73 |  | 63 | 93 | 0.043681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2574-1_0_6_line_74 |  | 64 | 102 | 0.024939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2574-1_0_6_line_75 |  | 65 | 66 | 0.060862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2574-1_0_6_line_76 |  | 65 | 67 | 0.041647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2574-1_0_6_line_77 |  | 66 | 107 | 0.027761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2574-1_0_6_line_78 |  | 67 | 104 | 0.03584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2574-1_0_6_line_79 |  | 69 | 70 | 0.016401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2574-1_0_6_line_80 |  | 73 | 74 | 0.0061667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2574-1_0_6_line_81 |  | 74 | 75 | 0.0082518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2574-1_0_6_line_82 |  | 75 | 86 | 0.0026208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2574-1_0_6_line_83 |  | 77 | 106 | 0.024933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2574-1_0_6_line_84 |  | 78 | 87 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2574-1_0_6_line_85 |  | 79 | 112 | 0.052296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2574-1_0_6_line_86 |  | 80 | 81 | 0.026589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2574-1_0_6_line_87 |  | 80 | 82 | 0.019704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2574-1_0_6_line_88 |  | 81 | 83 | 0.015841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2574-1_0_6_line_89 |  | 82 | 84 | 0.24948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_2574-1_0_6_line_90 |  | 83 | 85 | 0.02688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_2574-1_0_6_line_91 |  | 84 | 86 | 0.023461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_2574-1_0_6_line_92 |  | 85 | 87 | 0.017088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_2574-1_0_6_line_93 |  | 88 | 89 | 0.02608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_2574-1_0_6_line_94 |  | 88 | 90 | 0.013569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2574-1_0_6_line_95 |  | 89 | 91 | 0.032141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2574-1_0_6_line_96 |  | 90 | 92 | 0.044207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2574-1_0_6_line_97 |  | 91 | 93 | 0.0075218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2574-1_0_6_line_98 |  | 91 | 94 | 0.032012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2574-1_0_6_line_99 |  | 92 | 95 | 0.0041182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2574-1_0_6_line_100 |  | 94 | 96 | 0.048892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2574-1_0_6_line_101 |  | 95 | 97 | 0.029869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2574-1_0_6_line_102 |  | 96 | 98 | 0.050507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2574-1_0_6_line_103 |  | 97 | 102 | 0.016397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_2574-1_0_6_line_104 |  | 98 | 99 | 0.031317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2574-1_0_6_line_105 |  | 99 | 100 | 0.058638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2574-1_0_6_line_106 |  | 101 | 102 | 0.063684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2574-1_0_6_line_107 |  | 104 | 105 | 0.028524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2574-1_0_6_line_108 |  | 104 | 106 | 0.11769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2574-1_0_6_line_109 |  | 105 | 108 | 0.051719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2574-1_0_6_line_110 |  | 108 | 109 | 0.015288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2574-1_0_6_line_111 |  | 109 | 111 | 0.015504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2574-1_0_6_line_112 |  | 112 | 113 | 0.020752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2574-1_0_6_line_113 |  | 113 | 114 | 0.05064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2574-1_0_6_trafo_95 | 0.63 MVA 20/0.4 kV | 115 | 92 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2644674.5909 | 1248493.0702 | 2644604.6019 | 1248466.8025 | 2644514.458 | 1248428.2664 | 2644442.9635 | 1248395.9199 | 2644394.9401 | 1248369.0206
1 | 2644719.9756 | 1248466.9599 | 2644715.2178 | 1248473.0503 | 2644702.4003 | 1248503.5075 | 2644674.5909 | 1248493.0702
2 | 2644372.2746 | 1248356.325 | 2644394.9401 | 1248369.0206
3 | 2644319.2978 | 1248291.603 | 2644315.2036 | 1248302.9022 | 2644312.9033 | 1248311.6019 | 2644312.7007 | 1248318.505 | 2644314.4093 | 1248323.2876 | 2644317.0339 | 1248325.7533 | 2644322.7619 | 1248329.254 | 2644331.7074 | 1248333.6794 | 2644354.5007 | 1248346.3693 | 2644372.2746 | 1248356.325
4 | 2644319.2978 | 1248291.603 | 2644320.9013 | 1248286.2002 | 2644325.5273 | 1248273.4818 | 2644329.8558 | 1248263.1739
5 | 2644319.2978 | 1248291.603 | 2644325.0697 | 1248294.2923 | 2644328.6695 | 1248295.5979 | 2644332.4815 | 1248293.9845
6 | 2644329.8558 | 1248263.1739 | 2644315.6025 | 1248256.5964 | 2644310.0371 | 1248253.8162
7 | 2644329.8558 | 1248263.1739 | 2644333.0781 | 1248257.4053
8 | 2644755.159 | 1248355.7576 | 2644751.7685 | 1248353.6015 | 2644744.9589 | 1248345.3668 | 2644744.8245 | 1248342.1086
9 | 2644739.3199 | 1248280.0584 | 2644740.6598 | 1248280.6244 | 2644742.446 | 1248284.0846 | 2644741.4387 | 1248286.4897 | 2644737.1573 | 1248295.4635 | 2644734.2499 | 1248300.4782 | 2644733.8601 | 1248303.0993 | 2644735.2702 | 1248305.367 | 2644736.9945 | 1248307.0255 | 2644744.9415 | 1248312.6448 | 2644746.8062 | 1248313.7151 | 2644750.4182 | 1248315.3879 | 2644744.3525 | 1248330.6635 | 2644744.8245 | 1248342.1086
10 | 2644739.3199 | 1248280.0584 | 2644740.5407 | 1248276.3873 | 2644742.7566 | 1248268.9435 | 2644742.062 | 1248260.9218 | 2644738.8328 | 1248253.5369 | 2644728.933 | 1248244.5118
11 | 2644739.3199 | 1248280.0584 | 2644732.3181 | 1248293.2811 | 2644725.2919 | 1248305.7476 | 2644722.3824 | 1248308.0383 | 2644720.6832 | 1248308.3842
12 | 2644721.1996 | 1248233.5796 | 2644722.4573 | 1248237.0358 | 2644728.933 | 1248244.5118
13 | 2644714.9175 | 1248308.5824 | 2644717.1366 | 1248308.7214 | 2644719.4329 | 1248308.6387 | 2644720.6832 | 1248308.3842
14 | 2644728.9971 | 1248224.9993 | 2644724.7449 | 1248229.0922 | 2644721.1996 | 1248233.5796
15 | 2644648.5321 | 1248218.4444 | 2644661.116 | 1248217.0382 | 2644682.5724 | 1248217.7113 | 2644700.7266 | 1248220.6722 | 2644717.1616 | 1248225.2991 | 2644724.7449 | 1248229.0922 | 2644721.1996 | 1248233.5796
16 | 2644699.0304 | 1248296.6261 | 2644708.2225 | 1248304.1734 | 2644711.7653 | 1248307.0131 | 2644713.4562 | 1248308.1044 | 2644714.9175 | 1248308.5824 | 2644714.9175 | 1248308.5824
17 | 2644697.8395 | 1248295.6483 | 2644699.0304 | 1248296.6261
18 | 2644697.8395 | 1248295.6483 | 2644692.1066 | 1248290.9411
19 | 2644692.1066 | 1248290.9411 | 2644685.2347 | 1248285.2988 | 2644682.3376 | 1248282.942 | 2644682.2082 | 1248282.8025
20 | 2644682.2082 | 1248282.8025 | 2644680.5099 | 1248280.9714 | 2644679.3349 | 1248278.5609 | 2644678.9094 | 1248275.9115 | 2644679.2692 | 1248273.2569 | 2644680.3901 | 1248270.8193 | 2644686.2224 | 1248256.4425 | 2644689.0736 | 1248250.9417
21 | 2644728.9971 | 1248224.9993 | 2644729.7982 | 1248215.8992 | 2644728.9033 | 1248212.4012 | 2644728.6599 | 1248211.6318
22 | 2644648.5321 | 1248218.4444 | 2644639.7685 | 1248233.5548
23 | 2644166.8145 | 1248214.5654 | 2644165.8011 | 1248214.3958 | 2644150.9774 | 1248212.6785
24 | 2644166.8145 | 1248214.5654 | 2644195.6981 | 1248219.3995 | 2644200.3713 | 1248220.201
25 | 2644139.7262 | 1248213.3233 | 2644146.8254 | 1248212.1975 | 2644150.9774 | 1248212.6785
26 | 2644241.3151 | 1248227.7228 | 2644219.447 | 1248223.5347 | 2644216.0988 | 1248222.8983 | 2644200.3713 | 1248220.201
27 | 2644138.5588 | 1248217.9732 | 2644139.7262 | 1248213.3233
28 | 2644139.7262 | 1248213.3233 | 2644138.5762 | 1248207.5219 | 2644139.8025 | 1248192.9213 | 2644140.3051 | 1248190.3233 | 2644141.0073 | 1248188.3161 | 2644143.1049 | 1248186.5194 | 2644146.9024 | 1248185.6248 | 2644157.4741 | 1248185.6924 | 2644169.6979 | 1248185.9836 | 2644178.7192 | 1248185.3503 | 2644182.2997 | 1248184.1984 | 2644191.4386 | 1248185.4392
29 | 2644084.8676 | 1248451.5858 | 2644094.4014 | 1248456.1041 | 2644105.8806 | 1248462.0156 | 2644111.0814 | 1248452.1255 | 2644116.5904 | 1248442.4266 | 2644133.4167 | 1248418.8026 | 2644153.098 | 1248392.0756 | 2644168.0088 | 1248371.1837 | 2644198.5923 | 1248329.5614 | 2644211.3716 | 1248309.999 | 2644224.5501 | 1248284.5135 | 2644229.9839 | 1248271.79 | 2644233.102 | 1248263.7745 | 2644235.3132 | 1248259.9106 | 2644232.9474 | 1248258.1807 | 2644231.1598 | 1248255.8659 | 2644230.1079 | 1248253.134 | 2644229.8729 | 1248250.2192 | 2644230.4756 | 1248247.3662 | 2644232.0219 | 1248244.5759 | 2644234.364 | 1248242.3919 | 2644237.2588 | 1248241.0348 | 2644240.4334 | 1248240.6359 | 2644241.3151 | 1248227.7228
30 | 2644241.3151 | 1248227.7228 | 2644249.47 | 1248229.3572
31 | 2644138.5588 | 1248217.9732 | 2644109.8771 | 1248205.5792
32 | 2644212.4689 | 1248188.2944 | 2644191.4386 | 1248185.4392
33 | 2644084.8676 | 1248451.5858 | 2644154.3642 | 1248330.7052
34 | 2644084.8676 | 1248451.5858 | 2644094.4014 | 1248456.1041 | 2644105.8806 | 1248462.0156 | 2644104.1683 | 1248451.6071 | 2644161.4492 | 1248359.705 | 2644169.9665 | 1248362.826 | 2644200.5385 | 1248318.7019 | 2644205.7476 | 1248310.7799
35 | 2644259.1359 | 1248232.0139 | 2644253.7037 | 1248230.2057 | 2644249.47 | 1248229.3572
36 | 2644085.2738 | 1248192.7825 | 2644101.4868 | 1248201.9536 | 2644109.8771 | 1248205.5792
37 | 2644728.6599 | 1248211.6318 | 2644726.4029 | 1248204.4993 | 2644722.9979 | 1248198.4029 | 2644722.8864 | 1248198.2622
38 | 2644639.7685 | 1248233.5548 | 2644615.2742 | 1248275.7882 | 2644605.3746 | 1248295.1606
39 | 2644199.1729 | 1248307.3842 | 2644148.1024 | 1248273.9565
40 | 2644199.1729 | 1248307.3842 | 2644205.7476 | 1248310.7799
41 | 2644137.9618 | 1248267.3191 | 2644148.1024 | 1248273.9565
42 | 2644205.7476 | 1248310.7799 | 2644294.0705 | 1248357.2691
43 | 2644341.3319 | 1248383.6291 | 2644309.9924 | 1248365.6497 | 2644294.0705 | 1248357.2691
44 | 2644154.5054 | 1248330.4596 | 2644154.3642 | 1248330.7052
45 | 2644259.1359 | 1248232.0139 | 2644269.8992 | 1248235.5968 | 2644281.6857 | 1248240.4523
46 | 2644310.0371 | 1248253.8162 | 2644302.0002 | 1248249.8014 | 2644281.8015 | 1248240.5 | 2644281.6857 | 1248240.4523
47 | 2644333.0781 | 1248257.4053 | 2644338.001 | 1248248.4027 | 2644340.6011 | 1248244.3082
48 | 2644333.0781 | 1248257.4053 | 2644343.4258 | 1248261.1517
49 | 2644430.19 | 1248548.6598 | 2644433.3982 | 1248555.8553 | 2644437.5426 | 1248569.0952 | 2644438.9676 | 1248573.0231
50 | 2644430.19 | 1248548.6598 | 2644433.3688 | 1248539.8903
51 | 2644430.19 | 1248548.6598 | 2644420.1022 | 1248573.8011 | 2644419.1043 | 1248576.9113
52 | 2644452.6327 | 1248487.1089 | 2644446.0793 | 1248504.0934 | 2644438.4017 | 1248526.0061 | 2644433.3688 | 1248539.8903
53 | 2644412.3947 | 1248596.7032 | 2644414.1025 | 1248592.5021 | 2644419.1043 | 1248576.9113
54 | 2644452.6327 | 1248487.1089 | 2644458.863 | 1248492.0589 | 2644470.6347 | 1248499.1964 | 2644482.8832 | 1248505.1588 | 2644498.5987 | 1248514.0048 | 2644555.8994 | 1248539.7965 | 2644573.1395 | 1248547.7091 | 2644594.5499 | 1248558.3549 | 2644607.6439 | 1248567.326 | 2644617.3915 | 1248575.4714 | 2644619.5498 | 1248577.6557
55 | 2644412.3947 | 1248596.7032 | 2644419.9518 | 1248604.9653 | 2644425.6062 | 1248606.1461
56 | 2644373.1028 | 1248628.4972 | 2644375.2025 | 1248626.4004 | 2644378.6041 | 1248624.9026 | 2644382.9021 | 1248623.7006 | 2644389.2518 | 1248621.7801 | 2644393.7979 | 1248619.7017 | 2644402.2002 | 1248611.9038 | 2644409.3023 | 1248604.2963 | 2644412.3947 | 1248596.7032
57 | 2644412.3947 | 1248596.7032 | 2644409.3023 | 1248604.2963 | 2644414 | 1248609.2014 | 2644418.1028 | 1248613.9019 | 2644421.9037 | 1248621.6022 | 2644424.6916 | 1248631.463 | 2644428.0224 | 1248640.4273
58 | 2644638.1756 | 1248550.9224 | 2644635.2862 | 1248565.6105 | 2644619.5498 | 1248577.6557
59 | 2644425.6062 | 1248606.1461 | 2644435.2489 | 1248608.1598 | 2644441.5727 | 1248604.6492 | 2644446.7853 | 1248606.345 | 2644469.7 | 1248591.6068 | 2644467.3803 | 1248584.2092
60 | 2644373.1028 | 1248628.4972 | 2644375.2025 | 1248626.4004 | 2644386.183 | 1248635.2996
61 | 2644373.1028 | 1248628.4972 | 2644360.8982 | 1248619.7 | 2644346.7039 | 1248610.3988 | 2644330.1167 | 1248598.9672 | 2644310.738 | 1248587.2018
62 | 2644428.0224 | 1248640.4273 | 2644436.5999 | 1248634.7017
63 | 2644428.0224 | 1248640.4273 | 2644435.1355 | 1248659.56 | 2644445.4404 | 1248679.9953 | 2644452.8006 | 1248696.0019
64 | 2644427.6952 | 1248730.4518 | 2644395.9518 | 1248728.3795 | 2644371.3433 | 1248724.5935
65 | 2644427.6952 | 1248730.4518 | 2644426.8774 | 1248732.7694 | 2644420.2568 | 1248753.745 | 2644407.2029 | 1248757.5721
66 | 2644427.6952 | 1248730.4518 | 2644447.3683 | 1248730.0433 | 2644467.927 | 1248728.3406 | 2644494.1748 | 1248724.1791 | 2644489.4602 | 1248709.4672
67 | 2644462.0162 | 1248716.0437 | 2644489.4602 | 1248709.4672
68 | 2644489.4602 | 1248709.4672 | 2644482.9282 | 1248682.6857
69 | 2644462.0162 | 1248716.0437 | 2644452.8006 | 1248696.0019
70 | 2644386.183 | 1248635.2996 | 2644362.9693 | 1248663.9906
71 | 2644272.4012 | 1248563.9263 | 2644310.738 | 1248587.2018
72 | 2644436.5999 | 1248634.7017 | 2644447.1275 | 1248627.6746
73 | 2644235.0631 | 1248541.2572 | 2644272.4012 | 1248563.9263
74 | 2644341.3319 | 1248383.6291 | 2644328.4858 | 1248405.0252
75 | 2643968.4408 | 1248253.2894 | 2643947.9626 | 1248218.4478 | 2643939.9793 | 1248202.3335 | 2643938.8622 | 1248200.1367
76 | 2643968.4408 | 1248253.2894 | 2643994.2935 | 1248220.6378
77 | 2643920.2137 | 1248180.0468 | 2643923.9985 | 1248183.2024 | 2643932.3744 | 1248190.169 | 2643936.682 | 1248195.8492 | 2643938.8622 | 1248200.1367
78 | 2644016.5415 | 1248192.5388 | 2643994.2935 | 1248220.6378
79 | 2644460.7688 | 1248618.569 | 2644447.1275 | 1248627.6746
80 | 2644345.0036 | 1248240.005 | 2644340.7978 | 1248243.9984 | 2644340.6011 | 1248244.3082
81 | 2644345.0036 | 1248240.005 | 2644345.0036 | 1248240.005 | 2644350.1982 | 1248238.0981 | 2644352.9137 | 1248237.9758
82 | 2644352.9137 | 1248237.9758 | 2644355.5318 | 1248237.8579
83 | 2644137.9618 | 1248267.3191 | 2644120.4779 | 1248255.8752 | 2644117.0199 | 1248253.7928
84 | 2644714.1044 | 1248190.097 | 2644718.3974 | 1248192.5977 | 2644722.8864 | 1248198.2622
85 | 2644085.2738 | 1248192.7825 | 2644086.898 | 1248186.6016 | 2644087.2043 | 1248184.0021 | 2644087.1013 | 1248180.5991 | 2644085.5028 | 1248176.2065 | 2644076.2034 | 1248166.4976 | 2644060.4334 | 1248151.4973
86 | 2644630.6904 | 1248172.0315 | 2644639.604 | 1248174.6035 | 2644655.8182 | 1248180.6697
87 | 2644611.398 | 1248168.6985 | 2644618.797 | 1248168.8987 | 2644625.4001 | 1248170.505 | 2644630.6904 | 1248172.0315
88 | 2644670.7233 | 1248186.0099 | 2644668.2043 | 1248185.3036 | 2644655.8182 | 1248180.6697
89 | 2644611.398 | 1248168.6985 | 2644610.6043 | 1248171.8057 | 2644607.402 | 1248178.8975 | 2644601.4031 | 1248183.2998 | 2644548.5986 | 1248198.9025 | 2644529.2034 | 1248204.305 | 2644507.0023 | 1248212.2993 | 2644482.0021 | 1248224.9981 | 2644461.7998 | 1248231.3065 | 2644441.4985 | 1248233.7004 | 2644418.9 | 1248235.299 | 2644378.9711 | 1248236.856
90 | 2644670.7233 | 1248186.0099 | 2644675.7023 | 1248187.4059 | 2644688.5996 | 1248188.5038 | 2644697.3572 | 1248188.1502
91 | 2644378.9711 | 1248236.856 | 2644370.1031 | 1248237.2018 | 2644355.5318 | 1248237.8579
92 | 2644714.1044 | 1248190.097 | 2644710.0975 | 1248188.6992 | 2644706.0037 | 1248187.8011 | 2644697.3572 | 1248188.1502
93 | 2644260.9597 | 1248489.4367 | 2644258.6034 | 1248492.4065 | 2644244.9163 | 1248509.9976
94 | 2644260.9597 | 1248489.4367 | 2644269.3934 | 1248478.8072
95 | 2644229.2017 | 1248536.6057 | 2644228.6006 | 1248535.2003 | 2644228.4033 | 1248533.2975 | 2644229.1001 | 1248531.0012 | 2644234.099 | 1248523.9004 | 2644244.9163 | 1248509.9976
96 | 2644296.423 | 1248443.8314 | 2644283.2026 | 1248461.4026 | 2644269.3934 | 1248478.8072
97 | 2644229.2017 | 1248536.6057 | 2644230.1978 | 1248537.7028 | 2644232.9972 | 1248540.0029 | 2644235.0631 | 1248541.2572
98 | 2644229.2017 | 1248536.6057 | 2644203.7413 | 1248517.1029
99 | 2644296.423 | 1248443.8314 | 2644298.899 | 1248440.5406
100 | 2644203.7413 | 1248517.1029 | 2644201.2861 | 1248515.2167 | 2644190.3073 | 1248500.9587 | 2644179.0648 | 1248475.533
101 | 2644318.2042 | 1248417.7988 | 2644315.7112 | 1248420.896 | 2644305.397 | 1248431.9041 | 2644298.899 | 1248440.5406
102 | 2644165.2361 | 1248428.2135 | 2644163.8624 | 1248430.0922 | 2644166.0644 | 1248443.6621 | 2644172.8264 | 1248461.4243 | 2644179.0648 | 1248475.533
103 | 2644328.4858 | 1248405.0252 | 2644318.2042 | 1248417.7988
104 | 2644183.7207 | 1248402.933 | 2644165.2361 | 1248428.2135
105 | 2644183.7207 | 1248402.933 | 2644174.3868 | 1248392.8568 | 2644176.1301 | 1248382.8631 | 2644196.7019 | 1248354.8458
106 | 2644328.4858 | 1248405.0252 | 2644306.0826 | 1248388.6581 | 2644292.8441 | 1248394.8634 | 2644276.7934 | 1248380.8337
107 | 2644016.5415 | 1248192.5388 | 2643998.1401 | 1248180.094 | 2643992.9366 | 1248176.5255
108 | 2644016.5415 | 1248192.5388 | 2644051.1384 | 1248214.4546 | 2644068.0411 | 1248224.2978 | 2644117.0199 | 1248253.7928
109 | 2643949.1709 | 1248149.0047 | 2643978.8984 | 1248166.8981 | 2643992.9366 | 1248176.5255
110 | 2643949.1709 | 1248149.0047 | 2643936.073 | 1248141.1209
111 | 2643922.7898 | 1248133.1256 | 2643936.073 | 1248141.1209
112 | 2644045.3155 | 1248137.2821 | 2644059.804 | 1248150.8987 | 2644060.4334 | 1248151.4973
113 | 2644045.3155 | 1248137.2821 | 2644050.2841 | 1248132.2489 | 2644054.3958 | 1248129.7222 | 2644064.7733 | 1248129.5102 | 2644089.4598 | 1248143.7031

## bus_geodata
| x | y | coords
0 | 2644674.5909 | 1248493.0702
1 | 2644394.9401 | 1248369.0206
2 | 2644719.9756 | 1248466.9599
3 | 2644372.2746 | 1248356.325
4 | 2644319.2978 | 1248291.603
5 | 2644329.8558 | 1248263.1739
6 | 2644332.4815 | 1248293.9845
7 | 2644755.159 | 1248355.7576
8 | 2644744.8245 | 1248342.1086
9 | 2644739.3199 | 1248280.0584
10 | 2644728.933 | 1248244.5118
11 | 2644720.6832 | 1248308.3842
12 | 2644721.1996 | 1248233.5796
13 | 2644714.9175 | 1248308.5824
14 | 2644699.0304 | 1248296.6261
15 | 2644697.8395 | 1248295.6483
16 | 2644692.1066 | 1248290.9411
17 | 2644682.2082 | 1248282.8025
18 | 2644728.9971 | 1248224.9993
19 | 2644648.5321 | 1248218.4444
20 | 2644166.8145 | 1248214.5654
21 | 2644150.9774 | 1248212.6785
22 | 2644200.3713 | 1248220.201
23 | 2644139.7262 | 1248213.3233
24 | 2644241.3151 | 1248227.7228
25 | 2644138.5588 | 1248217.9732
26 | 2644191.4386 | 1248185.4392
27 | 2644084.8676 | 1248451.5858
28 | 2644249.47 | 1248229.3572
29 | 2644109.8771 | 1248205.5792
30 | 2644212.4689 | 1248188.2944
31 | 2644728.6599 | 1248211.6318
32 | 2644639.7685 | 1248233.5548
33 | 2644199.1729 | 1248307.3842
34 | 2644148.1024 | 1248273.9565
35 | 2644205.7476 | 1248310.7799
36 | 2644294.0705 | 1248357.2691
37 | 2644154.3642 | 1248330.7052
38 | 2644259.1359 | 1248232.0139
39 | 2644310.0371 | 1248253.8162
40 | 2644333.0781 | 1248257.4053
41 | 2644438.9676 | 1248573.0231
42 | 2644430.19 | 1248548.6598
43 | 2644433.3688 | 1248539.8903
44 | 2644419.1043 | 1248576.9113
45 | 2644452.6327 | 1248487.1089
46 | 2644412.3947 | 1248596.7032
47 | 2644619.5498 | 1248577.6557
48 | 2644425.6062 | 1248606.1461
49 | 2644373.1028 | 1248628.4972
50 | 2644428.0224 | 1248640.4273
51 | 2644281.6857 | 1248240.4523
52 | 2644371.3433 | 1248724.5935
53 | 2644427.6952 | 1248730.4518
54 | 2644407.2029 | 1248757.5721
55 | 2644489.4602 | 1248709.4672
56 | 2644462.0162 | 1248716.0437
57 | 2644482.9282 | 1248682.6857
58 | 2644386.183 | 1248635.2996
59 | 2644310.738 | 1248587.2018
60 | 2644452.8006 | 1248696.0019
61 | 2644436.5999 | 1248634.7017
62 | 2644362.9693 | 1248663.9906
63 | 2644272.4012 | 1248563.9263
64 | 2644341.3319 | 1248383.6291
65 | 2643968.4408 | 1248253.2894
66 | 2643938.8622 | 1248200.1367
67 | 2643994.2935 | 1248220.6378
68 | 2644154.5054 | 1248330.4596
69 | 2644447.1275 | 1248627.6746
70 | 2644460.7688 | 1248618.569
71 | 2644467.3803 | 1248584.2092
72 | 2644343.4258 | 1248261.1517
73 | 2644340.6011 | 1248244.3082
74 | 2644345.0036 | 1248240.005
75 | 2644352.9137 | 1248237.9758
76 | 2644605.3746 | 1248295.1606
77 | 2644137.9618 | 1248267.3191
78 | 2644722.8864 | 1248198.2622
79 | 2644085.2738 | 1248192.7825
80 | 2644630.6904 | 1248172.0315
81 | 2644655.8182 | 1248180.6697
82 | 2644611.398 | 1248168.6985
83 | 2644670.7233 | 1248186.0099
84 | 2644378.9711 | 1248236.856
85 | 2644697.3572 | 1248188.1502
86 | 2644355.5318 | 1248237.8579
87 | 2644714.1044 | 1248190.097
88 | 2644260.9597 | 1248489.4367
89 | 2644244.9163 | 1248509.9976
90 | 2644269.3934 | 1248478.8072
91 | 2644229.2017 | 1248536.6057
92 | 2644296.423 | 1248443.8314
93 | 2644235.0631 | 1248541.2572
94 | 2644203.7413 | 1248517.1029
95 | 2644298.899 | 1248440.5406
96 | 2644179.0648 | 1248475.533
97 | 2644318.2042 | 1248417.7988
98 | 2644165.2361 | 1248428.2135
99 | 2644183.7207 | 1248402.933
100 | 2644196.7019 | 1248354.8458
101 | 2644276.7934 | 1248380.8337
102 | 2644328.4858 | 1248405.0252
103 | 2644638.1756 | 1248550.9224
104 | 2644016.5415 | 1248192.5388
105 | 2643992.9366 | 1248176.5255
106 | 2644117.0199 | 1248253.7928
107 | 2643920.2137 | 1248180.0468
108 | 2643949.1709 | 1248149.0047
109 | 2643936.073 | 1248141.1209
110 | 2644689.0736 | 1248250.9417
111 | 2643922.7898 | 1248133.1256
112 | 2644060.4334 | 1248151.4973
113 | 2644045.3155 | 1248137.2821
114 | 2644089.4598 | 1248143.7031
115 | 2644328.4858 | 1248405.0252

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97499 | -0.4811 | 0.0016187 | 0.00040569
1 | 0.97555 | -0.47005 | 0.00071592 | 0.00017943
2 | 0.97497 | -0.48154 | 0.00034158 | 8.5609e-05
3 | 0.97562 | -0.46877 | 0.0004 | 0.00010025
4 | 0.9759 | -0.46313 | 0 | 0
5 | 0.97601 | -0.46101 | 0 | 0
6 | 0.97589 | -0.46332 | 0.00071671 | 0.00017962
7 | 0.97068 | -0.56609 | 0.0018527 | 0.00046434
8 | 0.97071 | -0.56547 | 0.00070063 | 0.0001756
9 | 0.97089 | -0.56192 | 0 | 0
10 | 0.97148 | -0.55034 | 0.0033276 | 0.00083397
11 | 0.97048 | -0.57006 | 0.00060933 | 0.00015271
12 | 0.97159 | -0.54802 | 0 | 0
13 | 0.97042 | -0.57135 | 0.00033773 | 8.4643e-05
14 | 0.9702 | -0.57569 | 0.0018768 | 0.00047037
15 | 0.97018 | -0.57597 | 0.0053319 | 0.0013363
16 | 0.97015 | -0.57659 | 0.0023107 | 0.00057912
17 | 0.97013 | -0.57711 | 0.001262 | 0.00031629
18 | 0.97167 | -0.54649 | 0 | 0
19 | 0.97138 | -0.55228 | 0 | 0
20 | 0.97657 | -0.45011 | 0.0015127 | 0.00037911
21 | 0.97635 | -0.45444 | 0.0015133 | 0.00037927
22 | 0.97708 | -0.43993 | 0.0042632 | 0.0010685
23 | 0.97621 | -0.45721 | 0 | 0
24 | 0.97788 | -0.42426 | 0 | 0
25 | 0.97617 | -0.45797 | 0 | 0
26 | 0.97587 | -0.46379 | 0.0024344 | 0.00061013
27 | 0.98635 | -0.25958 | 0 | 0
28 | 0.9777 | -0.42776 | 0.0019643 | 0.0004923
29 | 0.97592 | -0.46292 | 0.006694 | 0.0016777
30 | 0.97583 | -0.46466 | 0.0022425 | 0.00056201
31 | 0.97176 | -0.54471 | 0.00041007 | 0.00010277
32 | 0.97133 | -0.55317 | 0.0017382 | 0.00043564
33 | 0.99233 | -0.14514 | 0 | 0
34 | 0.99154 | -0.16043 | 0.0014107 | 0.00035357
35 | 0.99243 | -0.1433 | 0 | 0
36 | 0.99569 | -0.081395 | 9.2477e-05 | 2.3177e-05
37 | 0.98616 | -0.26344 | 0.00077028 | 0.00019305
38 | 0.97749 | -0.43186 | 0.0017996 | 0.00045102
39 | 0.97641 | -0.45311 | 0.0020731 | 0.00051957
40 | 0.97589 | -0.46324 | 0 | 0
41 | 0.98351 | -0.31671 | 0.0018905 | 0.00047381
42 | 0.98355 | -0.31583 | 0 | 0
43 | 0.98353 | -0.31637 | 0.0012998 | 0.00032575
44 | 0.98369 | -0.31305 | 0.0012769 | 0.00032002
45 | 0.98343 | -0.31828 | 0 | 0
46 | 0.98382 | -0.31065 | 0 | 0
47 | 0.9831 | -0.32476 | 0 | 0
48 | 0.98379 | -0.31126 | 0.00057222 | 0.00014341
49 | 0.98527 | -0.2825 | 0 | 0
50 | 0.98146 | -0.35625 | 0 | 0
51 | 0.977 | -0.44143 | 0.0041411 | 0.0010379
52 | 0.97299 | -0.52202 | 0.0070216 | 0.0017598
53 | 0.97336 | -0.51469 | 0 | 0
54 | 0.97212 | -0.53929 | 0.035096 | 0.0087958
55 | 0.9766 | -0.4511 | 0 | 0
56 | 0.97778 | -0.42792 | 0 | 0
57 | 0.97652 | -0.45262 | 0.0030191 | 0.00075665
58 | 0.98509 | -0.28601 | 0 | 0
59 | 0.98691 | -0.25088 | 0.028551 | 0.0071555
60 | 0.97871 | -0.40978 | 0.0032791 | 0.00082182
61 | 0.98144 | -0.35671 | 0.00049627 | 0.00012438
62 | 0.98471 | -0.2936 | 0.011445 | 0.0028685
63 | 0.98829 | -0.22436 | 0.049779 | 0.012476
64 | 0.99745 | -0.047966 | 0 | 0
65 | 0.9901 | -0.18843 | 0 | 0
66 | 0.98997 | -0.1909 | 0.0010656 | 0.00026707
67 | 0.99019 | -0.18675 | 0.00085962 | 0.00021544
68 | 0.98616 | -0.26344 | 0.00077028 | 0.00019305
69 | 0.98142 | -0.35717 | 0.00092369 | 0.0002315
70 | 0.9814 | -0.35748 | 0.0010541 | 0.00026417
71 | 0.98371 | -0.31274 | 0.0014211 | 0.00035616
72 | 0.97585 | -0.46411 | 0.0042964 | 0.0010768
73 | 0.97566 | -0.46795 | 0.0014159 | 0.00035486
74 | 0.97556 | -0.46981 | 0.0090611 | 0.0022709
75 | 0.97546 | -0.47186 | 0.0060377 | 0.0015132
76 | 0.97127 | -0.5545 | 0.0010164 | 0.00025473
77 | 0.9914 | -0.16316 | 0.0014749 | 0.00036964
78 | 0.97186 | -0.54276 | 0.0011938 | 0.00029919
79 | 0.97586 | -0.46392 | 0 | 0
80 | 0.97266 | -0.52692 | 0.0015779 | 0.00039547
81 | 0.97243 | -0.53158 | 0.0010692 | 0.00026797
82 | 0.97285 | -0.52327 | 0 | 0
83 | 0.97229 | -0.53425 | 0.001026 | 0.00025715
84 | 0.97518 | -0.47721 | 0.0033327 | 0.00083525
85 | 0.97207 | -0.53863 | 0.0035251 | 0.00088347
86 | 0.97543 | -0.47241 | 0.00099908 | 0.00025039
87 | 0.97195 | -0.54104 | 0 | 0
88 | 0.99486 | -0.098017 | 0.044124 | 0.011059
89 | 0.99292 | -0.13509 | 0.020883 | 0.0052339
90 | 0.99604 | -0.075279 | 0.0061266 | 0.0015355
91 | 0.99074 | -0.177 | 0 | 0
92 | 1 | 0 | -0.4127 | -0.10519
93 | 0.99029 | -0.18571 | 0.046442 | 0.011639
94 | 0.99 | -0.1914 | 0 | 0
95 | 0.99986 | -0.0027164 | 0.0018339 | 0.00045961
96 | 0.98886 | -0.21342 | 0.0038498 | 0.00096486
97 | 0.99882 | -0.022123 | 0.002004 | 0.00050226
98 | 0.98787 | -0.23275 | 0.0075234 | 0.0018855
99 | 0.98747 | -0.24054 | 0 | 0
100 | 0.98672 | -0.25515 | 0.013924 | 0.0034896
101 | 0.99803 | -0.037156 | 0.0040869 | 0.0010243
102 | 0.99827 | -0.032602 | 0 | 0
103 | 0.98304 | -0.32594 | 0.0018832 | 0.00047198
104 | 0.99029 | -0.18475 | 0 | 0
105 | 0.99017 | -0.18718 | 0.0017986 | 0.00045076
106 | 0.99115 | -0.16814 | 0.0033003 | 0.00082713
107 | 0.98994 | -0.1915 | 0.0012093 | 0.00030307
108 | 0.99002 | -0.18995 | 0.0010718 | 0.00026861
109 | 0.99 | -0.19047 | 0.00097352 | 0.00024399
110 | 0.97009 | -0.57772 | 0.00094179 | 0.00023604
111 | 0.98998 | -0.19074 | 0.00095799 | 0.0002401
112 | 0.97577 | -0.4658 | 0.00089043 | 0.00022316
113 | 0.97575 | -0.46621 | 0 | 0
114 | 0.9757 | -0.4672 | 0.0010704 | 0.00026827
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019603 | -0.00049042 | 0.0019613 | 0.00048726 | 1.0274e-06 | -3.1647e-06 | 0.0029915 | 0.0029901 | 0.0029915 | 0.97499 | -0.4811 | 0.97555 | -0.47005 | 0.82183
1 | 0.00034159 | 8.4734e-05 | -0.00034158 | -8.5609e-05 | 7.1785e-09 | -8.7432e-07 | 0.00052101 | 0.00052133 | 0.00052133 | 0.97499 | -0.4811 | 0.97497 | -0.48154 | 0.14322
2 | -0.0026772 | -0.00066668 | 0.0026774 | 0.00066646 | 1.6233e-07 | -2.2049e-07 | 0.0040821 | 0.004082 | 0.0040821 | 0.97555 | -0.47005 | 0.97562 | -0.46877 | 1.1215
3 | -0.0030774 | -0.00076671 | 0.0030782 | 0.00076599 | 8.2348e-07 | -7.1902e-07 | 0.0046921 | 0.0046916 | 0.0046921 | 0.97562 | -0.46877 | 0.9759 | -0.46313 | 1.289
4 | -0.003795 | -0.00094544 | 0.0037953 | 0.00094531 | 3.8078e-07 | -1.3554e-07 | 0.0057844 | 0.0057842 | 0.0057844 | 0.9759 | -0.46313 | 0.97601 | -0.46101 | 1.5891
5 | 0.00071672 | 0.00017945 | -0.00071671 | -0.00017962 | 6.4201e-09 | -1.7501e-07 | 0.0010928 | 0.0010928 | 0.0010928 | 0.9759 | -0.46313 | 0.97589 | -0.46332 | 0.30023
6 | -0.059198 | -0.014866 | 0.05922 | 0.01488 | 2.2323e-05 | 1.3465e-05 | 0.090263 | 0.090263 | 0.090263 | 0.97601 | -0.46101 | 0.97641 | -0.45311 | 8.2659
7 | 0.055402 | 0.013921 | -0.055396 | -0.013917 | 5.8914e-06 | 3.5229e-06 | 0.084479 | 0.084479 | 0.084479 | 0.97601 | -0.46101 | 0.97589 | -0.46324 | 7.7362
8 | -0.0018527 | -0.00046434 | 0.0018528 | 0.00046415 | 5.4341e-08 | -1.8729e-07 | 0.0028402 | 0.0028401 | 0.0028402 | 0.97068 | -0.56609 | 0.97071 | -0.56547 | 0.78027
9 | -0.0025534 | -0.00063975 | 0.0025539 | 0.0006391 | 4.3178e-07 | -6.53e-07 | 0.0039141 | 0.0039138 | 0.0039141 | 0.97071 | -0.56547 | 0.97089 | -0.56192 | 1.0753
10 | -0.015233 | -0.0038185 | 0.015241 | 0.0038234 | 8.4093e-06 | 4.8728e-06 | 0.023346 | 0.023346 | 0.023346 | 0.97089 | -0.56192 | 0.97148 | -0.55034 | 6.4138
11 | 0.012679 | 0.0031794 | -0.012674 | -0.0031767 | 4.9151e-06 | 2.7166e-06 | 0.019432 | 0.019433 | 0.019433 | 0.97089 | -0.56192 | 0.97048 | -0.57006 | 5.3386
12 | -0.018569 | -0.0046574 | 0.018571 | 0.0046583 | 2.0582e-06 | 9.8119e-07 | 0.028443 | 0.028443 | 0.028443 | 0.97148 | -0.55034 | 0.97159 | -0.54802 | 3.907
13 | 0.012064 | 0.003024 | -0.012064 | -0.0030236 | 7.439e-07 | 4.0447e-07 | 0.018498 | 0.018498 | 0.018498 | 0.97048 | -0.57006 | 0.97042 | -0.57135 | 5.082
14 | -0.021326 | -0.0053471 | 0.021327 | 0.0053476 | 1.5496e-06 | 5.5997e-07 | 0.032662 | 0.032662 | 0.032662 | 0.97159 | -0.54802 | 0.97167 | -0.54649 | 2.991
15 | 0.0027553 | 0.00068871 | -0.0027548 | -0.00068939 | 5.5943e-07 | -6.795e-07 | 0.0042192 | 0.0042195 | 0.0042195 | 0.97159 | -0.54802 | 0.97138 | -0.55228 | 1.1592
16 | 0.011726 | 0.0029389 | -0.011724 | -0.0029376 | 2.4228e-06 | 1.3037e-06 | 0.01798 | 0.017981 | 0.017981 | 0.97042 | -0.57135 | 0.9702 | -0.57569 | 4.9397
17 | 0.0098468 | 0.0024673 | -0.0098466 | -0.0024672 | 1.3179e-07 | 6.5316e-08 | 0.015102 | 0.015102 | 0.015102 | 0.9702 | -0.57569 | 0.97018 | -0.57597 | 4.1489
18 | 0.0045147 | 0.0011309 | -0.0045146 | -0.0011309 | 1.3337e-07 | -6.2406e-09 | 0.0069242 | 0.0069243 | 0.0069243 | 0.97018 | -0.57597 | 0.97015 | -0.57659 | 1.9023
19 | 0.0022039 | 0.00055179 | -0.0022038 | -0.00055191 | 5.4913e-08 | -1.2311e-07 | 0.0033801 | 0.0033802 | 0.0033802 | 0.97015 | -0.57659 | 0.97013 | -0.57711 | 0.92862
20 | 0.00094182 | 0.00023562 | -0.00094179 | -0.00023604 | 2.7336e-08 | -4.1384e-07 | 0.0014444 | 0.0014446 | 0.0014446 | 0.97013 | -0.57711 | 0.97009 | -0.57772 | 0.39687
21 | -0.021327 | -0.0053476 | 0.021329 | 0.0053483 | 1.8072e-06 | 6.5297e-07 | 0.032662 | 0.032662 | 0.032662 | 0.97167 | -0.54649 | 0.97176 | -0.54471 | 2.991
22 | 0.0027548 | 0.00068939 | -0.0027547 | -0.00068953 | 1.1663e-07 | -1.4158e-07 | 0.0042195 | 0.0042196 | 0.0042196 | 0.97138 | -0.55228 | 0.97133 | -0.55317 | 1.1592
23 | 0.014854 | 0.0037224 | -0.014851 | -0.0037207 | 3.0641e-06 | 1.7615e-06 | 0.022633 | 0.022634 | 0.022634 | 0.97657 | -0.45011 | 0.97635 | -0.45444 | 6.218
24 | -0.016367 | -0.0041015 | 0.016375 | 0.0041062 | 7.9357e-06 | 4.6529e-06 | 0.024938 | 0.024938 | 0.024938 | 0.97657 | -0.45011 | 0.97708 | -0.43993 | 6.8512
25 | 0.013338 | 0.0033414 | -0.013336 | -0.0033404 | 1.7614e-06 | 9.8516e-07 | 0.020327 | 0.020327 | 0.020327 | 0.97635 | -0.45444 | 0.97621 | -0.45721 | 5.5844
26 | -0.020638 | -0.0051747 | 0.020653 | 0.005184 | 1.5422e-05 | 9.3485e-06 | 0.031431 | 0.031431 | 0.031431 | 0.97708 | -0.43993 | 0.97788 | -0.42426 | 8.6348
27 | 0.0086575 | 0.0021685 | -0.0086572 | -0.0021683 | 3.1306e-07 | 1.4042e-07 | 0.013196 | 0.013196 | 0.013196 | 0.97621 | -0.45721 | 0.97617 | -0.45797 | 3.6253
28 | 0.0046785 | 0.0011719 | -0.004677 | -0.0011719 | 1.4652e-06 | -2.2503e-08 | 0.0071311 | 0.0071314 | 0.0071314 | 0.97621 | -0.45721 | 0.97587 | -0.46379 | 1.9592
29 | -0.08994 | -0.022619 | 0.090654 | 0.023064 | 0.00071345 | 0.00044504 | 0.13689 | 0.13688 | 0.13689 | 0.97788 | -0.42426 | 0.98635 | -0.25958 | 12.5355
30 | 0.069287 | 0.017435 | -0.069275 | -0.017427 | 1.1562e-05 | 7.0868e-06 | 0.10546 | 0.10546 | 0.10546 | 0.97788 | -0.42426 | 0.9777 | -0.42776 | 9.6573
31 | 0.0086572 | 0.0021683 | -0.0086552 | -0.0021674 | 2.0404e-06 | 9.1533e-07 | 0.013196 | 0.013196 | 0.013196 | 0.97617 | -0.45797 | 0.97592 | -0.46292 | 3.6253
32 | 0.0022426 | 0.00056181 | -0.0022425 | -0.00056201 | 9.3057e-08 | -2.0559e-07 | 0.0034194 | 0.0034195 | 0.0034195 | 0.97587 | -0.46379 | 0.97583 | -0.46466 | 0.93942
33 | 0.0015408 | 0.0003845 | -0.0015406 | -0.0003861 | 2.8247e-07 | -1.5986e-06 | 0.0023239 | 0.0023246 | 0.0023246 | 0.98635 | -0.25958 | 0.98616 | -0.26344 | 0.63862
34 | -0.092195 | -0.023448 | 0.092714 | 0.023772 | 0.00051967 | 0.00032432 | 0.13921 | 0.1392 | 0.13921 | 0.98635 | -0.25958 | 0.99243 | -0.1433 | 12.748
35 | 0.067311 | 0.016935 | -0.067298 | -0.016927 | 1.3181e-05 | 8.0582e-06 | 0.10247 | 0.10247 | 0.10247 | 0.9777 | -0.42776 | 0.97749 | -0.43186 | 9.3835
36 | 0.0019612 | 0.00048976 | -0.0019611 | -0.00049005 | 9.3074e-08 | -2.8737e-07 | 0.0029897 | 0.0029898 | 0.0029898 | 0.97592 | -0.46292 | 0.97586 | -0.46392 | 0.82137
37 | -0.021739 | -0.005451 | 0.021741 | 0.0054518 | 2.0285e-06 | 7.5391e-07 | 0.033289 | 0.033289 | 0.033289 | 0.97176 | -0.54471 | 0.97186 | -0.54276 | 3.0485
38 | 0.0010164 | 0.00025389 | -0.0010164 | -0.00025473 | 6.4158e-08 | -8.3249e-07 | 0.0015568 | 0.0015571 | 0.0015571 | 0.97133 | -0.55317 | 0.97127 | -0.5545 | 0.42778
39 | 0.014145 | 0.0035475 | -0.014135 | -0.0035417 | 1.0299e-05 | 5.8031e-06 | 0.021211 | 0.021212 | 0.021212 | 0.99233 | -0.14514 | 0.99154 | -0.16043 | 5.8274
40 | -0.014145 | -0.0035475 | 0.014146 | 0.0035482 | 1.2455e-06 | 7.0174e-07 | 0.021211 | 0.021211 | 0.021211 | 0.99233 | -0.14514 | 0.99243 | -0.1433 | 5.8273
41 | 0.012724 | 0.0031882 | -0.012722 | -0.0031873 | 1.6571e-06 | 9.0423e-07 | 0.019095 | 0.019095 | 0.019095 | 0.99154 | -0.16043 | 0.9914 | -0.16316 | 5.2458
42 | -0.10686 | -0.027321 | 0.10718 | 0.027522 | 0.00032105 | 0.00020159 | 0.16042 | 0.16041 | 0.16042 | 0.99243 | -0.1433 | 0.99569 | -0.081395 | 14.6901
43 | -0.10727 | -0.027545 | 0.10745 | 0.027655 | 0.00017439 | 0.0001095 | 0.16055 | 0.16055 | 0.16055 | 0.99569 | -0.081395 | 0.99745 | -0.047966 | 14.7026
44 | 0.00077028 | 0.00019305 | -0.00077028 | -0.00019305 | 1.4304e-10 | -3.5232e-09 | 0.0011623 | 0.0011623 | 0.0011623 | 0.98616 | -0.26344 | 0.98616 | -0.26344 | 0.31931
45 | 0.065498 | 0.016476 | -0.065468 | -0.016458 | 2.9951e-05 | 1.8263e-05 | 0.099729 | 0.099729 | 0.099729 | 0.97749 | -0.43186 | 0.977 | -0.44143 | 9.1327
46 | -0.061293 | -0.015399 | 0.061327 | 0.01542 | 3.4198e-05 | 2.071e-05 | 0.093422 | 0.093422 | 0.093422 | 0.97641 | -0.45311 | 0.977 | -0.44143 | 8.5552
47 | 0.0511 | 0.012841 | -0.051088 | -0.012834 | 1.1471e-05 | 6.775e-06 | 0.077928 | 0.077928 | 0.077928 | 0.97589 | -0.46324 | 0.97566 | -0.46795 | 7.1363
48 | 0.0042966 | 0.0010768 | -0.0042964 | -0.0010768 | 1.7713e-07 | -2.4135e-08 | 0.0065513 | 0.0065513 | 0.0065513 | 0.97589 | -0.46324 | 0.97585 | -0.46411 | 1.7998
49 | -0.0018905 | -0.00047381 | 0.0018906 | 0.00047353 | 7.9549e-08 | -2.7816e-07 | 0.0028603 | 0.0028602 | 0.0028603 | 0.98351 | -0.31671 | 0.98355 | -0.31583 | 0.78579
50 | 0.0031839 | 0.00079464 | -0.0031838 | -0.00079471 | 8.1123e-08 | -6.6461e-08 | 0.0048157 | 0.0048158 | 0.0048158 | 0.98355 | -0.31583 | 0.98353 | -0.31637 | 1.323
51 | -0.0050745 | -0.0012682 | 0.0050752 | 0.0012682 | 6.707e-07 | 4.3935e-08 | 0.0076759 | 0.0076758 | 0.0076759 | 0.98355 | -0.31583 | 0.98369 | -0.31305 | 2.1088
52 | 0.0018841 | 0.00046896 | -0.0018839 | -0.00046956 | 1.7109e-07 | -6.0354e-07 | 0.0028493 | 0.0028496 | 0.0028496 | 0.98353 | -0.31637 | 0.98343 | -0.31828 | 0.78285
53 | -0.0063521 | -0.0015882 | 0.0063528 | 0.0015884 | 7.2369e-07 | 1.977e-07 | 0.0096073 | 0.0096072 | 0.0096073 | 0.98369 | -0.31305 | 0.98382 | -0.31065 | 2.6394
54 | 0.0018839 | 0.00046956 | -0.0018833 | -0.0004716 | 5.7968e-07 | -2.0429e-06 | 0.0028496 | 0.0028504 | 0.0028504 | 0.98343 | -0.31828 | 0.9831 | -0.32476 | 0.78309
55 | 0.0019935 | 0.00049872 | -0.0019934 | -0.0004989 | 5.7853e-08 | -1.785e-07 | 0.0030148 | 0.0030149 | 0.0030149 | 0.98382 | -0.31065 | 0.98379 | -0.31126 | 0.82826
56 | -0.059736 | -0.015156 | 0.059817 | 0.015207 | 8.1008e-05 | 5.0501e-05 | 0.090416 | 0.090416 | 0.090416 | 0.98382 | -0.31065 | 0.98527 | -0.2825 | 12.4198
57 | 0.051389 | 0.013069 | -0.051277 | -0.012998 | 0.00011263 | 7.1454e-05 | 0.077794 | 0.077795 | 0.077795 | 0.98382 | -0.31065 | 0.98146 | -0.35625 | 21.3721
58 | 0.0018833 | 0.0004716 | -0.0018832 | -0.00047198 | 1.0589e-07 | -3.7284e-07 | 0.0028504 | 0.0028506 | 0.0028506 | 0.9831 | -0.32476 | 0.98304 | -0.32594 | 0.78313
59 | 0.0014212 | 0.00035549 | -0.0014211 | -0.00035616 | 9.9733e-08 | -6.6701e-07 | 0.0021493 | 0.0021496 | 0.0021496 | 0.98379 | -0.31126 | 0.98371 | -0.31274 | 0.59055
60 | 0.011452 | 0.0028717 | -0.01145 | -0.0028707 | 1.9183e-06 | 1.01e-06 | 0.017295 | 0.017295 | 0.017295 | 0.98527 | -0.2825 | 0.98509 | -0.28601 | 4.7515
61 | -0.071268 | -0.018078 | 0.071377 | 0.018145 | 0.00010852 | 6.6588e-05 | 0.10771 | 0.10771 | 0.10771 | 0.98527 | -0.2825 | 0.98691 | -0.25088 | 9.8636
62 | 0.0024741 | 0.00061962 | -0.0024741 | -0.00061972 | 5.4412e-08 | -9.5502e-08 | 0.0037509 | 0.003751 | 0.003751 | 0.98146 | -0.35625 | 0.98144 | -0.35671 | 1.0305
63 | 0.048803 | 0.012378 | -0.048677 | -0.012299 | 0.00012524 | 7.9386e-05 | 0.074044 | 0.074044 | 0.074044 | 0.98146 | -0.35625 | 0.97871 | -0.40978 | 20.3417
64 | -0.0070216 | -0.0017598 | 0.0070241 | 0.0017607 | 2.4521e-06 | 8.6476e-07 | 0.010738 | 0.010738 | 0.010738 | 0.97299 | -0.52202 | 0.97336 | -0.51469 | 2.9501
65 | 0.035137 | 0.0088217 | -0.035096 | -0.0087958 | 4.1186e-05 | 2.5886e-05 | 0.053721 | 0.053721 | 0.053721 | 0.97336 | -0.51469 | 0.97212 | -0.53929 | 14.7585
66 | -0.042161 | -0.010582 | 0.042289 | 0.010663 | 0.00012828 | 8.1072e-05 | 0.064459 | 0.064458 | 0.064459 | 0.97336 | -0.51469 | 0.9766 | -0.4511 | 17.7084
67 | -0.045309 | -0.01142 | 0.045359 | 0.011452 | 5.0329e-05 | 3.1858e-05 | 0.069059 | 0.069059 | 0.069059 | 0.9766 | -0.4511 | 0.97778 | -0.42792 | 18.9722
68 | 0.0030193 | 0.00075645 | -0.0030191 | -0.00075665 | 2.1878e-07 | -2.0488e-07 | 0.0046003 | 0.0046004 | 0.0046004 | 0.9766 | -0.4511 | 0.97652 | -0.45262 | 1.2639
69 | -0.045359 | -0.011452 | 0.045398 | 0.011477 | 3.945e-05 | 2.4971e-05 | 0.069059 | 0.069058 | 0.069059 | 0.97778 | -0.42792 | 0.97871 | -0.40978 | 18.9721
70 | 0.01145 | 0.0028707 | -0.011445 | -0.0028685 | 4.1399e-06 | 2.1799e-06 | 0.017295 | 0.017296 | 0.017296 | 0.98509 | -0.28601 | 0.98471 | -0.2936 | 4.7515
71 | -0.099927 | -0.0253 | 0.10005 | 0.02538 | 0.00012741 | 7.9824e-05 | 0.15076 | 0.15076 | 0.15076 | 0.98691 | -0.25088 | 0.98829 | -0.22436 | 13.8056
72 | 0.0019778 | 0.00049534 | -0.0019778 | -0.00049547 | 4.2678e-08 | -1.3263e-07 | 0.0029985 | 0.0029986 | 0.0029986 | 0.98144 | -0.35671 | 0.98142 | -0.35717 | 0.82379
73 | -0.14983 | -0.037856 | 0.15011 | 0.038032 | 0.00027815 | 0.00017634 | 0.22571 | 0.2257 | 0.22571 | 0.98829 | -0.22436 | 0.99029 | -0.18571 | 20.669
74 | -0.10745 | -0.027655 | 0.10753 | 0.027705 | 8.0356e-05 | 5.0451e-05 | 0.16055 | 0.16055 | 0.16055 | 0.99745 | -0.047966 | 0.99827 | -0.032602 | 14.7026
75 | 0.0022752 | 0.00056919 | -0.0022749 | -0.0005698 | 2.6681e-07 | -6.1188e-07 | 0.003419 | 0.0034193 | 0.0034193 | 0.9901 | -0.18843 | 0.98997 | -0.1909 | 0.93936
76 | -0.0022752 | -0.00056919 | 0.0022754 | 0.00056877 | 1.8255e-07 | -4.1883e-07 | 0.003419 | 0.0034188 | 0.003419 | 0.9901 | -0.18843 | 0.99019 | -0.18675 | 0.93929
77 | 0.0012093 | 0.00030273 | -0.0012093 | -0.00030307 | 3.4393e-08 | -3.3492e-07 | 0.0018175 | 0.0018177 | 0.0018177 | 0.98997 | -0.1909 | 0.98994 | -0.1915 | 0.49936
78 | -0.003135 | -0.00078422 | 0.0031353 | 0.00078395 | 2.9822e-07 | -2.702e-07 | 0.0047106 | 0.0047105 | 0.0047106 | 0.99019 | -0.18675 | 0.99029 | -0.18475 | 1.2941
79 | 0.0010541 | 0.00026397 | -0.0010541 | -0.00026417 | 1.5709e-08 | -1.9719e-07 | 0.0015981 | 0.0015982 | 0.0015982 | 0.98142 | -0.35717 | 0.9814 | -0.35748 | 0.43906
80 | 0.049673 | 0.012479 | -0.049668 | -0.012476 | 4.4253e-06 | 2.6012e-06 | 0.075769 | 0.075769 | 0.075769 | 0.97566 | -0.46795 | 0.97556 | -0.46981 | 6.9385
81 | 0.040607 | 0.010205 | -0.040603 | -0.010203 | 3.9583e-06 | 2.2243e-06 | 0.061948 | 0.061948 | 0.061948 | 0.97556 | -0.46981 | 0.97546 | -0.47186 | 5.6729
82 | 0.034565 | 0.00869 | -0.034564 | -0.0086896 | 9.1113e-07 | 4.8498e-07 | 0.052738 | 0.052738 | 0.052738 | 0.97546 | -0.47186 | 0.97543 | -0.47241 | 4.8295
83 | 0.011247 | 0.0028176 | -0.011245 | -0.0028163 | 2.6644e-06 | 1.3838e-06 | 0.016881 | 0.016881 | 0.016881 | 0.9914 | -0.16316 | 0.99115 | -0.16814 | 4.6377
84 | -0.022935 | -0.005751 | 0.022937 | 0.0057517 | 1.88e-06 | 7.4979e-07 | 0.035117 | 0.035117 | 0.035117 | 0.97186 | -0.54276 | 0.97195 | -0.54104 | 3.2159
85 | 0.0019611 | 0.00049005 | -0.0019609 | -0.00049059 | 1.7531e-07 | -5.411e-07 | 0.0029898 | 0.00299 | 0.00299 | 0.97586 | -0.46392 | 0.97577 | -0.4658 | 0.82144
86 | 0.028575 | 0.0071686 | -0.028569 | -0.0071655 | 6.3525e-06 | 3.0758e-06 | 0.043718 | 0.043719 | 0.043719 | 0.97266 | -0.52692 | 0.97243 | -0.53158 | 4.0035
87 | -0.030153 | -0.0075641 | 0.030159 | 0.0075667 | 5.2416e-06 | 2.6208e-06 | 0.046132 | 0.046132 | 0.046132 | 0.97266 | -0.52692 | 0.97285 | -0.52327 | 4.2246
88 | 0.0275 | 0.0068976 | -0.027496 | -0.0068959 | 3.5066e-06 | 1.6548e-06 | 0.042082 | 0.042083 | 0.042083 | 0.97243 | -0.53158 | 0.97229 | -0.53425 | 3.8537
89 | -0.030159 | -0.0075667 | 0.030225 | 0.0075999 | 6.6362e-05 | 3.3156e-05 | 0.046132 | 0.046129 | 0.046132 | 0.97285 | -0.52327 | 0.97518 | -0.47721 | 4.2245
90 | 0.02647 | 0.0066388 | -0.026465 | -0.0066363 | 5.5146e-06 | 2.5295e-06 | 0.040512 | 0.040513 | 0.040513 | 0.97229 | -0.53425 | 0.97207 | -0.53863 | 3.71
91 | -0.033558 | -0.0084351 | 0.033565 | 0.0084392 | 7.6918e-06 | 4.0444e-06 | 0.051214 | 0.051214 | 0.051214 | 0.97518 | -0.47721 | 0.97543 | -0.47241 | 4.6899
92 | 0.02294 | 0.0057528 | -0.022937 | -0.0057517 | 2.6342e-06 | 1.0504e-06 | 0.035117 | 0.035117 | 0.035117 | 0.97207 | -0.53863 | 0.97195 | -0.54104 | 3.2158
93 | 0.24378 | 0.061907 | -0.24334 | -0.06163 | 0.00043408 | 0.0002768 | 0.36491 | 0.36491 | 0.36491 | 0.99486 | -0.098017 | 0.99292 | -0.13509 | 33.4163
94 | -0.2879 | -0.072966 | 0.28821 | 0.073167 | 0.00031493 | 0.00020102 | 0.4309 | 0.4309 | 0.4309 | 0.99486 | -0.098017 | 0.99604 | -0.075279 | 39.4599
95 | 0.22246 | 0.056396 | -0.22201 | -0.056111 | 0.00044714 | 0.00028492 | 0.33361 | 0.33361 | 0.33361 | 0.99292 | -0.13509 | 0.99074 | -0.177 | 30.5504
96 | -0.29434 | -0.074702 | 0.29541 | 0.075385 | 0.0010701 | 0.00068311 | 0.44005 | 0.44005 | 0.44005 | 0.99604 | -0.075279 | 1 | 0 | 40.2981
97 | 0.19664 | 0.049724 | -0.19655 | -0.049672 | 8.2094e-05 | 5.225e-05 | 0.29549 | 0.29549 | 0.29549 | 0.99074 | -0.177 | 0.99029 | -0.18571 | 27.0594
98 | 0.025376 | 0.0063875 | -0.025358 | -0.0063768 | 1.7446e-05 | 1.0753e-05 | 0.038122 | 0.038122 | 0.038122 | 0.99074 | -0.177 | 0.99 | -0.1914 | 10.4731
99 | 0.11563 | 0.029804 | -0.11562 | -0.029795 | 1.5293e-05 | 9.6253e-06 | 0.17236 | 0.17236 | 0.17236 | 1 | 0 | 0.99986 | -0.0027164 | 15.7837
100 | 0.025358 | 0.0063768 | -0.025331 | -0.0063604 | 2.6645e-05 | 1.6425e-05 | 0.038122 | 0.038122 | 0.038122 | 0.99 | -0.1914 | 0.98886 | -0.21342 | 10.4732
101 | 0.11379 | 0.029335 | -0.11368 | -0.029267 | 0.00010743 | 6.7582e-05 | 0.16963 | 0.16963 | 0.16963 | 0.99986 | -0.0027164 | 0.99882 | -0.022123 | 15.5339
102 | 0.021482 | 0.0053955 | -0.021462 | -0.0053835 | 1.9796e-05 | 1.2022e-05 | 0.032329 | 0.032329 | 0.032329 | 0.98886 | -0.21342 | 0.98787 | -0.23275 | 8.8817
103 | 0.11167 | 0.028765 | -0.11162 | -0.028729 | 5.692e-05 | 3.5785e-05 | 0.16664 | 0.16664 | 0.16664 | 0.99882 | -0.022123 | 0.99827 | -0.032602 | 15.2605
104 | 0.013938 | 0.0034979 | -0.013933 | -0.003495 | 5.1777e-06 | 2.9129e-06 | 0.020997 | 0.020997 | 0.020997 | 0.98787 | -0.23275 | 0.98747 | -0.24054 | 5.7684
105 | 0.013933 | 0.003495 | -0.013924 | -0.0034896 | 9.6947e-06 | 5.4551e-06 | 0.020997 | 0.020997 | 0.020997 | 0.98747 | -0.24054 | 0.98672 | -0.25515 | 5.7685
106 | -0.0040869 | -0.0010243 | 0.0040878 | 0.001024 | 8.8665e-07 | -2.6494e-07 | 0.0060934 | 0.0060931 | 0.0060934 | 0.99803 | -0.037156 | 0.99827 | -0.032602 | 1.674
107 | 0.0048028 | 0.0012027 | -0.0048023 | -0.0012027 | 5.5705e-07 | -1.0427e-08 | 0.0072164 | 0.0072165 | 0.0072165 | 0.99029 | -0.18475 | 0.99017 | -0.18718 | 1.9826
108 | -0.0079381 | -0.0019866 | 0.0079444 | 0.0019891 | 6.2777e-06 | 2.5022e-06 | 0.011927 | 0.011926 | 0.011927 | 0.99029 | -0.18475 | 0.99115 | -0.16814 | 3.2766
109 | 0.0030037 | 0.00075192 | -0.0030033 | -0.00075234 | 3.9516e-07 | -4.1225e-07 | 0.0045137 | 0.0045139 | 0.0045139 | 0.99017 | -0.18718 | 0.99002 | -0.18995 | 1.2401
110 | 0.0019316 | 0.00048372 | -0.0019315 | -0.00048389 | 4.8315e-08 | -1.6565e-07 | 0.002903 | 0.0029031 | 0.0029031 | 0.99002 | -0.18995 | 0.99 | -0.19047 | 0.79756
111 | 0.000958 | 0.0002399 | -0.00095799 | -0.0002401 | 1.2054e-08 | -1.9163e-07 | 0.0014399 | 0.0014399 | 0.0014399 | 0.99 | -0.19047 | 0.98998 | -0.19074 | 0.39559
112 | 0.0010705 | 0.00026743 | -0.0010705 | -0.00026767 | 2.0731e-08 | -2.4594e-07 | 0.0016321 | 0.0016322 | 0.0016322 | 0.97577 | -0.4658 | 0.97575 | -0.46621 | 0.44842
113 | 0.0010705 | 0.00026767 | -0.0010704 | -0.00026827 | 5.06e-08 | -6.0011e-07 | 0.0016322 | 0.0016325 | 0.0016325 | 0.97575 | -0.46621 | 0.9757 | -0.4672 | 0.44848

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41503 | 0.10577

## res_load
| p_mw | q_mvar
0 | 0.0016187 | 0.00040569
1 | 0.00071592 | 0.00017943
2 | 0.00034158 | 8.5609e-05
3 | 0.0004 | 0.00010025
4 | 0.00071671 | 0.00017962
5 | 0.0018527 | 0.00046434
6 | 0.00070063 | 0.0001756
7 | 0.0033276 | 0.00083397
8 | 0.00060933 | 0.00015271
9 | 0.00033773 | 8.4643e-05
10 | 0.0018768 | 0.00047037
11 | 0.0053319 | 0.0013363
12 | 0.0023107 | 0.00057912
13 | 0.001262 | 0.00031629
14 | 0.0015127 | 0.00037911
15 | 0.0015133 | 0.00037927
16 | 0.0042632 | 0.0010685
17 | 0.0024344 | 0.00061013
18 | 0.0019643 | 0.0004923
19 | 0.006694 | 0.0016777
20 | 0.0022425 | 0.00056201
21 | 0.00041007 | 0.00010277
22 | 0.0017382 | 0.00043564
23 | 0.0014107 | 0.00035357
24 | 9.2477e-05 | 2.3177e-05
25 | 0.00077028 | 0.00019305
26 | 0.0017996 | 0.00045102
27 | 0.0020731 | 0.00051957
28 | 0.0018905 | 0.00047381
29 | 0.0012998 | 0.00032575
30 | 0.0012769 | 0.00032002
31 | 0.00057222 | 0.00014341
32 | 0.0041411 | 0.0010379
33 | 0.0070216 | 0.0017598
34 | 0.035096 | 0.0087958
35 | 0.0030191 | 0.00075665
36 | 0.028551 | 0.0071555
37 | 0.0032791 | 0.00082182
38 | 0.00049627 | 0.00012438
39 | 0.011445 | 0.0028685
40 | 0.049779 | 0.012476
41 | 0.0010656 | 0.00026707
42 | 0.00085962 | 0.00021544
43 | 0.00077028 | 0.00019305
44 | 0.00092369 | 0.0002315
45 | 0.0010541 | 0.00026417
46 | 0.0014211 | 0.00035616
47 | 0.0042964 | 0.0010768
48 | 0.0014159 | 0.00035486
49 | 0.0090611 | 0.0022709
50 | 0.0060377 | 0.0015132
51 | 0.0010164 | 0.00025473
52 | 0.0014749 | 0.00036964
53 | 0.0011938 | 0.00029919
54 | 0.0015779 | 0.00039547
55 | 0.0010692 | 0.00026797
56 | 0.001026 | 0.00025715
57 | 0.0033327 | 0.00083525
58 | 0.0035251 | 0.00088347
59 | 0.00099908 | 0.00025039
60 | 0.044124 | 0.011059
61 | 0.020883 | 0.0052339
62 | 0.0061266 | 0.0015355
63 | 0.0023329 | 0.00058467
64 | 0.046442 | 0.011639
65 | 0.0018339 | 0.00045961
66 | 0.0038498 | 0.00096486
67 | 0.002004 | 0.00050226
68 | 0.0075234 | 0.0018855
69 | 0.013924 | 0.0034896
70 | 0.0040869 | 0.0010243
71 | 0.0018832 | 0.00047198
72 | 0.0017986 | 0.00045076
73 | 0.0033003 | 0.00082713
74 | 0.0012093 | 0.00030307
75 | 0.0010718 | 0.00026861
76 | 0.00097352 | 0.00024399
77 | 0.00094179 | 0.00023604
78 | 0.00095799 | 0.0002401
79 | 0.00089043 | 0.00022316
80 | 0.0010704 | 0.00026827

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1