## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2576-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2576-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2576-7_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2576-7_0_3_node_18 | 0.4 | n |  | TRUE
4 | bus_LV_2576-7_0_3_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_2576-7_0_3_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2576-7_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2576-7_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2576-7_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2576-7_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2576-7_0_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2576-7_0_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_2576-7_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2576-7_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2576-7_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2576-7_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2576-7_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2576-7_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_2576-7_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2576-7_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2576-7_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2576-7_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2576-7_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2576-7_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2576-7_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2576-7_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_MV_398_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2576-7_0_3_load_0 | 0 | 0.0009123 | 0.00022865 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2576-7_0_3_load_1 | 1 | 0.00063927 | 0.00016022 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2576-7_0_3_load_28 | 4 | 0.00031388 | 7.8666e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2576-7_0_3_load_16 | 5 | 0.0024416 | 0.00061192 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2576-7_0_3_load_4 | 6 | 0.0014192 | 0.00035569 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2576-7_0_3_load_5 | 7 | 0.00038044 | 9.5348e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2576-7_0_3_load_6 | 8 | 0.0041699 | 0.0010451 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2576-7_0_3_load_7 | 9 | 0.00032536 | 8.1543e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2576-7_0_3_load_14 | 10 | 0.0017391 | 0.00043586 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2576-7_0_3_load_27 | 11 | 0.00046325 | 0.0001161 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2576-7_0_3_load_8 | 12 | 0.00027379 | 6.8618e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2576-7_0_3_load_9 | 13 | 0.0027905 | 0.00069937 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2576-7_0_3_load_13 | 16 | 0.0017547 | 0.00043977 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2576-7_0_3_load_24 | 17 | 0.00064696 | 0.00016214 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2576-7_0_3_load_25 | 20 | 0.00055062 | 0.000138 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2576-7_0_3_load_15 | 21 | 0.00033031 | 8.2784e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2576-7_0_3_load_19 | 22 | 0.02171 | 0.0054409 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2576-7_0_3_load_20 | 23 | 0.066197 | 0.016591 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2576-7_0_3_load_21 | 24 | 0.035714 | 0.0089509 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2576-7_0_3_line_0 |  | 0 | 1 | 0.035837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2576-7_0_3_line_1 |  | 1 | 2 | 0.010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2576-7_0_3_line_2 |  | 2 | 3 | 0.019143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2576-7_0_3_line_3 |  | 3 | 4 | 0.014976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2576-7_0_3_line_4 |  | 3 | 5 | 0.036064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2576-7_0_3_line_5 |  | 4 | 16 | 0.0097177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2576-7_0_3_line_6 |  | 5 | 21 | 0.0098883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2576-7_0_3_line_7 |  | 6 | 7 | 0.036206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2576-7_0_3_line_8 |  | 6 | 8 | 0.011249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2576-7_0_3_line_9 |  | 7 | 9 | 0.016728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2576-7_0_3_line_10 |  | 9 | 10 | 0.0064679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2576-7_0_3_line_11 |  | 10 | 11 | 0.011861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2576-7_0_3_line_12 |  | 11 | 18 | 0.035071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2576-7_0_3_line_13 |  | 12 | 13 | 0.024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2576-7_0_3_line_14 |  | 12 | 14 | 0.084645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2576-7_0_3_line_15 |  | 13 | 15 | 0.054865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2576-7_0_3_line_16 |  | 14 | 16 | 0.098826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2576-7_0_3_line_17 |  | 15 | 17 | 0.038336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2576-7_0_3_line_18 |  | 17 | 20 | 0.0026831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2576-7_0_3_line_19 |  | 18 | 19 | 0.057946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2576-7_0_3_line_20 |  | 19 | 21 | 0.091692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2576-7_0_3_line_21 |  | 20 | 25 | 0.15612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2576-7_0_3_line_22 |  | 22 | 23 | 0.021555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2576-7_0_3_line_23 |  | 22 | 24 | 0.045241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2576-7_0_3_line_24 |  | 22 | 25 | 0.22765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2576-7_0_3_trafo_19 | 0.63 MVA 20/0.4 kV | 26 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2642003.2104 | 1242997.2199 | 2642008.6038 | 1242998.5867 | 2642035.7145 | 1243012.0589
1 | 2642044.0265 | 1243018.1056 | 2642041.9463 | 1243015.1556 | 2642035.7145 | 1243012.0589
2 | 2642044.0265 | 1243018.1056 | 2642044.4471 | 1243021.6887 | 2642041.9803 | 1243037.0257
3 | 2642041.9803 | 1243037.0257 | 2642038.317 | 1243044.1599 | 2642034.3915 | 1243049.9026
4 | 2642041.9803 | 1243037.0257 | 2642058.9032 | 1243045.5066 | 2642066.7982 | 1243048.0975 | 2642074.8983 | 1243051.6016
5 | 2642026.2351 | 1243055.1854 | 2642034.3915 | 1243049.9026
6 | 2642074.8983 | 1243051.6016 | 2642082.5976 | 1243056.2036 | 2642083.3395 | 1243056.745
7 | 2641996.0356 | 1243212.4921 | 2642002.6763 | 1243212.4731 | 2642014.1699 | 1243212.7323 | 2642022.5946 | 1243208.7893 | 2642029.9809 | 1243204.0667
8 | 2641984.7864 | 1243212.5244 | 2641996.0356 | 1243212.4921
9 | 2642044.0741 | 1243195.0556 | 2642029.9809 | 1243204.0667
10 | 2642049.5233 | 1243191.5714 | 2642044.0741 | 1243195.0556
11 | 2642049.5233 | 1243191.5714 | 2642054.6871 | 1243188.2698 | 2642060.3576 | 1243187.4352
12 | 2642089.5528 | 1243169.9937 | 2642075.1715 | 1243182.5889 | 2642070.0381 | 1243186.0104 | 2642060.3576 | 1243187.4352
13 | 2641863.5818 | 1243178.7268 | 2641882.8817 | 1243164.461
14 | 2641956.192 | 1243123.1418 | 2641948.2305 | 1243124.631 | 2641939.7405 | 1243129.2407 | 2641883.1032 | 1243164.2973 | 2641882.8817 | 1243164.461
15 | 2641820.3353 | 1243212.4864 | 2641846.1984 | 1243192.0997 | 2641860.5006 | 1243181.0044 | 2641863.5818 | 1243178.7268
16 | 2641956.192 | 1243123.1418 | 2641960.3619 | 1243114.8881 | 2641966.0753 | 1243107.4681 | 2641979.3312 | 1243091.5514 | 2641992.9294 | 1243078.5391 | 2642024.1183 | 1243056.5564 | 2642026.2351 | 1243055.1854
17 | 2641820.3353 | 1243212.4864 | 2641792.6155 | 1243234.6724 | 2641790.2792 | 1243236.2715
18 | 2641788.0651 | 1243237.787 | 2641790.2792 | 1243236.2715
19 | 2642089.5528 | 1243169.9937 | 2642094.2866 | 1243174.9638 | 2642101.0989 | 1243168.1966 | 2642113.4405 | 1243150.1501 | 2642119.2282 | 1243140.8073 | 2642122.2407 | 1243132.7234
20 | 2642122.2407 | 1243132.7234 | 2642122.859 | 1243123.3439 | 2642117.1837 | 1243091.2827 | 2642113.3985 | 1243081.5051 | 2642109.3504 | 1243075.7615 | 2642092.598 | 1243063.5014 | 2642083.3395 | 1243056.745
21 | 2641640.2002 | 1243271.9039 | 2641682.0876 | 1243273.7434 | 2641702.6018 | 1243273.3983 | 2641723.1987 | 1243269.8962 | 2641745.404 | 1243262.3028 | 2641763.8114 | 1243253.104 | 2641770.7968 | 1243249.6064 | 2641788.0651 | 1243237.787
22 | 2641537.9732 | 1243068.5011 | 2641540.7326 | 1243064.5056 | 2641538.4589 | 1243047.9623
23 | 2641500.0062 | 1243087.8074 | 2641505.4084 | 1243082.5816 | 2641531.8527 | 1243077.363 | 2641537.9732 | 1243068.5011
24 | 2641640.2002 | 1243271.9039 | 2641537.9732 | 1243068.5011

## bus_geodata
| x | y | coords
0 | 2642003.2104 | 1242997.2199
1 | 2642035.7145 | 1243012.0589
2 | 2642044.0265 | 1243018.1056
3 | 2642041.9803 | 1243037.0257
4 | 2642034.3915 | 1243049.9026
5 | 2642074.8983 | 1243051.6016
6 | 2641996.0356 | 1243212.4921
7 | 2642029.9809 | 1243204.0667
8 | 2641984.7864 | 1243212.5244
9 | 2642044.0741 | 1243195.0556
10 | 2642049.5233 | 1243191.5714
11 | 2642060.3576 | 1243187.4352
12 | 2641882.8817 | 1243164.461
13 | 2641863.5818 | 1243178.7268
14 | 2641956.192 | 1243123.1418
15 | 2641820.3353 | 1243212.4864
16 | 2642026.2351 | 1243055.1854
17 | 2641790.2792 | 1243236.2715
18 | 2642089.5528 | 1243169.9937
19 | 2642122.2407 | 1243132.7234
20 | 2641788.0651 | 1243237.787
21 | 2642083.3395 | 1243056.745
22 | 2641537.9732 | 1243068.5011
23 | 2641538.4589 | 1243047.9623
24 | 2641500.0062 | 1243087.8074
25 | 2641640.2002 | 1243271.9039
26 | 2641475.1853 | 1243110.5109

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98846 | -0.22189 | 0.0009123 | 0.00022865
1 | 0.98849 | -0.22131 | 0.00063927 | 0.00016022
2 | 0.98851 | -0.22102 | 0 | 0
3 | 0.98854 | -0.22049 | 0 | 0
4 | 0.98871 | -0.21706 | 0.00031388 | 7.8666e-05
5 | 0.98816 | -0.22775 | 0.0024416 | 0.00061192
6 | 0.98624 | -0.26524 | 0.0014192 | 0.00035569
7 | 0.98642 | -0.26161 | 0.00038044 | 9.5348e-05
8 | 0.98619 | -0.26608 | 0.0041699 | 0.0010451
9 | 0.98651 | -0.25982 | 0.00032536 | 8.1543e-05
10 | 0.98655 | -0.25909 | 0.0017391 | 0.00043586
11 | 0.98664 | -0.25739 | 0.00046325 | 0.0001161
12 | 0.99134 | -0.16616 | 0.00027379 | 6.8618e-05
13 | 0.99167 | -0.1597 | 0.0027905 | 0.00069937
14 | 0.99018 | -0.18856 | 0 | 0
15 | 0.99258 | -0.14224 | 0 | 0
16 | 0.98883 | -0.21478 | 0.0017547 | 0.00043977
17 | 0.99321 | -0.13005 | 0.00064696 | 0.00016214
18 | 0.98691 | -0.25205 | 0 | 0
19 | 0.98737 | -0.24324 | 0 | 0
20 | 0.99325 | -0.12917 | 0.00055062 | 0.000138
21 | 0.98808 | -0.22931 | 0.00033031 | 8.2784e-05
22 | 1 | 0 | -0.12305 | -0.03054
23 | 0.9987 | -0.024902 | 0.066197 | 0.016591
24 | 0.99853 | -0.028203 | 0.035714 | 0.0089509
25 | 0.996 | -0.076421 | 0 | 0
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0009123 | -0.00022865 | 0.00091233 | 0.0002282 | 2.5345e-08 | -4.4317e-07 | 0.0013734 | 0.0013732 | 0.0013734 | 0.98846 | -0.22189 | 0.98849 | -0.22131 | 0.3773
1 | -0.0015516 | -0.00038842 | 0.0015516 | 0.0003883 | 2.1617e-08 | -1.2165e-07 | 0.0023355 | 0.0023355 | 0.0023355 | 0.98849 | -0.22131 | 0.98851 | -0.22102 | 0.64163
2 | -0.0015516 | -0.0003883 | 0.0015517 | 0.00038808 | 3.9154e-08 | -2.2035e-07 | 0.0023355 | 0.0023354 | 0.0023355 | 0.98851 | -0.22102 | 0.98854 | -0.22049 | 0.64161
3 | -0.012839 | -0.0032202 | 0.012841 | 0.0032213 | 2.0978e-06 | 1.1506e-06 | 0.019327 | 0.019327 | 0.019327 | 0.98854 | -0.22049 | 0.98871 | -0.21706 | 5.3097
4 | 0.011288 | 0.0028321 | -0.011284 | -0.0028301 | 3.9048e-06 | 2.0369e-06 | 0.016992 | 0.016992 | 0.016992 | 0.98854 | -0.22049 | 0.98816 | -0.22775 | 4.6682
5 | -0.013155 | -0.0033 | 0.013157 | 0.0033008 | 1.4286e-06 | 7.8967e-07 | 0.0198 | 0.0198 | 0.0198 | 0.98871 | -0.21706 | 0.98883 | -0.21478 | 5.4395
6 | 0.0088421 | 0.0022182 | -0.0088414 | -0.0022179 | 6.5746e-07 | 2.9411e-07 | 0.013316 | 0.013316 | 0.013316 | 0.98816 | -0.22775 | 0.98808 | -0.22931 | 3.6581
7 | -0.0055892 | -0.0014007 | 0.0055902 | 0.0014009 | 9.6552e-07 | 1.5583e-07 | 0.0084329 | 0.0084328 | 0.0084329 | 0.98624 | -0.26524 | 0.98642 | -0.26161 | 2.3167
8 | 0.00417 | 0.001045 | -0.0041699 | -0.0010451 | 1.6699e-07 | -3.6669e-08 | 0.0062916 | 0.0062917 | 0.0062917 | 0.98624 | -0.26524 | 0.98619 | -0.26608 | 1.7285
9 | -0.0059707 | -0.0014962 | 0.0059712 | 0.0014963 | 5.0885e-07 | 1.1211e-07 | 0.0090067 | 0.0090066 | 0.0090067 | 0.98642 | -0.26161 | 0.98651 | -0.25982 | 2.4744
10 | -0.0062965 | -0.0015779 | 0.0062967 | 0.0015779 | 2.1877e-07 | 5.7431e-08 | 0.0094973 | 0.0094973 | 0.0094973 | 0.98651 | -0.25982 | 0.98655 | -0.25909 | 2.6092
11 | -0.0080358 | -0.0020138 | 0.0080365 | 0.0020141 | 6.5339e-07 | 2.6671e-07 | 0.01212 | 0.01212 | 0.01212 | 0.98655 | -0.25909 | 0.98664 | -0.25739 | 3.3298
12 | -0.0084997 | -0.0021302 | 0.0085019 | 0.0021311 | 2.1611e-06 | 9.351e-07 | 0.012819 | 0.012819 | 0.012819 | 0.98664 | -0.25739 | 0.98691 | -0.25205 | 3.5217
13 | -0.01522 | -0.003829 | 0.015225 | 0.0038317 | 4.6992e-06 | 2.698e-06 | 0.02285 | 0.02285 | 0.02285 | 0.99134 | -0.16616 | 0.99167 | -0.1597 | 6.2776
14 | 0.014946 | 0.0037604 | -0.01493 | -0.0037512 | 1.5983e-05 | 9.1391e-06 | 0.022439 | 0.02244 | 0.02244 | 0.99134 | -0.16616 | 0.99018 | -0.18856 | 6.1648
15 | -0.018015 | -0.0045311 | 0.01803 | 0.00454 | 1.504e-05 | 8.9172e-06 | 0.027037 | 0.027037 | 0.027037 | 0.99167 | -0.1597 | 0.99258 | -0.14224 | 7.4279
16 | 0.01493 | 0.0037512 | -0.014911 | -0.0037406 | 1.8662e-05 | 1.0674e-05 | 0.02244 | 0.02244 | 0.02244 | 0.99018 | -0.18856 | 0.98883 | -0.21478 | 6.1649
17 | -0.01803 | -0.00454 | 0.018041 | 0.0045462 | 1.0509e-05 | 6.2299e-06 | 0.027037 | 0.027037 | 0.027037 | 0.99258 | -0.14224 | 0.99321 | -0.13005 | 7.4278
18 | -0.018688 | -0.0047084 | 0.018688 | 0.0047088 | 7.8917e-07 | 4.7034e-07 | 0.028006 | 0.028006 | 0.028006 | 0.99321 | -0.13005 | 0.99325 | -0.12917 | 7.694
19 | -0.0085019 | -0.0021311 | 0.0085055 | 0.0021326 | 3.5706e-06 | 1.5444e-06 | 0.012819 | 0.012819 | 0.012819 | 0.98691 | -0.25205 | 0.98737 | -0.24324 | 3.5217
20 | -0.0085055 | -0.0021326 | 0.0085111 | 0.0021351 | 5.6497e-06 | 2.4422e-06 | 0.012819 | 0.012818 | 0.012819 | 0.98737 | -0.24324 | 0.98808 | -0.22931 | 3.5216
21 | -0.019239 | -0.0048468 | 0.019288 | 0.0048759 | 4.8664e-05 | 2.9119e-05 | 0.028831 | 0.02883 | 0.028831 | 0.99325 | -0.12917 | 0.996 | -0.076421 | 7.9206
22 | 0.066276 | 0.016641 | -0.066197 | -0.016591 | 7.8631e-05 | 5.0041e-05 | 0.09863 | 0.09863 | 0.09863 | 1 | 0 | 0.9987 | -0.024902 | 27.0962
23 | 0.035763 | 0.0089811 | -0.035714 | -0.0089509 | 4.8055e-05 | 3.0162e-05 | 0.053222 | 0.053222 | 0.053222 | 1 | 0 | 0.99853 | -0.028203 | 14.6214
24 | 0.019359 | 0.0049184 | -0.019288 | -0.0048759 | 7.0954e-05 | 4.2436e-05 | 0.028829 | 0.02883 | 0.02883 | 1 | 0 | 0.996 | -0.076421 | 7.9204

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.14476 | 0.035981

## res_load
| p_mw | q_mvar
0 | 0.0009123 | 0.00022865
1 | 0.00063927 | 0.00016022
2 | 0.00031388 | 7.8666e-05
3 | 0.0024416 | 0.00061192
4 | 0.0014192 | 0.00035569
5 | 0.00038044 | 9.5348e-05
6 | 0.0041699 | 0.0010451
7 | 0.00032536 | 8.1543e-05
8 | 0.0017391 | 0.00043586
9 | 0.00046325 | 0.0001161
10 | 0.00027379 | 6.8618e-05
11 | 0.0027905 | 0.00069937
12 | 0.0017547 | 0.00043977
13 | 0.00064696 | 0.00016214
14 | 0.00055062 | 0.000138
15 | 0.00033031 | 8.2784e-05
16 | 0.02171 | 0.0054409
17 | 0.066197 | 0.016591
18 | 0.035714 | 0.0089509

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1