## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2579-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2579-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2579-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2579-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2579-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2579-5_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2579-5_0_3_node_126 | 0.4 | n |  | TRUE
7 | bus_LV_2579-5_0_3_node_191 | 0.4 | n |  | TRUE
8 | bus_LV_2579-5_0_3_node_222 | 0.4 | n |  | TRUE
9 | bus_LV_2579-5_0_3_node_125 | 0.4 | n |  | TRUE
10 | bus_LV_2579-5_0_3_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_2579-5_0_3_node_220 | 0.4 | n |  | TRUE
12 | bus_LV_2579-5_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2579-5_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2579-5_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2579-5_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2579-5_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2579-5_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2579-5_0_3_node_114 | 0.4 | n |  | TRUE
19 | bus_LV_2579-5_0_3_node_118 | 0.4 | n |  | TRUE
20 | bus_LV_2579-5_0_3_node_121 | 0.4 | n |  | TRUE
21 | bus_LV_2579-5_0_3_node_128 | 0.4 | n |  | TRUE
22 | bus_LV_2579-5_0_3_node_201 | 0.4 | n |  | TRUE
23 | bus_LV_2579-5_0_3_node_116 | 0.4 | n |  | TRUE
24 | bus_LV_2579-5_0_3_node_122 | 0.4 | n |  | TRUE
25 | bus_LV_2579-5_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_2579-5_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2579-5_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2579-5_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2579-5_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2579-5_0_3_node_179 | 0.4 | n |  | TRUE
31 | bus_LV_2579-5_0_3_node_120 | 0.4 | n |  | TRUE
32 | bus_LV_2579-5_0_3_node_185 | 0.4 | n |  | TRUE
33 | bus_LV_2579-5_0_3_node_174 | 0.4 | n |  | TRUE
34 | bus_LV_2579-5_0_3_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2579-5_0_3_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2579-5_0_3_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2579-5_0_3_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2579-5_0_3_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2579-5_0_3_node_139 | 0.4 | n |  | TRUE
40 | bus_LV_2579-5_0_3_node_138 | 0.4 | n |  | TRUE
41 | bus_LV_2579-5_0_3_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2579-5_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2579-5_0_3_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2579-5_0_3_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2579-5_0_3_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_2579-5_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2579-5_0_3_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_2579-5_0_3_node_186 | 0.4 | n |  | TRUE
49 | bus_LV_2579-5_0_3_node_236 | 0.4 | n |  | TRUE
50 | bus_LV_2579-5_0_3_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_2579-5_0_3_node_69 | 0.4 | n |  | TRUE
52 | bus_LV_2579-5_0_3_node_136 | 0.4 | n |  | TRUE
53 | bus_LV_2579-5_0_3_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_2579-5_0_3_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2579-5_0_3_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_2579-5_0_3_node_106 | 0.4 | n |  | TRUE
57 | bus_LV_2579-5_0_3_node_104 | 0.4 | n |  | TRUE
58 | bus_LV_2579-5_0_3_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_2579-5_0_3_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_2579-5_0_3_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2579-5_0_3_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_2579-5_0_3_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_2579-5_0_3_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_2579-5_0_3_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_2579-5_0_3_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_2579-5_0_3_node_135 | 0.4 | n |  | TRUE
67 | bus_LV_2579-5_0_3_node_133 | 0.4 | n |  | TRUE
68 | bus_LV_2579-5_0_3_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_2579-5_0_3_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_2579-5_0_3_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_2579-5_0_3_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_2579-5_0_3_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_2579-5_0_3_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_2579-5_0_3_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_2579-5_0_3_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_2579-5_0_3_node_215 | 0.4 | n |  | TRUE
77 | bus_LV_2579-5_0_3_node_172 | 0.4 | n |  | TRUE
78 | bus_LV_2579-5_0_3_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_2579-5_0_3_node_127 | 0.4 | n |  | TRUE
80 | bus_LV_2579-5_0_3_node_124 | 0.4 | n |  | TRUE
81 | bus_LV_2579-5_0_3_node_200 | 0.4 | n |  | TRUE
82 | bus_LV_2579-5_0_3_node_81 | 0.4 | n |  | TRUE
83 | bus_LV_2579-5_0_3_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_2579-5_0_3_node_84 | 0.4 | n |  | TRUE
85 | bus_LV_2579-5_0_3_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_2579-5_0_3_node_86 | 0.4 | n |  | TRUE
87 | bus_LV_2579-5_0_3_node_110 | 0.4 | n |  | TRUE
88 | bus_LV_2579-5_0_3_node_176 | 0.4 | n |  | TRUE
89 | bus_LV_2579-5_0_3_node_115 | 0.4 | n |  | TRUE
90 | bus_LV_2579-5_0_3_node_111 | 0.4 | n |  | TRUE
91 | bus_LV_2579-5_0_3_node_169 | 0.4 | n |  | TRUE
92 | bus_LV_2579-5_0_3_node_170 | 0.4 | n |  | TRUE
93 | bus_LV_2579-5_0_3_node_175 | 0.4 | n |  | TRUE
94 | bus_LV_2579-5_0_3_node_137 | 0.4 | n |  | TRUE
95 | bus_LV_2579-5_0_3_node_105 | 0.4 | n |  | TRUE
96 | bus_LV_2579-5_0_3_node_107 | 0.4 | n |  | TRUE
97 | bus_LV_2579-5_0_3_node_108 | 0.4 | n |  | TRUE
98 | bus_LV_2579-5_0_3_node_119 | 0.4 | n |  | TRUE
99 | bus_LV_2579-5_0_3_node_173 | 0.4 | n |  | TRUE
100 | bus_LV_2579-5_0_3_node_117 | 0.4 | n |  | TRUE
101 | bus_LV_2579-5_0_3_node_129 | 0.4 | n |  | TRUE
102 | bus_LV_2579-5_0_3_node_112 | 0.4 | n |  | TRUE
103 | bus_LV_2579-5_0_3_node_113 | 0.4 | n |  | TRUE
104 | bus_LV_2579-5_0_3_node_171 | 0.4 | n |  | TRUE
105 | bus_LV_2579-5_0_3_node_202 | 0.4 | n |  | TRUE
106 | bus_LV_2579-5_0_3_node_130 | 0.4 | n |  | TRUE
107 | bus_LV_2579-5_0_3_node_123 | 0.4 | n |  | TRUE
108 | bus_LV_2579-5_0_3_node_195 | 0.4 | n |  | TRUE
109 | bus_LV_2579-5_0_3_node_131 | 0.4 | n |  | TRUE
110 | bus_LV_2579-5_0_3_node_223 | 0.4 | n |  | TRUE
111 | bus_LV_2579-5_0_3_node_221 | 0.4 | n |  | TRUE
112 | bus_LV_2579-5_0_3_node_132 | 0.4 | n |  | TRUE
113 | bus_LV_2579-5_0_3_node_134 | 0.4 | n |  | TRUE
114 | bus_LV_2579-5_0_3_node_177 | 0.4 | n |  | TRUE
115 | bus_LV_2579-5_0_3_node_178 | 0.4 | n |  | TRUE
116 | bus_LV_2579-5_0_3_node_196 | 0.4 | n |  | TRUE
117 | bus_LV_2579-5_0_3_node_194 | 0.4 | n |  | TRUE
118 | bus_LV_2579-5_0_3_node_192 | 0.4 | n |  | TRUE
119 | bus_LV_2579-5_0_3_node_193 | 0.4 | n |  | TRUE
120 | bus_LV_2579-5_0_3_node_219 | 0.4 | n |  | TRUE
121 | bus_MV_480_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2579-5_0_3_load_0 | 0 | 0.0029589 | 0.00074158 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2579-5_0_3_load_1 | 1 | 0.0011026 | 0.00027634 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2579-5_0_3_load_4 | 4 | 0.0019893 | 0.00049856 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2579-5_0_3_load_5 | 5 | 0.0019578 | 0.00049067 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2579-5_0_3_load_126 | 6 | 0.0015231 | 0.00038173 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2579-5_0_3_load_191 | 7 | 0.0012646 | 0.00031693 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2579-5_0_3_load_222 | 8 | 0.0030929 | 0.00077516 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2579-5_0_3_load_125 | 9 | 0.00137 | 0.00034336 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2579-5_0_3_load_220 | 11 | 0.002219 | 0.00055613 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2579-5_0_3_load_6 | 12 | 0.0029808 | 0.00074705 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2579-5_0_3_load_7 | 13 | 0.0018863 | 0.00047276 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2579-5_0_3_load_9 | 15 | 0.001775 | 0.00044486 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2579-5_0_3_load_11 | 17 | 0.0032275 | 0.00080888 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2579-5_0_3_load_121 | 20 | 0.002298 | 0.00057593 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2579-5_0_3_load_128 | 21 | 0.0024735 | 0.00061991 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2579-5_0_3_load_201 | 22 | 0.0030412 | 0.0007622 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2579-5_0_3_load_116 | 23 | 0.0014667 | 0.0003676 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2579-5_0_3_load_122 | 24 | 0.0031004 | 0.00077704 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2579-5_0_3_load_12 | 25 | 0.0066553 | 0.001668 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2579-5_0_3_load_13 | 26 | 0.0022312 | 0.0005592 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2579-5_0_3_load_15 | 28 | 0.0038404 | 0.0009625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2579-5_0_3_load_120 | 31 | 0.0014676 | 0.00036781 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2579-5_0_3_load_185 | 32 | 0.0017452 | 0.00043738 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2579-5_0_3_load_174 | 33 | 0.0019197 | 0.00048111 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2579-5_0_3_load_17 | 34 | 0.0024542 | 0.00061509 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2579-5_0_3_load_18 | 35 | 0.0020435 | 0.00051215 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2579-5_0_3_load_19 | 36 | 0.0026115 | 0.00065449 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2579-5_0_3_load_20 | 37 | 0.0023401 | 0.00058647 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2579-5_0_3_load_21 | 38 | 0.0024477 | 0.00061346 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2579-5_0_3_load_139 | 39 | 0.0038029 | 0.00095309 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2579-5_0_3_load_138 | 40 | 0.0019609 | 0.00049145 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2579-5_0_3_load_22 | 41 | 0.0039665 | 0.00099411 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2579-5_0_3_load_25 | 44 | 0.0074599 | 0.0018696 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2579-5_0_3_load_27 | 46 | 0.0019175 | 0.00048058 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2579-5_0_3_load_87 | 47 | 0.0023299 | 0.00058393 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2579-5_0_3_load_186 | 48 | 0.0041764 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2579-5_0_3_load_236 | 49 | 0.0011291 | 0.00028299 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2579-5_0_3_load_69 | 51 | 0.0020083 | 0.00050332 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2579-5_0_3_load_136 | 52 | 0.0018532 | 0.00046445 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2579-5_0_3_load_28 | 53 | 0.0017183 | 0.00043064 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2579-5_0_3_load_29 | 54 | 0.0021752 | 0.00054515 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2579-5_0_3_load_30 | 55 | 0.0014858 | 0.00037239 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2579-5_0_3_load_106 | 56 | 0.0023062 | 0.00057798 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2579-5_0_3_load_36 | 58 | 0.0023197 | 0.00058136 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2579-5_0_3_load_37 | 59 | 0.0047937 | 0.0012014 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2579-5_0_3_load_39 | 60 | 0.0030493 | 0.00076423 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2579-5_0_3_load_68 | 61 | 0.0042152 | 0.0010564 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2579-5_0_3_load_40 | 62 | 0.0014694 | 0.00036826 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2579-5_0_3_load_43 | 64 | 0.0039892 | 0.00099979 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2579-5_0_3_load_44 | 65 | 0.0015385 | 0.00038559 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2579-5_0_3_load_135 | 66 | 0.0024165 | 0.00060564 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2579-5_0_3_load_133 | 67 | 0.0015098 | 0.00037839 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2579-5_0_3_load_46 | 68 | 0.0023365 | 0.00058558 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2579-5_0_3_load_48 | 69 | 0.001941 | 0.00048646 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2579-5_0_3_load_103 | 70 | 0.0029965 | 0.00075099 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2579-5_0_3_load_49 | 71 | 0.0019603 | 0.0004913 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2579-5_0_3_load_50 | 72 | 0.0012718 | 0.00031873 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2579-5_0_3_load_52 | 74 | 0.0015675 | 0.00039286 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2579-5_0_3_load_53 | 75 | 0.0025687 | 0.00064379 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2579-5_0_3_load_215 | 76 | 0.0019141 | 0.00047972 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2579-5_0_3_load_172 | 77 | 0.0022116 | 0.00055428 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2579-5_0_3_load_127 | 79 | 0.0020938 | 0.00052475 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2579-5_0_3_load_124 | 80 | 0.0014398 | 0.00036086 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2579-5_0_3_load_200 | 81 | 0.0020412 | 0.00051158 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2579-5_0_3_load_81 | 82 | 0.0022585 | 0.00056603 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2579-5_0_3_load_82 | 83 | 0.002259 | 0.00056617 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2579-5_0_3_load_84 | 84 | 0.0020549 | 0.00051499 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2579-5_0_3_load_86 | 86 | 0.0076097 | 0.0019072 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2579-5_0_3_load_176 | 88 | 0.0096498 | 0.0024185 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2579-5_0_3_load_115 | 89 | 0.0026579 | 0.00066613 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2579-5_0_3_load_111 | 90 | 0.0039489 | 0.0009897 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2579-5_0_3_load_169 | 91 | 0.0013561 | 0.00033987 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2579-5_0_3_load_170 | 92 | 0.0015245 | 0.00038206 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2579-5_0_3_load_175 | 93 | 0.0037569 | 0.00094157 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2579-5_0_3_load_137 | 94 | 0.0019523 | 0.00048929 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2579-5_0_3_load_107 | 96 | 0.0011568 | 0.00028991 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2579-5_0_3_load_108 | 97 | 0.0015359 | 0.00038493 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2579-5_0_3_load_119 | 98 | 0.0011431 | 0.00028649 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2579-5_0_3_load_173 | 99 | 0.0017621 | 0.00044161 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2579-5_0_3_load_117 | 100 | 0.0014404 | 0.00036099 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2579-5_0_3_load_129 | 101 | 0.0026923 | 0.00067475 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2579-5_0_3_load_112 | 102 | 0.0013638 | 0.00034181 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2579-5_0_3_load_113 | 103 | 0.0022197 | 0.0005563 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2579-5_0_3_load_202 | 105 | 0.0021994 | 0.00055122 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2579-5_0_3_load_130 | 106 | 0.0026466 | 0.00066329 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2579-5_0_3_load_123 | 107 | 0.00347 | 0.00086967 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2579-5_0_3_load_195 | 108 | 0.0031398 | 0.0007869 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2579-5_0_3_load_131 | 109 | 0.0024441 | 0.00061254 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2579-5_0_3_load_223 | 110 | 0.0019774 | 0.00049559 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2579-5_0_3_load_221 | 111 | 0.0019758 | 0.00049518 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2579-5_0_3_load_132 | 112 | 0.0024542 | 0.00061509 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2579-5_0_3_load_134 | 113 | 0.0023803 | 0.00059655 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2579-5_0_3_load_177 | 114 | 0.010227 | 0.0025631 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2579-5_0_3_load_178 | 115 | 0.0099967 | 0.0025054 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2579-5_0_3_load_196 | 116 | 0.0078867 | 0.0019766 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2579-5_0_3_load_194 | 117 | 0.010335 | 0.0025903 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2579-5_0_3_load_192 | 118 | 0.0017925 | 0.00044923 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2579-5_0_3_load_193 | 119 | 0.0017963 | 0.00045019 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2579-5_0_3_load_219 | 120 | 0.0017561 | 0.00044012 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 109 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2579-5_0_3_line_0 |  | 0 | 1 | 0.005055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2579-5_0_3_line_1 |  | 0 | 2 | 0.016715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2579-5_0_3_line_2 |  | 1 | 3 | 0.011833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2579-5_0_3_line_3 |  | 2 | 4 | 0.016537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2579-5_0_3_line_4 |  | 2 | 5 | 0.023929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2579-5_0_3_line_5 |  | 3 | 6 | 0.020685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2579-5_0_3_line_6 |  | 4 | 7 | 0.022163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2579-5_0_3_line_7 |  | 5 | 8 | 0.0169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2579-5_0_3_line_8 |  | 6 | 9 | 0.0017412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2579-5_0_3_line_9 |  | 7 | 10 | 0.0035719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2579-5_0_3_line_10 |  | 8 | 11 | 0.017347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2579-5_0_3_line_11 |  | 9 | 80 | 0.023844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2579-5_0_3_line_12 |  | 10 | 56 | 0.021736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2579-5_0_3_line_13 |  | 10 | 55 | 0.015137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2579-5_0_3_line_14 |  | 11 | 120 | 0.0028444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2579-5_0_3_line_15 |  | 12 | 13 | 0.010348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2579-5_0_3_line_16 |  | 12 | 14 | 0.0068929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2579-5_0_3_line_17 |  | 13 | 15 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2579-5_0_3_line_18 |  | 14 | 16 | 0.014051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2579-5_0_3_line_19 |  | 14 | 17 | 0.031397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2579-5_0_3_line_20 |  | 15 | 18 | 0.005642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2579-5_0_3_line_21 |  | 16 | 19 | 0.016714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2579-5_0_3_line_22 |  | 16 | 20 | 0.017737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2579-5_0_3_line_23 |  | 17 | 21 | 0.0090364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2579-5_0_3_line_24 |  | 18 | 22 | 0.034092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2579-5_0_3_line_25 |  | 19 | 23 | 0.020969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2579-5_0_3_line_26 |  | 20 | 24 | 0.0043195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2579-5_0_3_line_27 |  | 22 | 105 | 0.011878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2579-5_0_3_line_28 |  | 23 | 100 | 0.018968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2579-5_0_3_line_29 |  | 24 | 107 | 0.023258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2579-5_0_3_line_30 |  | 25 | 26 | 0.013486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2579-5_0_3_line_31 |  | 25 | 27 | 0.013401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2579-5_0_3_line_32 |  | 26 | 28 | 0.0065175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2579-5_0_3_line_33 |  | 27 | 29 | 0.024619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2579-5_0_3_line_34 |  | 28 | 30 | 0.017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2579-5_0_3_line_35 |  | 29 | 31 | 0.032384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2579-5_0_3_line_36 |  | 30 | 32 | 0.015581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2579-5_0_3_line_37 |  | 30 | 33 | 0.0047544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2579-5_0_3_line_38 |  | 32 | 38 | 0.020916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2579-5_0_3_line_39 |  | 33 | 99 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2579-5_0_3_line_40 |  | 34 | 35 | 0.0011062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2579-5_0_3_line_41 |  | 34 | 36 | 0.0078191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2579-5_0_3_line_42 |  | 35 | 37 | 0.0018611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2579-5_0_3_line_43 |  | 36 | 38 | 0.0074714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2579-5_0_3_line_44 |  | 37 | 39 | 0.01785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2579-5_0_3_line_45 |  | 39 | 40 | 0.0078594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2579-5_0_3_line_46 |  | 40 | 94 | 0.0068363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2579-5_0_3_line_47 |  | 41 | 42 | 0.062092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2579-5_0_3_line_48 |  | 41 | 43 | 0.013883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2579-5_0_3_line_49 |  | 42 | 44 | 0.037139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2579-5_0_3_line_50 |  | 43 | 45 | 0.003977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2579-5_0_3_line_51 |  | 43 | 46 | 0.016635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2579-5_0_3_line_52 |  | 45 | 47 | 0.055791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2579-5_0_3_line_53 |  | 45 | 48 | 0.025428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2579-5_0_3_line_54 |  | 46 | 49 | 0.030448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2579-5_0_3_line_55 |  | 47 | 50 | 0.01819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2579-5_0_3_line_56 |  | 48 | 51 | 0.020128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2579-5_0_3_line_57 |  | 49 | 52 | 0.032603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2579-5_0_3_line_58 |  | 50 | 85 | 0.014248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2579-5_0_3_line_59 |  | 50 | 86 | 0.034011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2579-5_0_3_line_60 |  | 50 | 82 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2579-5_0_3_line_61 |  | 51 | 61 | 0.018754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2579-5_0_3_line_62 |  | 52 | 113 | 0.014762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2579-5_0_3_line_63 |  | 53 | 54 | 0.014042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2579-5_0_3_line_64 |  | 53 | 55 | 0.017643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2579-5_0_3_line_65 |  | 56 | 57 | 0.016059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2579-5_0_3_line_66 |  | 57 | 70 | 0.0060063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2579-5_0_3_line_67 |  | 57 | 69 | 0.031231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2579-5_0_3_line_68 |  | 58 | 59 | 0.032368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2579-5_0_3_line_69 |  | 59 | 60 | 0.031743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2579-5_0_3_line_70 |  | 60 | 61 | 0.013766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2579-5_0_3_line_71 |  | 62 | 63 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2579-5_0_3_line_72 |  | 63 | 64 | 0.030102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2579-5_0_3_line_73 |  | 63 | 65 | 0.0044774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2579-5_0_3_line_74 |  | 64 | 66 | 0.027022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2579-5_0_3_line_75 |  | 66 | 67 | 0.0012647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2579-5_0_3_line_76 |  | 67 | 112 | 0.02549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2579-5_0_3_line_77 |  | 68 | 69 | 0.030644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2579-5_0_3_line_78 |  | 70 | 95 | 0.022631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2579-5_0_3_line_79 |  | 71 | 72 | 0.00573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2579-5_0_3_line_80 |  | 71 | 73 | 0.039439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2579-5_0_3_line_81 |  | 72 | 74 | 0.025864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2579-5_0_3_line_82 |  | 73 | 75 | 0.0083952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2579-5_0_3_line_83 |  | 74 | 76 | 0.00089106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2579-5_0_3_line_84 |  | 76 | 77 | 0.030152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2579-5_0_3_line_85 |  | 77 | 85 | 0.028604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2579-5_0_3_line_86 |  | 78 | 79 | 0.015598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2579-5_0_3_line_87 |  | 78 | 80 | 0.0074883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2579-5_0_3_line_88 |  | 79 | 81 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2579-5_0_3_line_89 |  | 81 | 108 | 0.0089329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2579-5_0_3_line_90 |  | 82 | 83 | 0.019182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2579-5_0_3_line_91 |  | 83 | 84 | 0.0034226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2579-5_0_3_line_92 |  | 84 | 87 | 0.022839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2579-5_0_3_line_93 |  | 86 | 88 | 0.033177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2579-5_0_3_line_94 |  | 87 | 89 | 0.017557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2579-5_0_3_line_95 |  | 87 | 90 | 0.016947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2579-5_0_3_line_96 |  | 88 | 93 | 0.0012471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2579-5_0_3_line_97 |  | 89 | 101 | 0.0084765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2579-5_0_3_line_98 |  | 90 | 102 | 0.034237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2579-5_0_3_line_99 |  | 91 | 92 | 0.025809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2579-5_0_3_line_100 |  | 92 | 104 | 0.0079702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2579-5_0_3_line_101 |  | 93 | 114 | 0.013429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2579-5_0_3_line_102 |  | 95 | 96 | 0.014297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2579-5_0_3_line_103 |  | 95 | 97 | 0.013084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2579-5_0_3_line_104 |  | 96 | 98 | 0.0078475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2579-5_0_3_line_105 |  | 97 | 99 | 0.0015751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2579-5_0_3_line_106 |  | 98 | 100 | 0.018143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2579-5_0_3_line_107 |  | 101 | 106 | 0.0086595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2579-5_0_3_line_108 |  | 102 | 103 | 0.025495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2579-5_0_3_line_109 |  | 103 | 104 | 0.0088426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2579-5_0_3_line_110 |  | 106 | 109 | 0.014448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2579-5_0_3_line_111 |  | 108 | 119 | 0.0076784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2579-5_0_3_line_112 |  | 109 | 110 | 0.011201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_2579-5_0_3_line_113 |  | 110 | 111 | 0.006646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_2579-5_0_3_line_114 |  | 111 | 120 | 0.0081142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_2579-5_0_3_line_115 |  | 112 | 113 | 0.0086112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2579-5_0_3_line_116 |  | 115 | 116 | 0.012926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2579-5_0_3_line_117 |  | 116 | 117 | 0.0023597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2579-5_0_3_line_118 |  | 117 | 118 | 0.022747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2579-5_0_3_line_119 |  | 118 | 119 | 0.0066566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2579-5_0_3_trafo_131 | 0.63 MVA 20/0.4 kV | 121 | 109 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2630523.5501 | 1243279.5533 | 2630522.2585 | 1243284.4405
1 | 2630527.821 | 1243263.3932 | 2630523.5501 | 1243279.5533
2 | 2630519.2349 | 1243295.8811 | 2630522.2585 | 1243284.4405
3 | 2630527.821 | 1243263.3932 | 2630532.3495 | 1243247.4886
4 | 2630527.821 | 1243263.3932 | 2630514.5911 | 1243256.8211 | 2630507.6105 | 1243250.8959
5 | 2630519.2349 | 1243295.8811 | 2630515.2299 | 1243316.1743
6 | 2630538.4186 | 1243226.1731 | 2630532.3495 | 1243247.4886
7 | 2630507.6105 | 1243250.8959 | 2630494.7257 | 1243239.9594
8 | 2630515.2299 | 1243316.1743 | 2630514.8928 | 1243317.8826
9 | 2630539.3967 | 1243222.7378 | 2630538.4186 | 1243226.1731
10 | 2630481.5003 | 1243228.7337 | 2630494.7257 | 1243239.9594
11 | 2630510.6152 | 1243341.3396 | 2630514.4783 | 1243319.9832 | 2630514.8928 | 1243317.8826
12 | 2630539.3967 | 1243222.7378 | 2630546.4169 | 1243202.1662
13 | 2630539.3967 | 1243222.7378 | 2630554 | 1243226.723
14 | 2630481.5003 | 1243228.7337 | 2630479.3317 | 1243226.893
15 | 2630473.9856 | 1243137.979 | 2630467.494 | 1243146.0379
16 | 2630478.3095 | 1243132.6109 | 2630473.9856 | 1243137.979
17 | 2630451.5737 | 1243159.9206 | 2630461.4081 | 1243153.6711 | 2630465.7517 | 1243148.201 | 2630467.494 | 1243146.0379
18 | 2630478.3095 | 1243132.6109 | 2630487.3962 | 1243121.8729
19 | 2630478.3095 | 1243132.6109 | 2630502.158 | 1243153.0313
20 | 2630446.8119 | 1243162.9467 | 2630451.5737 | 1243159.9206
21 | 2630501.2297 | 1243112.5045 | 2630492.6328 | 1243117.6415 | 2630487.3962 | 1243121.8729
22 | 2630487.3962 | 1243121.8729 | 2630481.5984 | 1243120.5979 | 2630478.1042 | 1243119.6015 | 2630471.9001 | 1243116.5011 | 2630470.9393 | 1243115.73
23 | 2630509.022 | 1243158.9086 | 2630502.158 | 1243153.0313
24 | 2630446.8119 | 1243162.9467 | 2630450.0866 | 1243166.9438 | 2630455.5617 | 1243172.1863 | 2630471.6197 | 1243186.2476
25 | 2630501.2297 | 1243112.5045 | 2630503.8994 | 1243115.0977 | 2630511.8969 | 1243122.1988 | 2630517.124 | 1243126.1496
26 | 2630467.5706 | 1243113.0263 | 2630470.9393 | 1243115.73
27 | 2630480.5562 | 1243194.0729 | 2630471.6197 | 1243186.2476
28 | 2630517.124 | 1243126.1496 | 2630532.256 | 1243137.5868
29 | 2630467.5706 | 1243113.0263 | 2630459.4356 | 1243106.4974 | 2630449.2652 | 1243098.6811
30 | 2630600.0377 | 1243096.5797 | 2630598.9358 | 1243105.4133 | 2630597.4289 | 1243109.7426
31 | 2630599.5038 | 1243083.1909 | 2630600.0474 | 1243096.5022 | 2630600.0377 | 1243096.5797
32 | 2630597.4289 | 1243109.7426 | 2630596.7802 | 1243111.6062 | 2630594.7712 | 1243115.6822
33 | 2630575.1002 | 1243081.5976 | 2630579.6537 | 1243082.3438 | 2630589.3725 | 1243083.9281 | 2630599.5038 | 1243083.1909
34 | 2630586.8207 | 1243131.8123 | 2630594.7712 | 1243115.6822
35 | 2630575.1002 | 1243081.5976 | 2630569.014 | 1243084.9463 | 2630548.0022 | 1243091.0199 | 2630544.631 | 1243092.1793
36 | 2630586.8207 | 1243131.8123 | 2630589.6043 | 1243134.306 | 2630596.7533 | 1243137.3559 | 2630600.556 | 1243138.8113
37 | 2630586.8207 | 1243131.8123 | 2630583.9769 | 1243135.6224
38 | 2630619.5098 | 1243147.6241 | 2630619.5098 | 1243147.6241 | 2630604.7036 | 1243140.3988 | 2630600.556 | 1243138.8113
39 | 2630583.9769 | 1243135.6224 | 2630573.4509 | 1243149.7252
40 | 2630633.3955 | 1243155.9132 | 2630632.3308 | 1243155.6131
41 | 2630625.4918 | 1243152.1004 | 2630628.8906 | 1243154.6436 | 2630632.3308 | 1243155.6131
42 | 2630633.3955 | 1243155.9132 | 2630635.1868 | 1243156.418
43 | 2630625.4918 | 1243152.1004 | 2630619.5098 | 1243147.6241
44 | 2630635.1868 | 1243156.418 | 2630635.4412 | 1243156.4897 | 2630647.4018 | 1243158.5971 | 2630652.7187 | 1243159.7502
45 | 2630652.7187 | 1243159.7502 | 2630660.3995 | 1243161.4159
46 | 2630667.0618 | 1243162.9468 | 2630663.1043 | 1243162.0025 | 2630660.3995 | 1243161.4159
47 | 2630310.1714 | 1243337.0264 | 2630311.4809 | 1243333.6531 | 2630318.549 | 1243309.6071 | 2630323.5145 | 1243294.7785 | 2630329.6777 | 1243278.109
48 | 2630334.3829 | 1243265.0483 | 2630332.3811 | 1243270.7973 | 2630329.6777 | 1243278.109
49 | 2630310.1714 | 1243337.0264 | 2630306.0866 | 1243331.8356 | 2630296.747 | 1243321.17 | 2630284.7038 | 1243310.1015
50 | 2630334.3829 | 1243265.0483 | 2630332.2992 | 1243261.6577
51 | 2630334.3829 | 1243265.0483 | 2630337.5796 | 1243271.0128 | 2630340.1025 | 1243277.1963 | 2630341.5 | 1243280.0635
52 | 2630332.2992 | 1243261.6577 | 2630335.7733 | 1243259.1849 | 2630342.6379 | 1243223.2192 | 2630347.6869 | 1243211.2929 | 2630349.0087 | 1243209.845
53 | 2630332.2992 | 1243261.6577 | 2630328.908 | 1243256.8039 | 2630323.8286 | 1243251.0076 | 2630318.2999 | 1243245.8984 | 2630315.0911 | 1243243.0776
54 | 2630356.2005 | 1243306.6974 | 2630349.9191 | 1243296.5589 | 2630344.5302 | 1243286.2803 | 2630341.5 | 1243280.0635
55 | 2630363.8133 | 1243199.8012 | 2630357.9826 | 1243202.0062 | 2630351.8291 | 1243206.7556 | 2630349.0087 | 1243209.845
56 | 2630298.9882 | 1243231.0392 | 2630300.0979 | 1243231.6965 | 2630306.1 | 1243235.8964 | 2630312.4989 | 1243240.7989 | 2630315.0911 | 1243243.0776
57 | 2630356.2005 | 1243306.6974 | 2630356.2005 | 1243306.6974 | 2630364.697 | 1243316.7028 | 2630378.1129 | 1243330.8229
58 | 2630363.8133 | 1243199.8012 | 2630362.9568 | 1243192.8924 | 2630361.9129 | 1243185.6825
59 | 2630363.8133 | 1243199.8012 | 2630365.9219 | 1243210.1408 | 2630367.3726 | 1243216.141 | 2630369.543 | 1243223.2677 | 2630371.4932 | 1243229.1037 | 2630373.4737 | 1243232.2084
60 | 2630363.8133 | 1243199.8012 | 2630382.35 | 1243193.8471
61 | 2630298.9882 | 1243231.0392 | 2630291.5006 | 1243226.6049 | 2630282.9314 | 1243221.3512
62 | 2630378.1129 | 1243330.8229 | 2630381.7983 | 1243334.7017 | 2630388.4192 | 1243341.3904
63 | 2630571.0203 | 1243231.3677 | 2630584.5669 | 1243235.0646
64 | 2630571.0203 | 1243231.3677 | 2630554 | 1243226.723
65 | 2630552.0274 | 1243187.1243 | 2630548.5663 | 1243195.8677 | 2630546.4169 | 1243202.1662
66 | 2630552.0274 | 1243187.1243 | 2630554.3551 | 1243181.5874
67 | 2630552.0274 | 1243187.1243 | 2630561.9977 | 1243191.2004 | 2630569.3985 | 1243193.7957 | 2630577.6008 | 1243196.3062 | 2630581.4023 | 1243197.6721
68 | 2630244.1339 | 1243197.5649 | 2630242.4006 | 1243196.5023 | 2630222.197 | 1243185.0033 | 2630215.3976 | 1243183.0007
69 | 2630244.1339 | 1243197.5649 | 2630271.1959 | 1243214.1563
70 | 2630271.1959 | 1243214.1563 | 2630282.9314 | 1243221.3512
71 | 2630455.7994 | 1243404.4029 | 2630451.198 | 1243408.6043 | 2630444.732 | 1243413.9837
72 | 2630455.7994 | 1243404.4029 | 2630448.6017 | 1243399.096 | 2630438.0979 | 1243391.504 | 2630432.0271 | 1243385.9935
73 | 2630455.7994 | 1243404.4029 | 2630458.1027 | 1243406.2048 | 2630459.4159 | 1243407.0339
74 | 2630432.0271 | 1243385.9935 | 2630429.4998 | 1243383.6994 | 2630423.1989 | 1243377.3964 | 2630413.068 | 1243366.7497
75 | 2630412.1962 | 1243365.8336 | 2630413.068 | 1243366.7497
76 | 2630412.1962 | 1243365.8336 | 2630401.7979 | 1243354.9059 | 2630394.4772 | 1243347.5103
77 | 2630581.4023 | 1243197.6721 | 2630587.898 | 1243200.006 | 2630598.9037 | 1243202.5976 | 2630610.9778 | 1243205.5724
78 | 2630564.6825 | 1243161.473 | 2630556.4116 | 1243176.6957 | 2630554.3551 | 1243181.5874
79 | 2630288.633 | 1243134.9733 | 2630293.711 | 1243137.6279
80 | 2630258.3084 | 1243112.1737 | 2630259.5628 | 1243116.6607 | 2630261.798 | 1243119.9965 | 2630264.4038 | 1243121.7998 | 2630268.5998 | 1243124.5007 | 2630288.633 | 1243134.9733
81 | 2630293.711 | 1243137.6279 | 2630299.3988 | 1243140.6012 | 2630316.5821 | 1243149.7042
82 | 2630258.3084 | 1243112.1737 | 2630249.9178 | 1243112.4534
83 | 2630316.5821 | 1243149.7042 | 2630317.3695 | 1243150.1214
84 | 2630317.3695 | 1243150.1214 | 2630321.0989 | 1243152.097 | 2630337.098 | 1243161.1067 | 2630343.6781 | 1243164.5981 | 2630343.7839 | 1243164.6571
85 | 2630361.9129 | 1243185.6825 | 2630359.0581 | 1243179.3861 | 2630356.5428 | 1243174.6591 | 2630352.5117 | 1243170.7916 | 2630349.27 | 1243167.7175 | 2630343.7839 | 1243164.6571
86 | 2630509.2823 | 1243348.7082 | 2630499.7644 | 1243347.8033 | 2630494.6873 | 1243346.0427 | 2630494.1075 | 1243345.7206
87 | 2630509.2823 | 1243348.7082 | 2630510.6152 | 1243341.3396
88 | 2630479.8077 | 1243337.061 | 2630485.5386 | 1243340.9592 | 2630494.1075 | 1243345.7206
89 | 2630472.4247 | 1243332.0323 | 2630476.8099 | 1243335.0218 | 2630479.8077 | 1243337.061
90 | 2630382.35 | 1243193.8471 | 2630384.8356 | 1243193.0488 | 2630400.8463 | 1243188.7752
91 | 2630404.1531 | 1243187.8926 | 2630400.8463 | 1243188.7752
92 | 2630423.7746 | 1243176.4818 | 2630411.0784 | 1243185.178 | 2630405.5569 | 1243187.5179 | 2630404.1531 | 1243187.8926
93 | 2630373.4737 | 1243232.2084 | 2630375.8193 | 1243235.8857 | 2630380.2042 | 1243241.5117 | 2630389.7411 | 1243252.0227 | 2630394.9729 | 1243257.3821
94 | 2630423.7746 | 1243176.4818 | 2630428.0333 | 1243181.6625 | 2630436.1216 | 1243188.8954
95 | 2630423.7746 | 1243176.4818 | 2630416.9988 | 1243169.8985 | 2630412.6362 | 1243163.7981
96 | 2630395.844 | 1243258.2745 | 2630394.9729 | 1243257.3821
97 | 2630442.4402 | 1243194.5457 | 2630436.1216 | 1243188.8954
98 | 2630390.4667 | 1243137.7518 | 2630397.197 | 1243144.9034 | 2630409.2021 | 1243158.996 | 2630412.6362 | 1243163.7981
99 | 2630366.7132 | 1243149.9841 | 2630366.7132 | 1243149.9841 | 2630365.009 | 1243131.4858 | 2630364.4702 | 1243124.2733
100 | 2630363.658 | 1243116.347 | 2630364.2097 | 1243120.786 | 2630364.4702 | 1243124.2733
101 | 2630405.2248 | 1243267.8839 | 2630395.844 | 1243258.2745
102 | 2630564.6825 | 1243161.473 | 2630559.1989 | 1243157.898 | 2630553.0084 | 1243153.2343
103 | 2630564.6825 | 1243161.473 | 2630572.5087 | 1243150.9875
104 | 2630553.0084 | 1243153.2343 | 2630546.7405 | 1243148.5123
105 | 2630573.4509 | 1243149.7252 | 2630572.5087 | 1243150.9875
106 | 2630546.7405 | 1243148.5123 | 2630537.6972 | 1243141.6994 | 2630532.256 | 1243137.5868
107 | 2630448.8953 | 1243200.318 | 2630442.4402 | 1243194.5457
108 | 2630390.4667 | 1243137.7518 | 2630389.1013 | 1243136.3009 | 2630370.8385 | 1243121.5076
109 | 2630363.658 | 1243116.347 | 2630370.8267 | 1243121.498 | 2630370.8385 | 1243121.5076
110 | 2630459.6648 | 1243209.9485 | 2630448.8953 | 1243200.318
111 | 2630472.4247 | 1243332.0323 | 2630468.0511 | 1243329.0508 | 2630466.213 | 1243327.5307
112 | 2630459.6648 | 1243209.9485 | 2630465.198 | 1243214.8964 | 2630468.0787 | 1243217.3415
113 | 2630473.1455 | 1243221.6423 | 2630468.0787 | 1243217.3415
114 | 2630473.1455 | 1243221.6423 | 2630479.3317 | 1243226.893
115 | 2630388.4192 | 1243341.3904 | 2630394.4772 | 1243347.5103
116 | 2630442.6563 | 1243306.2632 | 2630433.6356 | 1243297.0047
117 | 2630442.6563 | 1243306.2632 | 2630443.21 | 1243306.8315 | 2630444.3331 | 1243307.9233
118 | 2630461.0834 | 1243323.2884 | 2630454.7533 | 1243318.0534 | 2630444.3331 | 1243307.9233
119 | 2630461.0834 | 1243323.2884 | 2630466.213 | 1243327.5307

## bus_geodata
| x | y | coords
0 | 2630523.5501 | 1243279.5533
1 | 2630522.2585 | 1243284.4405
2 | 2630527.821 | 1243263.3932
3 | 2630519.2349 | 1243295.8811
4 | 2630532.3495 | 1243247.4886
5 | 2630507.6105 | 1243250.8959
6 | 2630515.2299 | 1243316.1743
7 | 2630538.4186 | 1243226.1731
8 | 2630494.7257 | 1243239.9594
9 | 2630514.8928 | 1243317.8826
10 | 2630539.3967 | 1243222.7378
11 | 2630481.5003 | 1243228.7337
12 | 2630473.9856 | 1243137.979
13 | 2630467.494 | 1243146.0379
14 | 2630478.3095 | 1243132.6109
15 | 2630451.5737 | 1243159.9206
16 | 2630487.3962 | 1243121.8729
17 | 2630502.158 | 1243153.0313
18 | 2630446.8119 | 1243162.9467
19 | 2630501.2297 | 1243112.5045
20 | 2630470.9393 | 1243115.73
21 | 2630509.022 | 1243158.9086
22 | 2630471.6197 | 1243186.2476
23 | 2630517.124 | 1243126.1496
24 | 2630467.5706 | 1243113.0263
25 | 2630600.0377 | 1243096.5797
26 | 2630597.4289 | 1243109.7426
27 | 2630599.5038 | 1243083.1909
28 | 2630594.7712 | 1243115.6822
29 | 2630575.1002 | 1243081.5976
30 | 2630586.8207 | 1243131.8123
31 | 2630544.631 | 1243092.1793
32 | 2630600.556 | 1243138.8113
33 | 2630583.9769 | 1243135.6224
34 | 2630632.3308 | 1243155.6131
35 | 2630633.3955 | 1243155.9132
36 | 2630625.4918 | 1243152.1004
37 | 2630635.1868 | 1243156.418
38 | 2630619.5098 | 1243147.6241
39 | 2630652.7187 | 1243159.7502
40 | 2630660.3995 | 1243161.4159
41 | 2630329.6777 | 1243278.109
42 | 2630310.1714 | 1243337.0264
43 | 2630334.3829 | 1243265.0483
44 | 2630284.7038 | 1243310.1015
45 | 2630332.2992 | 1243261.6577
46 | 2630341.5 | 1243280.0635
47 | 2630349.0087 | 1243209.845
48 | 2630315.0911 | 1243243.0776
49 | 2630356.2005 | 1243306.6974
50 | 2630363.8133 | 1243199.8012
51 | 2630298.9882 | 1243231.0392
52 | 2630378.1129 | 1243330.8229
53 | 2630571.0203 | 1243231.3677
54 | 2630584.5669 | 1243235.0646
55 | 2630554 | 1243226.723
56 | 2630546.4169 | 1243202.1662
57 | 2630552.0274 | 1243187.1243
58 | 2630215.3976 | 1243183.0007
59 | 2630244.1339 | 1243197.5649
60 | 2630271.1959 | 1243214.1563
61 | 2630282.9314 | 1243221.3512
62 | 2630444.732 | 1243413.9837
63 | 2630455.7994 | 1243404.4029
64 | 2630432.0271 | 1243385.9935
65 | 2630459.4159 | 1243407.0339
66 | 2630413.068 | 1243366.7497
67 | 2630412.1962 | 1243365.8336
68 | 2630610.9778 | 1243205.5724
69 | 2630581.4023 | 1243197.6721
70 | 2630554.3551 | 1243181.5874
71 | 2630288.633 | 1243134.9733
72 | 2630293.711 | 1243137.6279
73 | 2630258.3084 | 1243112.1737
74 | 2630316.5821 | 1243149.7042
75 | 2630249.9178 | 1243112.4534
76 | 2630317.3695 | 1243150.1214
77 | 2630343.7839 | 1243164.6571
78 | 2630509.2823 | 1243348.7082
79 | 2630494.1075 | 1243345.7206
80 | 2630510.6152 | 1243341.3396
81 | 2630479.8077 | 1243337.061
82 | 2630382.35 | 1243193.8471
83 | 2630400.8463 | 1243188.7752
84 | 2630404.1531 | 1243187.8926
85 | 2630361.9129 | 1243185.6825
86 | 2630373.4737 | 1243232.2084
87 | 2630423.7746 | 1243176.4818
88 | 2630394.9729 | 1243257.3821
89 | 2630436.1216 | 1243188.8954
90 | 2630412.6362 | 1243163.7981
91 | 2630366.7132 | 1243149.9841
92 | 2630364.4702 | 1243124.2733
93 | 2630395.844 | 1243258.2745
94 | 2630667.0618 | 1243162.9468
95 | 2630564.6825 | 1243161.473
96 | 2630553.0084 | 1243153.2343
97 | 2630572.5087 | 1243150.9875
98 | 2630546.7405 | 1243148.5123
99 | 2630573.4509 | 1243149.7252
100 | 2630532.256 | 1243137.5868
101 | 2630442.4403 | 1243194.5457
102 | 2630390.4667 | 1243137.7518
103 | 2630370.8385 | 1243121.5076
104 | 2630363.658 | 1243116.347
105 | 2630480.5562 | 1243194.0729
106 | 2630448.8953 | 1243200.318
107 | 2630449.2652 | 1243098.6811
108 | 2630472.4247 | 1243332.0323
109 | 2630459.6648 | 1243209.9485
110 | 2630468.0787 | 1243217.3415
111 | 2630473.1455 | 1243221.6423
112 | 2630394.4772 | 1243347.5103
113 | 2630388.4192 | 1243341.3904
114 | 2630405.2248 | 1243267.8839
115 | 2630433.6356 | 1243297.0047
116 | 2630442.6563 | 1243306.2632
117 | 2630444.3331 | 1243307.9233
118 | 2630461.0834 | 1243323.2884
119 | 2630466.213 | 1243327.5307
120 | 2630479.3317 | 1243226.893
121 | 2630423.7746 | 1243176.4818

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99202 | -0.15235 | 0.0029589 | 0.00074158
1 | 0.99181 | -0.15634 | 0.0011026 | 0.00027634
2 | 0.99274 | -0.13831 | 0 | 0
3 | 0.99134 | -0.16545 | 0 | 0
4 | 0.99136 | -0.16486 | 0.0019893 | 0.00049856
5 | 0.99579 | -0.080025 | 0.0019578 | 0.00049067
6 | 0.99051 | -0.18139 | 0.0015231 | 0.00038173
7 | 0.98955 | -0.19978 | 0.0012646 | 0.00031693
8 | 0.99688 | -0.059237 | 0.0030929 | 0.00077516
9 | 0.99045 | -0.18269 | 0.00137 | 0.00034336
10 | 0.98926 | -0.20534 | 0 | 0
11 | 0.99802 | -0.037478 | 0.002219 | 0.00055613
12 | 0.98166 | -0.35317 | 0.0029808 | 0.00074705
13 | 0.98157 | -0.35484 | 0.0018863 | 0.00047276
14 | 0.98173 | -0.35169 | 0 | 0
15 | 0.98143 | -0.35756 | 0.001775 | 0.00044486
16 | 0.98196 | -0.34722 | 0 | 0
17 | 0.98157 | -0.35493 | 0.0032275 | 0.00080888
18 | 0.98141 | -0.35809 | 0 | 0
19 | 0.98237 | -0.33923 | 0 | 0
20 | 0.98182 | -0.35006 | 0.002298 | 0.00057593
21 | 0.98155 | -0.35533 | 0.0024735 | 0.00061991
22 | 0.98124 | -0.36133 | 0.0030412 | 0.0007622
23 | 0.98288 | -0.32921 | 0.0014667 | 0.0003676
24 | 0.98179 | -0.35058 | 0.0031004 | 0.00077704
25 | 0.98279 | -0.33105 | 0.0066553 | 0.001668
26 | 0.98289 | -0.32907 | 0.0022312 | 0.0005592
27 | 0.98277 | -0.3314 | 0 | 0
28 | 0.98295 | -0.32785 | 0.0038404 | 0.0009625
29 | 0.98274 | -0.33206 | 0 | 0
30 | 0.98319 | -0.32325 | 0 | 0
31 | 0.9827 | -0.33292 | 0.0014676 | 0.00036781
32 | 0.98288 | -0.32925 | 0.0017452 | 0.00043738
33 | 0.98335 | -0.3202 | 0.0019197 | 0.00048111
34 | 0.98228 | -0.34103 | 0.0024542 | 0.00061509
35 | 0.98227 | -0.34127 | 0.0020435 | 0.00051215
36 | 0.98239 | -0.33897 | 0.0026115 | 0.00065449
37 | 0.98225 | -0.34161 | 0.0023401 | 0.00058647
38 | 0.9825 | -0.33666 | 0.0024477 | 0.00061346
39 | 0.98212 | -0.3441 | 0.0038029 | 0.00095309
40 | 0.98209 | -0.34465 | 0.0019609 | 0.00049145
41 | 0.98472 | -0.29382 | 0.0039665 | 0.00099411
42 | 0.9843 | -0.30216 | 0 | 0
43 | 0.98487 | -0.29097 | 0 | 0
44 | 0.98404 | -0.30714 | 0.0074599 | 0.0018696
45 | 0.98499 | -0.28868 | 0 | 0
46 | 0.98455 | -0.29715 | 0.0019175 | 0.00048058
47 | 0.98769 | -0.23604 | 0.0023299 | 0.00058393
48 | 0.98451 | -0.29808 | 0.0041764 | 0.0010467
49 | 0.98403 | -0.30742 | 0.0011291 | 0.00028299
50 | 0.98862 | -0.21819 | 0 | 0
51 | 0.9842 | -0.30401 | 0.0020083 | 0.00050332
52 | 0.9835 | -0.31776 | 0.0018532 | 0.00046445
53 | 0.98912 | -0.20801 | 0.0017183 | 0.00043064
54 | 0.9891 | -0.20856 | 0.0021752 | 0.00054515
55 | 0.98919 | -0.20679 | 0.0014858 | 0.00037239
56 | 0.98762 | -0.23715 | 0.0023062 | 0.00057798
57 | 0.98643 | -0.26005 | 0 | 0
58 | 0.98355 | -0.31681 | 0.0023197 | 0.00058136
59 | 0.98362 | -0.31545 | 0.0047937 | 0.0012014
60 | 0.98382 | -0.31139 | 0.0030493 | 0.00076423
61 | 0.98395 | -0.30887 | 0.0042152 | 0.0010564
62 | 0.98263 | -0.33471 | 0.0014694 | 0.00036826
63 | 0.98265 | -0.33432 | 0 | 0
64 | 0.98273 | -0.33269 | 0.0039892 | 0.00099979
65 | 0.98264 | -0.33444 | 0.0015385 | 0.00038559
66 | 0.98291 | -0.32927 | 0.0024165 | 0.00060564
67 | 0.98292 | -0.32906 | 0.0015098 | 0.00037839
68 | 0.98625 | -0.26373 | 0.0023365 | 0.00058558
69 | 0.98631 | -0.26245 | 0.001941 | 0.00048646
70 | 0.98602 | -0.26817 | 0.0029965 | 0.00075099
71 | 0.98774 | -0.23524 | 0.0019603 | 0.0004913
72 | 0.98776 | -0.23477 | 0.0012718 | 0.00031873
73 | 0.98765 | -0.23705 | 0 | 0
74 | 0.9879 | -0.23209 | 0.0015675 | 0.00039286
75 | 0.98763 | -0.23743 | 0.0025687 | 0.00064379
76 | 0.98791 | -0.23198 | 0.0019141 | 0.00047972
77 | 0.98816 | -0.22698 | 0.0022116 | 0.00055428
78 | 0.98929 | -0.20508 | 0 | 0
79 | 0.98873 | -0.21595 | 0.0020938 | 0.00052475
80 | 0.98956 | -0.19987 | 0.0014398 | 0.00036086
81 | 0.98816 | -0.22699 | 0.0020412 | 0.00051158
82 | 0.99037 | -0.18431 | 0.0022585 | 0.00056603
83 | 0.99213 | -0.15029 | 0.002259 | 0.00056617
84 | 0.99245 | -0.14409 | 0.0020549 | 0.00051499
85 | 0.98847 | -0.22111 | 0 | 0
86 | 0.98764 | -0.23716 | 0.0076097 | 0.0019072
87 | 0.99465 | -0.10203 | 0 | 0
88 | 0.98692 | -0.25118 | 0.0096498 | 0.0024185
89 | 0.9965 | -0.066605 | 0.0026579 | 0.00066613
90 | 0.99449 | -0.10514 | 0.0039489 | 0.0009897
91 | 0.99409 | -0.11281 | 0.0013561 | 0.00033987
92 | 0.99412 | -0.11219 | 0.0015245 | 0.00038206
93 | 0.9869 | -0.25149 | 0.0037569 | 0.00094157
94 | 0.98208 | -0.34489 | 0.0019523 | 0.00048929
95 | 0.9845 | -0.29761 | 0 | 0
96 | 0.98408 | -0.30575 | 0.0011568 | 0.00028991
97 | 0.98401 | -0.30721 | 0.0015359 | 0.00038493
98 | 0.98386 | -0.31006 | 0.0011431 | 0.00028649
99 | 0.98395 | -0.30832 | 0.0017621 | 0.00044161
100 | 0.98337 | -0.31966 | 0.0014404 | 0.00036099
101 | 0.99741 | -0.049156 | 0.0026923 | 0.00067475
102 | 0.99428 | -0.10904 | 0.0013638 | 0.00034181
103 | 0.99417 | -0.11133 | 0.0022197 | 0.0005563
104 | 0.99414 | -0.11178 | 0 | 0
105 | 0.98122 | -0.3618 | 0.0021994 | 0.00055122
106 | 0.99837 | -0.030955 | 0.0026466 | 0.00066329
107 | 0.98172 | -0.35204 | 0.00347 | 0.00086967
108 | 0.98787 | -0.23256 | 0.0031398 | 0.0007869
109 | 1 | 0 | -0.27885 | -0.070775
110 | 0.99922 | -0.014764 | 0.0019774 | 0.00049559
111 | 0.99876 | -0.023421 | 0.0019758 | 0.00049518
112 | 0.98318 | -0.32403 | 0.0024542 | 0.00061509
113 | 0.98328 | -0.32196 | 0.0023803 | 0.00059655
114 | 0.98678 | -0.25395 | 0.010227 | 0.0025631
115 | 0.98672 | -0.25505 | 0.0099967 | 0.0025054
116 | 0.98684 | -0.25273 | 0.0078867 | 0.0019766
117 | 0.98688 | -0.25198 | 0.010335 | 0.0025903
118 | 0.98747 | -0.2405 | 0.0017925 | 0.00044923
119 | 0.98765 | -0.23693 | 0.0017963 | 0.00045019
120 | 0.99821 | -0.03386 | 0.0017561 | 0.00044012
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.044702 | 0.011273 | -0.044694 | -0.011268 | 8.5293e-06 | 5.3935e-06 | 0.067078 | 0.067078 | 0.067078 | 0.99202 | -0.15235 | 0.99181 | -0.15634 | 18.428
1 | -0.047661 | -0.012015 | 0.047693 | 0.012035 | 3.2059e-05 | 2.0301e-05 | 0.071516 | 0.071516 | 0.071516 | 0.99202 | -0.15235 | 0.99274 | -0.13831 | 19.6473
2 | 0.043591 | 0.010991 | -0.043572 | -0.010979 | 1.8994e-05 | 1.2003e-05 | 0.065424 | 0.065424 | 0.065424 | 0.99181 | -0.15634 | 0.99134 | -0.16545 | 17.9735
3 | 0.091425 | 0.023209 | -0.091309 | -0.023134 | 0.00011663 | 7.4432e-05 | 0.13714 | 0.13714 | 0.13714 | 0.99274 | -0.13831 | 0.99136 | -0.16486 | 37.6763
4 | -0.13912 | -0.035244 | 0.13951 | 0.035494 | 0.00039068 | 0.00024972 | 0.20866 | 0.20866 | 0.20866 | 0.99274 | -0.13831 | 0.99579 | -0.080025 | 57.3236
5 | 0.043572 | 0.010979 | -0.043539 | -0.010958 | 3.3201e-05 | 2.0982e-05 | 0.065424 | 0.065424 | 0.065424 | 0.99134 | -0.16545 | 0.99051 | -0.18139 | 17.9736
6 | 0.089319 | 0.022636 | -0.08917 | -0.02254 | 0.00014958 | 9.5446e-05 | 0.13416 | 0.13416 | 0.13416 | 0.99136 | -0.16486 | 0.98955 | -0.19978 | 36.856
7 | -0.14147 | -0.035984 | 0.14161 | 0.036075 | 0.00014186 | 9.0351e-05 | 0.21158 | 0.21158 | 0.21158 | 0.99579 | -0.080025 | 0.99688 | -0.059237 | 29.0636
8 | 0.042016 | 0.010577 | -0.042013 | -0.010575 | 2.6028e-06 | 1.6434e-06 | 0.063136 | 0.063136 | 0.063136 | 0.99051 | -0.18139 | 0.99045 | -0.18269 | 17.345
9 | 0.087905 | 0.022223 | -0.087882 | -0.022208 | 2.3429e-05 | 1.4948e-05 | 0.13225 | 0.13225 | 0.13225 | 0.98955 | -0.19978 | 0.98926 | -0.20534 | 36.3336
10 | -0.1447 | -0.03685 | 0.14485 | 0.036947 | 0.00015203 | 9.6849e-05 | 0.2162 | 0.2162 | 0.2162 | 0.99688 | -0.059237 | 0.99802 | -0.037478 | 29.6978
11 | 0.040643 | 0.010232 | -0.04061 | -0.010211 | 3.3356e-05 | 2.1041e-05 | 0.061077 | 0.061077 | 0.061077 | 0.99045 | -0.18269 | 0.98956 | -0.19987 | 16.7795
12 | 0.082502 | 0.02086 | -0.082376 | -0.02078 | 0.00012566 | 8.0144e-05 | 0.12416 | 0.12416 | 0.12416 | 0.98926 | -0.20534 | 0.98762 | -0.23715 | 34.1105
13 | 0.0053799 | 0.001348 | -0.0053796 | -0.0013479 | 3.7172e-07 | 4.3568e-08 | 0.0080922 | 0.0080923 | 0.0080923 | 0.98926 | -0.20534 | 0.98919 | -0.20679 | 2.2232
14 | -0.14707 | -0.037503 | 0.1471 | 0.037519 | 2.5698e-05 | 1.6372e-05 | 0.21951 | 0.21951 | 0.21951 | 0.99802 | -0.037478 | 0.99821 | -0.03386 | 30.1522
15 | 0.0089046 | 0.0022317 | -0.0089039 | -0.0022313 | 7.07e-07 | 3.2166e-07 | 0.013498 | 0.013498 | 0.013498 | 0.98166 | -0.35317 | 0.98157 | -0.35484 | 3.7082
16 | -0.011885 | -0.0029787 | 0.011886 | 0.0029792 | 8.3898e-07 | 4.498e-07 | 0.018016 | 0.018016 | 0.018016 | 0.98166 | -0.35317 | 0.98173 | -0.35169 | 4.9494
17 | 0.0070175 | 0.0017586 | -0.0070166 | -0.0017583 | 9.0882e-07 | 3.11e-07 | 0.010638 | 0.010638 | 0.010638 | 0.98157 | -0.35484 | 0.98143 | -0.35756 | 2.9226
18 | -0.017588 | -0.004408 | 0.017592 | 0.0044102 | 3.7446e-06 | 2.2188e-06 | 0.026658 | 0.026658 | 0.026658 | 0.98173 | -0.35169 | 0.98196 | -0.34722 | 7.3237
19 | 0.0057019 | 0.0014289 | -0.005701 | -0.0014287 | 8.7938e-07 | 1.6588e-07 | 0.0086423 | 0.0086424 | 0.0086424 | 0.98173 | -0.35169 | 0.98157 | -0.35493 | 2.3743
20 | 0.0052416 | 0.0013134 | -0.0052415 | -0.0013134 | 1.3362e-07 | 1.4224e-08 | 0.007947 | 0.0079471 | 0.0079471 | 0.98143 | -0.35756 | 0.98141 | -0.35809 | 2.1833
21 | -0.026462 | -0.0066333 | 0.026472 | 0.0066396 | 1.0078e-05 | 6.2386e-06 | 0.040099 | 0.040099 | 0.040099 | 0.98196 | -0.34722 | 0.98237 | -0.33923 | 11.0163
22 | 0.0088701 | 0.0022231 | -0.0088689 | -0.0022226 | 1.2017e-06 | 5.4476e-07 | 0.013441 | 0.013441 | 0.013441 | 0.98196 | -0.34722 | 0.98182 | -0.35006 | 3.6927
23 | 0.0024735 | 0.00061983 | -0.0024735 | -0.00061991 | 4.7646e-08 | -8.3725e-08 | 0.0037497 | 0.0037498 | 0.0037498 | 0.98157 | -0.35493 | 0.98155 | -0.35533 | 1.0302
24 | 0.0052415 | 0.0013134 | -0.0052407 | -0.0013133 | 8.0743e-07 | 8.6044e-08 | 0.0079471 | 0.0079472 | 0.0079472 | 0.98141 | -0.35809 | 0.98124 | -0.36133 | 2.1833
25 | -0.026472 | -0.0066396 | 0.026485 | 0.0066474 | 1.2644e-05 | 7.8266e-06 | 0.040099 | 0.040099 | 0.040099 | 0.98237 | -0.33923 | 0.98288 | -0.32921 | 11.0163
26 | 0.0065709 | 0.0016466 | -0.0065707 | -0.0016466 | 1.6064e-07 | 4.8185e-08 | 0.0099586 | 0.0099586 | 0.0099586 | 0.98182 | -0.35006 | 0.98179 | -0.35058 | 2.7359
27 | 0.0021995 | 0.00055111 | -0.0021994 | -0.00055122 | 4.9554e-08 | -1.1833e-07 | 0.0033354 | 0.0033354 | 0.0033354 | 0.98124 | -0.36133 | 0.98122 | -0.3618 | 0.91632
28 | -0.027951 | -0.007015 | 0.027964 | 0.0070229 | 1.2739e-05 | 7.9125e-06 | 0.04232 | 0.04232 | 0.04232 | 0.98288 | -0.32921 | 0.98337 | -0.31966 | 11.6263
29 | 0.0034703 | 0.00086953 | -0.00347 | -0.00086967 | 2.4127e-07 | -1.3968e-07 | 0.0052595 | 0.0052596 | 0.0052596 | 0.98179 | -0.35058 | 0.98172 | -0.35204 | 1.445
30 | -0.008123 | -0.002035 | 0.0081238 | 0.0020353 | 7.6493e-07 | 3.1865e-07 | 0.012299 | 0.012298 | 0.012299 | 0.98279 | -0.33105 | 0.98289 | -0.32907 | 3.3787
31 | 0.0014677 | 0.000367 | -0.0014677 | -0.00036715 | 2.4809e-08 | -1.5393e-07 | 0.0022219 | 0.002222 | 0.002222 | 0.98279 | -0.33105 | 0.98277 | -0.3314 | 0.61043
32 | -0.010355 | -0.0025945 | 0.010356 | 0.0025948 | 6.0062e-07 | 3.0179e-07 | 0.015676 | 0.015676 | 0.015676 | 0.98289 | -0.32907 | 0.98295 | -0.32785 | 4.3067
33 | 0.0014677 | 0.00036715 | -0.0014676 | -0.00036744 | 4.5583e-08 | -2.8277e-07 | 0.002222 | 0.0022221 | 0.0022221 | 0.98277 | -0.3314 | 0.98274 | -0.33206 | 0.61046
34 | -0.014196 | -0.0035573 | 0.014199 | 0.0035591 | 3.1144e-06 | 1.7652e-06 | 0.02149 | 0.02149 | 0.02149 | 0.98295 | -0.32785 | 0.98319 | -0.32325 | 5.9039
35 | 0.0014676 | 0.00036744 | -0.0014676 | -0.00036781 | 5.9965e-08 | -3.7191e-07 | 0.0022221 | 0.0022222 | 0.0022222 | 0.98274 | -0.33206 | 0.9827 | -0.33292 | 0.6105
36 | 0.021376 | 0.0053631 | -0.02137 | -0.0053594 | 6.1162e-06 | 3.7168e-06 | 0.032354 | 0.032354 | 0.032354 | 0.98319 | -0.32325 | 0.98288 | -0.32925 | 8.8884
37 | -0.035575 | -0.0089222 | 0.03558 | 0.0089254 | 5.1688e-06 | 3.2478e-06 | 0.053844 | 0.053844 | 0.053844 | 0.98319 | -0.32325 | 0.98335 | -0.3202 | 14.7922
38 | 0.019625 | 0.004922 | -0.019618 | -0.0049178 | 6.9241e-06 | 4.1665e-06 | 0.029712 | 0.029712 | 0.029712 | 0.98288 | -0.32925 | 0.9825 | -0.33666 | 8.1626
39 | -0.0375 | -0.0094065 | 0.037521 | 0.0094199 | 2.1252e-05 | 1.3378e-05 | 0.056748 | 0.056748 | 0.056748 | 0.98335 | -0.3202 | 0.98395 | -0.30832 | 15.5902
40 | 0.012101 | 0.0030329 | -0.012101 | -0.0030328 | 1.394e-07 | 7.5211e-08 | 0.018331 | 0.018331 | 0.018331 | 0.98228 | -0.34103 | 0.98227 | -0.34127 | 5.0361
41 | -0.014555 | -0.0036479 | 0.014557 | 0.0036488 | 1.4255e-06 | 8.1334e-07 | 0.022049 | 0.022049 | 0.022049 | 0.98228 | -0.34103 | 0.98239 | -0.33897 | 6.0574
42 | 0.010057 | 0.0025206 | -0.010057 | -0.0025206 | 1.62e-07 | 8.0124e-08 | 0.015236 | 0.015236 | 0.015236 | 0.98227 | -0.34127 | 0.98225 | -0.34161 | 4.1856
43 | -0.017168 | -0.0043033 | 0.01717 | 0.0043044 | 1.8947e-06 | 1.118e-06 | 0.026005 | 0.026005 | 0.026005 | 0.98239 | -0.33897 | 0.9825 | -0.33666 | 7.1441
44 | 0.0077171 | 0.0019341 | -0.0077162 | -0.0019337 | 9.1484e-07 | 3.5959e-07 | 0.011691 | 0.011691 | 0.011691 | 0.98225 | -0.34161 | 0.98212 | -0.3441 | 3.2118
45 | 0.0039133 | 0.00098064 | -0.0039132 | -0.00098067 | 1.0361e-07 | -3.3144e-08 | 0.005929 | 0.0059291 | 0.0059291 | 0.98212 | -0.3441 | 0.98209 | -0.34465 | 1.6289
46 | 0.0019523 | 0.00048922 | -0.0019523 | -0.00048929 | 2.2432e-08 | -7.2147e-08 | 0.002958 | 0.0029581 | 0.0029581 | 0.98209 | -0.34465 | 0.98208 | -0.34489 | 0.81265
47 | 0.0074646 | 0.0018714 | -0.0074616 | -0.0018703 | 2.9627e-06 | 1.1066e-06 | 0.01128 | 0.01128 | 0.01128 | 0.98472 | -0.29382 | 0.9843 | -0.30216 | 3.099
48 | -0.011431 | -0.0028655 | 0.011433 | 0.0028663 | 1.5534e-06 | 8.1755e-07 | 0.017274 | 0.017274 | 0.017274 | 0.98472 | -0.29382 | 0.98487 | -0.29097 | 4.7455
49 | 0.0074616 | 0.0018703 | -0.0074599 | -0.0018696 | 1.7722e-06 | 6.6226e-07 | 0.01128 | 0.01128 | 0.01128 | 0.9843 | -0.30216 | 0.98404 | -0.30714 | 3.099
50 | -0.032123 | -0.0080619 | 0.032127 | 0.0080641 | 3.5136e-06 | 2.1981e-06 | 0.048538 | 0.048538 | 0.048538 | 0.98487 | -0.29097 | 0.98499 | -0.28868 | 13.3346
51 | 0.02069 | 0.0051956 | -0.020684 | -0.0051919 | 6.0975e-06 | 3.6908e-06 | 0.031264 | 0.031264 | 0.031264 | 0.98487 | -0.29097 | 0.98455 | -0.29715 | 8.5891
52 | -0.052709 | -0.013228 | 0.052842 | 0.013313 | 0.00013267 | 8.4199e-05 | 0.079634 | 0.079633 | 0.079634 | 0.98499 | -0.28868 | 0.98769 | -0.23604 | 21.8774
53 | 0.020582 | 0.0051644 | -0.020573 | -0.0051588 | 9.2206e-06 | 5.5777e-06 | 0.031096 | 0.031096 | 0.031096 | 0.98499 | -0.28868 | 0.98451 | -0.29808 | 8.5428
54 | 0.018767 | 0.0047113 | -0.018758 | -0.0047058 | 9.1875e-06 | 5.493e-06 | 0.028366 | 0.028366 | 0.028366 | 0.98455 | -0.29715 | 0.98403 | -0.30742 | 7.7929
55 | -0.055172 | -0.013897 | 0.055219 | 0.013927 | 4.7155e-05 | 2.9946e-05 | 0.083144 | 0.083144 | 0.083144 | 0.98769 | -0.23604 | 0.98862 | -0.21819 | 22.8416
56 | 0.016397 | 0.0041121 | -0.016392 | -0.0041094 | 4.6362e-06 | 2.7113e-06 | 0.024784 | 0.024784 | 0.024784 | 0.98451 | -0.29808 | 0.9842 | -0.30401 | 6.8087
57 | 0.017628 | 0.0044228 | -0.01762 | -0.0044177 | 8.6892e-06 | 5.1471e-06 | 0.026659 | 0.026659 | 0.026659 | 0.98403 | -0.30742 | 0.9835 | -0.31776 | 7.3239
58 | 0.011502 | 0.0028839 | -0.011501 | -0.0028831 | 1.6015e-06 | 8.423e-07 | 0.017313 | 0.017313 | 0.017313 | 0.98862 | -0.21819 | 0.98847 | -0.22111 | 4.7563
59 | 0.031289 | 0.0078584 | -0.031261 | -0.0078407 | 2.8294e-05 | 1.7673e-05 | 0.0471 | 0.0471 | 0.0471 | 0.98862 | -0.21819 | 0.98764 | -0.23716 | 12.9397
60 | -0.09801 | -0.024669 | 0.098169 | 0.02477 | 0.00015897 | 0.00010149 | 0.14756 | 0.14756 | 0.14756 | 0.98862 | -0.21819 | 0.99037 | -0.18431 | 40.5376
61 | 0.014384 | 0.0036061 | -0.014381 | -0.0036042 | 3.3261e-06 | 1.8904e-06 | 0.021747 | 0.021748 | 0.021748 | 0.9842 | -0.30401 | 0.98395 | -0.30887 | 5.9746
62 | 0.015767 | 0.0039532 | -0.015763 | -0.0039514 | 3.1502e-06 | 1.8289e-06 | 0.023855 | 0.023855 | 0.023855 | 0.9835 | -0.31776 | 0.98328 | -0.32196 | 6.5536
63 | 0.0021752 | 0.00054501 | -0.0021752 | -0.00054515 | 5.6387e-08 | -1.4414e-07 | 0.0032723 | 0.0032724 | 0.0032724 | 0.98912 | -0.20801 | 0.9891 | -0.20856 | 0.89901
64 | -0.0038935 | -0.00097564 | 0.0038937 | 0.00097556 | 2.2697e-07 | -8.1203e-08 | 0.0058572 | 0.0058572 | 0.0058572 | 0.98912 | -0.20801 | 0.98919 | -0.20679 | 1.6091
65 | 0.08007 | 0.020202 | -0.079982 | -0.020146 | 8.7713e-05 | 5.5931e-05 | 0.12069 | 0.12069 | 0.12069 | 0.98762 | -0.23715 | 0.98643 | -0.26005 | 33.156
66 | 0.075704 | 0.019075 | -0.075675 | -0.019056 | 2.9392e-05 | 1.8734e-05 | 0.11423 | 0.11423 | 0.11423 | 0.98643 | -0.26005 | 0.98602 | -0.26817 | 31.3831
67 | 0.0042781 | 0.0010716 | -0.0042776 | -0.0010717 | 4.8774e-07 | -8.6492e-08 | 0.0064532 | 0.0064534 | 0.0064534 | 0.98643 | -0.26005 | 0.98631 | -0.26245 | 1.7729
68 | -0.0023197 | -0.00058136 | 0.0023198 | 0.00058104 | 1.4949e-07 | -3.1514e-07 | 0.0035094 | 0.0035093 | 0.0035094 | 0.98355 | -0.31681 | 0.98362 | -0.31545 | 0.96413
69 | -0.0071135 | -0.0017825 | 0.0071148 | 0.0017829 | 1.3784e-06 | 4.7921e-07 | 0.010761 | 0.010761 | 0.010761 | 0.98362 | -0.31545 | 0.98382 | -0.31139 | 2.9564
70 | -0.010164 | -0.0025472 | 0.010165 | 0.0025478 | 1.2199e-06 | 6.0595e-07 | 0.015373 | 0.015373 | 0.015373 | 0.98382 | -0.31139 | 0.98395 | -0.30887 | 4.2234
71 | -0.0014694 | -0.00036826 | 0.0014694 | 0.0003681 | 2.7185e-08 | -1.6808e-07 | 0.0022251 | 0.0022251 | 0.0022251 | 0.98263 | -0.33471 | 0.98265 | -0.33432 | 0.6113
72 | -0.0030079 | -0.00075363 | 0.0030082 | 0.0007534 | 2.3418e-07 | -2.3149e-07 | 0.0045548 | 0.0045547 | 0.0045548 | 0.98265 | -0.33432 | 0.98273 | -0.33269 | 1.2513
73 | 0.0015385 | 0.00038554 | -0.0015385 | -0.00038559 | 9.1133e-09 | -5.0887e-08 | 0.0023297 | 0.0023298 | 0.0023298 | 0.98265 | -0.33432 | 0.98264 | -0.33444 | 0.64005
74 | -0.0069974 | -0.0017532 | 0.0069985 | 0.0017536 | 1.1375e-06 | 3.8556e-07 | 0.010595 | 0.010595 | 0.010595 | 0.98273 | -0.33269 | 0.98291 | -0.32927 | 2.9107
75 | -0.0094151 | -0.0023592 | 0.0094152 | 0.0023593 | 9.6347e-08 | 4.5633e-08 | 0.014253 | 0.014253 | 0.014253 | 0.98291 | -0.32927 | 0.98292 | -0.32906 | 3.9157
76 | -0.010925 | -0.0027377 | 0.010928 | 0.002739 | 2.6147e-06 | 1.3502e-06 | 0.016539 | 0.016539 | 0.016539 | 0.98292 | -0.32906 | 0.98318 | -0.32403 | 4.5436
77 | -0.0023365 | -0.00058558 | 0.0023366 | 0.00058528 | 1.428e-07 | -2.9968e-07 | 0.0035252 | 0.0035251 | 0.0035252 | 0.98625 | -0.26373 | 0.98631 | -0.26245 | 0.96846
78 | 0.072678 | 0.018305 | -0.072576 | -0.01824 | 0.00010215 | 6.5089e-05 | 0.10971 | 0.10971 | 0.10971 | 0.98602 | -0.26817 | 0.9845 | -0.29761 | 30.1408
79 | -0.0045293 | -0.0011346 | 0.0045294 | 0.0011346 | 1.0004e-07 | -9.3206e-09 | 0.0068232 | 0.0068231 | 0.0068232 | 0.98774 | -0.23524 | 0.98776 | -0.23477 | 1.8745
80 | 0.002569 | 0.00064335 | -0.0025688 | -0.00064371 | 2.2151e-07 | -3.6299e-07 | 0.00387 | 0.0038702 | 0.0038702 | 0.98774 | -0.23524 | 0.98765 | -0.23705 | 1.0632
81 | -0.0058012 | -0.0014534 | 0.0058019 | 0.0014535 | 7.4069e-07 | 1.4293e-07 | 0.008739 | 0.0087388 | 0.008739 | 0.98776 | -0.23477 | 0.9879 | -0.23209 | 2.4008
82 | 0.0025688 | 0.00064371 | -0.0025687 | -0.00064379 | 4.7155e-08 | -7.7254e-08 | 0.0038702 | 0.0038702 | 0.0038702 | 0.98765 | -0.23705 | 0.98763 | -0.23743 | 1.0632
83 | -0.0073694 | -0.0018464 | 0.0073695 | 0.0018464 | 4.117e-08 | 1.4939e-08 | 0.0111 | 0.0111 | 0.0111 | 0.9879 | -0.23209 | 0.98791 | -0.23198 | 3.0494
84 | -0.0092836 | -0.0023261 | 0.0092858 | 0.0023271 | 2.2108e-06 | 1.0287e-06 | 0.013983 | 0.013983 | 0.013983 | 0.98791 | -0.23198 | 0.98816 | -0.22698 | 3.8415
85 | -0.011497 | -0.0028814 | 0.011501 | 0.0028831 | 3.2152e-06 | 1.6912e-06 | 0.017313 | 0.017313 | 0.017313 | 0.98816 | -0.22698 | 0.98847 | -0.22111 | 4.7564
86 | 0.03916 | 0.0098437 | -0.03914 | -0.0098309 | 2.03e-05 | 1.2792e-05 | 0.058912 | 0.058912 | 0.058912 | 0.98929 | -0.20508 | 0.98873 | -0.21595 | 16.1847
87 | -0.03916 | -0.0098437 | 0.03917 | 0.0098498 | 9.746e-06 | 6.1412e-06 | 0.058912 | 0.058912 | 0.058912 | 0.98929 | -0.20508 | 0.98956 | -0.19987 | 16.1847
88 | 0.037046 | 0.0093061 | -0.037027 | -0.0092939 | 1.9512e-05 | 1.2273e-05 | 0.055761 | 0.055761 | 0.055761 | 0.98873 | -0.21595 | 0.98816 | -0.22699 | 15.3191
89 | 0.034985 | 0.0087823 | -0.034976 | -0.0087764 | 9.2991e-06 | 5.837e-06 | 0.052688 | 0.052688 | 0.052688 | 0.98816 | -0.22699 | 0.98787 | -0.23256 | 14.4746
90 | -0.10043 | -0.025336 | 0.10059 | 0.025441 | 0.0001639 | 0.00010465 | 0.15095 | 0.15095 | 0.15095 | 0.99037 | -0.18431 | 0.99213 | -0.15029 | 41.4698
91 | -0.10285 | -0.026007 | 0.10288 | 0.026027 | 3.0573e-05 | 1.9522e-05 | 0.15434 | 0.15434 | 0.15434 | 0.99213 | -0.15029 | 0.99245 | -0.14409 | 42.4006
92 | -0.10494 | -0.026542 | 0.10515 | 0.026677 | 0.00021223 | 0.00013553 | 0.15742 | 0.15742 | 0.15742 | 0.99245 | -0.14409 | 0.99465 | -0.10203 | 43.247
93 | 0.023651 | 0.0059336 | -0.023635 | -0.0059239 | 1.5799e-05 | 9.6872e-06 | 0.035635 | 0.035636 | 0.035636 | 0.98764 | -0.23716 | 0.98692 | -0.25118 | 9.79
94 | -0.11556 | -0.029288 | 0.11576 | 0.029414 | 0.00019705 | 0.00012589 | 0.173 | 0.173 | 0.173 | 0.99465 | -0.10203 | 0.9965 | -0.066605 | 47.528
95 | 0.010416 | 0.0026104 | -0.010415 | -0.0026096 | 1.5433e-06 | 7.6777e-07 | 0.015583 | 0.015583 | 0.015583 | 0.99465 | -0.10203 | 0.99449 | -0.10514 | 4.2811
96 | 0.013985 | 0.0035054 | -0.013985 | -0.0035053 | 2.0794e-07 | 1.1715e-07 | 0.021086 | 0.021086 | 0.021086 | 0.98692 | -0.25118 | 0.9869 | -0.25149 | 5.7929
97 | -0.11842 | -0.03008 | 0.11852 | 0.030143 | 9.9552e-05 | 6.3603e-05 | 0.17697 | 0.17697 | 0.17697 | 0.9965 | -0.066605 | 0.99741 | -0.049156 | 48.6184
98 | 0.006466 | 0.0016199 | -0.0064648 | -0.0016196 | 1.2017e-06 | 3.2496e-07 | 0.0096746 | 0.0096747 | 0.0096747 | 0.99449 | -0.10514 | 0.99428 | -0.10904 | 2.6579
99 | -0.0013561 | -0.00033987 | 0.0013561 | 0.00033956 | 3.9878e-08 | -3.091e-07 | 0.0020299 | 0.0020298 | 0.0020299 | 0.99409 | -0.11281 | 0.99412 | -0.11219 | 0.55766
100 | -0.0028806 | -0.00072163 | 0.0028806 | 0.00072156 | 5.5562e-08 | -6.778e-08 | 0.0043116 | 0.0043116 | 0.0043116 | 0.99412 | -0.11219 | 0.99414 | -0.11178 | 1.1845
101 | 0.010228 | 0.0025637 | -0.010227 | -0.0025631 | 1.1977e-06 | 5.9494e-07 | 0.015422 | 0.015422 | 0.015422 | 0.9869 | -0.25149 | 0.98678 | -0.25395 | 4.2367
102 | 0.031736 | 0.0079804 | -0.031724 | -0.0079726 | 1.2341e-05 | 7.7163e-06 | 0.047977 | 0.047977 | 0.047977 | 0.9845 | -0.29761 | 0.98408 | -0.30575 | 13.1805
103 | 0.04084 | 0.01026 | -0.040821 | -0.010248 | 1.87e-05 | 1.1802e-05 | 0.061736 | 0.061736 | 0.061736 | 0.9845 | -0.29761 | 0.98401 | -0.30721 | 16.9603
104 | 0.030567 | 0.0076827 | -0.030561 | -0.0076788 | 6.2889e-06 | 3.9252e-06 | 0.046228 | 0.046228 | 0.046228 | 0.98408 | -0.30575 | 0.98386 | -0.31006 | 12.7
105 | 0.039285 | 0.0098628 | -0.039283 | -0.0098615 | 2.085e-06 | 1.3144e-06 | 0.059413 | 0.059413 | 0.059413 | 0.98401 | -0.30721 | 0.98395 | -0.30832 | 16.3223
106 | 0.029418 | 0.0073923 | -0.029404 | -0.0073839 | 1.3472e-05 | 8.3921e-06 | 0.044499 | 0.044499 | 0.044499 | 0.98386 | -0.31006 | 0.98337 | -0.31966 | 12.2251
107 | -0.12121 | -0.030818 | 0.12132 | 0.030886 | 0.00010637 | 6.7964e-05 | 0.18099 | 0.18099 | 0.18099 | 0.99741 | -0.049156 | 0.99837 | -0.030955 | 49.7218
108 | 0.0051009 | 0.0012778 | -0.0051004 | -0.0012778 | 5.5713e-07 | 2.5943e-08 | 0.0076337 | 0.0076338 | 0.0076338 | 0.99428 | -0.10904 | 0.99417 | -0.11133 | 2.0972
109 | 0.0028807 | 0.00072148 | -0.0028806 | -0.00072156 | 6.1642e-08 | -7.5206e-08 | 0.0043115 | 0.0043116 | 0.0043116 | 0.99417 | -0.11133 | 0.99414 | -0.11178 | 1.1845
110 | -0.12396 | -0.031549 | 0.12415 | 0.031668 | 0.00018529 | 0.0001184 | 0.18493 | 0.18493 | 0.18493 | 0.99837 | -0.030955 | 1 | 0 | 50.8054
111 | 0.031836 | 0.0079896 | -0.03183 | -0.0079854 | 6.6226e-06 | 4.1402e-06 | 0.047958 | 0.047958 | 0.047958 | 0.98787 | -0.23256 | 0.98765 | -0.23693 | 13.1754
112 | 0.15306 | 0.039108 | -0.15295 | -0.039038 | 0.00010919 | 6.9589e-05 | 0.22801 | 0.22801 | 0.22801 | 1 | 0 | 0.99922 | -0.014764 | 31.3206
113 | 0.15097 | 0.038542 | -0.15091 | -0.038502 | 6.3124e-05 | 4.0225e-05 | 0.22507 | 0.22507 | 0.22507 | 0.99922 | -0.014764 | 0.99876 | -0.023421 | 30.9161
114 | 0.14893 | 0.038007 | -0.14885 | -0.037959 | 7.5066e-05 | 4.783e-05 | 0.22213 | 0.22213 | 0.22213 | 0.99876 | -0.023421 | 0.99821 | -0.03386 | 30.5118
115 | -0.013382 | -0.0033541 | 0.013383 | 0.0033548 | 1.3246e-06 | 7.3852e-07 | 0.020253 | 0.020253 | 0.020253 | 0.98318 | -0.32403 | 0.98328 | -0.32196 | 5.5641
116 | -0.0099967 | -0.0025054 | 0.0099978 | 0.0025059 | 1.1017e-06 | 5.3993e-07 | 0.015075 | 0.015075 | 0.015075 | 0.98672 | -0.25505 | 0.98684 | -0.25273 | 4.1416
117 | -0.017884 | -0.0044825 | 0.017885 | 0.0044829 | 6.4353e-07 | 3.8171e-07 | 0.026967 | 0.026967 | 0.026967 | 0.98684 | -0.25273 | 0.98688 | -0.25198 | 7.4086
118 | -0.02822 | -0.0070732 | 0.028236 | 0.0070828 | 1.5445e-05 | 9.5937e-06 | 0.042551 | 0.042551 | 0.042551 | 0.98688 | -0.25198 | 0.98747 | -0.2405 | 11.6899
119 | -0.030028 | -0.007532 | 0.030034 | 0.0075352 | 5.1116e-06 | 3.1863e-06 | 0.045252 | 0.045252 | 0.045252 | 0.98747 | -0.2405 | 0.98765 | -0.23693 | 12.4319

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2813 | 0.071388

## res_load
| p_mw | q_mvar
0 | 0.0029589 | 0.00074158
1 | 0.0011026 | 0.00027634
2 | 0.0019893 | 0.00049856
3 | 0.0019578 | 0.00049067
4 | 0.0015231 | 0.00038173
5 | 0.0012646 | 0.00031693
6 | 0.0030929 | 0.00077516
7 | 0.00137 | 0.00034336
8 | 0.002219 | 0.00055613
9 | 0.0029808 | 0.00074705
10 | 0.0018863 | 0.00047276
11 | 0.001775 | 0.00044486
12 | 0.0032275 | 0.00080888
13 | 0.002298 | 0.00057593
14 | 0.0024735 | 0.00061991
15 | 0.0030412 | 0.0007622
16 | 0.0014667 | 0.0003676
17 | 0.0031004 | 0.00077704
18 | 0.0066553 | 0.001668
19 | 0.0022312 | 0.0005592
20 | 0.0038404 | 0.0009625
21 | 0.0014676 | 0.00036781
22 | 0.0017452 | 0.00043738
23 | 0.0019197 | 0.00048111
24 | 0.0024542 | 0.00061509
25 | 0.0020435 | 0.00051215
26 | 0.0026115 | 0.00065449
27 | 0.0023401 | 0.00058647
28 | 0.0024477 | 0.00061346
29 | 0.0038029 | 0.00095309
30 | 0.0019609 | 0.00049145
31 | 0.0039665 | 0.00099411
32 | 0.0074599 | 0.0018696
33 | 0.0019175 | 0.00048058
34 | 0.0023299 | 0.00058393
35 | 0.0041764 | 0.0010467
36 | 0.0011291 | 0.00028299
37 | 0.0020083 | 0.00050332
38 | 0.0018532 | 0.00046445
39 | 0.0017183 | 0.00043064
40 | 0.0021752 | 0.00054515
41 | 0.0014858 | 0.00037239
42 | 0.0023062 | 0.00057798
43 | 0.0023197 | 0.00058136
44 | 0.0047937 | 0.0012014
45 | 0.0030493 | 0.00076423
46 | 0.0042152 | 0.0010564
47 | 0.0014694 | 0.00036826
48 | 0.0039892 | 0.00099979
49 | 0.0015385 | 0.00038559
50 | 0.0024165 | 0.00060564
51 | 0.0015098 | 0.00037839
52 | 0.0023365 | 0.00058558
53 | 0.001941 | 0.00048646
54 | 0.0029965 | 0.00075099
55 | 0.0019603 | 0.0004913
56 | 0.0012718 | 0.00031873
57 | 0.0015675 | 0.00039286
58 | 0.0025687 | 0.00064379
59 | 0.0019141 | 0.00047972
60 | 0.0022116 | 0.00055428
61 | 0.0020938 | 0.00052475
62 | 0.0014398 | 0.00036086
63 | 0.0020412 | 0.00051158
64 | 0.0022585 | 0.00056603
65 | 0.002259 | 0.00056617
66 | 0.0020549 | 0.00051499
67 | 0.0076097 | 0.0019072
68 | 0.0096498 | 0.0024185
69 | 0.0026579 | 0.00066613
70 | 0.0039489 | 0.0009897
71 | 0.0013561 | 0.00033987
72 | 0.0015245 | 0.00038206
73 | 0.0037569 | 0.00094157
74 | 0.0019523 | 0.00048929
75 | 0.0011568 | 0.00028991
76 | 0.0015359 | 0.00038493
77 | 0.0011431 | 0.00028649
78 | 0.0017621 | 0.00044161
79 | 0.0014404 | 0.00036099
80 | 0.0026923 | 0.00067475
81 | 0.0013638 | 0.00034181
82 | 0.0022197 | 0.0005563
83 | 0.0021994 | 0.00055122
84 | 0.0026466 | 0.00066329
85 | 0.00347 | 0.00086967
86 | 0.0031398 | 0.0007869
87 | 0.0024441 | 0.00061254
88 | 0.0019774 | 0.00049559
89 | 0.0019758 | 0.00049518
90 | 0.0024542 | 0.00061509
91 | 0.0023803 | 0.00059655
92 | 0.010227 | 0.0025631
93 | 0.0099967 | 0.0025054
94 | 0.0078867 | 0.0019766
95 | 0.010335 | 0.0025903
96 | 0.0017925 | 0.00044923
97 | 0.0017963 | 0.00045019
98 | 0.0017561 | 0.00044012

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1