## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2580-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2580-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2580-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2580-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2580-2_0_4_node_122 | 0.4 | n |  | TRUE
5 | bus_LV_2580-2_0_4_node_113 | 0.4 | n |  | TRUE
6 | bus_LV_2580-2_0_4_node_118 | 0.4 | n |  | TRUE
7 | bus_LV_2580-2_0_4_node_69 | 0.4 | n |  | TRUE
8 | bus_LV_2580-2_0_4_node_117 | 0.4 | n |  | TRUE
9 | bus_LV_2580-2_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2580-2_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2580-2_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2580-2_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2580-2_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2580-2_0_4_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_2580-2_0_4_node_89 | 0.4 | n |  | TRUE
16 | bus_LV_2580-2_0_4_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_2580-2_0_4_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_2580-2_0_4_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_2580-2_0_4_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_2580-2_0_4_node_87 | 0.4 | n |  | TRUE
21 | bus_LV_2580-2_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2580-2_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2580-2_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2580-2_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2580-2_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2580-2_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2580-2_0_4_node_116 | 0.4 | n |  | TRUE
28 | bus_LV_2580-2_0_4_node_128 | 0.4 | n |  | TRUE
29 | bus_LV_2580-2_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2580-2_0_4_node_115 | 0.4 | n |  | TRUE
31 | bus_LV_2580-2_0_4_node_129 | 0.4 | n |  | TRUE
32 | bus_LV_2580-2_0_4_node_125 | 0.4 | n |  | TRUE
33 | bus_LV_2580-2_0_4_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_2580-2_0_4_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_2580-2_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2580-2_0_4_node_59 | 0.4 | n |  | TRUE
37 | bus_LV_2580-2_0_4_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_2580-2_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_2580-2_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_2580-2_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2580-2_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2580-2_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2580-2_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2580-2_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2580-2_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2580-2_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2580-2_0_4_node_110 | 0.4 | n |  | TRUE
48 | bus_LV_2580-2_0_4_node_108 | 0.4 | n |  | TRUE
49 | bus_LV_2580-2_0_4_node_104 | 0.4 | n |  | TRUE
50 | bus_LV_2580-2_0_4_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_2580-2_0_4_node_83 | 0.4 | n |  | TRUE
52 | bus_LV_2580-2_0_4_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_2580-2_0_4_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_2580-2_0_4_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_2580-2_0_4_node_94 | 0.4 | n |  | TRUE
56 | bus_LV_2580-2_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2580-2_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_2580-2_0_4_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_2580-2_0_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2580-2_0_4_node_31 | 0.4 | n |  | TRUE
61 | bus_LV_2580-2_0_4_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_2580-2_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2580-2_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_2580-2_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_2580-2_0_4_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_2580-2_0_4_node_98 | 0.4 | n |  | TRUE
67 | bus_LV_2580-2_0_4_node_97 | 0.4 | n |  | TRUE
68 | bus_LV_2580-2_0_4_node_127 | 0.4 | n |  | TRUE
69 | bus_LV_2580-2_0_4_node_126 | 0.4 | n |  | TRUE
70 | bus_LV_2580-2_0_4_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_2580-2_0_4_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2580-2_0_4_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2580-2_0_4_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2580-2_0_4_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_2580-2_0_4_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_2580-2_0_4_node_44 | 0.4 | n |  | TRUE
77 | bus_LV_2580-2_0_4_node_112 | 0.4 | n |  | TRUE
78 | bus_LV_2580-2_0_4_node_96 | 0.4 | n |  | TRUE
79 | bus_LV_2580-2_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_2580-2_0_4_node_95 | 0.4 | n |  | TRUE
81 | bus_LV_2580-2_0_4_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_2580-2_0_4_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_2580-2_0_4_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_2580-2_0_4_node_50 | 0.4 | n |  | TRUE
85 | bus_LV_2580-2_0_4_node_51 | 0.4 | n |  | TRUE
86 | bus_LV_2580-2_0_4_node_52 | 0.4 | n |  | TRUE
87 | bus_LV_2580-2_0_4_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_2580-2_0_4_node_92 | 0.4 | n |  | TRUE
89 | bus_LV_2580-2_0_4_node_119 | 0.4 | n |  | TRUE
90 | bus_LV_2580-2_0_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_2580-2_0_4_node_120 | 0.4 | n |  | TRUE
92 | bus_LV_2580-2_0_4_node_55 | 0.4 | n |  | TRUE
93 | bus_LV_2580-2_0_4_node_57 | 0.4 | n |  | TRUE
94 | bus_LV_2580-2_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_2580-2_0_4_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_2580-2_0_4_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2580-2_0_4_node_61 | 0.4 | n |  | TRUE
98 | bus_LV_2580-2_0_4_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2580-2_0_4_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_2580-2_0_4_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_2580-2_0_4_node_64 | 0.4 | n |  | TRUE
102 | bus_LV_2580-2_0_4_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_2580-2_0_4_node_109 | 0.4 | n |  | TRUE
104 | bus_LV_2580-2_0_4_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_2580-2_0_4_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_2580-2_0_4_node_66 | 0.4 | n |  | TRUE
107 | bus_LV_2580-2_0_4_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_2580-2_0_4_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_2580-2_0_4_node_71 | 0.4 | n |  | TRUE
110 | bus_LV_2580-2_0_4_node_72 | 0.4 | n |  | TRUE
111 | bus_LV_2580-2_0_4_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_2580-2_0_4_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_2580-2_0_4_node_99 | 0.4 | n |  | TRUE
114 | bus_LV_2580-2_0_4_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_2580-2_0_4_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_2580-2_0_4_node_76 | 0.4 | n |  | TRUE
117 | bus_LV_2580-2_0_4_node_77 | 0.4 | n |  | TRUE
118 | bus_LV_2580-2_0_4_node_78 | 0.4 | n |  | TRUE
119 | bus_LV_2580-2_0_4_node_91 | 0.4 | n |  | TRUE
120 | bus_LV_2580-2_0_4_node_79 | 0.4 | n |  | TRUE
121 | bus_LV_2580-2_0_4_node_82 | 0.4 | n |  | TRUE
122 | bus_LV_2580-2_0_4_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_2580-2_0_4_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_2580-2_0_4_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_2580-2_0_4_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_2580-2_0_4_node_105 | 0.4 | n |  | TRUE
127 | bus_LV_2580-2_0_4_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_2580-2_0_4_node_130 | 0.4 | n |  | TRUE
129 | bus_MV_480_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2580-2_0_4_load_0 | 0 | 0.0021426 | 0.00053698 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2580-2_0_4_load_1 | 1 | 0.002079 | 0.00052104 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2580-2_0_4_load_2 | 2 | 0.0023024 | 0.00057704 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2580-2_0_4_load_122 | 4 | 0.0022665 | 0.00056804 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2580-2_0_4_load_113 | 5 | 0.0016694 | 0.00041839 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2580-2_0_4_load_69 | 7 | 0.00071587 | 0.00017941 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2580-2_0_4_load_117 | 8 | 0.0016005 | 0.00040112 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2580-2_0_4_load_4 | 9 | 0.00060069 | 0.00015055 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2580-2_0_4_load_5 | 10 | 0.0015084 | 0.00037805 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2580-2_0_4_load_6 | 11 | 0.00060285 | 0.00015109 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2580-2_0_4_load_7 | 12 | 0.0019168 | 0.0004804 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2580-2_0_4_load_124 | 14 | 0.0025309 | 0.00063431 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2580-2_0_4_load_89 | 15 | 0.0006058 | 0.00015183 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2580-2_0_4_load_86 | 16 | 0.0040145 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2580-2_0_4_load_58 | 18 | 0.00061335 | 0.00015372 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2580-2_0_4_load_54 | 19 | 0.00075611 | 0.0001895 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2580-2_0_4_load_9 | 21 | 0.0038764 | 0.00097151 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2580-2_0_4_load_10 | 22 | 0.0038978 | 0.00097689 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2580-2_0_4_load_12 | 23 | 0.012544 | 0.0031439 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2580-2_0_4_load_11 | 24 | 0.012322 | 0.0030882 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2580-2_0_4_load_18 | 26 | 0.003484 | 0.00087317 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2580-2_0_4_load_16 | 29 | 0.0024016 | 0.0006019 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2580-2_0_4_load_115 | 30 | 0.0013532 | 0.00033914 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2580-2_0_4_load_125 | 32 | 0.01232 | 0.0030876 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2580-2_0_4_load_14 | 33 | 0.0019354 | 0.00048505 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2580-2_0_4_load_15 | 34 | 0.0019011 | 0.00047646 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2580-2_0_4_load_17 | 35 | 0.0019243 | 0.00048228 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2580-2_0_4_load_59 | 36 | 0.0018151 | 0.00045492 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2580-2_0_4_load_60 | 37 | 0.0019622 | 0.00049177 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2580-2_0_4_load_19 | 38 | 0.0024564 | 0.00061563 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2580-2_0_4_load_20 | 39 | 0.0025318 | 0.00063452 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2580-2_0_4_load_23 | 42 | 0.0017209 | 0.00043129 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2580-2_0_4_load_24 | 43 | 0.0036298 | 0.00090972 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2580-2_0_4_load_25 | 44 | 0.0019831 | 0.00049701 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2580-2_0_4_load_27 | 46 | 0.0021695 | 0.00054374 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2580-2_0_4_load_110 | 47 | 0.0017176 | 0.00043048 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2580-2_0_4_load_108 | 48 | 0.0022142 | 0.00055494 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2580-2_0_4_load_35 | 50 | 0.0036767 | 0.00092146 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2580-2_0_4_load_83 | 51 | 0.0025588 | 0.0006413 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2580-2_0_4_load_26 | 52 | 0.0036131 | 0.00090554 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2580-2_0_4_load_111 | 53 | 0.0041068 | 0.0010293 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2580-2_0_4_load_106 | 54 | 0.003547 | 0.00088897 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2580-2_0_4_load_28 | 56 | 0.0015935 | 0.00039937 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2580-2_0_4_load_29 | 57 | 0.0015762 | 0.00039504 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2580-2_0_4_load_33 | 58 | 0.0045453 | 0.0011392 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2580-2_0_4_load_84 | 59 | 0.002247 | 0.00056315 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2580-2_0_4_load_31 | 60 | 0.0030905 | 0.00077455 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2580-2_0_4_load_32 | 61 | 0.0026852 | 0.00067298 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2580-2_0_4_load_34 | 62 | 0.007998 | 0.0020045 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2580-2_0_4_load_45 | 63 | 0.0016012 | 0.0004013 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2580-2_0_4_load_46 | 64 | 0.002091 | 0.00052405 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2580-2_0_4_load_36 | 65 | 0.0028774 | 0.00072116 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2580-2_0_4_load_98 | 66 | 0.0024 | 0.00060151 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2580-2_0_4_load_97 | 67 | 0.0014008 | 0.00035107 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2580-2_0_4_load_127 | 68 | 0.0014363 | 0.00035996 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2580-2_0_4_load_126 | 69 | 0.0015142 | 0.0003795 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2580-2_0_4_load_38 | 70 | 0.0023957 | 0.00060042 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2580-2_0_4_load_39 | 71 | 0.0015775 | 0.00039535 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2580-2_0_4_load_42 | 74 | 0.0011128 | 0.00027888 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2580-2_0_4_load_43 | 75 | 0.0015599 | 0.00039096 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2580-2_0_4_load_44 | 76 | 0.0015107 | 0.00037862 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2580-2_0_4_load_112 | 77 | 0.0027237 | 0.00068262 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2580-2_0_4_load_96 | 78 | 0.0014089 | 0.0003531 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2580-2_0_4_load_95 | 80 | 0.0022171 | 0.00055566 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2580-2_0_4_load_47 | 81 | 0.0076043 | 0.0019058 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2580-2_0_4_load_48 | 82 | 0.0097634 | 0.0024469 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2580-2_0_4_load_49 | 83 | 0.001747 | 0.00043785 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2580-2_0_4_load_51 | 85 | 0.001762 | 0.00044161 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2580-2_0_4_load_52 | 86 | 0.013283 | 0.003329 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2580-2_0_4_load_53 | 87 | 0.0080904 | 0.0020276 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2580-2_0_4_load_92 | 88 | 0.0017616 | 0.0004415 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2580-2_0_4_load_119 | 89 | 0.013514 | 0.003387 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2580-2_0_4_load_90 | 90 | 0.0019574 | 0.00049057 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2580-2_0_4_load_120 | 91 | 0.0015998 | 0.00040095 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2580-2_0_4_load_55 | 92 | 0.0025509 | 0.00063932 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2580-2_0_4_load_73 | 95 | 0.0012452 | 0.00031208 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2580-2_0_4_load_74 | 96 | 0.0014065 | 0.00035251 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2580-2_0_4_load_61 | 97 | 0.0017601 | 0.00044112 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2580-2_0_4_load_88 | 98 | 0.0017708 | 0.0004438 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2580-2_0_4_load_62 | 99 | 0.0015758 | 0.00039492 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2580-2_0_4_load_63 | 100 | 0.0034807 | 0.00087235 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2580-2_0_4_load_64 | 101 | 0.0047541 | 0.0011915 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2580-2_0_4_load_65 | 102 | 0.0017206 | 0.00043122 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2580-2_0_4_load_114 | 104 | 0.0016482 | 0.00041309 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2580-2_0_4_load_107 | 105 | 0.0040074 | 0.0010043 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2580-2_0_4_load_66 | 106 | 0.0018404 | 0.00046124 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2580-2_0_4_load_67 | 107 | 0.0010592 | 0.00026545 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2580-2_0_4_load_71 | 109 | 0.001389 | 0.00034811 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2580-2_0_4_load_72 | 110 | 0.0027273 | 0.00068353 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2580-2_0_4_load_100 | 111 | 0.0025674 | 0.00064344 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2580-2_0_4_load_80 | 112 | 0.0011801 | 0.00029576 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2580-2_0_4_load_99 | 113 | 0.0022601 | 0.00056644 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2580-2_0_4_load_75 | 115 | 0.0017722 | 0.00044416 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2580-2_0_4_load_76 | 116 | 0.0023388 | 0.00058617 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2580-2_0_4_load_77 | 117 | 0.0023862 | 0.00059803 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2580-2_0_4_load_78 | 118 | 0.0018106 | 0.00045379 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2580-2_0_4_load_91 | 119 | 0.0018731 | 0.00046944 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2580-2_0_4_load_79 | 120 | 0.013516 | 0.0033875 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2580-2_0_4_load_82 | 121 | 0.002863 | 0.00071753 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2580-2_0_4_load_121 | 122 | 0.001957 | 0.00049047 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2580-2_0_4_load_102 | 123 | 0.0015265 | 0.00038259 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2580-2_0_4_load_103 | 124 | 0.0015118 | 0.00037888 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2580-2_0_4_load_101 | 125 | 0.0026109 | 0.00065434 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2580-2_0_4_load_105 | 126 | 0.0021441 | 0.00053737 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2580-2_0_4_load_123 | 127 | 0.0034632 | 0.00086795 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2580-2_0_4_load_130 | 128 | 0.013632 | 0.0034165 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2580-2_0_4_line_0 |  | 0 | 1 | 0.019052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2580-2_0_4_line_1 |  | 0 | 2 | 0.0048001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2580-2_0_4_line_2 |  | 1 | 3 | 0.014849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2580-2_0_4_line_3 |  | 3 | 4 | 0.014231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2580-2_0_4_line_4 |  | 4 | 5 | 0.024586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2580-2_0_4_line_5 |  | 5 | 57 | 0.012582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2580-2_0_4_line_6 |  | 6 | 7 | 0.0061719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2580-2_0_4_line_7 |  | 6 | 8 | 0.019456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2580-2_0_4_line_8 |  | 7 | 107 | 0.010489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2580-2_0_4_line_9 |  | 8 | 27 | 0.017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2580-2_0_4_line_10 |  | 9 | 10 | 0.047555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2580-2_0_4_line_11 |  | 9 | 11 | 0.00014252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2580-2_0_4_line_12 |  | 10 | 12 | 0.0068105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2580-2_0_4_line_13 |  | 11 | 13 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2580-2_0_4_line_14 |  | 12 | 14 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2580-2_0_4_line_15 |  | 13 | 15 | 0.036078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2580-2_0_4_line_16 |  | 14 | 16 | 0.023368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2580-2_0_4_line_17 |  | 15 | 20 | 0.034254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2580-2_0_4_line_18 |  | 16 | 45 | 0.032689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2580-2_0_4_line_19 |  | 17 | 18 | 0.0048715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2580-2_0_4_line_20 |  | 17 | 19 | 0.018679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2580-2_0_4_line_21 |  | 18 | 95 | 0.019493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2580-2_0_4_line_22 |  | 19 | 92 | 0.021606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2580-2_0_4_line_23 |  | 20 | 98 | 0.011019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2580-2_0_4_line_24 |  | 20 | 97 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2580-2_0_4_line_25 |  | 21 | 22 | 0.025976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2580-2_0_4_line_26 |  | 22 | 23 | 0.0014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2580-2_0_4_line_27 |  | 23 | 26 | 0.021886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2580-2_0_4_line_28 |  | 24 | 25 | 0.018601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2580-2_0_4_line_29 |  | 25 | 27 | 0.033017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2580-2_0_4_line_30 |  | 25 | 28 | 0.042217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2580-2_0_4_line_31 |  | 26 | 29 | 0.024717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2580-2_0_4_line_32 |  | 27 | 30 | 0.00076784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2580-2_0_4_line_33 |  | 28 | 31 | 0.053295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2580-2_0_4_line_34 |  | 28 | 32 | 0.049729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2580-2_0_4_line_35 |  | 29 | 33 | 0.022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2580-2_0_4_line_36 |  | 30 | 81 | 0.019313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2580-2_0_4_line_37 |  | 31 | 128 | 0.030806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2580-2_0_4_line_38 |  | 32 | 120 | 0.041803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2580-2_0_4_line_39 |  | 33 | 34 | 0.0024882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2580-2_0_4_line_40 |  | 34 | 35 | 0.027834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2580-2_0_4_line_41 |  | 35 | 36 | 0.0011911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2580-2_0_4_line_42 |  | 36 | 37 | 0.0093817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2580-2_0_4_line_43 |  | 37 | 97 | 0.0052963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2580-2_0_4_line_44 |  | 38 | 39 | 0.00061247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2580-2_0_4_line_45 |  | 38 | 40 | 0.018882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2580-2_0_4_line_46 |  | 39 | 41 | 0.0093474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2580-2_0_4_line_47 |  | 40 | 42 | 0.011838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2580-2_0_4_line_48 |  | 40 | 43 | 0.028744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2580-2_0_4_line_49 |  | 40 | 44 | 0.01998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2580-2_0_4_line_50 |  | 41 | 45 | 0.045827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2580-2_0_4_line_51 |  | 41 | 46 | 0.014067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2580-2_0_4_line_52 |  | 42 | 47 | 0.01947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2580-2_0_4_line_53 |  | 43 | 48 | 0.01045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2580-2_0_4_line_54 |  | 44 | 49 | 0.044188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2580-2_0_4_line_55 |  | 45 | 50 | 0.011608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2580-2_0_4_line_56 |  | 45 | 51 | 0.037247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2580-2_0_4_line_57 |  | 46 | 52 | 0.019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2580-2_0_4_line_58 |  | 47 | 53 | 0.010425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2580-2_0_4_line_59 |  | 48 | 54 | 0.010648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2580-2_0_4_line_60 |  | 49 | 55 | 0.047857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2580-2_0_4_line_61 |  | 50 | 58 | 0.019822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2580-2_0_4_line_62 |  | 51 | 59 | 0.01947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2580-2_0_4_line_63 |  | 52 | 56 | 0.02005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2580-2_0_4_line_64 |  | 54 | 126 | 0.0096604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2580-2_0_4_line_65 |  | 55 | 123 | 0.043959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2580-2_0_4_line_66 |  | 56 | 57 | 0.0087347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2580-2_0_4_line_67 |  | 58 | 60 | 0.00036282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_2580-2_0_4_line_68 |  | 59 | 94 | 0.01608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2580-2_0_4_line_69 |  | 60 | 61 | 0.017279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_2580-2_0_4_line_70 |  | 61 | 62 | 0.018909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_2580-2_0_4_line_71 |  | 62 | 63 | 0.0019007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_2580-2_0_4_line_72 |  | 63 | 64 | 0.017514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2580-2_0_4_line_73 |  | 64 | 81 | 0.0038943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2580-2_0_4_line_74 |  | 65 | 66 | 0.058745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2580-2_0_4_line_75 |  | 66 | 67 | 0.010261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2580-2_0_4_line_76 |  | 67 | 80 | 0.0019289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2580-2_0_4_line_77 |  | 68 | 69 | 0.006281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2580-2_0_4_line_78 |  | 69 | 76 | 0.0080608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2580-2_0_4_line_79 |  | 70 | 71 | 0.024233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2580-2_0_4_line_80 |  | 70 | 72 | 0.007973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2580-2_0_4_line_81 |  | 71 | 73 | 0.026405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2580-2_0_4_line_82 |  | 72 | 74 | 0.015877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2580-2_0_4_line_83 |  | 72 | 75 | 0.015078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2580-2_0_4_line_84 |  | 73 | 76 | 0.041648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2580-2_0_4_line_85 |  | 74 | 77 | 0.023683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2580-2_0_4_line_86 |  | 75 | 78 | 0.027817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2580-2_0_4_line_87 |  | 77 | 79 | 0.031738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2580-2_0_4_line_88 |  | 78 | 80 | 0.023324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2580-2_0_4_line_89 |  | 79 | 111 | 0.022756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2580-2_0_4_line_90 |  | 79 | 108 | 0.006711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2580-2_0_4_line_91 |  | 82 | 83 | 0.023457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2580-2_0_4_line_92 |  | 82 | 84 | 0.024445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2580-2_0_4_line_93 |  | 83 | 85 | 0.0025402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2580-2_0_4_line_94 |  | 84 | 86 | 0.025351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2580-2_0_4_line_95 |  | 84 | 87 | 0.048141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2580-2_0_4_line_96 |  | 85 | 88 | 0.0017099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2580-2_0_4_line_97 |  | 87 | 89 | 0.040478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2580-2_0_4_line_98 |  | 88 | 90 | 0.0022093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2580-2_0_4_line_99 |  | 89 | 91 | 0.011587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2580-2_0_4_line_100 |  | 90 | 119 | 0.014734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2580-2_0_4_line_101 |  | 91 | 128 | 0.020707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2580-2_0_4_line_102 |  | 92 | 93 | 0.017401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2580-2_0_4_line_103 |  | 93 | 94 | 0.007106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2580-2_0_4_line_104 |  | 95 | 96 | 0.024469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2580-2_0_4_line_105 |  | 98 | 122 | 0.0016864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2580-2_0_4_line_106 |  | 99 | 100 | 0.0063992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2580-2_0_4_line_107 |  | 99 | 101 | 0.010588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2580-2_0_4_line_108 |  | 100 | 102 | 0.0072888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2580-2_0_4_line_109 |  | 102 | 103 | 0.016855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2580-2_0_4_line_110 |  | 103 | 104 | 0.04577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2580-2_0_4_line_111 |  | 103 | 105 | 0.043168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2580-2_0_4_line_112 |  | 104 | 127 | 0.022643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2580-2_0_4_line_113 |  | 105 | 126 | 0.010853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2580-2_0_4_line_114 |  | 106 | 107 | 0.001432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2580-2_0_4_line_115 |  | 106 | 108 | 0.024251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2580-2_0_4_line_116 |  | 108 | 109 | 0.01791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2580-2_0_4_line_117 |  | 108 | 110 | 0.071385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2580-2_0_4_line_118 |  | 109 | 112 | 0.006255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2580-2_0_4_line_119 |  | 111 | 113 | 0.028411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2580-2_0_4_line_120 |  | 112 | 114 | 0.014183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2580-2_0_4_line_121 |  | 113 | 125 | 0.016012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2580-2_0_4_line_122 |  | 114 | 121 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2580-2_0_4_line_123 |  | 115 | 116 | 0.0057246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2580-2_0_4_line_124 |  | 115 | 117 | 0.0058366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2580-2_0_4_line_125 |  | 116 | 118 | 0.0087653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2580-2_0_4_line_126 |  | 118 | 119 | 0.0048339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2580-2_0_4_line_127 |  | 123 | 124 | 0.015969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2580-2_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 129 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2630861.998 | 1241226.552 | 2630864.0676 | 1241245.491
1 | 2630861.4765 | 1241221.7803 | 2630861.998 | 1241226.552
2 | 2630861.2741 | 1241259.3031 | 2630864.9047 | 1241253.1513 | 2630864.0676 | 1241245.491
3 | 2630861.2741 | 1241259.3031 | 2630858.6926 | 1241254.1531 | 2630854.4071 | 1241249.5612 | 2630852.8728 | 1241248.0001
4 | 2630836.0045 | 1241230.1203 | 2630844.0063 | 1241238.9783 | 2630852.8728 | 1241248.0001
5 | 2630836.0045 | 1241230.1203 | 2630827.5701 | 1241220.7834
6 | 2630861.4941 | 1241312.9939 | 2630865.7356 | 1241317.4775
7 | 2630861.4941 | 1241312.9939 | 2630848.6534 | 1241303.5101 | 2630845.8868 | 1241301.3783
8 | 2630873.1293 | 1241324.9153 | 2630868.1107 | 1241319.9883 | 2630865.7356 | 1241317.4775
9 | 2630831.6431 | 1241290.4024 | 2630845.8868 | 1241301.3783
10 | 2630649.6609 | 1241167.2097 | 2630671.4974 | 1241181.9051 | 2630688.7995 | 1241192.8013 | 2630689.4731 | 1241193.2075
11 | 2630649.6609 | 1241167.2097 | 2630649.5426 | 1241167.1302
12 | 2630689.4731 | 1241193.2075 | 2630695.3053 | 1241196.7244
13 | 2630632.2898 | 1241155.5195 | 2630649.5426 | 1241167.1302
14 | 2630695.3053 | 1241196.7244 | 2630703.3982 | 1241201.6045 | 2630707.2036 | 1241204.285
15 | 2630632.2898 | 1241155.5195 | 2630630.8412 | 1241159.3478 | 2630613.3393 | 1241186.1188
16 | 2630726.6114 | 1241217.2859 | 2630717.5976 | 1241211.6064 | 2630707.2036 | 1241204.285
17 | 2630594.6591 | 1241214.8301 | 2630595.2309 | 1241213.9102 | 2630598.4014 | 1241208.9679 | 2630613.3393 | 1241186.1188
18 | 2630756.1352 | 1241209.5488 | 2630749.6028 | 1241213.9956 | 2630745.9998 | 1241216.3007 | 2630739.8021 | 1241218.9036 | 2630735.3974 | 1241219.8036 | 2630732.0039 | 1241219.5971 | 2630727.8989 | 1241218.0971 | 2630726.6114 | 1241217.2859
19 | 2630666.4115 | 1241105.3302 | 2630664.0251 | 1241101.8713 | 2630663.655 | 1241101.3138
20 | 2630666.4115 | 1241105.3302 | 2630676.7082 | 1241118.6029 | 2630677.9117 | 1241120.0474
21 | 2630663.655 | 1241101.3138 | 2630652.8729 | 1241085.0736
22 | 2630677.9117 | 1241120.0474 | 2630685.5745 | 1241129.2443 | 2630692.077 | 1241136.3547
23 | 2630594.6591 | 1241214.8301 | 2630589.2344 | 1241224.4209
24 | 2630594.6591 | 1241214.8301 | 2630609.8419 | 1241216.0801
25 | 2630739.4312 | 1241268.0195 | 2630728.321 | 1241260.7264 | 2630718.2428 | 1241253.0212
26 | 2630718.2428 | 1241253.0212 | 2630717.1223 | 1241252.1645
27 | 2630699.425 | 1241239.3397 | 2630703.0941 | 1241241.4394 | 2630717.1223 | 1241252.1645
28 | 2630814.7734 | 1241318.6774 | 2630810.5141 | 1241313.4297 | 2630800.4943 | 1241307.1174
29 | 2630831.6431 | 1241290.4024 | 2630819.3087 | 1241313.0084 | 2630816.0467 | 1241316.616 | 2630814.7734 | 1241318.6774
30 | 2630790.0498 | 1241352.6264 | 2630799.6169 | 1241343.1811 | 2630814.7734 | 1241318.6774
31 | 2630699.425 | 1241239.3397 | 2630686.978 | 1241232.217 | 2630677.3748 | 1241228.2873
32 | 2630831.0219 | 1241289.9511 | 2630831.6431 | 1241290.4024
33 | 2630790.0498 | 1241352.6264 | 2630777.1644 | 1241375.1184 | 2630774.2435 | 1241378.5722 | 2630770.1788 | 1241379.5184 | 2630765.5391 | 1241379.1053 | 2630753.7629 | 1241371.3616
34 | 2630790.0498 | 1241352.6264 | 2630790.2758 | 1241345.4897 | 2630787.4104 | 1241339.6934 | 2630774.8852 | 1241330.5672 | 2630772.5794 | 1241327.6534 | 2630768.9137 | 1241324.5547 | 2630758.894 | 1241317.7541
35 | 2630655.7827 | 1241220.5795 | 2630657.0004 | 1241220.7661 | 2630675.0355 | 1241227.33 | 2630677.3748 | 1241228.2873
36 | 2630831.0219 | 1241289.9511 | 2630815.3971 | 1241278.5996
37 | 2630753.7629 | 1241371.3616 | 2630728.0205 | 1241354.4399
38 | 2630723.9267 | 1241295.6758 | 2630733.62 | 1241304.704 | 2630739.9892 | 1241308.3948 | 2630747.8936 | 1241313.45 | 2630758.894 | 1241317.7541 | 2630758.894 | 1241317.7541
39 | 2630655.7827 | 1241220.5795 | 2630653.3232 | 1241220.2025
40 | 2630653.3232 | 1241220.2025 | 2630641.6124 | 1241218.4075 | 2630625.6672 | 1241217.2568
41 | 2630624.4792 | 1241217.171 | 2630625.6672 | 1241217.2568
42 | 2630624.4792 | 1241217.171 | 2630615.1218 | 1241216.4957
43 | 2630609.8419 | 1241216.0801 | 2630613.2419 | 1241216.3601 | 2630615.1218 | 1241216.4957
44 | 2630790.8765 | 1241166.736 | 2630791.1992 | 1241166.2154
45 | 2630801.1468 | 1241150.1663 | 2630791.1992 | 1241166.2154
46 | 2630785.952 | 1241174.681 | 2630790.8765 | 1241166.736
47 | 2630801.1468 | 1241150.1663 | 2630808.4383 | 1241159.4921
48 | 2630801.1468 | 1241150.1663 | 2630786.1303 | 1241125.6565
49 | 2630801.1468 | 1241150.1663 | 2630809.2604 | 1241139.6795 | 2630813.3058 | 1241134.312
50 | 2630756.1352 | 1241209.5488 | 2630761.8031 | 1241202.696 | 2630785.952 | 1241174.681
51 | 2630785.952 | 1241174.681 | 2630795.3771 | 1241185.1237
52 | 2630820.746 | 1241174.5769 | 2630811.8042 | 1241163.7969 | 2630808.4383 | 1241159.4921
53 | 2630786.1303 | 1241125.6565 | 2630780.6712 | 1241116.7462
54 | 2630839.9018 | 1241099.0237 | 2630813.3058 | 1241134.312
55 | 2630756.1352 | 1241209.5488 | 2630758.1028 | 1241212.1051 | 2630763.3573 | 1241218.6357
56 | 2630756.1352 | 1241209.5488 | 2630745.2002 | 1241195.5056 | 2630732.4891 | 1241180.7856
57 | 2630808.2794 | 1241199.4189 | 2630795.3771 | 1241185.1237
58 | 2630827.4018 | 1241182.6008 | 2630820.746 | 1241174.5769
59 | 2630780.6712 | 1241116.7462 | 2630775.1084 | 1241107.6666
60 | 2630839.9018 | 1241099.0237 | 2630846.5205 | 1241108.5641 | 2630855.2843 | 1241119.9501 | 2630861.2772 | 1241126.263 | 2630867.6813 | 1241130.5323 | 2630872.6584 | 1241132.9708
61 | 2630775.3552 | 1241234.4095 | 2630767.5978 | 1241223.9061 | 2630763.3573 | 1241218.6357
62 | 2630732.4891 | 1241180.7856 | 2630726.2016 | 1241173.5045 | 2630719.4959 | 1241166.2902
63 | 2630821.7149 | 1241214.3018 | 2630818.3958 | 1241210.6275 | 2630808.2794 | 1241199.4189
64 | 2630770.0616 | 1241099.4293 | 2630775.1084 | 1241107.6666
65 | 2630872.6584 | 1241132.9708 | 2630871.5797 | 1241138.3242 | 2630874.0887 | 1241147.254 | 2630876.0589 | 1241176.4101
66 | 2630821.7149 | 1241214.3018 | 2630827.5701 | 1241220.7834
67 | 2630775.3552 | 1241234.4095 | 2630775.5708 | 1241234.7013
68 | 2630708.5483 | 1241154.5123 | 2630719.4959 | 1241166.2902
69 | 2630775.5708 | 1241234.7013 | 2630785.0979 | 1241247.6007 | 2630785.8817 | 1241248.5648
70 | 2630798.1623 | 1241262.9254 | 2630794.2028 | 1241258.7994 | 2630785.8817 | 1241248.5648
71 | 2630799.4783 | 1241264.2968 | 2630798.1623 | 1241262.9254
72 | 2630799.4783 | 1241264.2968 | 2630801.3013 | 1241266.1964 | 2630812.4735 | 1241276.027
73 | 2630815.3971 | 1241278.5996 | 2630815.3971 | 1241278.5996 | 2630812.4735 | 1241276.027
74 | 2630990.8999 | 1241333.4023 | 2631045.8303 | 1241312.5781
75 | 2630990.8999 | 1241333.4023 | 2630983.6166 | 1241326.174
76 | 2630982.2475 | 1241324.8152 | 2630983.6166 | 1241326.174
77 | 2630999.9022 | 1241267.096 | 2630995.5169 | 1241262.5993
78 | 2630995.5169 | 1241262.5993 | 2630989.8889 | 1241256.8284
79 | 2630938.6343 | 1241271.8054 | 2630944.3729 | 1241261.2585 | 2630949.8456 | 1241250.3259
80 | 2630934.8238 | 1241278.8089 | 2630938.6343 | 1241271.8054
81 | 2630961.3373 | 1241226.5581 | 2630957.368 | 1241235.2985 | 2630949.8456 | 1241250.3259
82 | 2630934.8238 | 1241278.8089 | 2630927.6131 | 1241292.954
83 | 2630934.8238 | 1241278.8089 | 2630940.3991 | 1241282.4958 | 2630945.4031 | 1241287.0025 | 2630946.5446 | 1241288.2073
84 | 2630961.3373 | 1241226.5581 | 2630964.7989 | 1241231.1012 | 2630989.8889 | 1241256.8284
85 | 2630917.0559 | 1241314.154 | 2630925.7344 | 1241296.6396 | 2630927.6131 | 1241292.954
86 | 2630946.5446 | 1241288.2073 | 2630965.2 | 1241307.8966 | 2630965.6923 | 1241308.3852
87 | 2630900.3074 | 1241340.6687 | 2630906.4229 | 1241334.9746 | 2630910.2168 | 1241327.9566 | 2630917.0559 | 1241314.154
88 | 2630982.2475 | 1241324.8152 | 2630965.6923 | 1241308.3852
89 | 2630900.3074 | 1241340.6687 | 2630910.3005 | 1241351.105 | 2630916.7484 | 1241356.3421
90 | 2630893.6287 | 1241339.8334 | 2630900.3074 | 1241340.6687
91 | 2630627.9061 | 1241273.2165 | 2630630.6982 | 1241260.4002 | 2630632.0973 | 1241255.9045 | 2630633.6001 | 1241253.2995 | 2630635.5972 | 1241251.5976
92 | 2630622.2992 | 1241297.0024 | 2630624.4028 | 1241289.2972 | 2630627.9061 | 1241273.2165
93 | 2630635.5972 | 1241251.5976 | 2630635.5972 | 1241251.5976 | 2630637.9987 | 1241250.7696
94 | 2630622.2992 | 1241297.0024 | 2630612.1014 | 1241293.9035 | 2630597.7939 | 1241290.5624
95 | 2630622.2992 | 1241297.0024 | 2630642.098 | 1241303.0972 | 2630658.3008 | 1241311.5972 | 2630666.1082 | 1241316.3276
96 | 2630639.6945 | 1241250.6173 | 2630638.2025 | 1241250.6994 | 2630637.9987 | 1241250.7696
97 | 2630700.6267 | 1241337.4397 | 2630699.0032 | 1241336.701 | 2630678.6042 | 1241323.8987 | 2630666.1082 | 1241316.3276
98 | 2630641.9005 | 1241250.4961 | 2630641.9005 | 1241250.4961 | 2630639.6945 | 1241250.6173
99 | 2630700.6267 | 1241337.4397 | 2630705.6028 | 1241339.7037 | 2630710.7169 | 1241343.0654
100 | 2630641.9005 | 1241250.4961 | 2630651.4987 | 1241252.6024 | 2630656.1016 | 1241254.305
101 | 2630728.0205 | 1241354.4399 | 2630710.7169 | 1241343.0654
102 | 2630703.8203 | 1241149.1956 | 2630692.077 | 1241136.3547
103 | 2630703.8203 | 1241149.1956 | 2630708.5483 | 1241154.5123
104 | 2630639.128 | 1241064.8336 | 2630643.5969 | 1241071.102 | 2630652.8729 | 1241085.0736
105 | 2630589.2344 | 1241224.4209 | 2630588.4041 | 1241225.8888
106 | 2630721.4157 | 1241077.8756 | 2630725.5831 | 1241073.0195
107 | 2630714.5202 | 1241085.9107 | 2630721.4157 | 1241077.8756
108 | 2630730.3299 | 1241067.4883 | 2630725.5831 | 1241073.0195
109 | 2630740.6318 | 1241054.1588 | 2630733.4141 | 1241063.8944 | 2630730.3299 | 1241067.4883
110 | 2630740.6318 | 1241054.1588 | 2630722.1035 | 1241030.3035 | 2630712.2462 | 1241018.2586
111 | 2630740.6318 | 1241054.1588 | 2630753.8933 | 1241073.0394 | 2630764.3917 | 1241090.1749
112 | 2630696.8016 | 1241001.7102 | 2630710.3982 | 1241016.0006 | 2630712.2462 | 1241018.2586
113 | 2630770.0616 | 1241099.4293 | 2630764.3917 | 1241090.1749
114 | 2630873.1293 | 1241324.9153 | 2630874.1512 | 1241325.9185
115 | 2630893.6287 | 1241339.8334 | 2630884.6007 | 1241335.7061 | 2630880.6344 | 1241332.2833 | 2630874.1512 | 1241325.9185
116 | 2630893.6287 | 1241339.8334 | 2630888.9845 | 1241357.1311
117 | 2630893.6287 | 1241339.8334 | 2630897.7987 | 1241323 | 2630899.8128 | 1241310.7693 | 2630900.7553 | 1241296.7097 | 2630899.9096 | 1241284.8867 | 2630897.6848 | 1241269.3419
118 | 2630887.2618 | 1241363.1432 | 2630888.1319 | 1241360.3068 | 2630888.9845 | 1241357.1311
119 | 2630938.7812 | 1241374.2793 | 2630923.5125 | 1241361.8361 | 2630916.7484 | 1241356.3421
120 | 2630883.1024 | 1241376.7022 | 2630887.2618 | 1241363.1432
121 | 2630951.1933 | 1241384.3945 | 2630938.7812 | 1241374.2793
122 | 2630883.1024 | 1241376.7022 | 2630890.7996 | 1241382.3013 | 2630900.5689 | 1241389.7001
123 | 2630672.5448 | 1241264.4391 | 2630667.7276 | 1241261.3463
124 | 2630672.5448 | 1241264.4391 | 2630677.4563 | 1241267.5923
125 | 2630667.7276 | 1241261.3463 | 2630660.7982 | 1241256.8976 | 2630660.3335 | 1241256.6411
126 | 2630656.1016 | 1241254.305 | 2630656.1016 | 1241254.305 | 2630660.3335 | 1241256.6411
127 | 2630877.1356 | 1241192.3429 | 2630876.0589 | 1241176.4101

## bus_geodata
| x | y | coords
0 | 2630861.998 | 1241226.552
1 | 2630864.0676 | 1241245.491
2 | 2630861.4765 | 1241221.7803
3 | 2630861.2741 | 1241259.3031
4 | 2630852.8728 | 1241248.0001
5 | 2630836.0045 | 1241230.1203
6 | 2630861.4941 | 1241312.9939
7 | 2630865.7356 | 1241317.4775
8 | 2630845.8868 | 1241301.3783
9 | 2630649.6609 | 1241167.2097
10 | 2630689.4731 | 1241193.2075
11 | 2630649.5426 | 1241167.1302
12 | 2630695.3053 | 1241196.7244
13 | 2630632.2898 | 1241155.5195
14 | 2630707.2036 | 1241204.285
15 | 2630613.3393 | 1241186.1188
16 | 2630726.6114 | 1241217.2859
17 | 2630666.4115 | 1241105.3302
18 | 2630663.655 | 1241101.3138
19 | 2630677.9117 | 1241120.0474
20 | 2630594.6591 | 1241214.8301
21 | 2630739.4312 | 1241268.0195
22 | 2630718.2428 | 1241253.0212
23 | 2630717.1223 | 1241252.1645
24 | 2630800.4943 | 1241307.1174
25 | 2630814.7734 | 1241318.6774
26 | 2630699.425 | 1241239.3397
27 | 2630831.6431 | 1241290.4024
28 | 2630790.0498 | 1241352.6264
29 | 2630677.3748 | 1241228.2873
30 | 2630831.0219 | 1241289.9511
31 | 2630753.7629 | 1241371.3616
32 | 2630758.894 | 1241317.7541
33 | 2630655.7827 | 1241220.5795
34 | 2630653.3232 | 1241220.2025
35 | 2630625.6672 | 1241217.2568
36 | 2630624.4792 | 1241217.171
37 | 2630615.1218 | 1241216.4957
38 | 2630791.1992 | 1241166.2154
39 | 2630790.8765 | 1241166.736
40 | 2630801.1468 | 1241150.1663
41 | 2630785.952 | 1241174.681
42 | 2630808.4383 | 1241159.4921
43 | 2630786.1303 | 1241125.6565
44 | 2630813.3058 | 1241134.312
45 | 2630756.1352 | 1241209.5488
46 | 2630795.3771 | 1241185.1237
47 | 2630820.746 | 1241174.5769
48 | 2630780.6712 | 1241116.7462
49 | 2630839.9018 | 1241099.0237
50 | 2630763.3573 | 1241218.6357
51 | 2630732.4891 | 1241180.7856
52 | 2630808.2794 | 1241199.4189
53 | 2630827.4018 | 1241182.6008
54 | 2630775.1084 | 1241107.6666
55 | 2630872.6584 | 1241132.9708
56 | 2630821.7149 | 1241214.3018
57 | 2630827.5701 | 1241220.7834
58 | 2630775.3552 | 1241234.4095
59 | 2630719.4959 | 1241166.2902
60 | 2630775.5708 | 1241234.7013
61 | 2630785.8817 | 1241248.5648
62 | 2630798.1623 | 1241262.9254
63 | 2630799.4783 | 1241264.2968
64 | 2630812.4735 | 1241276.027
65 | 2631045.8303 | 1241312.5781
66 | 2630990.8999 | 1241333.4023
67 | 2630983.6166 | 1241326.174
68 | 2630999.9022 | 1241267.096
69 | 2630995.5169 | 1241262.5993
70 | 2630938.6343 | 1241271.8054
71 | 2630949.8456 | 1241250.3259
72 | 2630934.8238 | 1241278.8089
73 | 2630961.3373 | 1241226.5581
74 | 2630927.6131 | 1241292.954
75 | 2630946.5446 | 1241288.2073
76 | 2630989.8889 | 1241256.8284
77 | 2630917.0559 | 1241314.154
78 | 2630965.6923 | 1241308.3852
79 | 2630900.3074 | 1241340.6687
80 | 2630982.2475 | 1241324.8152
81 | 2630815.3971 | 1241278.5996
82 | 2630627.9061 | 1241273.2165
83 | 2630635.5972 | 1241251.5976
84 | 2630622.2992 | 1241297.0024
85 | 2630637.9987 | 1241250.7696
86 | 2630597.7939 | 1241290.5624
87 | 2630666.1082 | 1241316.3276
88 | 2630639.6945 | 1241250.6173
89 | 2630700.6267 | 1241337.4397
90 | 2630641.9005 | 1241250.4961
91 | 2630710.7169 | 1241343.0654
92 | 2630692.077 | 1241136.3547
93 | 2630703.8203 | 1241149.1956
94 | 2630708.5483 | 1241154.5123
95 | 2630652.8729 | 1241085.0736
96 | 2630639.128 | 1241064.8336
97 | 2630609.8419 | 1241216.0801
98 | 2630589.2344 | 1241224.4209
99 | 2630721.4157 | 1241077.8756
100 | 2630725.5831 | 1241073.0195
101 | 2630714.5202 | 1241085.9107
102 | 2630730.3299 | 1241067.4883
103 | 2630740.6318 | 1241054.1588
104 | 2630712.2462 | 1241018.2586
105 | 2630764.3917 | 1241090.1749
106 | 2630874.1512 | 1241325.9185
107 | 2630873.1293 | 1241324.9153
108 | 2630893.6287 | 1241339.8334
109 | 2630888.9845 | 1241357.1311
110 | 2630897.6848 | 1241269.3419
111 | 2630916.7484 | 1241356.3421
112 | 2630887.2618 | 1241363.1432
113 | 2630938.7812 | 1241374.2793
114 | 2630883.1024 | 1241376.7022
115 | 2630672.5448 | 1241264.4391
116 | 2630667.7276 | 1241261.3463
117 | 2630677.4563 | 1241267.5923
118 | 2630660.3335 | 1241256.6411
119 | 2630656.1016 | 1241254.305
120 | 2630723.9267 | 1241295.6758
121 | 2630900.5689 | 1241389.7001
122 | 2630588.4041 | 1241225.8888
123 | 2630876.0589 | 1241176.4101
124 | 2630877.1356 | 1241192.3429
125 | 2630951.1933 | 1241384.3945
126 | 2630770.0616 | 1241099.4293
127 | 2630696.8016 | 1241001.7102
128 | 2630728.0205 | 1241354.4399
129 | 2630756.1352 | 1241209.5488

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99169 | -0.15946 | 0.0021426 | 0.00053698
1 | 0.99177 | -0.15796 | 0.002079 | 0.00052104
2 | 0.99168 | -0.15966 | 0.0023024 | 0.00057704
3 | 0.99186 | -0.15625 | 0 | 0
4 | 0.99195 | -0.1546 | 0.0022665 | 0.00056804
5 | 0.99214 | -0.15077 | 0.0016694 | 0.00041839
6 | 0.9921 | -0.1506 | 0 | 0
7 | 0.99185 | -0.15534 | 0.00071587 | 0.00017941
8 | 0.99287 | -0.13567 | 0.0016005 | 0.00040112
9 | 0.99065 | -0.17913 | 0.00060069 | 0.00015055
10 | 0.99253 | -0.14285 | 0.0015084 | 0.00037805
11 | 0.99064 | -0.17924 | 0.00060285 | 0.00015109
12 | 0.99281 | -0.13748 | 0.0019168 | 0.0004804
13 | 0.98984 | -0.19471 | 0 | 0
14 | 0.99341 | -0.12589 | 0.0025309 | 0.00063431
15 | 0.98845 | -0.2216 | 0.0006058 | 0.00015183
16 | 0.99447 | -0.10569 | 0.0040145 | 0.0010061
17 | 0.99514 | -0.092962 | 0 | 0
18 | 0.99513 | -0.093243 | 0.00061335 | 0.00015372
19 | 0.9952 | -0.091889 | 0.00075611 | 0.0001895
20 | 0.98715 | -0.24683 | 0 | 0
21 | 0.98368 | -0.31447 | 0.0038764 | 0.00097151
22 | 0.98377 | -0.31266 | 0.0038978 | 0.00097689
23 | 0.98378 | -0.31246 | 0.012544 | 0.0031439
24 | 0.98987 | -0.193 | 0.012322 | 0.0030882
25 | 0.99008 | -0.18893 | 0 | 0
26 | 0.98419 | -0.30445 | 0.003484 | 0.00087317
27 | 0.99361 | -0.12138 | 0 | 0
28 | 0.98604 | -0.26667 | 0 | 0
29 | 0.98473 | -0.29387 | 0.0024016 | 0.0006019
30 | 0.99367 | -0.1203 | 0.0013532 | 0.00033914
31 | 0.98221 | -0.34081 | 0 | 0
32 | 0.98486 | -0.28973 | 0.01232 | 0.0030876
33 | 0.98529 | -0.28307 | 0.0019354 | 0.00048505
34 | 0.98535 | -0.28181 | 0.0019011 | 0.00047646
35 | 0.98612 | -0.26681 | 0.0019243 | 0.00048228
36 | 0.98616 | -0.26613 | 0.0018151 | 0.00045492
37 | 0.98645 | -0.26045 | 0.0019622 | 0.00049177
38 | 0.99271 | -0.13978 | 0.0024564 | 0.00061563
39 | 0.99274 | -0.13926 | 0.0025318 | 0.00063452
40 | 0.99194 | -0.15474 | 0 | 0
41 | 0.99316 | -0.13104 | 0 | 0
42 | 0.99185 | -0.15632 | 0.0017209 | 0.00043129
43 | 0.99109 | -0.17114 | 0.0036298 | 0.00090972
44 | 0.99184 | -0.15652 | 0.0019831 | 0.00049701
45 | 0.99606 | -0.075191 | 0 | 0
46 | 0.99291 | -0.13587 | 0.0021695 | 0.00054374
47 | 0.99175 | -0.15833 | 0.0017176 | 0.00043048
48 | 0.99082 | -0.17644 | 0.0022142 | 0.00055494
49 | 0.99172 | -0.1589 | 0 | 0
50 | 0.99748 | -0.04799 | 0.0036767 | 0.00092146
51 | 0.99568 | -0.082643 | 0.0025588 | 0.0006413
52 | 0.99261 | -0.14174 | 0.0036131 | 0.00090554
53 | 0.99171 | -0.15909 | 0.0041068 | 0.0010293
54 | 0.99056 | -0.18142 | 0.003547 | 0.00088897
55 | 0.99159 | -0.16148 | 0 | 0
56 | 0.99236 | -0.14658 | 0.0015935 | 0.00039937
57 | 0.99226 | -0.14844 | 0.0015762 | 0.00039504
58 | 0.99998 | -0.00044837 | 0.0045453 | 0.0011392
59 | 0.99552 | -0.085664 | 0.002247 | 0.00056315
60 | 1 | 0 | -0.33118 | -0.084126
61 | 0.99854 | -0.027713 | 0.0026852 | 0.00067298
62 | 0.99696 | -0.057689 | 0.007998 | 0.0020045
63 | 0.9968 | -0.060574 | 0.0016012 | 0.0004013
64 | 0.99542 | -0.086953 | 0.002091 | 0.00052405
65 | 0.98801 | -0.22983 | 0.0028774 | 0.00072116
66 | 0.98817 | -0.22681 | 0.0024 | 0.00060151
67 | 0.98822 | -0.22585 | 0.0014008 | 0.00035107
68 | 0.98834 | -0.22342 | 0.0014363 | 0.00035996
69 | 0.98835 | -0.22326 | 0.0015142 | 0.0003795
70 | 0.98879 | -0.21481 | 0.0023957 | 0.00060042
71 | 0.98865 | -0.21742 | 0.0015775 | 0.00039535
72 | 0.98885 | -0.21361 | 0 | 0
73 | 0.98854 | -0.21952 | 0 | 0
74 | 0.98914 | -0.20786 | 0.0011128 | 0.00027888
75 | 0.98868 | -0.2168 | 0.0015599 | 0.00039096
76 | 0.98837 | -0.22284 | 0.0015107 | 0.00037862
77 | 0.98961 | -0.19883 | 0.0027237 | 0.00068262
78 | 0.98842 | -0.22191 | 0.0014089 | 0.0003531
79 | 0.99031 | -0.1852 | 0 | 0
80 | 0.98823 | -0.22562 | 0.0022171 | 0.00055566
81 | 0.99511 | -0.092757 | 0.0076043 | 0.0019058
82 | 0.97384 | -0.50474 | 0.0097634 | 0.0024469
83 | 0.97346 | -0.51224 | 0.001747 | 0.00043785
84 | 0.97446 | -0.49254 | 0 | 0
85 | 0.97342 | -0.51298 | 0.001762 | 0.00044161
86 | 0.97414 | -0.49872 | 0.013283 | 0.003329
87 | 0.97627 | -0.45685 | 0.0080904 | 0.0020276
88 | 0.9734 | -0.51341 | 0.0017616 | 0.0004415
89 | 0.9781 | -0.42098 | 0.013514 | 0.003387
90 | 0.97337 | -0.51391 | 0.0019574 | 0.00049057
91 | 0.97877 | -0.40788 | 0.0015998 | 0.00040095
92 | 0.99528 | -0.090359 | 0.0025509 | 0.00063932
93 | 0.99538 | -0.088346 | 0 | 0
94 | 0.99542 | -0.087524 | 0 | 0
95 | 0.99508 | -0.094153 | 0.0012452 | 0.00031208
96 | 0.99505 | -0.094759 | 0.0014065 | 0.00035251
97 | 0.98662 | -0.25706 | 0.0017601 | 0.00044112
98 | 0.98711 | -0.24757 | 0.0017708 | 0.0004438
99 | 0.98921 | -0.20756 | 0.0015758 | 0.00039492
100 | 0.98925 | -0.20684 | 0.0034807 | 0.00087235
101 | 0.98917 | -0.20846 | 0.0047541 | 0.0011915
102 | 0.98932 | -0.20557 | 0.0017206 | 0.00043122
103 | 0.98949 | -0.2021 | 0 | 0
104 | 0.98928 | -0.20627 | 0.0016482 | 0.00041309
105 | 0.99015 | -0.18932 | 0.0040074 | 0.0010043
106 | 0.99139 | -0.16432 | 0.0018404 | 0.00046124
107 | 0.99144 | -0.16327 | 0.0010592 | 0.00026545
108 | 0.99051 | -0.18143 | 0 | 0
109 | 0.99042 | -0.18316 | 0.001389 | 0.00034811
110 | 0.99033 | -0.1849 | 0.0027273 | 0.00068353
111 | 0.99016 | -0.18821 | 0.0025674 | 0.00064344
112 | 0.99039 | -0.18361 | 0.0011801 | 0.00029576
113 | 0.99003 | -0.19067 | 0.0022601 | 0.00056644
114 | 0.99036 | -0.18434 | 0 | 0
115 | 0.97312 | -0.51889 | 0.0017722 | 0.00044416
116 | 0.97314 | -0.51845 | 0.0023388 | 0.00058617
117 | 0.97311 | -0.51915 | 0.0023862 | 0.00059803
118 | 0.9732 | -0.51741 | 0.0018106 | 0.00045379
119 | 0.97323 | -0.51667 | 0.0018731 | 0.00046944
120 | 0.98433 | -0.29989 | 0.013516 | 0.0033875
121 | 0.9903 | -0.18544 | 0.002863 | 0.00071753
122 | 0.98711 | -0.24763 | 0.001957 | 0.00049047
123 | 0.99147 | -0.16385 | 0.0015265 | 0.00038259
124 | 0.99145 | -0.16428 | 0.0015118 | 0.00037888
125 | 0.98999 | -0.19142 | 0.0026109 | 0.00065434
126 | 0.99036 | -0.18534 | 0.0021441 | 0.00053737
127 | 0.98921 | -0.20767 | 0.0034632 | 0.00086795
128 | 0.98 | -0.38393 | 0.013632 | 0.0034165
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.004445 | -0.001114 | 0.0044453 | 0.0011139 | 3.1781e-07 | -4.2433e-08 | 0.0066696 | 0.0066695 | 0.0066696 | 0.99169 | -0.15946 | 0.99177 | -0.15796 | 1.8323
1 | 0.0023024 | 0.00057699 | -0.0023024 | -0.00057704 | 2.1484e-08 | -4.8182e-08 | 0.0034547 | 0.0034548 | 0.0034548 | 0.99169 | -0.15946 | 0.99168 | -0.15966 | 0.94911
2 | -0.0065243 | -0.001635 | 0.0065248 | 0.0016351 | 5.3356e-07 | 1.4984e-07 | 0.0097887 | 0.0097887 | 0.0097887 | 0.99177 | -0.15796 | 0.99186 | -0.15625 | 2.6892
3 | -0.0065248 | -0.0016351 | 0.0065253 | 0.0016353 | 5.1133e-07 | 1.4356e-07 | 0.0097887 | 0.0097886 | 0.0097887 | 0.99186 | -0.15625 | 0.99195 | -0.1546 | 2.6892
4 | -0.0087918 | -0.0022033 | 0.0087935 | 0.002204 | 1.6037e-06 | 7.0892e-07 | 0.013189 | 0.013188 | 0.013189 | 0.99195 | -0.1546 | 0.99214 | -0.15077 | 3.6232
5 | -0.010463 | -0.0026224 | 0.010464 | 0.002623 | 1.1619e-06 | 5.811e-07 | 0.015692 | 0.015692 | 0.015692 | 0.99214 | -0.15077 | 0.99226 | -0.14844 | 4.3111
6 | 0.043457 | 0.010926 | -0.043447 | -0.01092 | 9.8365e-06 | 6.2157e-06 | 0.065192 | 0.065192 | 0.065192 | 0.9921 | -0.1506 | 0.99185 | -0.15534 | 17.9099
7 | -0.043457 | -0.010926 | 0.043488 | 0.010946 | 3.1008e-05 | 1.9594e-05 | 0.065192 | 0.065192 | 0.065192 | 0.9921 | -0.1506 | 0.99287 | -0.13567 | 17.9099
8 | 0.042731 | 0.010741 | -0.042715 | -0.010731 | 1.6171e-05 | 1.0214e-05 | 0.064118 | 0.064118 | 0.064118 | 0.99185 | -0.15534 | 0.99144 | -0.16327 | 17.6149
9 | -0.045088 | -0.011347 | 0.045119 | 0.011367 | 3.0807e-05 | 1.9483e-05 | 0.067591 | 0.067591 | 0.067591 | 0.99287 | -0.13567 | 0.99361 | -0.12138 | 18.5689
10 | -0.043266 | -0.010928 | 0.043342 | 0.010976 | 7.5388e-05 | 4.7635e-05 | 0.065019 | 0.065019 | 0.065019 | 0.99065 | -0.17913 | 0.99253 | -0.14285 | 17.8623
11 | 0.042666 | 0.010778 | -0.042665 | -0.010778 | 2.1971e-07 | 1.3878e-07 | 0.064117 | 0.064117 | 0.064117 | 0.99065 | -0.17913 | 0.99064 | -0.17924 | 17.6144
12 | -0.04485 | -0.011354 | 0.044862 | 0.011361 | 1.1561e-05 | 7.3108e-06 | 0.06728 | 0.06728 | 0.06728 | 0.99253 | -0.14285 | 0.99281 | -0.13748 | 18.4835
13 | 0.042062 | 0.010627 | -0.042031 | -0.010607 | 3.116e-05 | 1.9675e-05 | 0.063211 | 0.063211 | 0.063211 | 0.99064 | -0.17924 | 0.98984 | -0.19471 | 17.3657
14 | -0.046778 | -0.011842 | 0.046804 | 0.011858 | 2.6032e-05 | 1.6478e-05 | 0.070153 | 0.070153 | 0.070153 | 0.99281 | -0.13748 | 0.99341 | -0.12589 | 19.2728
15 | 0.042031 | 0.010607 | -0.041977 | -0.010573 | 5.4058e-05 | 3.4134e-05 | 0.063211 | 0.063211 | 0.063211 | 0.98984 | -0.19471 | 0.98845 | -0.2216 | 17.3657
16 | -0.049335 | -0.012493 | 0.049383 | 0.012523 | 4.7913e-05 | 3.0361e-05 | 0.073944 | 0.073944 | 0.073944 | 0.99341 | -0.12589 | 0.99447 | -0.10569 | 20.3143
17 | 0.041371 | 0.010421 | -0.041322 | -0.01039 | 4.9855e-05 | 3.1469e-05 | 0.062299 | 0.062299 | 0.062299 | 0.98845 | -0.2216 | 0.98715 | -0.24683 | 17.1152
18 | -0.053398 | -0.013529 | 0.053476 | 0.013579 | 7.8358e-05 | 4.9724e-05 | 0.079951 | 0.079951 | 0.079951 | 0.99447 | -0.10569 | 0.99606 | -0.075191 | 21.9645
19 | 0.0032653 | 0.0008178 | -0.0032652 | -0.00081783 | 4.3546e-08 | -3.5421e-08 | 0.0048823 | 0.0048823 | 0.0048823 | 0.99514 | -0.092962 | 0.99513 | -0.093243 | 1.3413
20 | -0.0032653 | -0.0008178 | 0.0032654 | 0.00081766 | 1.6696e-07 | -1.3583e-07 | 0.0048823 | 0.0048822 | 0.0048823 | 0.99514 | -0.092962 | 0.9952 | -0.091889 | 1.3413
21 | 0.0026519 | 0.00066411 | -0.0026518 | -0.00066429 | 1.1494e-07 | -1.7968e-07 | 0.0039652 | 0.0039653 | 0.0039653 | 0.99513 | -0.093243 | 0.99508 | -0.094153 | 1.0894
22 | -0.0040215 | -0.0010072 | 0.0040218 | 0.0010071 | 2.9292e-07 | -9.3296e-08 | 0.0060127 | 0.0060127 | 0.0060127 | 0.9952 | -0.091889 | 0.99528 | -0.090359 | 1.6519
23 | 0.0037279 | 0.00093419 | -0.0037278 | -0.00093425 | 1.3048e-07 | -5.7354e-08 | 0.0056194 | 0.0056194 | 0.0056194 | 0.98715 | -0.24683 | 0.98711 | -0.24757 | 1.5438
24 | 0.037594 | 0.0094554 | -0.037575 | -0.0094438 | 1.8353e-05 | 1.1551e-05 | 0.05668 | 0.05668 | 0.05668 | 0.98715 | -0.24683 | 0.98662 | -0.25706 | 15.5715
25 | -0.0038764 | -0.00097151 | 0.0038767 | 0.0009714 | 3.3494e-07 | -1.1543e-07 | 0.0058638 | 0.0058637 | 0.0058638 | 0.98368 | -0.31447 | 0.98377 | -0.31266 | 1.6109
26 | -0.0077745 | -0.0019483 | 0.0077746 | 0.0019483 | 7.3144e-08 | 2.8903e-08 | 0.011759 | 0.011759 | 0.011759 | 0.98377 | -0.31266 | 0.98378 | -0.31246 | 3.2306
27 | -0.020319 | -0.0050922 | 0.020327 | 0.0050969 | 7.752e-06 | 4.6833e-06 | 0.030733 | 0.030733 | 0.030733 | 0.98378 | -0.31246 | 0.98419 | -0.30445 | 8.4433
28 | -0.012322 | -0.0030882 | 0.012325 | 0.0030895 | 2.3933e-06 | 1.2926e-06 | 0.018523 | 0.018523 | 0.018523 | 0.98987 | -0.193 | 0.99008 | -0.18893 | 5.0888
29 | -0.11661 | -0.02967 | 0.11699 | 0.029914 | 0.00038098 | 0.0002434 | 0.17541 | 0.17541 | 0.17541 | 0.99008 | -0.18893 | 0.99361 | -0.12138 | 48.1909
30 | 0.10429 | 0.026581 | -0.1039 | -0.026332 | 0.00038969 | 0.00024886 | 0.15689 | 0.15689 | 0.15689 | 0.99008 | -0.18893 | 0.98604 | -0.26667 | 43.1022
31 | -0.023811 | -0.0059701 | 0.023823 | 0.0059775 | 1.2013e-05 | 7.374e-06 | 0.036001 | 0.036001 | 0.036001 | 0.98419 | -0.30445 | 0.98473 | -0.29387 | 9.8903
32 | -0.16211 | -0.04128 | 0.16212 | 0.041286 | 8.5016e-06 | 5.4211e-06 | 0.243 | 0.243 | 0.243 | 0.99361 | -0.12138 | 0.99367 | -0.1203 | 33.3798
33 | 0.078024 | 0.019836 | -0.077747 | -0.019659 | 0.00027755 | 0.00017696 | 0.11785 | 0.11785 | 0.11785 | 0.98604 | -0.26667 | 0.98221 | -0.34081 | 32.3753
34 | 0.025871 | 0.0064964 | -0.025843 | -0.0064788 | 2.8431e-05 | 1.7563e-05 | 0.039046 | 0.039046 | 0.039046 | 0.98604 | -0.26667 | 0.98486 | -0.28973 | 10.727
35 | -0.026224 | -0.0065794 | 0.026238 | 0.0065877 | 1.3517e-05 | 8.359e-06 | 0.03963 | 0.03963 | 0.03963 | 0.98473 | -0.29387 | 0.98529 | -0.28307 | 10.8873
36 | -0.16347 | -0.041625 | 0.16369 | 0.041764 | 0.00021742 | 0.00013865 | 0.24503 | 0.24503 | 0.24503 | 0.99367 | -0.1203 | 0.99511 | -0.092757 | 33.6581
37 | 0.077747 | 0.019659 | -0.077586 | -0.019556 | 0.00016043 | 0.00010229 | 0.11785 | 0.11785 | 0.11785 | 0.98221 | -0.34081 | 0.98 | -0.38393 | 32.3753
38 | 0.013523 | 0.0033912 | -0.013516 | -0.0033875 | 6.5447e-06 | 3.6569e-06 | 0.020433 | 0.020433 | 0.020433 | 0.98486 | -0.28973 | 0.98433 | -0.29989 | 5.6134
39 | -0.028173 | -0.0070728 | 0.028175 | 0.0070738 | 1.6896e-06 | 1.0496e-06 | 0.042552 | 0.042552 | 0.042552 | 0.98529 | -0.28307 | 0.98535 | -0.28181 | 11.6902
40 | -0.030076 | -0.0075503 | 0.030098 | 0.0075637 | 2.1536e-05 | 1.3428e-05 | 0.045423 | 0.045423 | 0.045423 | 0.98535 | -0.28181 | 0.98612 | -0.26681 | 12.479
41 | -0.032022 | -0.008046 | 0.032023 | 0.0080466 | 1.0432e-06 | 6.5246e-07 | 0.048327 | 0.048327 | 0.048327 | 0.98612 | -0.26681 | 0.98616 | -0.26613 | 13.2766
42 | -0.033838 | -0.0085016 | 0.033847 | 0.0085073 | 9.1743e-06 | 5.7518e-06 | 0.051066 | 0.051066 | 0.051066 | 0.98616 | -0.26613 | 0.98645 | -0.26045 | 14.0291
43 | -0.035809 | -0.0089991 | 0.035815 | 0.0090027 | 5.797e-06 | 3.6425e-06 | 0.054026 | 0.054026 | 0.054026 | 0.98645 | -0.26045 | 0.98662 | -0.25706 | 14.8422
44 | -0.047304 | -0.011887 | 0.047305 | 0.011888 | 1.1551e-06 | 7.3135e-07 | 0.070918 | 0.070918 | 0.070918 | 0.99271 | -0.13978 | 0.99274 | -0.13926 | 19.4829
45 | 0.044848 | 0.011271 | -0.044816 | -0.011251 | 3.2009e-05 | 2.0242e-05 | 0.067236 | 0.067236 | 0.067236 | 0.99271 | -0.13978 | 0.99194 | -0.15474 | 18.4714
46 | -0.049837 | -0.012522 | 0.049857 | 0.012535 | 1.9566e-05 | 1.2402e-05 | 0.074713 | 0.074713 | 0.074713 | 0.99274 | -0.13926 | 0.99316 | -0.13104 | 20.5254
47 | 0.0075466 | 0.0018913 | -0.0075461 | -0.0018911 | 5.6893e-07 | 2.1132e-07 | 0.011321 | 0.011321 | 0.011321 | 0.99194 | -0.15474 | 0.99185 | -0.15632 | 3.1101
48 | 0.032246 | 0.0081027 | -0.032221 | -0.0080869 | 2.523e-05 | 1.5777e-05 | 0.048381 | 0.048381 | 0.048381 | 0.99194 | -0.15474 | 0.99109 | -0.17114 | 13.2914
49 | 0.0050229 | 0.0012572 | -0.0050225 | -0.0012572 | 4.2534e-07 | 1.4321e-08 | 0.0075344 | 0.0075344 | 0.0075344 | 0.99194 | -0.15474 | 0.99184 | -0.15652 | 2.0699
50 | -0.069287 | -0.017409 | 0.069472 | 0.017527 | 0.00018525 | 0.00011797 | 0.10383 | 0.10383 | 0.10383 | 0.99316 | -0.13104 | 0.99606 | -0.075191 | 28.5234
51 | 0.01943 | 0.0048745 | -0.019425 | -0.0048718 | 4.471e-06 | 2.6795e-06 | 0.029113 | 0.029113 | 0.029113 | 0.99316 | -0.13104 | 0.99291 | -0.13587 | 7.998
52 | 0.0058252 | 0.0014598 | -0.0058246 | -0.0014597 | 5.5763e-07 | 1.0561e-07 | 0.0087391 | 0.0087392 | 0.0087392 | 0.99185 | -0.15632 | 0.99175 | -0.15833 | 2.4009
53 | 0.028591 | 0.0071772 | -0.028584 | -0.0071727 | 7.2223e-06 | 4.4876e-06 | 0.042931 | 0.042931 | 0.042931 | 0.99109 | -0.17114 | 0.99082 | -0.17644 | 11.7942
54 | 0.0030394 | 0.00076021 | -0.0030391 | -0.00076056 | 3.4448e-07 | -3.4977e-07 | 0.0045593 | 0.0045595 | 0.0045595 | 0.99184 | -0.15652 | 0.99172 | -0.1589 | 1.2526
55 | -0.13433 | -0.03396 | 0.13451 | 0.034072 | 0.00017549 | 0.00011216 | 0.20078 | 0.20078 | 0.20078 | 0.99606 | -0.075191 | 0.99748 | -0.04799 | 55.1605
56 | 0.011385 | 0.0028539 | -0.011381 | -0.0028518 | 4.0408e-06 | 2.1015e-06 | 0.017009 | 0.017009 | 0.017009 | 0.99606 | -0.075191 | 0.99568 | -0.082643 | 4.6728
57 | 0.017256 | 0.0043281 | -0.017251 | -0.0043253 | 4.8298e-06 | 2.8421e-06 | 0.025862 | 0.025862 | 0.025862 | 0.99291 | -0.13587 | 0.99261 | -0.14174 | 7.1048
58 | 0.004107 | 0.0010292 | -0.0041068 | -0.0010293 | 1.4845e-07 | -3.9513e-08 | 0.0061621 | 0.0061621 | 0.0061621 | 0.99175 | -0.15833 | 0.99171 | -0.15909 | 1.6929
59 | 0.02637 | 0.0066177 | -0.026364 | -0.0066139 | 6.2636e-06 | 3.8716e-06 | 0.039606 | 0.039606 | 0.039606 | 0.99082 | -0.17644 | 0.99056 | -0.18142 | 10.8807
60 | 0.0030391 | 0.00076056 | -0.0030387 | -0.00076094 | 3.7311e-07 | -3.7863e-07 | 0.0045595 | 0.0045597 | 0.0045597 | 0.99172 | -0.1589 | 0.99159 | -0.16148 | 1.2527
61 | -0.13819 | -0.034994 | 0.1385 | 0.035196 | 0.00031626 | 0.00020215 | 0.20627 | 0.20627 | 0.20627 | 0.99748 | -0.04799 | 0.99998 | -0.00044837 | 56.6673
62 | 0.0088225 | 0.0022105 | -0.0088212 | -0.00221 | 1.2692e-06 | 5.5912e-07 | 0.013185 | 0.013185 | 0.013185 | 0.99568 | -0.082643 | 0.99552 | -0.085664 | 3.6222
63 | 0.013638 | 0.0034197 | -0.013635 | -0.003418 | 3.1429e-06 | 1.7524e-06 | 0.020445 | 0.020445 | 0.020445 | 0.99261 | -0.14174 | 0.99236 | -0.14658 | 5.6168
64 | 0.022817 | 0.0057249 | -0.022812 | -0.0057223 | 4.2564e-06 | 2.5998e-06 | 0.034277 | 0.034277 | 0.034277 | 0.99056 | -0.18142 | 0.99036 | -0.18534 | 9.4169
65 | 0.0030387 | 0.00076094 | -0.0030383 | -0.00076129 | 3.4275e-07 | -3.4762e-07 | 0.0045597 | 0.0045599 | 0.0045599 | 0.99159 | -0.16148 | 0.99147 | -0.16385 | 1.2527
66 | 0.012041 | 0.0030186 | -0.01204 | -0.003018 | 1.0679e-06 | 5.706e-07 | 0.018056 | 0.018056 | 0.018056 | 0.99236 | -0.14658 | 0.99226 | -0.14844 | 4.9604
67 | -0.14305 | -0.036335 | 0.14305 | 0.036337 | 3.0873e-06 | 1.9664e-06 | 0.21303 | 0.21303 | 0.21303 | 0.99998 | -0.00044837 | 1 | 0 | 29.2627
68 | 0.0065742 | 0.0016468 | -0.0065737 | -0.0016466 | 5.8224e-07 | 1.6358e-07 | 0.0098263 | 0.0098264 | 0.0098264 | 0.99552 | -0.085664 | 0.99542 | -0.087524 | 2.6996
69 | 0.18648 | 0.047789 | -0.18623 | -0.047629 | 0.00025012 | 0.00015963 | 0.27786 | 0.27786 | 0.27786 | 1 | 0 | 0.99854 | -0.027713 | 38.1671
70 | 0.18354 | 0.046956 | -0.18328 | -0.046787 | 0.0002659 | 0.00016968 | 0.27385 | 0.27386 | 0.27386 | 0.99854 | -0.027713 | 0.99696 | -0.057689 | 37.6174
71 | 0.17528 | 0.044782 | -0.17525 | -0.044766 | 2.4448e-05 | 1.5597e-05 | 0.26192 | 0.26192 | 0.26192 | 0.99696 | -0.057689 | 0.9968 | -0.060574 | 35.9777
72 | 0.17365 | 0.044365 | -0.17343 | -0.044224 | 0.00022119 | 0.0001411 | 0.25953 | 0.25953 | 0.25953 | 0.9968 | -0.060574 | 0.99542 | -0.086953 | 35.6494
73 | 0.17134 | 0.0437 | -0.17129 | -0.043669 | 4.8004e-05 | 3.0621e-05 | 0.2564 | 0.2564 | 0.2564 | 0.99542 | -0.086953 | 0.99511 | -0.092757 | 35.22
74 | -0.0028774 | -0.00072116 | 0.0028779 | 0.00072067 | 4.1369e-07 | -4.8768e-07 | 0.0043336 | 0.0043334 | 0.0043336 | 0.98801 | -0.22983 | 0.98817 | -0.22681 | 1.1906
75 | -0.0052779 | -0.0013222 | 0.0052781 | 0.0013222 | 2.4304e-07 | 2.4087e-08 | 0.0079474 | 0.0079474 | 0.0079474 | 0.98817 | -0.22681 | 0.98822 | -0.22585 | 2.1834
76 | -0.0066789 | -0.0016733 | 0.006679 | 0.0016733 | 7.3156e-08 | 2.2106e-08 | 0.010057 | 0.010057 | 0.010057 | 0.98822 | -0.22585 | 0.98823 | -0.22562 | 2.7628
77 | -0.0014363 | -0.00035996 | 0.0014363 | 0.00035988 | 1.1013e-08 | -7.3445e-08 | 0.0021624 | 0.0021623 | 0.0021624 | 0.98834 | -0.22342 | 0.98835 | -0.22326 | 0.59406
78 | -0.0029505 | -0.00073939 | 0.0029506 | 0.00073932 | 5.9646e-08 | -6.5131e-08 | 0.0044421 | 0.0044421 | 0.0044421 | 0.98835 | -0.22326 | 0.98837 | -0.22284 | 1.2204
79 | 0.0060407 | 0.0015133 | -0.0060399 | -0.0015132 | 7.5093e-07 | 1.6981e-07 | 0.0090903 | 0.0090904 | 0.0090904 | 0.98879 | -0.21481 | 0.98865 | -0.21742 | 2.4974
80 | -0.0084364 | -0.0021138 | 0.0084369 | 0.002114 | 4.819e-07 | 2.0615e-07 | 0.012696 | 0.012696 | 0.012696 | 0.98879 | -0.21481 | 0.98885 | -0.21361 | 3.4878
81 | 0.0044624 | 0.0011178 | -0.004462 | -0.0011179 | 4.4664e-07 | -5.2702e-08 | 0.0067162 | 0.0067163 | 0.0067163 | 0.98865 | -0.21742 | 0.98854 | -0.21952 | 1.8451
82 | -0.020308 | -0.0050899 | 0.020313 | 0.0050932 | 5.5601e-06 | 3.3547e-06 | 0.030559 | 0.030559 | 0.030559 | 0.98885 | -0.21361 | 0.98914 | -0.20786 | 8.3954
83 | 0.011871 | 0.0029759 | -0.011869 | -0.002975 | 1.8043e-06 | 9.6137e-07 | 0.017863 | 0.017864 | 0.017864 | 0.98885 | -0.21361 | 0.98868 | -0.2168 | 4.9076
84 | 0.004462 | 0.0011179 | -0.0044613 | -0.0011179 | 7.0452e-07 | -8.2955e-08 | 0.0067163 | 0.0067165 | 0.0067165 | 0.98854 | -0.21952 | 0.98837 | -0.22284 | 1.8452
85 | -0.021426 | -0.0053721 | 0.021435 | 0.0053777 | 9.2273e-06 | 5.6013e-06 | 0.032233 | 0.032233 | 0.032233 | 0.98914 | -0.20786 | 0.98961 | -0.19883 | 8.8552
86 | 0.010309 | 0.002584 | -0.010307 | -0.0025828 | 2.5113e-06 | 1.2506e-06 | 0.015516 | 0.015516 | 0.015516 | 0.98868 | -0.2168 | 0.98842 | -0.22191 | 4.2626
87 | -0.024159 | -0.0060603 | 0.024175 | 0.00607 | 1.5707e-05 | 9.6445e-06 | 0.036328 | 0.036328 | 0.036328 | 0.98961 | -0.19883 | 0.99031 | -0.1852 | 9.9803
88 | 0.0088977 | 0.0022297 | -0.0088961 | -0.002229 | 1.5694e-06 | 7.0549e-07 | 0.013395 | 0.013395 | 0.013395 | 0.98842 | -0.22191 | 0.98823 | -0.22562 | 3.68
89 | 0.0074401 | 0.0018645 | -0.007439 | -0.0018641 | 1.0665e-06 | 3.8981e-07 | 0.011179 | 0.011179 | 0.011179 | 0.99031 | -0.1852 | 0.99016 | -0.18821 | 3.0712
90 | -0.031615 | -0.0079345 | 0.03162 | 0.007938 | 5.6799e-06 | 3.5488e-06 | 0.047507 | 0.047507 | 0.047507 | 0.99031 | -0.1852 | 0.99051 | -0.18143 | 13.0515
91 | 0.017418 | 0.0043683 | -0.017412 | -0.0043646 | 6.2315e-06 | 3.6964e-06 | 0.026616 | 0.026616 | 0.026616 | 0.97384 | -0.50474 | 0.97346 | -0.51224 | 7.3122
92 | -0.027182 | -0.0068152 | 0.027198 | 0.006825 | 1.5814e-05 | 9.8167e-06 | 0.041535 | 0.041535 | 0.041535 | 0.97384 | -0.50474 | 0.97446 | -0.49254 | 11.4106
93 | 0.015665 | 0.0039267 | -0.015665 | -0.0039264 | 5.4621e-07 | 3.18e-07 | 0.023946 | 0.023946 | 0.023946 | 0.97346 | -0.51224 | 0.97342 | -0.51298 | 6.5785
94 | 0.013287 | 0.0033312 | -0.013283 | -0.003329 | 3.9137e-06 | 2.189e-06 | 0.02029 | 0.02029 | 0.02029 | 0.97446 | -0.49254 | 0.97414 | -0.49872 | 5.5742
95 | -0.040485 | -0.010156 | 0.040554 | 0.0102 | 6.9003e-05 | 4.3561e-05 | 0.061824 | 0.061824 | 0.061824 | 0.97446 | -0.49254 | 0.97627 | -0.45685 | 16.9847
96 | 0.013903 | 0.0034848 | -0.013902 | -0.0034846 | 2.8961e-07 | 1.6409e-07 | 0.021252 | 0.021252 | 0.021252 | 0.97342 | -0.51298 | 0.9734 | -0.51341 | 5.8386
97 | -0.048644 | -0.012227 | 0.048728 | 0.01228 | 8.3471e-05 | 5.2914e-05 | 0.074156 | 0.074155 | 0.074156 | 0.97627 | -0.45685 | 0.9781 | -0.42098 | 20.3724
98 | 0.012141 | 0.0030431 | -0.01214 | -0.003043 | 2.8538e-07 | 1.5518e-07 | 0.018559 | 0.018559 | 0.018559 | 0.9734 | -0.51341 | 0.97337 | -0.51391 | 5.0987
99 | -0.062242 | -0.015667 | 0.062281 | 0.015692 | 3.898e-05 | 2.4802e-05 | 0.094715 | 0.094715 | 0.094715 | 0.9781 | -0.42098 | 0.97877 | -0.40788 | 26.0207
100 | 0.010183 | 0.0025524 | -0.010182 | -0.0025517 | 1.339e-06 | 6.7383e-07 | 0.015567 | 0.015567 | 0.015567 | 0.97337 | -0.51391 | 0.97323 | -0.51667 | 4.2767
101 | -0.063881 | -0.016093 | 0.063954 | 0.01614 | 7.3285e-05 | 4.6642e-05 | 0.097147 | 0.097147 | 0.097147 | 0.97877 | -0.40788 | 0.98 | -0.38393 | 26.6888
102 | -0.0065728 | -0.0016464 | 0.0065734 | 0.0016466 | 6.3008e-07 | 1.7709e-07 | 0.0098265 | 0.0098264 | 0.0098265 | 0.99528 | -0.090359 | 0.99538 | -0.088346 | 2.6996
103 | -0.0065734 | -0.0016466 | 0.0065737 | 0.0016466 | 2.573e-07 | 7.2303e-08 | 0.0098264 | 0.0098264 | 0.0098264 | 0.99538 | -0.088346 | 0.99542 | -0.087524 | 2.6996
104 | 0.0014066 | 0.00035221 | -0.0014065 | -0.00035251 | 4.0591e-08 | -2.9187e-07 | 0.0021032 | 0.0021033 | 0.0021033 | 0.99508 | -0.094153 | 0.99505 | -0.094759 | 0.57784
105 | 0.001957 | 0.00049045 | -0.001957 | -0.00049047 | 5.5038e-09 | -1.8036e-08 | 0.0029501 | 0.0029501 | 0.0029501 | 0.98711 | -0.24757 | 0.98711 | -0.24763 | 0.81046
106 | -0.0063301 | -0.0015864 | 0.0063303 | 0.0015865 | 2.1757e-07 | 5.7093e-08 | 0.009522 | 0.0095219 | 0.009522 | 0.98921 | -0.20756 | 0.98925 | -0.20684 | 2.6159
107 | 0.0047543 | 0.0011915 | -0.0047541 | -0.0011915 | 2.0308e-07 | -5.9515e-09 | 0.0071516 | 0.0071517 | 0.0071517 | 0.98921 | -0.20756 | 0.98917 | -0.20846 | 1.9647
108 | -0.009811 | -0.0024588 | 0.0098116 | 0.0024591 | 5.9527e-07 | 2.8739e-07 | 0.014758 | 0.014758 | 0.014758 | 0.98925 | -0.20684 | 0.98932 | -0.20557 | 4.0543
109 | -0.011532 | -0.0028903 | 0.011534 | 0.0028913 | 1.9017e-06 | 1.0006e-06 | 0.017345 | 0.017345 | 0.017345 | 0.98932 | -0.20557 | 0.98949 | -0.2021 | 4.7652
110 | 0.0051127 | 0.001281 | -0.0051116 | -0.0012809 | 1.0146e-06 | 6.1546e-08 | 0.0076883 | 0.0076886 | 0.0076886 | 0.98949 | -0.2021 | 0.98928 | -0.20627 | 2.1122
111 | -0.016647 | -0.0041723 | 0.016657 | 0.0041782 | 1.0145e-05 | 5.9378e-06 | 0.025034 | 0.025034 | 0.025034 | 0.98949 | -0.2021 | 0.99015 | -0.18932 | 6.8774
112 | 0.0034634 | 0.00086781 | -0.0034632 | -0.00086795 | 2.3043e-07 | -1.4323e-07 | 0.0052094 | 0.0052095 | 0.0052095 | 0.98928 | -0.20627 | 0.98921 | -0.20767 | 1.4312
113 | -0.020664 | -0.0051826 | 0.020668 | 0.0051849 | 3.9253e-06 | 2.3726e-06 | 0.031056 | 0.031056 | 0.031056 | 0.99015 | -0.18932 | 0.99036 | -0.18534 | 8.5318
114 | -0.041654 | -0.010464 | 0.041656 | 0.010465 | 2.0996e-06 | 1.3253e-06 | 0.062529 | 0.062529 | 0.062529 | 0.99139 | -0.16432 | 0.99144 | -0.16327 | 17.1782
115 | 0.039813 | 0.010003 | -0.039781 | -0.009982 | 3.2484e-05 | 2.0478e-05 | 0.059766 | 0.059766 | 0.059766 | 0.99139 | -0.16432 | 0.99051 | -0.18143 | 16.4193
116 | 0.0054328 | 0.0013611 | -0.0054324 | -0.0013611 | 4.4738e-07 | 5.5813e-08 | 0.0081615 | 0.0081615 | 0.0081615 | 0.99051 | -0.18143 | 0.99042 | -0.18316 | 2.2422
117 | 0.0027278 | 0.0006829 | -0.0027273 | -0.00068353 | 4.495e-07 | -6.3098e-07 | 0.0040976 | 0.0040979 | 0.0040979 | 0.99051 | -0.18143 | 0.99033 | -0.1849 | 1.1258
118 | 0.0040434 | 0.001013 | -0.0040433 | -0.001013 | 8.656e-08 | -2.5096e-08 | 0.0060747 | 0.0060748 | 0.0060748 | 0.99042 | -0.18316 | 0.99039 | -0.18361 | 1.6689
119 | 0.0048717 | 0.0012206 | -0.0048711 | -0.0012206 | 5.7105e-07 | 8.7868e-11 | 0.0073211 | 0.0073212 | 0.0073212 | 0.99016 | -0.18821 | 0.99003 | -0.19067 | 2.0113
120 | 0.0028632 | 0.00071722 | -0.0028631 | -0.00071734 | 9.8418e-08 | -1.1951e-07 | 0.0043017 | 0.0043018 | 0.0043018 | 0.99039 | -0.18361 | 0.99036 | -0.18434 | 1.1818
121 | 0.002611 | 0.0006542 | -0.0026109 | -0.00065434 | 9.2466e-08 | -1.4671e-07 | 0.0039242 | 0.0039243 | 0.0039243 | 0.99003 | -0.19067 | 0.98999 | -0.19142 | 1.0781
122 | 0.0028631 | 0.00071734 | -0.002863 | -0.00071753 | 1.511e-07 | -1.8345e-07 | 0.0043018 | 0.0043019 | 0.0043019 | 0.99036 | -0.18434 | 0.9903 | -0.18544 | 1.1818
123 | -0.0041584 | -0.0010421 | 0.0041585 | 0.0010421 | 8.6798e-08 | -1.5571e-08 | 0.0063587 | 0.0063587 | 0.0063587 | 0.97312 | -0.51889 | 0.97314 | -0.51845 | 1.7469
124 | 0.0023862 | 0.00059798 | -0.0023862 | -0.00059803 | 2.914e-08 | -5.386e-08 | 0.0036488 | 0.0036488 | 0.0036488 | 0.97312 | -0.51889 | 0.97311 | -0.51915 | 1.0024
125 | -0.0064973 | -0.0016283 | 0.0064977 | 0.0016284 | 3.2443e-07 | 9.873e-08 | 0.0099349 | 0.0099349 | 0.0099349 | 0.97314 | -0.51845 | 0.9732 | -0.51741 | 2.7294
126 | -0.0083083 | -0.0020822 | 0.0083086 | 0.0020823 | 2.9252e-07 | 1.2715e-07 | 0.012703 | 0.012703 | 0.012703 | 0.9732 | -0.51741 | 0.97323 | -0.51667 | 3.4899
127 | 0.0015118 | 0.0003787 | -0.0015118 | -0.00037888 | 3.0828e-08 | -1.8621e-07 | 0.0022689 | 0.0022689 | 0.0022689 | 0.99147 | -0.16385 | 0.99145 | -0.16428 | 0.62334

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33427 | 0.0849

## res_load
| p_mw | q_mvar
0 | 0.0021426 | 0.00053698
1 | 0.002079 | 0.00052104
2 | 0.0023024 | 0.00057704
3 | 0.0022665 | 0.00056804
4 | 0.0016694 | 0.00041839
5 | 0.00071587 | 0.00017941
6 | 0.0016005 | 0.00040112
7 | 0.00060069 | 0.00015055
8 | 0.0015084 | 0.00037805
9 | 0.00060285 | 0.00015109
10 | 0.0019168 | 0.0004804
11 | 0.0025309 | 0.00063431
12 | 0.0006058 | 0.00015183
13 | 0.0040145 | 0.0010061
14 | 0.00061335 | 0.00015372
15 | 0.00075611 | 0.0001895
16 | 0.0038764 | 0.00097151
17 | 0.0038978 | 0.00097689
18 | 0.012544 | 0.0031439
19 | 0.012322 | 0.0030882
20 | 0.003484 | 0.00087317
21 | 0.0024016 | 0.0006019
22 | 0.0013532 | 0.00033914
23 | 0.01232 | 0.0030876
24 | 0.0019354 | 0.00048505
25 | 0.0019011 | 0.00047646
26 | 0.0019243 | 0.00048228
27 | 0.0018151 | 0.00045492
28 | 0.0019622 | 0.00049177
29 | 0.0024564 | 0.00061563
30 | 0.0025318 | 0.00063452
31 | 0.0017209 | 0.00043129
32 | 0.0036298 | 0.00090972
33 | 0.0019831 | 0.00049701
34 | 0.0021695 | 0.00054374
35 | 0.0017176 | 0.00043048
36 | 0.0022142 | 0.00055494
37 | 0.0036767 | 0.00092146
38 | 0.0025588 | 0.0006413
39 | 0.0036131 | 0.00090554
40 | 0.0041068 | 0.0010293
41 | 0.003547 | 0.00088897
42 | 0.0015935 | 0.00039937
43 | 0.0015762 | 0.00039504
44 | 0.0045453 | 0.0011392
45 | 0.002247 | 0.00056315
46 | 0.0030905 | 0.00077455
47 | 0.0026852 | 0.00067298
48 | 0.007998 | 0.0020045
49 | 0.0016012 | 0.0004013
50 | 0.002091 | 0.00052405
51 | 0.0028774 | 0.00072116
52 | 0.0024 | 0.00060151
53 | 0.0014008 | 0.00035107
54 | 0.0014363 | 0.00035996
55 | 0.0015142 | 0.0003795
56 | 0.0023957 | 0.00060042
57 | 0.0015775 | 0.00039535
58 | 0.0011128 | 0.00027888
59 | 0.0015599 | 0.00039096
60 | 0.0015107 | 0.00037862
61 | 0.0027237 | 0.00068262
62 | 0.0014089 | 0.0003531
63 | 0.0022171 | 0.00055566
64 | 0.0076043 | 0.0019058
65 | 0.0097634 | 0.0024469
66 | 0.001747 | 0.00043785
67 | 0.001762 | 0.00044161
68 | 0.013283 | 0.003329
69 | 0.0080904 | 0.0020276
70 | 0.0017616 | 0.0004415
71 | 0.013514 | 0.003387
72 | 0.0019574 | 0.00049057
73 | 0.0015998 | 0.00040095
74 | 0.0025509 | 0.00063932
75 | 0.0012452 | 0.00031208
76 | 0.0014065 | 0.00035251
77 | 0.0017601 | 0.00044112
78 | 0.0017708 | 0.0004438
79 | 0.0015758 | 0.00039492
80 | 0.0034807 | 0.00087235
81 | 0.0047541 | 0.0011915
82 | 0.0017206 | 0.00043122
83 | 0.0016482 | 0.00041309
84 | 0.0040074 | 0.0010043
85 | 0.0018404 | 0.00046124
86 | 0.0010592 | 0.00026545
87 | 0.001389 | 0.00034811
88 | 0.0027273 | 0.00068353
89 | 0.0025674 | 0.00064344
90 | 0.0011801 | 0.00029576
91 | 0.0022601 | 0.00056644
92 | 0.0017722 | 0.00044416
93 | 0.0023388 | 0.00058617
94 | 0.0023862 | 0.00059803
95 | 0.0018106 | 0.00045379
96 | 0.0018731 | 0.00046944
97 | 0.013516 | 0.0033875
98 | 0.002863 | 0.00071753
99 | 0.001957 | 0.00049047
100 | 0.0015265 | 0.00038259
101 | 0.0015118 | 0.00037888
102 | 0.0026109 | 0.00065434
103 | 0.0021441 | 0.00053737
104 | 0.0034632 | 0.00086795
105 | 0.013632 | 0.0034165

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1