## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2580-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2580-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2580-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2580-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2580-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2580-4_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2580-4_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2580-4_0_4_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_2580-4_0_4_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_2580-4_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2580-4_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_2580-4_0_4_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_2580-4_0_4_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_2580-4_0_4_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_2580-4_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_2580-4_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_2580-4_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_2580-4_0_4_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_2580-4_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_2580-4_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2580-4_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2580-4_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2580-4_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2580-4_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2580-4_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2580-4_0_4_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_2580-4_0_4_node_111 | 0.4 | n |  | TRUE
27 | bus_LV_2580-4_0_4_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_2580-4_0_4_node_112 | 0.4 | n |  | TRUE
29 | bus_LV_2580-4_0_4_node_93 | 0.4 | n |  | TRUE
30 | bus_LV_2580-4_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2580-4_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2580-4_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_2580-4_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2580-4_0_4_node_122 | 0.4 | n |  | TRUE
35 | bus_LV_2580-4_0_4_node_123 | 0.4 | n |  | TRUE
36 | bus_LV_2580-4_0_4_node_120 | 0.4 | n |  | TRUE
37 | bus_LV_2580-4_0_4_node_119 | 0.4 | n |  | TRUE
38 | bus_LV_2580-4_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2580-4_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_2580-4_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_2580-4_0_4_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_2580-4_0_4_node_104 | 0.4 | n |  | TRUE
43 | bus_LV_2580-4_0_4_node_56 | 0.4 | n |  | TRUE
44 | bus_LV_2580-4_0_4_node_96 | 0.4 | n |  | TRUE
45 | bus_LV_2580-4_0_4_node_80 | 0.4 | n |  | TRUE
46 | bus_LV_2580-4_0_4_node_79 | 0.4 | n |  | TRUE
47 | bus_LV_2580-4_0_4_node_105 | 0.4 | n |  | TRUE
48 | bus_LV_2580-4_0_4_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_2580-4_0_4_node_57 | 0.4 | n |  | TRUE
50 | bus_LV_2580-4_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2580-4_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_2580-4_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_2580-4_0_4_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_2580-4_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_2580-4_0_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_2580-4_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_2580-4_0_4_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_2580-4_0_4_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_2580-4_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_2580-4_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_2580-4_0_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_2580-4_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2580-4_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_2580-4_0_4_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_2580-4_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2580-4_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_2580-4_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2580-4_0_4_node_106 | 0.4 | n |  | TRUE
69 | bus_LV_2580-4_0_4_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_2580-4_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_2580-4_0_4_node_88 | 0.4 | n |  | TRUE
72 | bus_LV_2580-4_0_4_node_107 | 0.4 | n |  | TRUE
73 | bus_LV_2580-4_0_4_node_108 | 0.4 | n |  | TRUE
74 | bus_LV_2580-4_0_4_node_89 | 0.4 | n |  | TRUE
75 | bus_LV_2580-4_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_2580-4_0_4_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_2580-4_0_4_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_2580-4_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_2580-4_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2580-4_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2580-4_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_2580-4_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_2580-4_0_4_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_2580-4_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_2580-4_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_2580-4_0_4_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_2580-4_0_4_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_2580-4_0_4_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_2580-4_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_2580-4_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2580-4_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_2580-4_0_4_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_2580-4_0_4_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2580-4_0_4_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_2580-4_0_4_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_2580-4_0_4_node_124 | 0.4 | n |  | TRUE
97 | bus_LV_2580-4_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_2580-4_0_4_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_2580-4_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_2580-4_0_4_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_2580-4_0_4_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_2580-4_0_4_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_2580-4_0_4_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2580-4_0_4_node_117 | 0.4 | n |  | TRUE
105 | bus_LV_2580-4_0_4_node_118 | 0.4 | n |  | TRUE
106 | bus_LV_2580-4_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_2580-4_0_4_node_115 | 0.4 | n |  | TRUE
108 | bus_LV_2580-4_0_4_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_2580-4_0_4_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_2580-4_0_4_node_109 | 0.4 | n |  | TRUE
111 | bus_LV_2580-4_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_2580-4_0_4_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_2580-4_0_4_node_121 | 0.4 | n |  | TRUE
114 | bus_LV_2580-4_0_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_2580-4_0_4_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_2580-4_0_4_node_97 | 0.4 | n |  | TRUE
117 | bus_LV_2580-4_0_4_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_2580-4_0_4_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_2580-4_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_2580-4_0_4_node_116 | 0.4 | n |  | TRUE
121 | bus_MV_480_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2580-4_0_4_load_0 | 0 | 0.0021795 | 0.00054624 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2580-4_0_4_load_1 | 1 | 0.004011 | 0.0010053 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2580-4_0_4_load_2 | 2 | 0.0024177 | 0.00060594 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2580-4_0_4_load_4 | 4 | 0.0028775 | 0.00072116 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2580-4_0_4_load_6 | 5 | 0.0042391 | 0.0010624 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2580-4_0_4_load_5 | 6 | 0.0021551 | 0.00054012 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2580-4_0_4_load_22 | 11 | 0.0025915 | 0.0006495 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2580-4_0_4_load_19 | 12 | 0.0039369 | 0.00098669 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2580-4_0_4_load_23 | 14 | 0.0027951 | 0.00070051 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2580-4_0_4_load_25 | 16 | 0.002216 | 0.00055538 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2580-4_0_4_load_26 | 17 | 0.0025574 | 0.00064094 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2580-4_0_4_load_28 | 18 | 0.018762 | 0.0047022 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2580-4_0_4_load_8 | 19 | 0.010288 | 0.0025784 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2580-4_0_4_load_9 | 20 | 0.0038005 | 0.0009525 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2580-4_0_4_load_11 | 21 | 0.0012434 | 0.00031161 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2580-4_0_4_load_12 | 23 | 0.0004335 | 0.00010864 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2580-4_0_4_load_14 | 24 | 0.0048141 | 0.0012065 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2580-4_0_4_load_34 | 25 | 0.0026165 | 0.00065577 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2580-4_0_4_load_112 | 28 | 0.0023086 | 0.00057858 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2580-4_0_4_load_93 | 29 | 0.0068455 | 0.0017156 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2580-4_0_4_load_15 | 31 | 0.0019427 | 0.00048689 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2580-4_0_4_load_16 | 32 | 0.013447 | 0.0033701 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2580-4_0_4_load_18 | 33 | 0.0036699 | 0.00091976 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2580-4_0_4_load_123 | 35 | 0.002004 | 0.00050224 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2580-4_0_4_load_120 | 36 | 0.0033908 | 0.00084982 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2580-4_0_4_load_119 | 37 | 0.0024344 | 0.00061013 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2580-4_0_4_load_29 | 38 | 0.0021912 | 0.00054917 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2580-4_0_4_load_30 | 39 | 0.0071926 | 0.0018026 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2580-4_0_4_load_27 | 40 | 0.0058798 | 0.0014736 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2580-4_0_4_load_98 | 41 | 0.0026825 | 0.00067229 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2580-4_0_4_load_104 | 42 | 0.00092875 | 0.00023277 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2580-4_0_4_load_56 | 43 | 0.0014724 | 0.00036903 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2580-4_0_4_load_96 | 44 | 0.0021151 | 0.00053009 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2580-4_0_4_load_105 | 47 | 0.0012464 | 0.00031238 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2580-4_0_4_load_57 | 49 | 0.0016663 | 0.00041762 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2580-4_0_4_load_31 | 50 | 0.0013275 | 0.00033271 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2580-4_0_4_load_35 | 51 | 0.0019493 | 0.00048854 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2580-4_0_4_load_36 | 52 | 0.011431 | 0.002865 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2580-4_0_4_load_37 | 53 | 0.0019661 | 0.00049275 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2580-4_0_4_load_38 | 54 | 0.0019638 | 0.00049217 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2580-4_0_4_load_39 | 55 | 0.0082971 | 0.0020794 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2580-4_0_4_load_40 | 56 | 0.0019902 | 0.00049879 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2580-4_0_4_load_41 | 57 | 0.012594 | 0.0031563 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2580-4_0_4_load_60 | 58 | 0.0019882 | 0.00049828 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2580-4_0_4_load_42 | 60 | 0.0031845 | 0.0007981 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2580-4_0_4_load_43 | 61 | 0.0019952 | 0.00050005 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2580-4_0_4_load_45 | 63 | 0.0019476 | 0.00048811 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2580-4_0_4_load_46 | 64 | 0.008841 | 0.0022158 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2580-4_0_4_load_47 | 65 | 0.014141 | 0.0035441 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2580-4_0_4_load_48 | 66 | 0.0019521 | 0.00048924 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2580-4_0_4_load_49 | 67 | 0.0087723 | 0.0021985 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2580-4_0_4_load_106 | 68 | 0.005161 | 0.0012935 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2580-4_0_4_load_50 | 69 | 0.011211 | 0.0028097 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2580-4_0_4_load_51 | 70 | 0.0021741 | 0.00054487 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2580-4_0_4_load_107 | 72 | 0.005147 | 0.00129 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2580-4_0_4_load_108 | 73 | 0.005116 | 0.0012822 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2580-4_0_4_load_59 | 75 | 0.0019868 | 0.00049793 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2580-4_0_4_load_58 | 76 | 0.0012522 | 0.00031384 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2580-4_0_4_load_61 | 77 | 0.0061054 | 0.0015302 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2580-4_0_4_load_62 | 78 | 0.0068396 | 0.0017142 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2580-4_0_4_load_63 | 79 | 0.0013102 | 0.00032836 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2580-4_0_4_load_64 | 80 | 0.0015965 | 0.00040013 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2580-4_0_4_load_67 | 83 | 0.0089155 | 0.0022344 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2580-4_0_4_load_73 | 85 | 0.0028471 | 0.00071356 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2580-4_0_4_load_72 | 86 | 0.0048931 | 0.0012263 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2580-4_0_4_load_78 | 87 | 0.002171 | 0.0005441 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2580-4_0_4_load_74 | 88 | 0.0046805 | 0.0011731 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2580-4_0_4_load_71 | 89 | 0.0089187 | 0.0022352 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2580-4_0_4_load_68 | 90 | 0.0091533 | 0.002294 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2580-4_0_4_load_69 | 91 | 0.013948 | 0.0034956 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2580-4_0_4_load_70 | 92 | 0.014002 | 0.0035092 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2580-4_0_4_load_75 | 93 | 0.0024587 | 0.0006162 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2580-4_0_4_load_90 | 94 | 0.0044324 | 0.0011109 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2580-4_0_4_load_124 | 96 | 0.006671 | 0.0016719 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2580-4_0_4_load_81 | 97 | 0.0012586 | 0.00031545 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2580-4_0_4_load_82 | 98 | 0.00091927 | 0.00023039 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2580-4_0_4_load_83 | 99 | 0.0012618 | 0.00031624 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2580-4_0_4_load_84 | 100 | 0.0055326 | 0.0013866 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2580-4_0_4_load_85 | 101 | 0.0014784 | 0.00037053 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2580-4_0_4_load_87 | 103 | 0.0012477 | 0.00031271 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2580-4_0_4_load_117 | 104 | 0.0034288 | 0.00085934 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2580-4_0_4_load_118 | 105 | 0.0010422 | 0.00026119 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2580-4_0_4_load_101 | 106 | 0.0014409 | 0.00036113 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2580-4_0_4_load_115 | 107 | 0.0023162 | 0.00058048 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2580-4_0_4_load_102 | 108 | 0.0016693 | 0.00041836 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2580-4_0_4_load_94 | 109 | 0.0036237 | 0.00090819 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2580-4_0_4_load_109 | 110 | 0.001063 | 0.0002664 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2580-4_0_4_load_113 | 111 | 0.004498 | 0.0011273 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2580-4_0_4_load_92 | 112 | 0.0023776 | 0.00059588 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2580-4_0_4_load_121 | 113 | 0.0052184 | 0.0013079 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2580-4_0_4_load_95 | 115 | 0.0016368 | 0.00041023 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2580-4_0_4_load_97 | 116 | 0.0012613 | 0.0003161 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2580-4_0_4_load_99 | 117 | 0.0014466 | 0.00036255 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2580-4_0_4_load_100 | 118 | 0.0016649 | 0.00041726 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2580-4_0_4_load_103 | 119 | 0.0015881 | 0.00039801 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2580-4_0_4_load_116 | 120 | 0.0017891 | 0.0004484 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 115 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2580-4_0_4_line_0 |  | 0 | 1 | 0.001423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2580-4_0_4_line_1 |  | 0 | 2 | 0.010039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2580-4_0_4_line_2 |  | 1 | 3 | 0.017874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2580-4_0_4_line_3 |  | 2 | 4 | 0.010369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2580-4_0_4_line_4 |  | 3 | 5 | 0.030624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2580-4_0_4_line_5 |  | 5 | 8 | 0.026958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2580-4_0_4_line_6 |  | 6 | 7 | 0.052329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2580-4_0_4_line_7 |  | 7 | 13 | 0.047807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2580-4_0_4_line_8 |  | 8 | 14 | 0.043478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2580-4_0_4_line_9 |  | 8 | 15 | 0.005911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2580-4_0_4_line_10 |  | 8 | 12 | 0.02746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2580-4_0_4_line_11 |  | 9 | 10 | 0.007254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2580-4_0_4_line_12 |  | 9 | 11 | 0.017843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2580-4_0_4_line_13 |  | 9 | 12 | 0.034391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2580-4_0_4_line_14 |  | 10 | 16 | 0.020059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2580-4_0_4_line_15 |  | 10 | 17 | 0.031379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2580-4_0_4_line_16 |  | 11 | 18 | 0.02441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2580-4_0_4_line_17 |  | 13 | 48 | 0.0094942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2580-4_0_4_line_18 |  | 14 | 38 | 0.0010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2580-4_0_4_line_19 |  | 15 | 39 | 0.037058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2580-4_0_4_line_20 |  | 15 | 40 | 0.02848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2580-4_0_4_line_21 |  | 16 | 41 | 0.001074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2580-4_0_4_line_22 |  | 17 | 42 | 0.025673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2580-4_0_4_line_23 |  | 19 | 20 | 0.043767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2580-4_0_4_line_24 |  | 20 | 21 | 0.012203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2580-4_0_4_line_25 |  | 21 | 22 | 0.038829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2580-4_0_4_line_26 |  | 22 | 25 | 0.025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2580-4_0_4_line_27 |  | 22 | 26 | 0.008557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2580-4_0_4_line_28 |  | 23 | 24 | 0.00059815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2580-4_0_4_line_29 |  | 24 | 27 | 0.018047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2580-4_0_4_line_30 |  | 25 | 27 | 0.011863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2580-4_0_4_line_31 |  | 26 | 28 | 0.014979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2580-4_0_4_line_32 |  | 26 | 29 | 0.032226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2580-4_0_4_line_33 |  | 27 | 30 | 0.042231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2580-4_0_4_line_34 |  | 29 | 95 | 0.036554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2580-4_0_4_line_35 |  | 30 | 50 | 0.020423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2580-4_0_4_line_36 |  | 31 | 32 | 0.0019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2580-4_0_4_line_37 |  | 32 | 33 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2580-4_0_4_line_38 |  | 33 | 36 | 0.031651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2580-4_0_4_line_39 |  | 34 | 35 | 0.049286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2580-4_0_4_line_40 |  | 34 | 36 | 0.018422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2580-4_0_4_line_41 |  | 36 | 37 | 0.020747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2580-4_0_4_line_42 |  | 37 | 113 | 0.026168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2580-4_0_4_line_43 |  | 39 | 43 | 0.0092624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2580-4_0_4_line_44 |  | 41 | 44 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2580-4_0_4_line_45 |  | 42 | 45 | 0.033127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2580-4_0_4_line_46 |  | 43 | 49 | 0.00012134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2580-4_0_4_line_47 |  | 44 | 115 | 0.0054112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2580-4_0_4_line_48 |  | 45 | 46 | 0.003687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2580-4_0_4_line_49 |  | 45 | 84 | 0.026228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2580-4_0_4_line_50 |  | 46 | 47 | 0.033842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2580-4_0_4_line_51 |  | 47 | 96 | 0.0082275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2580-4_0_4_line_52 |  | 48 | 57 | 0.034902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2580-4_0_4_line_53 |  | 49 | 76 | 0.0010209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2580-4_0_4_line_54 |  | 51 | 52 | 0.0015621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2580-4_0_4_line_55 |  | 51 | 53 | 0.0059695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2580-4_0_4_line_56 |  | 52 | 54 | 0.0044057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2580-4_0_4_line_57 |  | 53 | 55 | 0.018647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2580-4_0_4_line_58 |  | 54 | 56 | 0.0060267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2580-4_0_4_line_59 |  | 55 | 57 | 0.038366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2580-4_0_4_line_60 |  | 56 | 58 | 0.0058132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2580-4_0_4_line_61 |  | 58 | 59 | 0.035722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2580-4_0_4_line_62 |  | 59 | 75 | 0.016293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2580-4_0_4_line_63 |  | 59 | 70 | 0.015485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2580-4_0_4_line_64 |  | 60 | 61 | 0.0080986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2580-4_0_4_line_65 |  | 60 | 62 | 0.030711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2580-4_0_4_line_66 |  | 61 | 63 | 0.0010184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2580-4_0_4_line_67 |  | 62 | 64 | 0.022828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2580-4_0_4_line_68 |  | 62 | 65 | 0.022451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2580-4_0_4_line_69 |  | 63 | 66 | 0.00099403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2580-4_0_4_line_70 |  | 64 | 67 | 0.00085681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2580-4_0_4_line_71 |  | 64 | 68 | 0.066231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2580-4_0_4_line_72 |  | 65 | 69 | 0.045633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2580-4_0_4_line_73 |  | 66 | 70 | 0.0066696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2580-4_0_4_line_74 |  | 67 | 71 | 0.018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2580-4_0_4_line_75 |  | 68 | 72 | 0.030889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2580-4_0_4_line_76 |  | 68 | 73 | 0.026751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2580-4_0_4_line_77 |  | 71 | 74 | 0.008751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2580-4_0_4_line_78 |  | 73 | 110 | 0.0084972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2580-4_0_4_line_79 |  | 74 | 109 | 0.010587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2580-4_0_4_line_80 |  | 75 | 76 | 8.1519e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2580-4_0_4_line_81 |  | 77 | 78 | 0.031756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2580-4_0_4_line_82 |  | 77 | 79 | 0.0032028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2580-4_0_4_line_83 |  | 78 | 80 | 0.010282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2580-4_0_4_line_84 |  | 79 | 81 | 0.021034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2580-4_0_4_line_85 |  | 80 | 82 | 0.02085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2580-4_0_4_line_86 |  | 81 | 83 | 0.024332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2580-4_0_4_line_87 |  | 82 | 84 | 0.022518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2580-4_0_4_line_88 |  | 82 | 85 | 0.015653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2580-4_0_4_line_89 |  | 83 | 86 | 0.007651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2580-4_0_4_line_90 |  | 84 | 87 | 0.028343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2580-4_0_4_line_91 |  | 85 | 88 | 0.0047378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2580-4_0_4_line_92 |  | 86 | 89 | 0.011783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2580-4_0_4_line_93 |  | 87 | 94 | 0.0066054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2580-4_0_4_line_94 |  | 88 | 93 | 0.028609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2580-4_0_4_line_95 |  | 89 | 92 | 0.023327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2580-4_0_4_line_96 |  | 90 | 91 | 0.029364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2580-4_0_4_line_97 |  | 90 | 92 | 0.014682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2580-4_0_4_line_98 |  | 94 | 95 | 0.028175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2580-4_0_4_line_99 |  | 95 | 112 | 0.018864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2580-4_0_4_line_100 |  | 97 | 98 | 0.0093058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2580-4_0_4_line_101 |  | 97 | 99 | 0.0093508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2580-4_0_4_line_102 |  | 98 | 100 | 0.0022369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2580-4_0_4_line_103 |  | 99 | 101 | 0.0019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2580-4_0_4_line_104 |  | 100 | 102 | 0.0079641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2580-4_0_4_line_105 |  | 101 | 103 | 0.0027527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2580-4_0_4_line_106 |  | 102 | 104 | 0.013474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2580-4_0_4_line_107 |  | 102 | 105 | 0.0033178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2580-4_0_4_line_108 |  | 103 | 106 | 0.0009237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2580-4_0_4_line_109 |  | 104 | 107 | 0.0072863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2580-4_0_4_line_110 |  | 106 | 108 | 0.0039526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2580-4_0_4_line_111 |  | 108 | 119 | 0.00020407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2580-4_0_4_line_112 |  | 109 | 111 | 0.019862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2580-4_0_4_line_113 |  | 111 | 114 | 0.0043179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2580-4_0_4_line_114 |  | 112 | 113 | 0.0047451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2580-4_0_4_line_115 |  | 114 | 120 | 0.009359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2580-4_0_4_line_116 |  | 115 | 116 | 0.0051998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2580-4_0_4_line_117 |  | 116 | 117 | 0.0039498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2580-4_0_4_line_118 |  | 117 | 118 | 0.0039498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2580-4_0_4_line_119 |  | 118 | 119 | 0.0040452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2580-4_0_4_trafo_95 | 0.63 MVA 20/0.4 kV | 121 | 115 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2630656.3958 | 1241747.0456 | 2630655.5297 | 1241748.1746
1 | 2630656.3958 | 1241747.0456 | 2630656.7212 | 1241746.6214 | 2630663.2053 | 1241739.6726
2 | 2630646.0901 | 1241763.1882 | 2630648.532 | 1241757.297 | 2630655.5297 | 1241748.1746
3 | 2630672.7419 | 1241735.8692 | 2630667.2015 | 1241737.3028 | 2630663.2053 | 1241739.6726 | 2630663.2053 | 1241739.6726
4 | 2630646.0901 | 1241763.1882 | 2630672.4421 | 1241778.7891
5 | 2630695.7569 | 1241792.3186 | 2630688.6034 | 1241788.3569 | 2630672.4421 | 1241778.7891
6 | 2630608.8754 | 1241861.3367 | 2630614.8973 | 1241844.3014 | 2630627.4935 | 1241812.4401
7 | 2630608.8754 | 1241861.3367 | 2630653.3152 | 1241879.2883
8 | 2630695.7569 | 1241792.3186 | 2630690.9573 | 1241802.4336 | 2630685.3605 | 1241817.6143 | 2630678.55 | 1241832.2061
9 | 2630701.333 | 1241794.3264 | 2630695.7569 | 1241792.3186
10 | 2630695.7569 | 1241792.3186 | 2630703.6262 | 1241766.0099
11 | 2630719.0201 | 1241731.878 | 2630711.7818 | 1241732.6078
12 | 2630711.7818 | 1241732.6078 | 2630714.7826 | 1241715.0189
13 | 2630711.7818 | 1241732.6078 | 2630704.9878 | 1241761.4577 | 2630703.6262 | 1241766.0099
14 | 2630719.0201 | 1241731.878 | 2630734.1928 | 1241731.7564 | 2630739.0783 | 1241731.7989
15 | 2630719.0201 | 1241731.878 | 2630724.0302 | 1241700.9019
16 | 2630714.7826 | 1241715.0189 | 2630717.8938 | 1241696.7832 | 2630719.3298 | 1241691.0499
17 | 2630653.3152 | 1241879.2883 | 2630658.0681 | 1241881.1251 | 2630660.28 | 1241877.323
18 | 2630678.55 | 1241832.2061 | 2630678.1031 | 1241833.1638
19 | 2630701.333 | 1241794.3264 | 2630735.6255 | 1241808.3739
20 | 2630701.333 | 1241794.3264 | 2630709.3026 | 1241769.096 | 2630709.8599 | 1241767.1535
21 | 2630740.1523 | 1241731.8083 | 2630739.0783 | 1241731.7989
22 | 2630730.1903 | 1241675.9959 | 2630729.6425 | 1241677.565 | 2630724.4554 | 1241698.2736 | 2630724.0302 | 1241700.9019
23 | 2630902.7836 | 1241657.2091 | 2630880.8524 | 1241643.7493 | 2630872.4237 | 1241659.6934
24 | 2630878.8845 | 1241670.0452 | 2630872.4237 | 1241659.6934 | 2630872.4237 | 1241659.6934
25 | 2630866.4363 | 1241701.9003 | 2630883.5062 | 1241674.2269 | 2630879.7335 | 1241671.4055 | 2630878.8845 | 1241670.0452
26 | 2630866.4363 | 1241701.9003 | 2630887.1993 | 1241716.7832
27 | 2630859.4925 | 1241696.8722 | 2630866.4363 | 1241701.9003
28 | 2630906.9576 | 1241708.7499 | 2630907.2929 | 1241708.2546
29 | 2630896.8411 | 1241723.6944 | 2630906.9576 | 1241708.7499
30 | 2630896.8411 | 1241723.6944 | 2630887.1993 | 1241716.7832
31 | 2630859.4925 | 1241696.8722 | 2630853.4288 | 1241702.8668 | 2630848.8455 | 1241707.4091
32 | 2630859.4925 | 1241696.8722 | 2630838.9306 | 1241680.7997 | 2630834.2379 | 1241676.8593
33 | 2630896.8411 | 1241723.6944 | 2630932.7459 | 1241746.0954
34 | 2630805.4576 | 1241654.3538 | 2630821.1974 | 1241665.9094 | 2630834.2379 | 1241676.8593
35 | 2630932.7459 | 1241746.0954 | 2630944.3368 | 1241729.2806
36 | 2630889.1482 | 1241594.6239 | 2630888.064 | 1241596.2153
37 | 2630874.4422 | 1241616.21 | 2630888.064 | 1241596.2153
38 | 2630848.2719 | 1241598.4076 | 2630874.4422 | 1241616.21
39 | 2630858.1344 | 1241582.8481 | 2630816.4283 | 1241556.3927
40 | 2630858.1344 | 1241582.8481 | 2630848.2719 | 1241598.4076
41 | 2630836.5682 | 1241615.5197 | 2630842.1964 | 1241607.9925 | 2630848.2719 | 1241598.4076
42 | 2630836.5682 | 1241615.5197 | 2630826.073 | 1241629.5559 | 2630820.6405 | 1241636.2772
43 | 2630735.6255 | 1241808.3739 | 2630744.1966 | 1241811.885
44 | 2630753.1024 | 1241733.1612 | 2630746.7714 | 1241731.8659 | 2630740.1523 | 1241731.8083
45 | 2630742.7361 | 1241645.3789 | 2630735.2057 | 1241661.6281 | 2630730.1903 | 1241675.9959
46 | 2630744.3089 | 1241811.931 | 2630744.1966 | 1241811.885
47 | 2630758.4038 | 1241734.2458 | 2630753.1024 | 1241733.1612
48 | 2630742.7361 | 1241645.3789 | 2630739.6928 | 1241643.284
49 | 2630742.7361 | 1241645.3789 | 2630746.7506 | 1241636.5496 | 2630749.9512 | 1241628.7056 | 2630752.3119 | 1241621.0018
50 | 2630739.6928 | 1241643.284 | 2630734.961 | 1241640.2465 | 2630710.2754 | 1241627.711 | 2630709.7423 | 1241627.7082
51 | 2630702.2061 | 1241629.7817 | 2630705.0442 | 1241627.6839 | 2630709.7423 | 1241627.7082
52 | 2630660.28 | 1241877.323 | 2630693.2709 | 1241888.715
53 | 2630745.2536 | 1241812.318 | 2630744.3089 | 1241811.931
54 | 2630734.7572 | 1241864.7787 | 2630735.5435 | 1241863.4289
55 | 2630734.7572 | 1241864.7787 | 2630731.7522 | 1241869.9367
56 | 2630735.5435 | 1241863.4289 | 2630737.7613 | 1241859.6221
57 | 2630731.7522 | 1241869.9367 | 2630722.3654 | 1241886.0491 | 2630722.3654 | 1241886.0491
58 | 2630740.7951 | 1241854.4147 | 2630737.7613 | 1241859.6221
59 | 2630722.3654 | 1241886.0491 | 2630714.0966 | 1241881.4367 | 2630707.4797 | 1241893.6214 | 2630693.2709 | 1241888.715
60 | 2630740.7951 | 1241854.4147 | 2630743.7214 | 1241849.3917 | 2630743.7214 | 1241849.3917
61 | 2630760.4061 | 1241818.525 | 2630743.4606 | 1241845.7324 | 2630743.7214 | 1241849.3917
62 | 2630760.4061 | 1241818.525 | 2630745.3291 | 1241812.3489
63 | 2630760.4061 | 1241818.525 | 2630774.818 | 1241824.1886
64 | 2630790.4358 | 1241830.3261 | 2630782.8984 | 1241827.3641
65 | 2630819.2699 | 1241840.7107 | 2630814.2483 | 1241839.684 | 2630790.4358 | 1241830.3261
66 | 2630781.9506 | 1241826.9916 | 2630782.8984 | 1241827.3641
67 | 2630819.2699 | 1241840.7107 | 2630824.7983 | 1241840.2391 | 2630828.8227 | 1241838.2587 | 2630832.3635 | 1241834.7637 | 2630836.461 | 1241828.1044
68 | 2630819.2699 | 1241840.7107 | 2630819.0009 | 1241845.946 | 2630809.8214 | 1241860.5019
69 | 2630781.9506 | 1241826.9916 | 2630781.0254 | 1241826.628
70 | 2630836.461 | 1241828.1044 | 2630836.9101 | 1241827.3747
71 | 2630836.461 | 1241828.1044 | 2630884.4746 | 1241873.7244
72 | 2630809.8214 | 1241860.5019 | 2630794.191 | 1241885.2869 | 2630785.8113 | 1241899.3036
73 | 2630781.0254 | 1241826.628 | 2630774.818 | 1241824.1886
74 | 2630846.7115 | 1241811.4455 | 2630836.9101 | 1241827.3747
75 | 2630884.4746 | 1241873.7244 | 2630866.352 | 1241898.7385
76 | 2630884.4746 | 1241873.7244 | 2630897.0888 | 1241856.3135 | 2630900.7069 | 1241852.5077 | 2630900.7069 | 1241852.5077
77 | 2630846.7115 | 1241811.4455 | 2630851.301 | 1241803.9868
78 | 2630900.7069 | 1241852.5077 | 2630904.119 | 1241850.513 | 2630908.6541 | 1241850.2164
79 | 2630851.301 | 1241803.9868 | 2630856.8313 | 1241794.9588
80 | 2630745.3291 | 1241812.3489 | 2630745.2536 | 1241812.318
81 | 2630702.2322 | 1241567.9883 | 2630703.0067 | 1241568.4802 | 2630719.9879 | 1241579.8085 | 2630728.9292 | 1241585.1697
82 | 2630702.2322 | 1241567.9883 | 2630699.5285 | 1241566.2713
83 | 2630728.9292 | 1241585.1697 | 2630735.4375 | 1241589.072 | 2630737.885 | 1241590.1952
84 | 2630681.7729 | 1241554.9953 | 2630699.5285 | 1241566.2713
85 | 2630756.8107 | 1241598.9444 | 2630746.6597 | 1241594.2222 | 2630737.885 | 1241590.1952
86 | 2630681.7729 | 1241554.9953 | 2630670.4852 | 1241563.9539 | 2630665.2065 | 1241572.3548
87 | 2630756.8107 | 1241598.9444 | 2630755.0351 | 1241608.986 | 2630752.3119 | 1241621.0018
88 | 2630756.8107 | 1241598.9444 | 2630759.8315 | 1241583.5852
89 | 2630661.1359 | 1241578.8331 | 2630665.2065 | 1241572.3548
90 | 2630752.3119 | 1241621.0018 | 2630761.5386 | 1241624.6407 | 2630768.115 | 1241627.6656 | 2630777.7337 | 1241633.3759
91 | 2630759.8315 | 1241583.5852 | 2630760.1027 | 1241582.2063 | 2630761.2009 | 1241579.0601
92 | 2630661.1359 | 1241578.8331 | 2630654.8668 | 1241588.8102
93 | 2630777.7337 | 1241633.3759 | 2630779.1484 | 1241634.2158 | 2630783.1334 | 1241637.1692
94 | 2630773.9465 | 1241553.5656 | 2630769.5973 | 1241560.3971 | 2630763.7016 | 1241571.8961 | 2630761.2009 | 1241579.0601
95 | 2630654.8668 | 1241588.8102 | 2630644.7064 | 1241604.9804 | 2630642.4292 | 1241608.5442
96 | 2630634.5241 | 1241620.916 | 2630618.7137 | 1241645.6599
97 | 2630634.5241 | 1241620.916 | 2630642.4292 | 1241608.5442
98 | 2630805.4576 | 1241654.3538 | 2630791.6721 | 1241643.4976 | 2630783.1334 | 1241637.1692
99 | 2630805.4576 | 1241654.3538 | 2630814.7439 | 1241643.5728 | 2630817.6577 | 1241639.9676
100 | 2630793.632 | 1241742.6239 | 2630796.5581 | 1241743.6423 | 2630802.7649 | 1241743.7398
101 | 2630793.632 | 1241742.6239 | 2630789.2612 | 1241741.1029 | 2630784.6542 | 1241740.063
102 | 2630805.0015 | 1241743.775 | 2630802.7649 | 1241743.7398
103 | 2630782.7907 | 1241739.6424 | 2630784.6542 | 1241740.063
104 | 2630812.7001 | 1241741.7358 | 2630805.0015 | 1241743.775
105 | 2630782.7907 | 1241739.6424 | 2630780.1055 | 1241739.0364
106 | 2630812.7001 | 1241741.7358 | 2630816.0992 | 1241745.1778 | 2630822.3758 | 1241751.1103
107 | 2630812.7001 | 1241741.7358 | 2630815.5518 | 1241740.0401
108 | 2630780.1055 | 1241739.0364 | 2630779.2045 | 1241738.833
109 | 2630827.7397 | 1241756.04 | 2630825.5853 | 1241754.1439 | 2630822.3758 | 1241751.1103
110 | 2630779.2045 | 1241738.833 | 2630775.3489 | 1241737.9628
111 | 2630775.3489 | 1241737.9628 | 2630775.1498 | 1241737.9178
112 | 2630867.2063 | 1241778.022 | 2630856.8313 | 1241794.9588
113 | 2630869.4617 | 1241774.34 | 2630867.2063 | 1241778.022
114 | 2630817.6577 | 1241639.9676 | 2630820.6405 | 1241636.2772
115 | 2630869.4617 | 1241774.34 | 2630874.364 | 1241766.3603
116 | 2630758.4038 | 1241734.2458 | 2630763.4981 | 1241735.288 | 2630763.4981 | 1241735.288
117 | 2630763.4981 | 1241735.288 | 2630767.351 | 1241736.1576
118 | 2630771.2039 | 1241737.0272 | 2630767.351 | 1241736.1576
119 | 2630771.2039 | 1241737.0272 | 2630775.1498 | 1241737.9178

## bus_geodata
| x | y | coords
0 | 2630656.3958 | 1241747.0456
1 | 2630655.5297 | 1241748.1746
2 | 2630663.2053 | 1241739.6726
3 | 2630646.0901 | 1241763.1882
4 | 2630672.7419 | 1241735.8692
5 | 2630672.4421 | 1241778.7891
6 | 2630627.4935 | 1241812.4401
7 | 2630608.8754 | 1241861.3367
8 | 2630695.7569 | 1241792.3186
9 | 2630711.7818 | 1241732.6078
10 | 2630719.0201 | 1241731.878
11 | 2630714.7826 | 1241715.0189
12 | 2630703.6262 | 1241766.0099
13 | 2630653.3152 | 1241879.2883
14 | 2630678.55 | 1241832.2061
15 | 2630701.333 | 1241794.3264
16 | 2630739.0783 | 1241731.7989
17 | 2630724.0302 | 1241700.9019
18 | 2630719.3298 | 1241691.0499
19 | 2630902.7836 | 1241657.2091
20 | 2630872.4237 | 1241659.6934
21 | 2630878.8845 | 1241670.0452
22 | 2630866.4363 | 1241701.9003
23 | 2630907.2929 | 1241708.2546
24 | 2630906.9576 | 1241708.7499
25 | 2630887.1993 | 1241716.7832
26 | 2630859.4925 | 1241696.8722
27 | 2630896.8411 | 1241723.6944
28 | 2630848.8455 | 1241707.4091
29 | 2630834.2379 | 1241676.8593
30 | 2630932.7459 | 1241746.0954
31 | 2630889.1482 | 1241594.6239
32 | 2630888.064 | 1241596.2153
33 | 2630874.4422 | 1241616.21
34 | 2630858.1344 | 1241582.8481
35 | 2630816.4283 | 1241556.3927
36 | 2630848.2719 | 1241598.4076
37 | 2630836.5682 | 1241615.5197
38 | 2630678.1031 | 1241833.1638
39 | 2630735.6255 | 1241808.3739
40 | 2630709.8599 | 1241767.1535
41 | 2630740.1523 | 1241731.8083
42 | 2630730.1903 | 1241675.9959
43 | 2630744.1966 | 1241811.885
44 | 2630753.1024 | 1241733.1612
45 | 2630742.7361 | 1241645.3789
46 | 2630739.6928 | 1241643.2841
47 | 2630709.7423 | 1241627.7082
48 | 2630660.28 | 1241877.323
49 | 2630744.3089 | 1241811.931
50 | 2630944.3368 | 1241729.2806
51 | 2630734.7572 | 1241864.7787
52 | 2630735.5435 | 1241863.4289
53 | 2630731.7522 | 1241869.9367
54 | 2630737.7613 | 1241859.6221
55 | 2630722.3654 | 1241886.0491
56 | 2630740.7951 | 1241854.4147
57 | 2630693.2709 | 1241888.715
58 | 2630743.7214 | 1241849.3917
59 | 2630760.4061 | 1241818.525
60 | 2630790.4358 | 1241830.3261
61 | 2630782.8984 | 1241827.3641
62 | 2630819.2699 | 1241840.7107
63 | 2630781.9506 | 1241826.9916
64 | 2630836.461 | 1241828.1044
65 | 2630809.8214 | 1241860.5019
66 | 2630781.0254 | 1241826.628
67 | 2630836.9101 | 1241827.3747
68 | 2630884.4746 | 1241873.7244
69 | 2630785.8113 | 1241899.3036
70 | 2630774.818 | 1241824.1886
71 | 2630846.7115 | 1241811.4455
72 | 2630866.352 | 1241898.7385
73 | 2630900.7069 | 1241852.5077
74 | 2630851.301 | 1241803.9868
75 | 2630745.3291 | 1241812.3489
76 | 2630745.2536 | 1241812.318
77 | 2630702.2322 | 1241567.9883
78 | 2630728.9292 | 1241585.1697
79 | 2630699.5285 | 1241566.2713
80 | 2630737.885 | 1241590.1952
81 | 2630681.7729 | 1241554.9953
82 | 2630756.8107 | 1241598.9444
83 | 2630665.2065 | 1241572.3548
84 | 2630752.3119 | 1241621.0018
85 | 2630759.8315 | 1241583.5852
86 | 2630661.1359 | 1241578.8331
87 | 2630777.7337 | 1241633.3759
88 | 2630761.2009 | 1241579.0601
89 | 2630654.8668 | 1241588.8102
90 | 2630634.5241 | 1241620.916
91 | 2630618.7137 | 1241645.6599
92 | 2630642.4292 | 1241608.5442
93 | 2630773.9465 | 1241553.5656
94 | 2630783.1334 | 1241637.1692
95 | 2630805.4576 | 1241654.3538
96 | 2630702.2061 | 1241629.7817
97 | 2630793.632 | 1241742.6239
98 | 2630802.7649 | 1241743.7398
99 | 2630784.6542 | 1241740.063
100 | 2630805.0015 | 1241743.775
101 | 2630782.7907 | 1241739.6424
102 | 2630812.7001 | 1241741.7358
103 | 2630780.1055 | 1241739.0364
104 | 2630822.3758 | 1241751.1103
105 | 2630815.5518 | 1241740.0401
106 | 2630779.2045 | 1241738.833
107 | 2630827.7397 | 1241756.04
108 | 2630775.3489 | 1241737.9628
109 | 2630856.8313 | 1241794.9588
110 | 2630908.6541 | 1241850.2164
111 | 2630867.2063 | 1241778.022
112 | 2630817.6577 | 1241639.9676
113 | 2630820.6405 | 1241636.2772
114 | 2630869.4617 | 1241774.34
115 | 2630758.4038 | 1241734.2458
116 | 2630763.4981 | 1241735.288
117 | 2630767.351 | 1241736.1576
118 | 2630771.2039 | 1241737.0272
119 | 2630775.1498 | 1241737.9178
120 | 2630874.364 | 1241766.3603
121 | 2630719.0201 | 1241731.878

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99032 | -0.18442 | 0.0021795 | 0.00054624
1 | 0.99033 | -0.18423 | 0.004011 | 0.0010053
2 | 0.99028 | -0.18536 | 0.0024177 | 0.00060594
3 | 0.99052 | -0.18058 | 0 | 0
4 | 0.99025 | -0.18589 | 0.0028775 | 0.00072116
5 | 0.99084 | -0.17433 | 0.0042391 | 0.0010624
6 | 0.97946 | -0.39503 | 0.0021551 | 0.00054012
7 | 0.97957 | -0.39298 | 0 | 0
8 | 0.99123 | -0.16681 | 0 | 0
9 | 0.99512 | -0.092495 | 0 | 0
10 | 0.99555 | -0.084394 | 0 | 0
11 | 0.99477 | -0.099204 | 0.0025915 | 0.0006495
12 | 0.99333 | -0.12667 | 0.0039369 | 0.00098669
13 | 0.97966 | -0.39111 | 0 | 0
14 | 0.99103 | -0.17066 | 0.0027951 | 0.00070051
15 | 0.99084 | -0.17438 | 0 | 0
16 | 0.99778 | -0.041887 | 0.002216 | 0.00055538
17 | 0.99389 | -0.11606 | 0.0025574 | 0.00064094
18 | 0.99436 | -0.10727 | 0.018762 | 0.0047022
19 | 0.98146 | -0.35651 | 0.010288 | 0.0025784
20 | 0.98188 | -0.34836 | 0.0038005 | 0.0009525
21 | 0.98204 | -0.34525 | 0.0012434 | 0.00031161
22 | 0.98259 | -0.3345 | 0 | 0
23 | 0.98221 | -0.34186 | 0.0004335 | 0.00010864
24 | 0.98221 | -0.34186 | 0.0048141 | 0.0012065
25 | 0.98237 | -0.33874 | 0.0026165 | 0.00065577
26 | 0.98278 | -0.33071 | 0 | 0
27 | 0.9823 | -0.34015 | 0 | 0
28 | 0.98275 | -0.33133 | 0.0023086 | 0.00057858
29 | 0.98358 | -0.31511 | 0.0068455 | 0.0017156
30 | 0.98225 | -0.34116 | 0 | 0
31 | 0.98195 | -0.34692 | 0.0019427 | 0.00048689
32 | 0.98195 | -0.34685 | 0.013447 | 0.0033701
33 | 0.9823 | -0.34012 | 0.0036699 | 0.00091976
34 | 0.98282 | -0.32989 | 0 | 0
35 | 0.98273 | -0.33168 | 0.002004 | 0.00050224
36 | 0.98286 | -0.32923 | 0.0033908 | 0.00084982
37 | 0.98332 | -0.32008 | 0.0024344 | 0.00061013
38 | 0.99103 | -0.1707 | 0.0021912 | 0.00054917
39 | 0.98608 | -0.26597 | 0.0071926 | 0.0018026
40 | 0.99068 | -0.17736 | 0.0058798 | 0.0014736
41 | 0.99791 | -0.039603 | 0.0026825 | 0.00067229
42 | 0.99255 | -0.14166 | 0.00092875 | 0.00023277
43 | 0.98495 | -0.2878 | 0.0014724 | 0.00036903
44 | 0.99938 | -0.011618 | 0.0021151 | 0.00053009
45 | 0.99083 | -0.17461 | 0 | 0
46 | 0.9908 | -0.17513 | 0 | 0
47 | 0.99056 | -0.17989 | 0.0012464 | 0.00031238
48 | 0.97968 | -0.39074 | 0 | 0
49 | 0.98494 | -0.28809 | 0.0016663 | 0.00041762
50 | 0.98222 | -0.34165 | 0.0013275 | 0.00033271
51 | 0.98081 | -0.3686 | 0.0019493 | 0.00048854
52 | 0.98085 | -0.36783 | 0.011431 | 0.002865
53 | 0.98067 | -0.3713 | 0.0019661 | 0.00049275
54 | 0.981 | -0.36477 | 0.0019638 | 0.00049217
55 | 0.98027 | -0.3791 | 0.0082971 | 0.0020794
56 | 0.98123 | -0.36036 | 0.0019902 | 0.00049879
57 | 0.97975 | -0.38937 | 0.012594 | 0.0031563
58 | 0.98146 | -0.35591 | 0.0019882 | 0.00049828
59 | 0.98292 | -0.32729 | 0 | 0
60 | 0.98059 | -0.3727 | 0.0031845 | 0.0007981
61 | 0.98114 | -0.36206 | 0.0019952 | 0.00050005
62 | 0.97862 | -0.4114 | 0 | 0
63 | 0.98121 | -0.36068 | 0.0019476 | 0.00048811
64 | 0.97768 | -0.4297 | 0.008841 | 0.0022158
65 | 0.97809 | -0.42176 | 0.014141 | 0.0035441
66 | 0.98128 | -0.35931 | 0.0019521 | 0.00048924
67 | 0.97767 | -0.42999 | 0.0087723 | 0.0021985
68 | 0.97667 | -0.44964 | 0.005161 | 0.0012935
69 | 0.97761 | -0.43109 | 0.011211 | 0.0028097
70 | 0.98176 | -0.34984 | 0.0021741 | 0.00054487
71 | 0.9775 | -0.43338 | 0 | 0
72 | 0.97652 | -0.45254 | 0.005147 | 0.00129
73 | 0.97652 | -0.45266 | 0.005116 | 0.0012822
74 | 0.97742 | -0.43496 | 0 | 0
75 | 0.98481 | -0.29063 | 0.0019868 | 0.00049793
76 | 0.98482 | -0.29044 | 0.0012522 | 0.00031384
77 | 0.98296 | -0.32689 | 0.0061054 | 0.0015302
78 | 0.98493 | -0.28844 | 0.0068396 | 0.0017142
79 | 0.98278 | -0.33042 | 0.0013102 | 0.00032836
80 | 0.98564 | -0.27477 | 0.0015965 | 0.00040013
81 | 0.98161 | -0.35316 | 0 | 0
82 | 0.9871 | -0.2465 | 0 | 0
83 | 0.98026 | -0.37953 | 0.0089155 | 0.0022344
84 | 0.98889 | -0.21205 | 0 | 0
85 | 0.98696 | -0.24929 | 0.0028471 | 0.00071356
86 | 0.9799 | -0.3866 | 0.0048931 | 0.0012263
87 | 0.98693 | -0.2499 | 0.002171 | 0.0005441
88 | 0.98693 | -0.2499 | 0.0046805 | 0.0011731
89 | 0.9794 | -0.39645 | 0.0089187 | 0.0022352
90 | 0.97828 | -0.41837 | 0.0091533 | 0.002294
91 | 0.9779 | -0.42583 | 0.013948 | 0.0034956
92 | 0.9786 | -0.41219 | 0.014002 | 0.0035092
93 | 0.98686 | -0.25116 | 0.0024587 | 0.0006162
94 | 0.98649 | -0.25849 | 0.0044324 | 0.0011109
95 | 0.98471 | -0.29295 | 0 | 0
96 | 0.99051 | -0.18087 | 0.006671 | 0.0016719
97 | 0.99932 | -0.013125 | 0.0012586 | 0.00031545
98 | 0.99921 | -0.015276 | 0.00091927 | 0.00023039
99 | 0.99944 | -0.010759 | 0.0012618 | 0.00031624
100 | 0.99918 | -0.015757 | 0.0055326 | 0.0013866
101 | 0.99947 | -0.010234 | 0.0014784 | 0.00037053
102 | 0.99913 | -0.016701 | 0 | 0
103 | 0.99951 | -0.0094056 | 0.0012477 | 0.00031271
104 | 0.99906 | -0.018052 | 0.0034288 | 0.00085934
105 | 0.99913 | -0.016761 | 0.0010422 | 0.00026119
106 | 0.99953 | -0.0091077 | 0.0014409 | 0.00036113
107 | 0.99905 | -0.018347 | 0.0023162 | 0.00058048
108 | 0.9996 | -0.0077336 | 0.0016693 | 0.00041836
109 | 0.97732 | -0.43687 | 0.0036237 | 0.00090819
110 | 0.97651 | -0.45282 | 0.001063 | 0.0002664
111 | 0.9772 | -0.43915 | 0.004498 | 0.0011273
112 | 0.98411 | -0.30466 | 0.0023776 | 0.00059588
113 | 0.98397 | -0.3074 | 0.0052184 | 0.0013079
114 | 0.9772 | -0.43929 | 0 | 0
115 | 1 | 0 | -0.40433 | -0.10318
116 | 0.99987 | -0.002498 | 0.0012613 | 0.0003161
117 | 0.99978 | -0.0043091 | 0.0014466 | 0.00036255
118 | 0.99969 | -0.0060208 | 0.0016649 | 0.00041726
119 | 0.9996 | -0.0076567 | 0.0015881 | 0.00039801
120 | 0.97718 | -0.4396 | 0.0017891 | 0.0004484
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.007475 | -0.0018733 | 0.0074751 | 0.0018733 | 6.7315e-08 | 2.4773e-08 | 0.011232 | 0.011232 | 0.011232 | 0.99032 | -0.18442 | 0.99033 | -0.18423 | 3.0856
1 | 0.0052955 | 0.001327 | -0.0052953 | -0.001327 | 2.3833e-07 | 2.3374e-08 | 0.0079567 | 0.0079568 | 0.0079568 | 0.99032 | -0.18442 | 0.99028 | -0.18536 | 2.1859
2 | -0.011486 | -0.0028786 | 0.011488 | 0.0028796 | 1.9964e-06 | 1.0477e-06 | 0.017258 | 0.017258 | 0.017258 | 0.99033 | -0.18423 | 0.99052 | -0.18058 | 4.7413
3 | 0.0028775 | 0.00072107 | -0.0028775 | -0.00072116 | 7.2695e-08 | -8.6871e-08 | 0.0043238 | 0.0043239 | 0.0043239 | 0.99028 | -0.18536 | 0.99025 | -0.18589 | 1.1879
4 | -0.011488 | -0.0028796 | 0.011492 | 0.0028814 | 3.4204e-06 | 1.7948e-06 | 0.017258 | 0.017258 | 0.017258 | 0.99052 | -0.18058 | 0.99084 | -0.17433 | 4.7413
5 | -0.015731 | -0.0039438 | 0.015736 | 0.0039471 | 5.642e-06 | 3.2635e-06 | 0.023624 | 0.023624 | 0.023624 | 0.99084 | -0.17433 | 0.99123 | -0.16681 | 6.4902
6 | -0.0021551 | -0.00054012 | 0.0021553 | 0.0005396 | 2.1034e-07 | -5.2406e-07 | 0.0032741 | 0.0032738 | 0.0032741 | 0.97946 | -0.39503 | 0.97957 | -0.39298 | 0.89947
7 | -0.0021553 | -0.0005396 | 0.0021555 | 0.00053912 | 1.9214e-07 | -4.7892e-07 | 0.0032738 | 0.0032736 | 0.0032738 | 0.97957 | -0.39298 | 0.97966 | -0.39111 | 0.89941
8 | 0.0049872 | 0.0012497 | -0.0049863 | -0.0012497 | 9.1388e-07 | 2.4546e-08 | 0.0074866 | 0.0074868 | 0.0074868 | 0.99123 | -0.16681 | 0.99103 | -0.17066 | 2.0568
9 | 0.14593 | 0.037158 | -0.14587 | -0.037124 | 5.3288e-05 | 3.3952e-05 | 0.21927 | 0.21927 | 0.21927 | 0.99123 | -0.16681 | 0.99084 | -0.17438 | 30.1199
10 | -0.16665 | -0.042355 | 0.16697 | 0.042561 | 0.00032279 | 0.00020587 | 0.25038 | 0.25038 | 0.25038 | 0.99123 | -0.16681 | 0.99333 | -0.12667 | 34.3933
11 | -0.19256 | -0.049087 | 0.19264 | 0.049135 | 7.5331e-05 | 4.7929e-05 | 0.28823 | 0.28823 | 0.28823 | 0.99512 | -0.092495 | 0.99555 | -0.084394 | 26.3949
12 | 0.021368 | 0.0053602 | -0.021361 | -0.005356 | 6.8316e-06 | 4.1405e-06 | 0.031953 | 0.031953 | 0.031953 | 0.99512 | -0.092495 | 0.99477 | -0.099204 | 8.7783
13 | 0.17119 | 0.043727 | -0.17091 | -0.043547 | 0.00028234 | 0.00017936 | 0.25628 | 0.25628 | 0.25628 | 0.99512 | -0.092495 | 0.99333 | -0.12667 | 23.4689
14 | -0.36659 | -0.093537 | 0.36734 | 0.094019 | 0.00075439 | 0.00048202 | 0.54852 | 0.54851 | 0.54852 | 0.99555 | -0.084394 | 0.99778 | -0.041887 | 50.2303
15 | 0.17395 | 0.044402 | -0.17368 | -0.044233 | 0.00026573 | 0.00016884 | 0.26028 | 0.26028 | 0.26028 | 0.99555 | -0.084394 | 0.99389 | -0.11606 | 23.8355
16 | 0.018769 | 0.0047065 | -0.018762 | -0.0047022 | 7.2157e-06 | 4.3013e-06 | 0.028077 | 0.028077 | 0.028077 | 0.99477 | -0.099204 | 0.99436 | -0.10727 | 7.7134
17 | -0.0021555 | -0.00053912 | 0.0021555 | 0.00053902 | 3.8154e-08 | -9.5126e-08 | 0.0032736 | 0.0032736 | 0.0032736 | 0.97966 | -0.39111 | 0.97968 | -0.39074 | 0.89935
18 | 0.0021912 | 0.00054916 | -0.0021912 | -0.00054917 | 4.2898e-09 | -1.0872e-08 | 0.0032901 | 0.0032901 | 0.0032901 | 0.99103 | -0.17066 | 0.99103 | -0.1707 | 0.90387
19 | 0.13999 | 0.03565 | -0.13938 | -0.035257 | 0.00061543 | 0.0003934 | 0.21044 | 0.21044 | 0.21044 | 0.99084 | -0.17438 | 0.98608 | -0.26597 | 57.8136
20 | 0.0058806 | 0.0014738 | -0.0058798 | -0.0014736 | 8.3298e-07 | 1.6634e-07 | 0.0088314 | 0.0088315 | 0.0088315 | 0.99084 | -0.17438 | 0.99068 | -0.17736 | 2.4262
21 | -0.36956 | -0.094574 | 0.3696 | 0.094601 | 4.0881e-05 | 2.6122e-05 | 0.55182 | 0.55182 | 0.55182 | 0.99778 | -0.041887 | 0.99791 | -0.039603 | 50.5329
22 | 0.17113 | 0.043592 | -0.17091 | -0.043458 | 0.00021106 | 0.00013408 | 0.25645 | 0.25645 | 0.25645 | 0.99389 | -0.11606 | 0.99255 | -0.14166 | 23.4849
23 | -0.010288 | -0.0025784 | 0.010292 | 0.0025804 | 3.9931e-06 | 2.0022e-06 | 0.015598 | 0.015598 | 0.015598 | 0.98146 | -0.35651 | 0.98188 | -0.34836 | 4.2851
24 | -0.014093 | -0.0035329 | 0.014095 | 0.0035341 | 2.0872e-06 | 1.1815e-06 | 0.021357 | 0.021357 | 0.021357 | 0.98188 | -0.34836 | 0.98204 | -0.34525 | 5.8674
25 | -0.015338 | -0.0038457 | 0.015346 | 0.0038503 | 7.8651e-06 | 4.5421e-06 | 0.023241 | 0.023241 | 0.023241 | 0.98204 | -0.34525 | 0.98259 | -0.3345 | 6.385
26 | 0.0091945 | 0.002304 | -0.0091927 | -0.0023031 | 1.8573e-06 | 8.6517e-07 | 0.013924 | 0.013924 | 0.013924 | 0.98259 | -0.3345 | 0.98237 | -0.33874 | 3.8253
27 | -0.02454 | -0.0061542 | 0.024545 | 0.0061569 | 4.4322e-06 | 2.7282e-06 | 0.037165 | 0.037165 | 0.037165 | 0.98259 | -0.3345 | 0.98278 | -0.33071 | 10.2102
28 | -0.0004335 | -0.00010864 | 0.0004335 | 0.00010864 | 9.713e-11 | -7.5087e-09 | 0.00065673 | 0.00065673 | 0.00065673 | 0.98221 | -0.34186 | 0.98221 | -0.34186 | 0.18042
29 | -0.0052476 | -0.0013152 | 0.005248 | 0.0013152 | 4.2771e-07 | 4.5307e-08 | 0.00795 | 0.0079499 | 0.00795 | 0.98221 | -0.34186 | 0.9823 | -0.34015 | 2.1841
30 | 0.0065761 | 0.0016473 | -0.0065757 | -0.0016472 | 4.4137e-07 | 1.323e-07 | 0.0099607 | 0.0099608 | 0.0099608 | 0.98237 | -0.33874 | 0.9823 | -0.34015 | 2.7365
31 | 0.0023086 | 0.00057843 | -0.0023086 | -0.00057858 | 6.8633e-08 | -1.4588e-07 | 0.0034954 | 0.0034955 | 0.0034955 | 0.98278 | -0.33071 | 0.98275 | -0.33133 | 0.96029
32 | -0.026853 | -0.0067354 | 0.026873 | 0.0067478 | 1.9979e-05 | 1.2378e-05 | 0.04066 | 0.04066 | 0.04066 | 0.98278 | -0.33071 | 0.98358 | -0.31511 | 11.1704
33 | 0.0013276 | 0.00033198 | -0.0013276 | -0.00033247 | 6.4043e-08 | -4.9358e-07 | 0.0020109 | 0.0020111 | 0.0020111 | 0.9823 | -0.34015 | 0.98225 | -0.34116 | 0.55249
34 | -0.033719 | -0.0084634 | 0.033755 | 0.0084858 | 3.5677e-05 | 2.2369e-05 | 0.051016 | 0.051016 | 0.051016 | 0.98358 | -0.31511 | 0.98471 | -0.29295 | 14.0155
35 | 0.0013276 | 0.00033247 | -0.0013275 | -0.00033271 | 3.0975e-08 | -2.3867e-07 | 0.0020111 | 0.0020112 | 0.0020112 | 0.98225 | -0.34116 | 0.98222 | -0.34165 | 0.55251
36 | -0.0019427 | -0.00048689 | 0.0019427 | 0.00048687 | 6.2584e-09 | -2.0354e-08 | 0.0029439 | 0.0029439 | 0.0029439 | 0.98195 | -0.34692 | 0.98195 | -0.34685 | 0.80877
37 | -0.01539 | -0.003857 | 0.015395 | 0.0038599 | 4.9343e-06 | 2.8518e-06 | 0.023321 | 0.023321 | 0.023321 | 0.98195 | -0.34685 | 0.9823 | -0.34012 | 6.4069
38 | -0.019065 | -0.0047796 | 0.019074 | 0.0047856 | 9.8997e-06 | 5.9349e-06 | 0.02888 | 0.02888 | 0.02888 | 0.9823 | -0.34012 | 0.98286 | -0.32923 | 7.9341
39 | 0.0020041 | 0.00050173 | -0.002004 | -0.00050224 | 1.7016e-07 | -5.1561e-07 | 0.0030341 | 0.0030343 | 0.0030343 | 0.98282 | -0.32989 | 0.98273 | -0.33168 | 0.83361
40 | -0.0020041 | -0.00050173 | 0.0020042 | 0.00050153 | 6.3594e-08 | -1.9276e-07 | 0.0030341 | 0.003034 | 0.0030341 | 0.98282 | -0.32989 | 0.98286 | -0.32923 | 0.83355
41 | -0.024469 | -0.0061369 | 0.02448 | 0.0061435 | 1.0678e-05 | 6.5711e-06 | 0.037048 | 0.037048 | 0.037048 | 0.98286 | -0.32923 | 0.98332 | -0.32008 | 10.1779
42 | -0.026915 | -0.0067536 | 0.026931 | 0.0067637 | 1.628e-05 | 1.0087e-05 | 0.040731 | 0.040731 | 0.040731 | 0.98332 | -0.32008 | 0.98397 | -0.3074 | 11.19
43 | 0.13219 | 0.033454 | -0.13205 | -0.033366 | 0.00013836 | 8.8435e-05 | 0.19959 | 0.19959 | 0.19959 | 0.98608 | -0.26597 | 0.98495 | -0.2878 | 54.8318
44 | -0.37228 | -0.095273 | 0.37278 | 0.095596 | 0.00050517 | 0.00032279 | 0.55582 | 0.55582 | 0.55582 | 0.99791 | -0.039603 | 0.99938 | -0.011618 | 50.8992
45 | 0.16999 | 0.043226 | -0.16972 | -0.043054 | 0.0002694 | 0.00017113 | 0.25506 | 0.25506 | 0.25506 | 0.99255 | -0.14166 | 0.99083 | -0.17461 | 23.3574
46 | 0.13058 | 0.032997 | -0.13057 | -0.032996 | 1.7725e-06 | 1.1328e-06 | 0.19736 | 0.19736 | 0.19736 | 0.98495 | -0.2878 | 0.98494 | -0.28809 | 54.2207
47 | -0.3749 | -0.096126 | 0.37511 | 0.096261 | 0.00021134 | 0.00013504 | 0.55897 | 0.55897 | 0.55897 | 0.99938 | -0.011618 | 1 | 0 | 51.1876
48 | 0.0079197 | 0.0019852 | -0.0079195 | -0.0019851 | 1.9559e-07 | 7.7692e-08 | 0.011894 | 0.011894 | 0.011894 | 0.99083 | -0.17461 | 0.9908 | -0.17513 | 3.2675
49 | 0.1618 | 0.041069 | -0.16151 | -0.040884 | 0.0002908 | 0.00018544 | 0.24317 | 0.24317 | 0.24317 | 0.99083 | -0.17461 | 0.98889 | -0.21205 | 33.4024
50 | 0.0079195 | 0.0019851 | -0.0079177 | -0.0019844 | 1.7953e-06 | 7.1325e-07 | 0.011894 | 0.011894 | 0.011894 | 0.9908 | -0.17513 | 0.99056 | -0.17989 | 3.2676
51 | 0.0066713 | 0.001672 | -0.006671 | -0.0016719 | 3.0987e-07 | 9.2413e-08 | 0.010022 | 0.010022 | 0.010022 | 0.99056 | -0.17989 | 0.99051 | -0.18087 | 2.7532
52 | -0.0021555 | -0.00053902 | 0.0021557 | 0.00053867 | 1.4025e-07 | -3.4975e-07 | 0.0032736 | 0.0032734 | 0.0032736 | 0.97968 | -0.39074 | 0.97975 | -0.38937 | 0.89934
53 | 0.12891 | 0.032578 | -0.12889 | -0.032569 | 1.4535e-05 | 9.2894e-06 | 0.19485 | 0.19485 | 0.19485 | 0.98494 | -0.28809 | 0.98482 | -0.29044 | 53.5291
54 | -0.026981 | -0.0067671 | 0.026982 | 0.0067677 | 9.8161e-07 | 6.0851e-07 | 0.040936 | 0.040936 | 0.040936 | 0.98081 | -0.3686 | 0.98085 | -0.36783 | 11.246
55 | 0.025032 | 0.0062786 | -0.025029 | -0.0062766 | 3.2288e-06 | 1.9911e-06 | 0.037978 | 0.037978 | 0.037978 | 0.98081 | -0.3686 | 0.98067 | -0.3713 | 10.4336
56 | -0.038413 | -0.0096327 | 0.038419 | 0.0096362 | 5.6112e-06 | 3.5355e-06 | 0.058278 | 0.058278 | 0.058278 | 0.98085 | -0.36783 | 0.981 | -0.36477 | 16.0104
57 | 0.023062 | 0.0057838 | -0.023054 | -0.0057786 | 8.5637e-06 | 5.2456e-06 | 0.034995 | 0.034995 | 0.034995 | 0.98067 | -0.3713 | 0.98027 | -0.3791 | 9.614
58 | -0.040383 | -0.010128 | 0.040391 | 0.010134 | 8.4804e-06 | 5.3513e-06 | 0.061256 | 0.061256 | 0.061256 | 0.981 | -0.36477 | 0.98123 | -0.36036 | 16.8287
59 | 0.014757 | 0.0036991 | -0.01475 | -0.003695 | 7.2193e-06 | 4.1369e-06 | 0.022401 | 0.022401 | 0.022401 | 0.98027 | -0.3791 | 0.97975 | -0.38937 | 6.154
60 | -0.042381 | -0.010633 | 0.04239 | 0.010638 | 9.0059e-06 | 5.6903e-06 | 0.064275 | 0.064274 | 0.064275 | 0.98123 | -0.36036 | 0.98146 | -0.35591 | 17.6578
61 | -0.044379 | -0.011137 | 0.044439 | 0.011175 | 6.0652e-05 | 3.8365e-05 | 0.067289 | 0.067289 | 0.067289 | 0.98146 | -0.35591 | 0.98292 | -0.32729 | 18.4859
62 | -0.12543 | -0.031615 | 0.12565 | 0.031756 | 0.00022045 | 0.00014088 | 0.18995 | 0.18995 | 0.18995 | 0.98292 | -0.32729 | 0.98481 | -0.29063 | 52.1846
63 | 0.080993 | 0.020441 | -0.080905 | -0.020385 | 8.7371e-05 | 5.5721e-05 | 0.12266 | 0.12266 | 0.12266 | 0.98292 | -0.32729 | 0.98176 | -0.34984 | 33.6987
64 | -0.072754 | -0.01831 | 0.072791 | 0.018333 | 3.7034e-05 | 2.36e-05 | 0.11043 | 0.11043 | 0.11043 | 0.98059 | -0.3727 | 0.98114 | -0.36206 | 30.3375
65 | 0.069569 | 0.017512 | -0.069441 | -0.01743 | 0.00012842 | 8.18e-05 | 0.1056 | 0.1056 | 0.1056 | 0.98059 | -0.3727 | 0.97862 | -0.4114 | 29.01
66 | -0.074786 | -0.018834 | 0.074791 | 0.018837 | 4.9156e-06 | 3.1331e-06 | 0.11345 | 0.11345 | 0.11345 | 0.98114 | -0.36206 | 0.98121 | -0.36068 | 31.1688
67 | 0.044071 | 0.011066 | -0.044033 | -0.011041 | 3.8449e-05 | 2.4321e-05 | 0.067019 | 0.067019 | 0.067019 | 0.97862 | -0.4114 | 0.97768 | -0.4297 | 18.4118
68 | 0.02537 | 0.0063642 | -0.025357 | -0.0063565 | 1.253e-05 | 7.737e-06 | 0.038578 | 0.038578 | 0.038578 | 0.97862 | -0.4114 | 0.97809 | -0.42176 | 10.5983
69 | -0.076738 | -0.019325 | 0.076743 | 0.019328 | 5.0512e-06 | 3.2202e-06 | 0.11641 | 0.11641 | 0.11641 | 0.98121 | -0.36068 | 0.98128 | -0.35931 | 31.9802
70 | 0.018687 | 0.0046842 | -0.018687 | -0.0046841 | 2.5992e-07 | 1.556e-07 | 0.028442 | 0.028442 | 0.028442 | 0.97768 | -0.4297 | 0.97767 | -0.42999 | 7.8137
71 | 0.016504 | 0.0041414 | -0.016489 | -0.0041322 | 1.5674e-05 | 9.2014e-06 | 0.025121 | 0.025121 | 0.025121 | 0.97768 | -0.4297 | 0.97667 | -0.44964 | 6.9014
72 | 0.011216 | 0.0028123 | -0.011211 | -0.0028097 | 4.9827e-06 | 2.6165e-06 | 0.017064 | 0.017064 | 0.017064 | 0.97809 | -0.42176 | 0.97761 | -0.43109 | 4.6879
73 | -0.078696 | -0.019817 | 0.078731 | 0.01984 | 3.5637e-05 | 2.2724e-05 | 0.11937 | 0.11937 | 0.11937 | 0.98128 | -0.35931 | 0.98176 | -0.34984 | 32.7934
74 | 0.0099148 | 0.0024855 | -0.0099132 | -0.0024847 | 1.5972e-06 | 7.8771e-07 | 0.015091 | 0.015091 | 0.015091 | 0.97767 | -0.42999 | 0.9775 | -0.43338 | 4.1458
75 | 0.0051477 | 0.00129 | -0.005147 | -0.00129 | 7.125e-07 | 6.9506e-08 | 0.0078428 | 0.007843 | 0.007843 | 0.97667 | -0.44964 | 0.97652 | -0.45254 | 2.1547
76 | 0.0061798 | 0.0015487 | -0.0061789 | -0.0015485 | 8.8931e-07 | 2.3443e-07 | 0.0094153 | 0.0094154 | 0.0094154 | 0.97667 | -0.44964 | 0.97652 | -0.45266 | 2.5867
77 | 0.0099132 | 0.0024847 | -0.0099125 | -0.0024844 | 7.4732e-07 | 3.686e-07 | 0.015091 | 0.015091 | 0.015091 | 0.9775 | -0.43338 | 0.97742 | -0.43496 | 4.1458
78 | 0.001063 | 0.0002663 | -0.001063 | -0.0002664 | 8.3597e-09 | -1.0095e-07 | 0.0016197 | 0.0016198 | 0.0016198 | 0.97652 | -0.45266 | 0.97651 | -0.45282 | 0.44499
79 | 0.0099125 | 0.0024844 | -0.0099115 | -0.0024839 | 9.0413e-07 | 4.4596e-07 | 0.015091 | 0.015091 | 0.015091 | 0.97742 | -0.43496 | 0.97732 | -0.43687 | 4.1458
80 | -0.12764 | -0.032254 | 0.12764 | 0.032255 | 1.1381e-06 | 7.2737e-07 | 0.19295 | 0.19295 | 0.19295 | 0.98481 | -0.29063 | 0.98482 | -0.29044 | 53.0093
81 | -0.067476 | -0.016999 | 0.0676 | 0.017078 | 0.00012433 | 7.9165e-05 | 0.10218 | 0.10218 | 0.10218 | 0.98296 | -0.32689 | 0.98493 | -0.28844 | 28.0706
82 | 0.06137 | 0.015468 | -0.06136 | -0.015462 | 1.0373e-05 | 6.5983e-06 | 0.092935 | 0.092935 | 0.092935 | 0.98296 | -0.32689 | 0.98278 | -0.33042 | 25.5315
83 | -0.07444 | -0.018792 | 0.074488 | 0.018823 | 4.8806e-05 | 3.1105e-05 | 0.11251 | 0.11251 | 0.11251 | 0.98493 | -0.28844 | 0.98564 | -0.27477 | 30.9094
84 | 0.06005 | 0.015134 | -0.059984 | -0.015092 | 6.5247e-05 | 4.1492e-05 | 0.090951 | 0.090951 | 0.090951 | 0.98278 | -0.33042 | 0.98161 | -0.35316 | 24.9865
85 | -0.076085 | -0.019223 | 0.076188 | 0.019289 | 0.00010326 | 6.5821e-05 | 0.11492 | 0.11492 | 0.11492 | 0.98564 | -0.27477 | 0.9871 | -0.2465 | 31.5715
86 | 0.059984 | 0.015092 | -0.059909 | -0.015044 | 7.548e-05 | 4.8e-05 | 0.090951 | 0.090951 | 0.090951 | 0.98161 | -0.35316 | 0.98026 | -0.37953 | 24.9865
87 | -0.086176 | -0.021792 | 0.086319 | 0.021883 | 0.00014266 | 9.1012e-05 | 0.12998 | 0.12998 | 0.12998 | 0.9871 | -0.2465 | 0.98889 | -0.21205 | 35.7079
88 | 0.009988 | 0.0025033 | -0.0099867 | -0.0025026 | 1.3307e-06 | 6.5161e-07 | 0.015057 | 0.015057 | 0.015057 | 0.9871 | -0.2465 | 0.98696 | -0.24929 | 4.1364
89 | 0.050993 | 0.01281 | -0.050976 | -0.012799 | 1.7196e-05 | 1.0909e-05 | 0.077417 | 0.077417 | 0.077417 | 0.98026 | -0.37953 | 0.9799 | -0.3866 | 21.2685
90 | 0.075187 | 0.019 | -0.075051 | -0.018914 | 0.00013618 | 8.6793e-05 | 0.11319 | 0.11319 | 0.11319 | 0.98889 | -0.21205 | 0.98693 | -0.2499 | 31.097
91 | 0.0071396 | 0.0017891 | -0.0071394 | -0.001789 | 2.0585e-07 | 7.1203e-08 | 0.010764 | 0.010764 | 0.010764 | 0.98696 | -0.24929 | 0.98693 | -0.2499 | 2.9572
92 | 0.046083 | 0.011572 | -0.046061 | -0.011559 | 2.1644e-05 | 1.3704e-05 | 0.069987 | 0.069987 | 0.069987 | 0.9799 | -0.3866 | 0.9794 | -0.39645 | 19.2272
93 | 0.07288 | 0.01837 | -0.07285 | -0.018351 | 2.9929e-05 | 1.907e-05 | 0.10992 | 0.10992 | 0.10992 | 0.98693 | -0.2499 | 0.98649 | -0.25849 | 30.1977
94 | 0.0024588 | 0.00061593 | -0.0024587 | -0.0006162 | 1.4744e-07 | -2.7119e-07 | 0.0037071 | 0.0037073 | 0.0037073 | 0.98693 | -0.2499 | 0.98686 | -0.25116 | 1.0185
95 | 0.037143 | 0.0093234 | -0.037115 | -0.0093059 | 2.7862e-05 | 1.7538e-05 | 0.056437 | 0.056437 | 0.056437 | 0.9794 | -0.39645 | 0.9786 | -0.41219 | 15.5046
96 | 0.013953 | 0.0034984 | -0.013948 | -0.0034956 | 4.9599e-06 | 2.8058e-06 | 0.021223 | 0.021224 | 0.021224 | 0.97828 | -0.41837 | 0.9779 | -0.42583 | 5.8306
97 | -0.023106 | -0.0057925 | 0.023113 | 0.0057966 | 6.8008e-06 | 4.1681e-06 | 0.035146 | 0.035146 | 0.035146 | 0.97828 | -0.41837 | 0.9786 | -0.41219 | 9.6555
98 | 0.068418 | 0.01724 | -0.068305 | -0.017168 | 0.0001126 | 7.1706e-05 | 0.10323 | 0.10323 | 0.10323 | 0.98649 | -0.25849 | 0.98471 | -0.29295 | 28.361
99 | 0.03455 | 0.0086822 | -0.034531 | -0.0086701 | 1.9289e-05 | 1.2105e-05 | 0.052218 | 0.052218 | 0.052218 | 0.98471 | -0.29295 | 0.98411 | -0.30466 | 14.3456
100 | 0.013241 | 0.0033189 | -0.01324 | -0.0033182 | 1.3566e-06 | 7.4635e-07 | 0.019717 | 0.019717 | 0.019717 | 0.99932 | -0.013125 | 0.99921 | -0.015276 | 5.4168
101 | -0.0145 | -0.0036344 | 0.014502 | 0.0036353 | 1.6347e-06 | 9.2366e-07 | 0.021591 | 0.021591 | 0.021591 | 0.99932 | -0.013125 | 0.99944 | -0.010759 | 5.9316
102 | 0.012321 | 0.0030878 | -0.01232 | -0.0030877 | 2.8239e-07 | 1.5143e-07 | 0.018348 | 0.018348 | 0.018348 | 0.99921 | -0.015276 | 0.99918 | -0.015757 | 5.0407
103 | -0.015763 | -0.0039516 | 0.015764 | 0.0039518 | 3.9462e-07 | 2.2752e-07 | 0.02347 | 0.02347 | 0.02347 | 0.99944 | -0.010759 | 0.99947 | -0.010234 | 6.4477
104 | 0.0067879 | 0.0017011 | -0.0067876 | -0.001701 | 3.0518e-07 | 9.1009e-08 | 0.010109 | 0.010109 | 0.010109 | 0.99918 | -0.015757 | 0.99913 | -0.016701 | 2.7771
105 | -0.017242 | -0.0043223 | 0.017243 | 0.0043227 | 6.8024e-07 | 3.9928e-07 | 0.025671 | 0.025671 | 0.025671 | 0.99947 | -0.010234 | 0.99951 | -0.0094056 | 7.0524
106 | 0.0057454 | 0.0014398 | -0.005745 | -0.0014398 | 3.6994e-07 | 6.0313e-08 | 0.0085566 | 0.0085567 | 0.0085567 | 0.99913 | -0.016701 | 0.99906 | -0.018052 | 2.3507
107 | 0.0010422 | 0.00026115 | -0.0010422 | -0.00026119 | 2.9973e-09 | -4.1533e-08 | 0.0015521 | 0.0015521 | 0.0015521 | 0.99913 | -0.016701 | 0.99913 | -0.016761 | 0.42641
108 | -0.018491 | -0.0046354 | 0.018491 | 0.0046356 | 2.625e-07 | 1.5589e-07 | 0.027528 | 0.027528 | 0.027528 | 0.99951 | -0.0094056 | 0.99953 | -0.0091077 | 7.5627
109 | 0.0023162 | 0.00058041 | -0.0023162 | -0.00058048 | 3.2517e-08 | -7.4599e-08 | 0.0034497 | 0.0034498 | 0.0034498 | 0.99906 | -0.018052 | 0.99905 | -0.018347 | 0.94774
110 | -0.019932 | -0.0049967 | 0.019933 | 0.0049975 | 1.3051e-06 | 7.8347e-07 | 0.029673 | 0.029673 | 0.029673 | 0.99953 | -0.0091077 | 0.9996 | -0.0077336 | 8.152
111 | -0.021602 | -0.0054158 | 0.021603 | 0.0054159 | 7.9139e-08 | 4.7974e-08 | 0.032158 | 0.032158 | 0.032158 | 0.9996 | -0.0077336 | 0.9996 | -0.0076567 | 8.8347
112 | 0.0062878 | 0.0015757 | -0.0062872 | -0.0015756 | 6.8265e-07 | 1.8803e-07 | 0.0095735 | 0.0095736 | 0.0095736 | 0.97732 | -0.43687 | 0.9772 | -0.43915 | 2.6301
113 | 0.0017892 | 0.00044825 | -0.0017892 | -0.0004483 | 1.2018e-08 | -4.6403e-08 | 0.0027244 | 0.0027244 | 0.0027244 | 0.9772 | -0.43915 | 0.9772 | -0.43929 | 0.74845
114 | 0.032153 | 0.0080742 | -0.032149 | -0.0080716 | 4.2069e-06 | 2.6321e-06 | 0.048623 | 0.048623 | 0.048623 | 0.98411 | -0.30466 | 0.98397 | -0.3074 | 13.3579
115 | 0.0017892 | 0.0004483 | -0.0017891 | -0.0004484 | 2.605e-08 | -1.0057e-07 | 0.0027244 | 0.0027244 | 0.0027244 | 0.9772 | -0.43929 | 0.97718 | -0.4396 | 0.74847
116 | 0.027573 | 0.0069156 | -0.027569 | -0.0069136 | 3.2827e-06 | 2.0327e-06 | 0.04103 | 0.041031 | 0.041031 | 1 | 0 | 0.99987 | -0.002498 | 11.2721
117 | 0.026308 | 0.0065975 | -0.026306 | -0.0065961 | 2.2706e-06 | 1.4014e-06 | 0.039153 | 0.039154 | 0.039154 | 0.99987 | -0.002498 | 0.99978 | -0.0043091 | 10.7565
118 | 0.024859 | 0.0062335 | -0.024857 | -0.0062323 | 2.0278e-06 | 1.246e-06 | 0.037 | 0.037 | 0.037 | 0.99978 | -0.0043091 | 0.99969 | -0.0060208 | 10.165
119 | 0.023192 | 0.005815 | -0.023191 | -0.0058139 | 1.8079e-06 | 1.104e-06 | 0.034522 | 0.034522 | 0.034522 | 0.99969 | -0.0060208 | 0.9996 | -0.0076567 | 9.4842

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40597 | 0.10359

## res_load
| p_mw | q_mvar
0 | 0.0021795 | 0.00054624
1 | 0.004011 | 0.0010053
2 | 0.0024177 | 0.00060594
3 | 0.0028775 | 0.00072116
4 | 0.0042391 | 0.0010624
5 | 0.0021551 | 0.00054012
6 | 0.0025915 | 0.0006495
7 | 0.0039369 | 0.00098669
8 | 0.0027951 | 0.00070051
9 | 0.002216 | 0.00055538
10 | 0.0025574 | 0.00064094
11 | 0.018762 | 0.0047022
12 | 0.010288 | 0.0025784
13 | 0.0038005 | 0.0009525
14 | 0.0012434 | 0.00031161
15 | 0.0004335 | 0.00010864
16 | 0.0048141 | 0.0012065
17 | 0.0026165 | 0.00065577
18 | 0.0023086 | 0.00057858
19 | 0.0068455 | 0.0017156
20 | 0.0019427 | 0.00048689
21 | 0.013447 | 0.0033701
22 | 0.0036699 | 0.00091976
23 | 0.002004 | 0.00050224
24 | 0.0033908 | 0.00084982
25 | 0.0024344 | 0.00061013
26 | 0.0021912 | 0.00054917
27 | 0.0071926 | 0.0018026
28 | 0.0058798 | 0.0014736
29 | 0.0026825 | 0.00067229
30 | 0.00092875 | 0.00023277
31 | 0.0014724 | 0.00036903
32 | 0.0021151 | 0.00053009
33 | 0.0012464 | 0.00031238
34 | 0.0016663 | 0.00041762
35 | 0.0013275 | 0.00033271
36 | 0.0019493 | 0.00048854
37 | 0.011431 | 0.002865
38 | 0.0019661 | 0.00049275
39 | 0.0019638 | 0.00049217
40 | 0.0082971 | 0.0020794
41 | 0.0019902 | 0.00049879
42 | 0.012594 | 0.0031563
43 | 0.0019882 | 0.00049828
44 | 0.0031845 | 0.0007981
45 | 0.0019952 | 0.00050005
46 | 0.0019476 | 0.00048811
47 | 0.008841 | 0.0022158
48 | 0.014141 | 0.0035441
49 | 0.0019521 | 0.00048924
50 | 0.0087723 | 0.0021985
51 | 0.005161 | 0.0012935
52 | 0.011211 | 0.0028097
53 | 0.0021741 | 0.00054487
54 | 0.005147 | 0.00129
55 | 0.005116 | 0.0012822
56 | 0.0019868 | 0.00049793
57 | 0.0012522 | 0.00031384
58 | 0.0061054 | 0.0015302
59 | 0.0068396 | 0.0017142
60 | 0.0013102 | 0.00032836
61 | 0.0015965 | 0.00040013
62 | 0.0089155 | 0.0022344
63 | 0.0028471 | 0.00071356
64 | 0.0048931 | 0.0012263
65 | 0.002171 | 0.0005441
66 | 0.0046805 | 0.0011731
67 | 0.0089187 | 0.0022352
68 | 0.0091533 | 0.002294
69 | 0.013948 | 0.0034956
70 | 0.014002 | 0.0035092
71 | 0.0024587 | 0.0006162
72 | 0.0044324 | 0.0011109
73 | 0.006671 | 0.0016719
74 | 0.0012586 | 0.00031545
75 | 0.00091927 | 0.00023039
76 | 0.0012618 | 0.00031624
77 | 0.0055326 | 0.0013866
78 | 0.0014784 | 0.00037053
79 | 0.0012477 | 0.00031271
80 | 0.0034288 | 0.00085934
81 | 0.0010422 | 0.00026119
82 | 0.0014409 | 0.00036113
83 | 0.0023162 | 0.00058048
84 | 0.0016693 | 0.00041836
85 | 0.0036237 | 0.00090819
86 | 0.001063 | 0.0002664
87 | 0.004498 | 0.0011273
88 | 0.0023776 | 0.00059588
89 | 0.0052184 | 0.0013079
90 | 0.0016368 | 0.00041023
91 | 0.0012613 | 0.0003161
92 | 0.0014466 | 0.00036255
93 | 0.0016649 | 0.00041726
94 | 0.0015881 | 0.00039801
95 | 0.0017891 | 0.0004484

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1