## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-25_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-25_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2581-25_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2581-25_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2581-25_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2581-25_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2581-25_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2581-25_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2581-25_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2581-25_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2581-25_0_5_node_100 | 0.4 | n |  | TRUE
11 | bus_LV_2581-25_0_5_node_74 | 0.4 | n |  | TRUE
12 | bus_LV_2581-25_0_5_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_2581-25_0_5_node_127 | 0.4 | n |  | TRUE
14 | bus_LV_2581-25_0_5_node_72 | 0.4 | n |  | TRUE
15 | bus_LV_2581-25_0_5_node_62 | 0.4 | n |  | TRUE
16 | bus_LV_2581-25_0_5_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_2581-25_0_5_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_2581-25_0_5_node_115 | 0.4 | n |  | TRUE
19 | bus_LV_2581-25_0_5_node_51 | 0.4 | n |  | TRUE
20 | bus_LV_2581-25_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2581-25_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2581-25_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2581-25_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2581-25_0_5_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2581-25_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2581-25_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2581-25_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2581-25_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2581-25_0_5_node_117 | 0.4 | n |  | TRUE
30 | bus_LV_2581-25_0_5_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_2581-25_0_5_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_2581-25_0_5_node_118 | 0.4 | n |  | TRUE
33 | bus_LV_2581-25_0_5_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_2581-25_0_5_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_2581-25_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2581-25_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2581-25_0_5_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_2581-25_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2581-25_0_5_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_2581-25_0_5_node_66 | 0.4 | n |  | TRUE
41 | bus_LV_2581-25_0_5_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_2581-25_0_5_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_2581-25_0_5_node_67 | 0.4 | n |  | TRUE
44 | bus_LV_2581-25_0_5_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_2581-25_0_5_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_2581-25_0_5_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2581-25_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2581-25_0_5_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2581-25_0_5_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2581-25_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2581-25_0_5_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_2581-25_0_5_node_101 | 0.4 | n |  | TRUE
53 | bus_LV_2581-25_0_5_node_61 | 0.4 | n |  | TRUE
54 | bus_LV_2581-25_0_5_node_102 | 0.4 | n |  | TRUE
55 | bus_LV_2581-25_0_5_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_2581-25_0_5_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_2581-25_0_5_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_2581-25_0_5_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_2581-25_0_5_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_2581-25_0_5_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2581-25_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2581-25_0_5_node_112 | 0.4 | n |  | TRUE
63 | bus_LV_2581-25_0_5_node_91 | 0.4 | n |  | TRUE
64 | bus_LV_2581-25_0_5_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_2581-25_0_5_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_2581-25_0_5_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_2581-25_0_5_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_2581-25_0_5_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_2581-25_0_5_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_2581-25_0_5_node_114 | 0.4 | n |  | TRUE
71 | bus_LV_2581-25_0_5_node_98 | 0.4 | n |  | TRUE
72 | bus_LV_2581-25_0_5_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_2581-25_0_5_node_96 | 0.4 | n |  | TRUE
74 | bus_LV_2581-25_0_5_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_2581-25_0_5_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_2581-25_0_5_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_2581-25_0_5_node_103 | 0.4 | n |  | TRUE
78 | bus_LV_2581-25_0_5_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_2581-25_0_5_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_2581-25_0_5_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_2581-25_0_5_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_2581-25_0_5_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2581-25_0_5_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_2581-25_0_5_node_116 | 0.4 | n |  | TRUE
85 | bus_LV_2581-25_0_5_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_2581-25_0_5_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_2581-25_0_5_node_132 | 0.4 | n |  | TRUE
88 | bus_LV_2581-25_0_5_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_2581-25_0_5_node_121 | 0.4 | n |  | TRUE
90 | bus_LV_2581-25_0_5_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_2581-25_0_5_node_68 | 0.4 | n |  | TRUE
92 | bus_LV_2581-25_0_5_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_2581-25_0_5_node_70 | 0.4 | n |  | TRUE
94 | bus_LV_2581-25_0_5_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_2581-25_0_5_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_2581-25_0_5_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_2581-25_0_5_node_129 | 0.4 | n |  | TRUE
98 | bus_LV_2581-25_0_5_node_124 | 0.4 | n |  | TRUE
99 | bus_LV_2581-25_0_5_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_2581-25_0_5_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_2581-25_0_5_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_2581-25_0_5_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_2581-25_0_5_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2581-25_0_5_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_2581-25_0_5_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_2581-25_0_5_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_2581-25_0_5_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_2581-25_0_5_node_111 | 0.4 | n |  | TRUE
109 | bus_LV_2581-25_0_5_node_125 | 0.4 | n |  | TRUE
110 | bus_LV_2581-25_0_5_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_2581-25_0_5_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2581-25_0_5_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_2581-25_0_5_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_2581-25_0_5_node_97 | 0.4 | n |  | TRUE
115 | bus_LV_2581-25_0_5_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_2581-25_0_5_node_128 | 0.4 | n |  | TRUE
117 | bus_LV_2581-25_0_5_node_126 | 0.4 | n |  | TRUE
118 | bus_LV_2581-25_0_5_node_130 | 0.4 | n |  | TRUE
119 | bus_LV_2581-25_0_5_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_2581-25_0_5_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_2581-25_0_5_node_123 | 0.4 | n |  | TRUE
122 | bus_LV_2581-25_0_5_node_131 | 0.4 | n |  | TRUE
123 | bus_MV_523_0_node_156 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-25_0_5_load_0 | 0 | 0.0018447 | 0.00046233 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-25_0_5_load_1 | 1 | 0.0034873 | 0.00087401 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-25_0_5_load_4 | 4 | 0.0016913 | 0.00042387 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-25_0_5_load_5 | 5 | 0.0015328 | 0.00038417 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-25_0_5_load_6 | 6 | 0.0025818 | 0.00064706 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-25_0_5_load_7 | 7 | 0.0080454 | 0.0020164 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-25_0_5_load_8 | 8 | 0.0022179 | 0.00055586 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-25_0_5_load_9 | 9 | 0.0016556 | 0.00041493 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-25_0_5_load_100 | 10 | 0.0081065 | 0.0020317 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-25_0_5_load_74 | 11 | 0.0029342 | 0.00073537 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-25_0_5_load_127 | 13 | 0.0044311 | 0.0011105 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-25_0_5_load_65 | 16 | 0.0017275 | 0.00043296 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-25_0_5_load_60 | 17 | 0.0019564 | 0.00049033 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-25_0_5_load_115 | 18 | 0.0013658 | 0.00034231 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-25_0_5_load_10 | 20 | 0.003348 | 0.00083908 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-25_0_5_load_11 | 21 | 0.0033613 | 0.00084243 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-25_0_5_load_13 | 23 | 0.0033239 | 0.00083304 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-25_0_5_load_14 | 24 | 0.096048 | 0.024072 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-25_0_5_load_16 | 25 | 0.0042673 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-25_0_5_load_18 | 27 | 0.0018198 | 0.00045607 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-25_0_5_load_19 | 28 | 0.0044305 | 0.0011104 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-25_0_5_load_117 | 29 | 0.0042787 | 0.0010723 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-25_0_5_load_46 | 30 | 0.0025116 | 0.00062946 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2581-25_0_5_load_58 | 31 | 0.003181 | 0.00079723 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2581-25_0_5_load_118 | 32 | 0.0022334 | 0.00055975 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2581-25_0_5_load_57 | 34 | 0.0031838 | 0.00079793 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2581-25_0_5_load_20 | 35 | 0.0075953 | 0.0019035 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2581-25_0_5_load_21 | 36 | 0.0075931 | 0.001903 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2581-25_0_5_load_22 | 37 | 0.0027145 | 0.00068031 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2581-25_0_5_load_24 | 38 | 0.0039306 | 0.0009851 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2581-25_0_5_load_26 | 39 | 0.006683 | 0.0016749 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2581-25_0_5_load_66 | 40 | 0.0068902 | 0.0017269 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2581-25_0_5_load_76 | 41 | 0.0056392 | 0.0014133 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2581-25_0_5_load_67 | 43 | 0.0036605 | 0.00091741 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2581-25_0_5_load_27 | 44 | 0.0019036 | 0.0004771 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2581-25_0_5_load_28 | 45 | 0.0023535 | 0.00058984 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2581-25_0_5_load_29 | 46 | 0.0019464 | 0.00048781 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2581-25_0_5_load_30 | 47 | 0.002203 | 0.00055212 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2581-25_0_5_load_31 | 48 | 0.0026654 | 0.00066801 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2581-25_0_5_load_32 | 49 | 0.0026727 | 0.00066983 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2581-25_0_5_load_33 | 50 | 0.0022763 | 0.00057049 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2581-25_0_5_load_101 | 52 | 0.0026375 | 0.00066102 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2581-25_0_5_load_102 | 54 | 0.0047882 | 0.0012 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2581-25_0_5_load_34 | 55 | 0.0025115 | 0.00062944 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2581-25_0_5_load_35 | 56 | 0.003341 | 0.00083733 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2581-25_0_5_load_36 | 57 | 0.0033637 | 0.00084302 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2581-25_0_5_load_37 | 58 | 0.002501 | 0.0006268 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2581-25_0_5_load_38 | 59 | 0.0031716 | 0.00079488 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2581-25_0_5_load_39 | 60 | 0.0013705 | 0.00034348 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2581-25_0_5_load_40 | 61 | 0.0031969 | 0.00080122 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2581-25_0_5_load_112 | 62 | 0.0014259 | 0.00035738 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2581-25_0_5_load_41 | 64 | 0.0036219 | 0.00090772 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2581-25_0_5_load_42 | 65 | 0.003632 | 0.00091026 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2581-25_0_5_load_44 | 66 | 0.0067026 | 0.0016798 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2581-25_0_5_load_47 | 68 | 0.0035752 | 0.00089602 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2581-25_0_5_load_48 | 69 | 0.0026911 | 0.00067444 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2581-25_0_5_load_114 | 70 | 0.0040537 | 0.001016 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2581-25_0_5_load_98 | 71 | 0.0011813 | 0.00029607 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2581-25_0_5_load_81 | 72 | 0.0038722 | 0.00097047 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2581-25_0_5_load_96 | 73 | 0.001175 | 0.00029447 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2581-25_0_5_load_49 | 74 | 0.0013759 | 0.00034482 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2581-25_0_5_load_50 | 75 | 0.0015799 | 0.00039597 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2581-25_0_5_load_54 | 76 | 0.0015451 | 0.00038723 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2581-25_0_5_load_103 | 77 | 0.0016252 | 0.00040732 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2581-25_0_5_load_52 | 78 | 0.0064185 | 0.0016086 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2581-25_0_5_load_53 | 79 | 0.0039222 | 0.00098299 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2581-25_0_5_load_73 | 80 | 0.0073045 | 0.0018307 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2581-25_0_5_load_119 | 81 | 0.0052827 | 0.001324 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2581-25_0_5_load_75 | 83 | 0.0017737 | 0.00044454 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2581-25_0_5_load_116 | 84 | 0.0016126 | 0.00040415 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2581-25_0_5_load_59 | 85 | 0.0013892 | 0.00034817 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2581-25_0_5_load_132 | 87 | 0.0027658 | 0.00069317 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2581-25_0_5_load_121 | 89 | 0.0024079 | 0.00060348 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2581-25_0_5_load_80 | 90 | 0.0037362 | 0.00093637 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2581-25_0_5_load_68 | 91 | 0.0020704 | 0.00051888 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2581-25_0_5_load_69 | 92 | 0.0031099 | 0.00077942 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2581-25_0_5_load_70 | 93 | 0.0022133 | 0.0005547 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2581-25_0_5_load_78 | 94 | 0.0045445 | 0.001139 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2581-25_0_5_load_79 | 95 | 0.0033712 | 0.0008449 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2581-25_0_5_load_82 | 96 | 0.002501 | 0.00062682 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2581-25_0_5_load_129 | 97 | 0.0036096 | 0.00090465 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2581-25_0_5_load_124 | 98 | 0.0026561 | 0.00066568 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2581-25_0_5_load_122 | 99 | 0.0024299 | 0.000609 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2581-25_0_5_load_84 | 100 | 0.0020805 | 0.00052143 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2581-25_0_5_load_85 | 101 | 0.0020814 | 0.00052166 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2581-25_0_5_load_87 | 103 | 0.013604 | 0.0034095 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2581-25_0_5_load_90 | 105 | 0.0012702 | 0.00031834 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2581-25_0_5_load_111 | 108 | 0.0027225 | 0.00068233 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2581-25_0_5_load_125 | 109 | 0.0033704 | 0.00084471 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2581-25_0_5_load_110 | 110 | 0.0030726 | 0.00077006 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2581-25_0_5_load_93 | 111 | 0.0013377 | 0.00033525 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2581-25_0_5_load_94 | 112 | 0.00131 | 0.00032833 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2581-25_0_5_load_95 | 113 | 0.0019582 | 0.00049076 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2581-25_0_5_load_97 | 114 | 0.0019511 | 0.00048899 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2581-25_0_5_load_99 | 115 | 0.0019305 | 0.00048384 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2581-25_0_5_load_128 | 116 | 0.0044239 | 0.0011087 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2581-25_0_5_load_130 | 118 | 0.010244 | 0.0025674 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2581-25_0_5_load_105 | 119 | 0.010317 | 0.0025857 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2581-25_0_5_load_109 | 120 | 0.0091143 | 0.0022843 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2581-25_0_5_load_123 | 121 | 0.0023502 | 0.00058902 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2581-25_0_5_load_131 | 122 | 0.0025671 | 0.00064337 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-25_0_5_line_0 |  | 0 | 1 | 0.015161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2581-25_0_5_line_1 |  | 0 | 2 | 0.023161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2581-25_0_5_line_2 |  | 1 | 3 | 0.010629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2581-25_0_5_line_3 |  | 2 | 4 | 0.029786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2581-25_0_5_line_4 |  | 2 | 5 | 0.0091274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-25_0_5_line_5 |  | 3 | 6 | 0.0008478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2581-25_0_5_line_6 |  | 3 | 7 | 0.007261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2581-25_0_5_line_7 |  | 4 | 8 | 0.020139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2581-25_0_5_line_8 |  | 5 | 9 | 0.00045009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2581-25_0_5_line_9 |  | 6 | 10 | 0.0044123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2581-25_0_5_line_10 |  | 7 | 11 | 0.013974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2581-25_0_5_line_11 |  | 9 | 12 | 0.019814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2581-25_0_5_line_12 |  | 10 | 13 | 0.0093126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2581-25_0_5_line_13 |  | 11 | 14 | 0.014829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2581-25_0_5_line_14 |  | 12 | 18 | 0.020216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2581-25_0_5_line_15 |  | 12 | 19 | 0.003848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2581-25_0_5_line_16 |  | 13 | 116 | 0.012193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2581-25_0_5_line_17 |  | 14 | 93 | 0.0076367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2581-25_0_5_line_18 |  | 15 | 16 | 0.0052035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2581-25_0_5_line_19 |  | 15 | 17 | 0.0083879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2581-25_0_5_line_20 |  | 16 | 84 | 0.013509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2581-25_0_5_line_21 |  | 17 | 85 | 0.014069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2581-25_0_5_line_22 |  | 18 | 84 | 0.024922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-25_0_5_line_23 |  | 19 | 76 | 0.012222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2581-25_0_5_line_24 |  | 19 | 75 | 0.011462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2581-25_0_5_line_25 |  | 20 | 21 | 0.0073516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2581-25_0_5_line_26 |  | 20 | 22 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2581-25_0_5_line_27 |  | 21 | 23 | 0.013738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2581-25_0_5_line_28 |  | 22 | 24 | 0.019061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2581-25_0_5_line_29 |  | 23 | 25 | 0.0085219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2581-25_0_5_line_30 |  | 25 | 29 | 0.011007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2581-25_0_5_line_31 |  | 26 | 27 | 0.015965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2581-25_0_5_line_32 |  | 26 | 28 | 0.017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2581-25_0_5_line_33 |  | 27 | 30 | 0.0012779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2581-25_0_5_line_34 |  | 28 | 31 | 0.0078821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2581-25_0_5_line_35 |  | 29 | 32 | 0.0095999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2581-25_0_5_line_36 |  | 30 | 33 | 0.0084109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2581-25_0_5_line_37 |  | 31 | 34 | 0.0076911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2581-25_0_5_line_38 |  | 32 | 121 | 0.012187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2581-25_0_5_line_39 |  | 33 | 67 | 0.029601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2581-25_0_5_line_40 |  | 33 | 64 | 0.016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2581-25_0_5_line_41 |  | 34 | 61 | 0.0071005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2581-25_0_5_line_42 |  | 35 | 36 | 0.015857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2581-25_0_5_line_43 |  | 35 | 37 | 0.0038068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2581-25_0_5_line_44 |  | 37 | 38 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2581-25_0_5_line_45 |  | 38 | 39 | 0.0027432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2581-25_0_5_line_46 |  | 39 | 40 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2581-25_0_5_line_47 |  | 40 | 43 | 0.0016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2581-25_0_5_line_48 |  | 41 | 42 | 0.038545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2581-25_0_5_line_49 |  | 42 | 94 | 0.038184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2581-25_0_5_line_50 |  | 42 | 95 | 0.021931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2581-25_0_5_line_51 |  | 42 | 90 | 0.020732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2581-25_0_5_line_52 |  | 43 | 88 | 0.016261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2581-25_0_5_line_53 |  | 44 | 45 | 0.007504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2581-25_0_5_line_54 |  | 44 | 46 | 0.007072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2581-25_0_5_line_55 |  | 45 | 47 | 0.0063371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2581-25_0_5_line_56 |  | 46 | 48 | 0.015451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2581-25_0_5_line_57 |  | 47 | 49 | 0.0091917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2581-25_0_5_line_58 |  | 48 | 50 | 0.01539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2581-25_0_5_line_59 |  | 49 | 51 | 0.029568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2581-25_0_5_line_60 |  | 50 | 52 | 0.0098178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2581-25_0_5_line_61 |  | 51 | 53 | 0.030104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2581-25_0_5_line_62 |  | 52 | 54 | 0.015721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2581-25_0_5_line_63 |  | 53 | 86 | 0.083911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2581-25_0_5_line_64 |  | 54 | 117 | 0.0088738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2581-25_0_5_line_65 |  | 55 | 56 | 0.007843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2581-25_0_5_line_66 |  | 55 | 57 | 0.01549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2581-25_0_5_line_67 |  | 56 | 58 | 0.015095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2581-25_0_5_line_68 |  | 57 | 59 | 0.0078838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2581-25_0_5_line_69 |  | 58 | 60 | 0.0070541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2581-25_0_5_line_70 |  | 59 | 61 | 0.0070878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2581-25_0_5_line_71 |  | 60 | 62 | 0.010263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2581-25_0_5_line_72 |  | 62 | 63 | 0.014848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2581-25_0_5_line_73 |  | 63 | 107 | 0.013108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2581-25_0_5_line_74 |  | 64 | 65 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2581-25_0_5_line_75 |  | 65 | 66 | 0.0062649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2581-25_0_5_line_76 |  | 66 | 68 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2581-25_0_5_line_77 |  | 67 | 69 | 0.0018894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2581-25_0_5_line_78 |  | 68 | 70 | 0.0010374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2581-25_0_5_line_79 |  | 69 | 71 | 0.010715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2581-25_0_5_line_80 |  | 70 | 72 | 4.5363e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2581-25_0_5_line_81 |  | 71 | 73 | 0.0063118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2581-25_0_5_line_82 |  | 72 | 94 | 0.014016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2581-25_0_5_line_83 |  | 73 | 112 | 0.0078714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2581-25_0_5_line_84 |  | 74 | 75 | 0.00026889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2581-25_0_5_line_85 |  | 76 | 77 | 0.0069789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2581-25_0_5_line_86 |  | 77 | 83 | 0.0085828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2581-25_0_5_line_87 |  | 78 | 79 | 0.036061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2581-25_0_5_line_88 |  | 78 | 80 | 0.045544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2581-25_0_5_line_89 |  | 80 | 81 | 0.032254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2581-25_0_5_line_90 |  | 80 | 82 | 0.0094113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_2581-25_0_5_line_91 |  | 82 | 92 | 0.010853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2581-25_0_5_line_92 |  | 86 | 87 | 0.057652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2581-25_0_5_line_93 |  | 88 | 89 | 0.011437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2581-25_0_5_line_94 |  | 88 | 90 | 0.039443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2581-25_0_5_line_95 |  | 89 | 99 | 0.00063322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2581-25_0_5_line_96 |  | 91 | 92 | 0.017904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2581-25_0_5_line_97 |  | 91 | 93 | 0.019369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2581-25_0_5_line_98 |  | 95 | 96 | 0.0032988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2581-25_0_5_line_99 |  | 96 | 97 | 0.019723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2581-25_0_5_line_100 |  | 97 | 98 | 0.024305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2581-25_0_5_line_101 |  | 99 | 117 | 0.015888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2581-25_0_5_line_102 |  | 100 | 101 | 0.0094873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2581-25_0_5_line_103 |  | 100 | 102 | 0.018706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2581-25_0_5_line_104 |  | 101 | 103 | 0.03807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2581-25_0_5_line_105 |  | 102 | 104 | 0.038828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2581-25_0_5_line_106 |  | 104 | 105 | 0.029303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2581-25_0_5_line_107 |  | 104 | 106 | 0.040099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2581-25_0_5_line_108 |  | 106 | 108 | 0.0095714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2581-25_0_5_line_109 |  | 106 | 107 | 0.041436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2581-25_0_5_line_110 |  | 107 | 109 | 0.016214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2581-25_0_5_line_111 |  | 108 | 110 | 0.0027033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2581-25_0_5_line_112 |  | 109 | 121 | 0.011037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2581-25_0_5_line_113 |  | 110 | 120 | 0.058849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2581-25_0_5_line_114 |  | 111 | 112 | 0.022149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2581-25_0_5_line_115 |  | 111 | 113 | 0.012152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2581-25_0_5_line_116 |  | 113 | 114 | 0.01337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2581-25_0_5_line_117 |  | 114 | 115 | 0.012057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2581-25_0_5_line_118 |  | 116 | 122 | 0.01885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2581-25_0_5_line_119 |  | 117 | 118 | 0.026416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2581-25_0_5_line_120 |  | 118 | 122 | 0.010616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2581-25_0_5_line_121 |  | 119 | 120 | 0.01754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-25_0_5_trafo_12 | 0.63 MVA 20/0.4 kV | 123 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2634785.2686 | 1244942.1745 | 2634799.9449 | 1244945.9761 | 2634799.9449 | 1244945.9761
1 | 2634763.5812 | 1244934.1777 | 2634778.8214 | 1244940.5044 | 2634785.2686 | 1244942.1745
2 | 2634809.6969 | 1244950.2027 | 2634799.9449 | 1244945.9761
3 | 2634763.5812 | 1244934.1777 | 2634736.0737 | 1244922.751
4 | 2634763.5812 | 1244934.1777 | 2634766.9814 | 1244925.7073
5 | 2634808.8531 | 1244950.285 | 2634809.6969 | 1244950.2027
6 | 2634809.6969 | 1244950.2027 | 2634816.9579 | 1244950.1785
7 | 2634736.0737 | 1244922.751 | 2634730.3797 | 1244920.3857 | 2634720.3889 | 1244910.6161
8 | 2634766.9814 | 1244925.7073 | 2634767.1491 | 1244925.2897
9 | 2634804.4617 | 1244950.7132 | 2634808.8531 | 1244950.285
10 | 2634816.9579 | 1244950.1785 | 2634821.2972 | 1244947.202 | 2634829.4003 | 1244944.003
11 | 2634774.5303 | 1244906.9019 | 2634767.1491 | 1244925.2897
12 | 2634804.4617 | 1244950.7132 | 2634795.193 | 1244951.617
13 | 2634842.0034 | 1244936.2052 | 2634840.698 | 1244937.1982 | 2634829.4003 | 1244944.003
14 | 2634774.5303 | 1244906.9019 | 2634757.3992 | 1244899.5969 | 2634755.9354 | 1244898.9699
15 | 2634778.0801 | 1244908.4126 | 2634774.5303 | 1244906.9019
16 | 2634783.1034 | 1244953.1819 | 2634791.198 | 1244952.0066 | 2634795.193 | 1244951.617
17 | 2634842.0034 | 1244936.2052 | 2634848.2682 | 1244931.838
18 | 2634715.9876 | 1244881.4207 | 2634720.1019 | 1244883.3015 | 2634720.723 | 1244883.5776
19 | 2634715.9876 | 1244881.4207 | 2634708.4183 | 1244877.8065
20 | 2634720.723 | 1244883.5776 | 2634733.0673 | 1244889.0642
21 | 2634708.4183 | 1244877.8065 | 2634701.702 | 1244874.5995 | 2634695.898 | 1244871.402
22 | 2634755.9354 | 1244898.9699 | 2634739.899 | 1244892.1008 | 2634733.0673 | 1244889.0642
23 | 2634778.0801 | 1244908.4126 | 2634789.2584 | 1244913.3549
24 | 2634778.0801 | 1244908.4126 | 2634782.2368 | 1244897.7311
25 | 2634858.7714 | 1245068.777 | 2634864.3304 | 1245073.5878
26 | 2634846.2001 | 1245057.8977 | 2634858.7714 | 1245068.777
27 | 2634875.0554 | 1245082.1669 | 2634867.0001 | 1245075.8982 | 2634864.3304 | 1245073.5878
28 | 2634846.2001 | 1245057.8977 | 2634850.8997 | 1245055.3014 | 2634863.2998 | 1245049.4961
29 | 2634875.0554 | 1245082.1669 | 2634881.7808 | 1245087.4007
30 | 2634881.7808 | 1245087.4007 | 2634890.4673 | 1245094.1606
31 | 2634816.1997 | 1245074.2991 | 2634812.9025 | 1245076.1032 | 2634801.1441 | 1245079.3814
32 | 2634816.1997 | 1245074.2991 | 2634824.6043 | 1245082.7984 | 2634828.6372 | 1245086.4397
33 | 2634799.9132 | 1245079.7246 | 2634801.1441 | 1245079.3814
34 | 2634828.6372 | 1245086.4397 | 2634834.4874 | 1245091.7218
35 | 2634898.0433 | 1245100.0564 | 2634890.4673 | 1245094.1606
36 | 2634791.8112 | 1245081.9834 | 2634799.9132 | 1245079.7246
37 | 2634840.3762 | 1245096.6633 | 2634836.8997 | 1245093.8999 | 2634834.4874 | 1245091.7218
38 | 2634907.59 | 1245107.6315 | 2634899.0018 | 1245100.8023 | 2634898.0433 | 1245100.0564
39 | 2634791.8112 | 1245081.9834 | 2634789.1764 | 1245086.8044 | 2634779.3001 | 1245094.7962 | 2634769.5412 | 1245100.7874
40 | 2634791.8112 | 1245081.9834 | 2634783.7036 | 1245082.1027 | 2634775.7681 | 1245080.1923
41 | 2634840.3762 | 1245096.6633 | 2634845.9346 | 1245101.0816
42 | 2634667.3237 | 1244952.2108 | 2634654.1275 | 1244943.4185
43 | 2634667.3237 | 1244952.2108 | 2634667.9035 | 1244952.5972 | 2634670.4777 | 1244954.3424
44 | 2634685.0566 | 1244964.2267 | 2634670.4777 | 1244954.3424
45 | 2634687.321 | 1244965.7752 | 2634686.1985 | 1244965.0009 | 2634685.0566 | 1244964.2267
46 | 2634687.321 | 1244965.7752 | 2634701.9322 | 1244975.8537
47 | 2634703.2504 | 1244976.763 | 2634701.9322 | 1244975.8537
48 | 2634685.9027 | 1245037.6019 | 2634673.1982 | 1245030.5008 | 2634653.6021 | 1245019.7017 | 2634652.1973 | 1245018.9029
49 | 2634685.9027 | 1245037.6019 | 2634695.9036 | 1245043.1972 | 2634718.5153 | 1245057.4416
50 | 2634685.9027 | 1245037.6019 | 2634680.2016 | 1245047.3971 | 2634674.9951 | 1245056.6271
51 | 2634685.9027 | 1245037.6019 | 2634696.5128 | 1245019.7904
52 | 2634716.6987 | 1244985.9038 | 2634707.8032 | 1244979.9034 | 2634703.2504 | 1244976.763
53 | 2634678.5566 | 1244908.9992 | 2634673.1736 | 1244903.7711
54 | 2634678.5566 | 1244908.9992 | 2634683.6297 | 1244913.9263
55 | 2634668.6351 | 1244899.3484 | 2634669.8021 | 1244900.4967 | 2634673.1736 | 1244903.7711
56 | 2634694.7138 | 1244924.6913 | 2634683.6297 | 1244913.9263
57 | 2634668.6351 | 1244899.3484 | 2634662.0834 | 1244892.9015
58 | 2634694.7138 | 1244924.6913 | 2634697.3971 | 1244927.2974 | 2634705.9706 | 1244935.1847
59 | 2634640.0981 | 1244873.806 | 2634641.5035 | 1244873.8031 | 2634644.5001 | 1244875.5995 | 2634662.0834 | 1244892.9015
60 | 2634705.9706 | 1244935.1847 | 2634713.196 | 1244941.8318
61 | 2634640.0981 | 1244873.806 | 2634646.4969 | 1244862.3026 | 2634653.8018 | 1244847.0019
62 | 2634723.8213 | 1244953.355 | 2634718.5972 | 1244946.8006 | 2634713.196 | 1244941.8318
63 | 2634653.8018 | 1244847.0019 | 2634658.2001 | 1244837.7994 | 2634668.0021 | 1244817.9993 | 2634670.7261 | 1244810.855 | 2634675.2766 | 1244809.225 | 2634679.0159 | 1244806.7674 | 2634680.534 | 1244804.2858 | 2634684.8646 | 1244793.7376 | 2634687.8776 | 1244787.5623 | 2634690.9988 | 1244784.8677 | 2634695.9302 | 1244782.7062 | 2634699.6259 | 1244781.249
64 | 2634727.7987 | 1244961.1971 | 2634727.1031 | 1244958.7025 | 2634724.5001 | 1244954.2066 | 2634723.8213 | 1244953.355
65 | 2634870.1059 | 1245119.5889 | 2634876.6391 | 1245123.9283
66 | 2634857.6546 | 1245110.3977 | 2634864.702 | 1245115.9996 | 2634870.1059 | 1245119.5889
67 | 2634876.6391 | 1245123.9283 | 2634877.5036 | 1245124.5025 | 2634888.1985 | 1245131.5032 | 2634889.3606 | 1245132.0269
68 | 2634857.6546 | 1245110.3977 | 2634851.483 | 1245105.492
69 | 2634895.7917 | 1245134.9254 | 2634889.3606 | 1245132.0269
70 | 2634851.483 | 1245105.492 | 2634845.9346 | 1245101.0816
71 | 2634895.7917 | 1245134.9254 | 2634896.397 | 1245135.1982 | 2634904.3978 | 1245137.8025 | 2634905.5721 | 1245137.9653
72 | 2634919.7009 | 1245135.9023 | 2634917.5005 | 1245137.5015 | 2634911.5997 | 1245138.801 | 2634905.5721 | 1245137.9653
73 | 2634927.898 | 1245125.6994 | 2634924.8034 | 1245130.3064 | 2634919.7009 | 1245135.9023
74 | 2634760.9606 | 1245076.4547 | 2634770.4023 | 1245078.9005 | 2634775.7681 | 1245080.1923
75 | 2634760.9606 | 1245076.4547 | 2634759.5994 | 1245076.1021 | 2634754.9718 | 1245074.6213
76 | 2634731.6929 | 1245064.8056 | 2634739.897 | 1245069.3047 | 2634749.9014 | 1245072.9989 | 2634754.9718 | 1245074.6213
77 | 2634769.5412 | 1245100.7874 | 2634767.8773 | 1245101.6824
78 | 2634731.6929 | 1245064.8056 | 2634730.7833 | 1245064.3068
79 | 2634758.443 | 1245106.7629 | 2634760.4007 | 1245105.7038 | 2634767.8773 | 1245101.6824
80 | 2634730.7435 | 1245064.285 | 2634730.7833 | 1245064.3068
81 | 2634758.443 | 1245106.7629 | 2634752.8915 | 1245109.7661
82 | 2634718.5153 | 1245057.4416 | 2634720.2029 | 1245058.5047 | 2634730.7435 | 1245064.285
83 | 2634745.8141 | 1245113.2027 | 2634750.6006 | 1245111.0055 | 2634752.8915 | 1245109.7661
84 | 2634782.2368 | 1244897.7311 | 2634782.3344 | 1244897.4805
85 | 2634795.6748 | 1244916.0988 | 2634792.3007 | 1244914.6999 | 2634789.2584 | 1244913.3549
86 | 2634795.6748 | 1244916.0988 | 2634803.6032 | 1244919.386
87 | 2634868.0135 | 1244833.12 | 2634864.2014 | 1244835.9037 | 2634861.2392 | 1244838.5436 | 2634872.3744 | 1244863.549
88 | 2634897.2629 | 1244901.691 | 2634872.3744 | 1244863.549
89 | 2634897.2629 | 1244901.691 | 2634899.4019 | 1244900.3967 | 2634919.2011 | 1244889.506 | 2634925.4072 | 1244885.9405
90 | 2634889.2109 | 1244906.5631 | 2634897.2629 | 1244901.691
91 | 2634889.2109 | 1244906.5631 | 2634879.9273 | 1244912.185
92 | 2634699.6259 | 1244781.249 | 2634748.4516 | 1244812.1323
93 | 2634716.6987 | 1244985.9038 | 2634721.0998 | 1244978.8027 | 2634722.6701 | 1244976.1503
94 | 2634716.6987 | 1244985.9038 | 2634696.5128 | 1245019.7904
95 | 2634722.9927 | 1244975.6054 | 2634722.6701 | 1244976.1503
96 | 2634864.6191 | 1244921.4701 | 2634876.1006 | 1244914.5024 | 2634879.9273 | 1244912.185
97 | 2634864.6191 | 1244921.4701 | 2634853.2012 | 1244928.3992 | 2634848.2682 | 1244931.838
98 | 2634674.9951 | 1245056.6271 | 2634673.3743 | 1245059.5004
99 | 2634673.3743 | 1245059.5004 | 2634668.2995 | 1245068.4969 | 2634663.1582 | 1245076.3584
100 | 2634649.8553 | 1245096.6997 | 2634663.1582 | 1245076.3584
101 | 2634727.7987 | 1244961.1971 | 2634728.1979 | 1244962.7004 | 2634728.2041 | 1244966.8031 | 2634722.9927 | 1244975.6054
102 | 2634950.683 | 1245151.1415 | 2634947.2535 | 1245159.9873
103 | 2634957.445 | 1245133.7007 | 2634950.683 | 1245151.1415
104 | 2634947.2535 | 1245159.9873 | 2634942.4006 | 1245172.504 | 2634937.1871 | 1245196.5915
105 | 2634972.5774 | 1245097.9332 | 2634965.1261 | 1245116.19 | 2634964.1525 | 1245118.5859 | 2634957.445 | 1245133.7007
106 | 2634972.5774 | 1245097.9332 | 2634977.5271 | 1245084.9539 | 2634979.7986 | 1245078.9967 | 2634982.6894 | 1245070.4353
107 | 2634949.6611 | 1245090.4045 | 2634953.325 | 1245094.3286 | 2634953.3156 | 1245095.9296 | 2634952.4477 | 1245099.6047 | 2634952.1258 | 1245101.6708 | 2634952.1118 | 1245104.0389 | 2634952.4116 | 1245105.7306 | 2634953.1741 | 1245107.1138 | 2634959.7557 | 1245103.1166 | 2634966.3024 | 1245101.1983 | 2634972.5774 | 1245097.9332
108 | 2634949.6611 | 1245090.4045 | 2634954.4385 | 1245082.1107
109 | 2634949.6611 | 1245090.4045 | 2634948.0982 | 1245092.7969 | 2634933.6035 | 1245116.5048 | 2634927.898 | 1245125.6994
110 | 2634927.898 | 1245125.6994 | 2634926.5039 | 1245123.8011 | 2634916.222 | 1245114.5084
111 | 2634955.7878 | 1245079.7682 | 2634954.4385 | 1245082.1107
112 | 2634907.59 | 1245107.6315 | 2634916.1026 | 1245114.4005 | 2634916.222 | 1245114.5084
113 | 2634967.7671 | 1245024.2352 | 2634966.377 | 1245026.9617 | 2634966.6413 | 1245033.4008 | 2634968.3402 | 1245041.2825 | 2634968.7057 | 1245049.768 | 2634961.699 | 1245069.5062 | 2634955.7878 | 1245079.7682
114 | 2634724.962 | 1245120.4308 | 2634727.1033 | 1245120.0962 | 2634738.4038 | 1245116.6044 | 2634745.8141 | 1245113.2027
115 | 2634724.962 | 1245120.4308 | 2634714.8979 | 1245122.0038 | 2634712.9327 | 1245122.0266
116 | 2634699.5631 | 1245122.1812 | 2634712.9327 | 1245122.0266
117 | 2634699.5631 | 1245122.1812 | 2634698.2977 | 1245122.1958 | 2634687.5458 | 1245121.2668
118 | 2634783.1034 | 1244953.1819 | 2634764.4489 | 1244955.8906
119 | 2634727.7987 | 1244961.1971 | 2634739.6028 | 1244959.4983 | 2634753.9432 | 1244957.4161
120 | 2634753.9432 | 1244957.4161 | 2634764.4489 | 1244955.8906
121 | 2634967.7671 | 1245024.2352 | 2634969.5645 | 1245020.7097 | 2634970.991 | 1245014.5475 | 2634969.483 | 1245007.4485

## bus_geodata
| x | y | coords
0 | 2634785.2686 | 1244942.1745
1 | 2634799.9449 | 1244945.9761
2 | 2634763.5812 | 1244934.1777
3 | 2634809.6969 | 1244950.2027
4 | 2634736.0737 | 1244922.751
5 | 2634766.9814 | 1244925.7073
6 | 2634808.8531 | 1244950.2849
7 | 2634816.9579 | 1244950.1785
8 | 2634720.3889 | 1244910.6161
9 | 2634767.1491 | 1244925.2897
10 | 2634804.4617 | 1244950.7132
11 | 2634829.4003 | 1244944.003
12 | 2634774.5303 | 1244906.9019
13 | 2634795.193 | 1244951.617
14 | 2634842.0034 | 1244936.2052
15 | 2634715.9876 | 1244881.4207
16 | 2634720.723 | 1244883.5776
17 | 2634708.4183 | 1244877.8065
18 | 2634755.9354 | 1244898.9699
19 | 2634778.0801 | 1244908.4126
20 | 2634858.7714 | 1245068.777
21 | 2634864.3304 | 1245073.5878
22 | 2634846.2001 | 1245057.8977
23 | 2634875.0554 | 1245082.1669
24 | 2634863.2998 | 1245049.4961
25 | 2634881.7808 | 1245087.4007
26 | 2634816.1997 | 1245074.2991
27 | 2634801.1441 | 1245079.3814
28 | 2634828.6372 | 1245086.4397
29 | 2634890.4673 | 1245094.1606
30 | 2634799.9132 | 1245079.7246
31 | 2634834.4874 | 1245091.7218
32 | 2634898.0433 | 1245100.0564
33 | 2634791.8112 | 1245081.9834
34 | 2634840.3762 | 1245096.6633
35 | 2634667.3237 | 1244952.2108
36 | 2634654.1275 | 1244943.4185
37 | 2634670.4777 | 1244954.3424
38 | 2634685.0566 | 1244964.2267
39 | 2634687.321 | 1244965.7752
40 | 2634701.9322 | 1244975.8537
41 | 2634652.1973 | 1245018.9029
42 | 2634685.9027 | 1245037.6019
43 | 2634703.2504 | 1244976.763
44 | 2634678.5566 | 1244908.9992
45 | 2634673.1736 | 1244903.7711
46 | 2634683.6297 | 1244913.9263
47 | 2634668.6351 | 1244899.3484
48 | 2634694.7138 | 1244924.6913
49 | 2634662.0834 | 1244892.9015
50 | 2634705.9706 | 1244935.1847
51 | 2634640.0981 | 1244873.806
52 | 2634713.196 | 1244941.8318
53 | 2634653.8018 | 1244847.0019
54 | 2634723.8213 | 1244953.355
55 | 2634870.1059 | 1245119.5889
56 | 2634876.6391 | 1245123.9283
57 | 2634857.6546 | 1245110.3977
58 | 2634889.3606 | 1245132.0269
59 | 2634851.483 | 1245105.492
60 | 2634895.7917 | 1245134.9254
61 | 2634845.9346 | 1245101.0816
62 | 2634905.5721 | 1245137.9653
63 | 2634919.7009 | 1245135.9023
64 | 2634775.7681 | 1245080.1923
65 | 2634760.9606 | 1245076.4547
66 | 2634754.9718 | 1245074.6213
67 | 2634769.5412 | 1245100.7874
68 | 2634731.6929 | 1245064.8056
69 | 2634767.8773 | 1245101.6824
70 | 2634730.7833 | 1245064.3068
71 | 2634758.443 | 1245106.7629
72 | 2634730.7435 | 1245064.285
73 | 2634752.8915 | 1245109.7661
74 | 2634782.3344 | 1244897.4805
75 | 2634782.2368 | 1244897.7311
76 | 2634789.2584 | 1244913.3549
77 | 2634795.6748 | 1244916.0988
78 | 2634872.3744 | 1244863.549
79 | 2634868.0135 | 1244833.12
80 | 2634897.2629 | 1244901.691
81 | 2634925.4072 | 1244885.9405
82 | 2634889.2109 | 1244906.5631
83 | 2634803.6032 | 1244919.386
84 | 2634733.0673 | 1244889.0642
85 | 2634695.898 | 1244871.402
86 | 2634699.6259 | 1244781.249
87 | 2634748.4516 | 1244812.1323
88 | 2634716.6987 | 1244985.9038
89 | 2634722.6701 | 1244976.1503
90 | 2634696.5128 | 1245019.7904
91 | 2634864.6191 | 1244921.4701
92 | 2634879.9273 | 1244912.185
93 | 2634848.2682 | 1244931.8381
94 | 2634718.5153 | 1245057.4416
95 | 2634674.9951 | 1245056.6271
96 | 2634673.3743 | 1245059.5004
97 | 2634663.1582 | 1245076.3584
98 | 2634649.8553 | 1245096.6997
99 | 2634722.9927 | 1244975.6054
100 | 2634950.683 | 1245151.1415
101 | 2634947.2535 | 1245159.9872
102 | 2634957.445 | 1245133.7007
103 | 2634937.1871 | 1245196.5915
104 | 2634972.5774 | 1245097.9332
105 | 2634982.6894 | 1245070.4353
106 | 2634949.6611 | 1245090.4045
107 | 2634927.898 | 1245125.6994
108 | 2634954.4385 | 1245082.1107
109 | 2634916.222 | 1245114.5084
110 | 2634955.7878 | 1245079.7682
111 | 2634724.962 | 1245120.4308
112 | 2634745.8141 | 1245113.2027
113 | 2634712.9327 | 1245122.0266
114 | 2634699.5631 | 1245122.1812
115 | 2634687.5458 | 1245121.2668
116 | 2634783.1034 | 1244953.1819
117 | 2634727.7987 | 1244961.1971
118 | 2634753.9432 | 1244957.4161
119 | 2634969.483 | 1245007.4485
120 | 2634967.7671 | 1245024.2352
121 | 2634907.59 | 1245107.6315
122 | 2634764.4489 | 1244955.8906
123 | 2634816.1997 | 1245074.2991

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97112 | -0.55663 | 0.0018447 | 0.00046233
1 | 0.97124 | -0.55431 | 0.0034873 | 0.00087401
2 | 0.97096 | -0.55992 | 0 | 0
3 | 0.97133 | -0.55245 | 0 | 0
4 | 0.97085 | -0.56208 | 0.0016913 | 0.00042387
5 | 0.97079 | -0.56315 | 0.0015328 | 0.00038417
6 | 0.97135 | -0.55218 | 0.0025818 | 0.00064706
7 | 0.97126 | -0.55383 | 0.0080454 | 0.0020164
8 | 0.97081 | -0.5629 | 0.0022179 | 0.00055586
9 | 0.97079 | -0.5633 | 0.0016556 | 0.00041493
10 | 0.97142 | -0.5507 | 0.0081065 | 0.0020317
11 | 0.97116 | -0.55598 | 0.0029342 | 0.00073537
12 | 0.97049 | -0.56915 | 0 | 0
13 | 0.9716 | -0.54725 | 0.0044311 | 0.0011105
14 | 0.97105 | -0.55806 | 0 | 0
15 | 0.9701 | -0.57684 | 0 | 0
16 | 0.97012 | -0.57652 | 0.0017275 | 0.00043296
17 | 0.97008 | -0.57736 | 0.0019564 | 0.00049033
18 | 0.97034 | -0.57216 | 0.0013658 | 0.00034231
19 | 0.97046 | -0.56971 | 0 | 0
20 | 0.99867 | -0.024963 | 0.003348 | 0.00083908
21 | 0.99809 | -0.035915 | 0.0033613 | 0.00084243
22 | 1 | 0 | -0.44877 | -0.11476
23 | 0.99701 | -0.056212 | 0.0033239 | 0.00083304
24 | 0.99834 | -0.031962 | 0.096048 | 0.024072
25 | 0.99635 | -0.068701 | 0.0042673 | 0.0010695
26 | 0.98342 | -0.316 | 0 | 0
27 | 0.98252 | -0.3334 | 0.0018198 | 0.00045607
28 | 0.9844 | -0.29709 | 0.0044305 | 0.0011104
29 | 0.99551 | -0.08465 | 0.0042787 | 0.0010723
30 | 0.98245 | -0.33478 | 0.0025116 | 0.00062946
31 | 0.98485 | -0.28838 | 0.003181 | 0.00079723
32 | 0.99479 | -0.0984 | 0.0022334 | 0.00055975
33 | 0.98198 | -0.3438 | 0 | 0
34 | 0.9853 | -0.27977 | 0.0031838 | 0.00079793
35 | 0.97242 | -0.53107 | 0.0075953 | 0.0019035
36 | 0.9723 | -0.53329 | 0.0075931 | 0.001903
37 | 0.97247 | -0.53001 | 0.0027145 | 0.00068031
38 | 0.97276 | -0.5242 | 0.0039306 | 0.0009851
39 | 0.97282 | -0.52309 | 0.006683 | 0.0016749
40 | 0.97329 | -0.51378 | 0.0068902 | 0.0017269
41 | 0.97617 | -0.45719 | 0.0056392 | 0.0014133
42 | 0.97637 | -0.45321 | 0 | 0
43 | 0.97335 | -0.51273 | 0.0036605 | 0.00091741
44 | 0.97187 | -0.54189 | 0.0019036 | 0.0004771
45 | 0.9718 | -0.54327 | 0.0023535 | 0.00058984
46 | 0.97195 | -0.54033 | 0.0019464 | 0.00048781
47 | 0.97175 | -0.54416 | 0.002203 | 0.00055212
48 | 0.97215 | -0.53638 | 0.0026654 | 0.00066801
49 | 0.97171 | -0.54509 | 0.0026727 | 0.00066983
50 | 0.97238 | -0.5317 | 0.0022763 | 0.00057049
51 | 0.97163 | -0.5466 | 0 | 0
52 | 0.97256 | -0.5283 | 0.0026375 | 0.00066102
53 | 0.97155 | -0.54814 | 0 | 0
54 | 0.97287 | -0.52209 | 0.0047882 | 0.0012
55 | 0.98756 | -0.23631 | 0.0025115 | 0.00062944
56 | 0.98804 | -0.22704 | 0.003341 | 0.00083733
57 | 0.98661 | -0.25447 | 0.0033637 | 0.00084302
58 | 0.98898 | -0.209 | 0.002501 | 0.0006268
59 | 0.98614 | -0.26361 | 0.0031716 | 0.00079488
60 | 0.98942 | -0.2005 | 0.0013705 | 0.00034348
61 | 0.98571 | -0.27173 | 0.0031969 | 0.00080122
62 | 0.99007 | -0.18809 | 0.0014259 | 0.00035738
63 | 0.99102 | -0.17007 | 0 | 0
64 | 0.98114 | -0.36026 | 0.0036219 | 0.00090772
65 | 0.98035 | -0.37549 | 0.003632 | 0.00091026
66 | 0.98004 | -0.38164 | 0.0067026 | 0.0016798
67 | 0.98161 | -0.35104 | 0 | 0
68 | 0.9788 | -0.40579 | 0.0035752 | 0.00089602
69 | 0.98159 | -0.35151 | 0.0026911 | 0.00067444
70 | 0.97875 | -0.40677 | 0.0040537 | 0.001016
71 | 0.98148 | -0.35361 | 0.0011813 | 0.00029607
72 | 0.97875 | -0.40681 | 0.0038722 | 0.00097047
73 | 0.98143 | -0.35471 | 0.001175 | 0.00029447
74 | 0.97043 | -0.57035 | 0.0013759 | 0.00034482
75 | 0.97043 | -0.57034 | 0.0015799 | 0.00039597
76 | 0.97041 | -0.57083 | 0.0015451 | 0.00038723
77 | 0.97038 | -0.57127 | 0.0016252 | 0.00040732
78 | 0.97016 | -0.57567 | 0.0064185 | 0.0016086
79 | 0.97003 | -0.57829 | 0.0039222 | 0.00098299
80 | 0.9706 | -0.56695 | 0.0073045 | 0.0018307
81 | 0.97044 | -0.5701 | 0.0052827 | 0.001324
82 | 0.9707 | -0.56495 | 0 | 0
83 | 0.97037 | -0.57155 | 0.0017737 | 0.00044454
84 | 0.97018 | -0.57525 | 0.0016126 | 0.00040415
85 | 0.97006 | -0.57772 | 0.0013892 | 0.00034817
86 | 0.97134 | -0.55243 | 0 | 0
87 | 0.97119 | -0.55538 | 0.0027658 | 0.00069317
88 | 0.97394 | -0.50105 | 0 | 0
89 | 0.97358 | -0.50805 | 0.0024079 | 0.00060348
90 | 0.97552 | -0.4699 | 0.0037362 | 0.00093637
91 | 0.97087 | -0.56165 | 0.0020704 | 0.00051888
92 | 0.97076 | -0.5638 | 0.0031099 | 0.00077942
93 | 0.971 | -0.55913 | 0.0022133 | 0.0005547
94 | 0.9781 | -0.41946 | 0.0045445 | 0.001139
95 | 0.97613 | -0.45808 | 0.0033712 | 0.0008449
96 | 0.9761 | -0.45861 | 0.002501 | 0.00062682
97 | 0.97598 | -0.46087 | 0.0036096 | 0.00090465
98 | 0.97592 | -0.46205 | 0.0026561 | 0.00066568
99 | 0.97356 | -0.50843 | 0.0024299 | 0.000609
100 | 0.98853 | -0.21854 | 0.0020805 | 0.00052143
101 | 0.98839 | -0.2212 | 0.0020814 | 0.00052166
102 | 0.98884 | -0.21262 | 0 | 0
103 | 0.98792 | -0.23044 | 0.013604 | 0.0034095
104 | 0.98947 | -0.20033 | 0 | 0
105 | 0.98943 | -0.20099 | 0.0012702 | 0.00031834
106 | 0.99017 | -0.18674 | 0 | 0
107 | 0.99185 | -0.15419 | 0 | 0
108 | 0.98995 | -0.19104 | 0.0027225 | 0.00068233
109 | 0.99305 | -0.13141 | 0.0033704 | 0.00084471
110 | 0.98989 | -0.19212 | 0.0030726 | 0.00077006
111 | 0.98122 | -0.3588 | 0.0013377 | 0.00033525
112 | 0.98137 | -0.35592 | 0.00131 | 0.00032833
113 | 0.98115 | -0.36008 | 0.0019582 | 0.00049076
114 | 0.98111 | -0.36102 | 0.0019511 | 0.00048899
115 | 0.98108 | -0.36145 | 0.0019305 | 0.00048384
116 | 0.97184 | -0.54247 | 0.0044239 | 0.0011087
117 | 0.97309 | -0.5178 | 0 | 0
118 | 0.97246 | -0.53022 | 0.010244 | 0.0025674
119 | 0.98868 | -0.21571 | 0.010317 | 0.0025857
120 | 0.98884 | -0.21248 | 0.0091143 | 0.0022843
121 | 0.99387 | -0.11577 | 0.0023502 | 0.00058902
122 | 0.97223 | -0.53471 | 0.0025671 | 0.00064337
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024909 | -0.0062451 | 0.024911 | 0.0062463 | 2.7607e-06 | 1.204e-06 | 0.038168 | 0.038167 | 0.038168 | 0.97112 | -0.55663 | 0.97124 | -0.55431 | 3.4952
1 | 0.023064 | 0.0057827 | -0.02306 | -0.0057813 | 3.616e-06 | 1.4547e-06 | 0.035341 | 0.035341 | 0.035341 | 0.97112 | -0.55663 | 0.97096 | -0.55992 | 3.2364
2 | -0.028399 | -0.0071203 | 0.028401 | 0.0071215 | 2.5152e-06 | 1.2151e-06 | 0.04351 | 0.04351 | 0.04351 | 0.97124 | -0.55431 | 0.97133 | -0.55245 | 3.9844
3 | 0.0039097 | 0.00097943 | -0.0039093 | -0.00097954 | 4.0099e-07 | -1.1173e-07 | 0.0059915 | 0.0059916 | 0.0059916 | 0.97096 | -0.55992 | 0.97085 | -0.56208 | 1.6461
4 | 0.019151 | 0.0048018 | -0.019148 | -0.0048001 | 2.9484e-06 | 1.7741e-06 | 0.02935 | 0.02935 | 0.02935 | 0.97096 | -0.55992 | 0.97079 | -0.56315 | 8.0631
5 | -0.069728 | -0.017483 | 0.069729 | 0.017483 | 9.0694e-07 | 5.3846e-07 | 0.10682 | 0.10682 | 0.10682 | 0.97133 | -0.55245 | 0.97135 | -0.55218 | 7.3366
6 | 0.041327 | 0.010361 | -0.041324 | -0.01036 | 2.7286e-06 | 1.3868e-06 | 0.063311 | 0.063311 | 0.063311 | 0.97133 | -0.55245 | 0.97126 | -0.55383 | 4.3483
7 | 0.002218 | 0.00055566 | -0.0022179 | -0.00055586 | 8.7277e-08 | -1.9317e-07 | 0.0033994 | 0.0033995 | 0.0033995 | 0.97085 | -0.56208 | 0.97081 | -0.5629 | 0.93393
8 | 0.017615 | 0.0044159 | -0.017615 | -0.0044158 | 1.2304e-07 | 7.3184e-08 | 0.027 | 0.027 | 0.027 | 0.97079 | -0.56315 | 0.97079 | -0.5633 | 7.4176
9 | -0.072311 | -0.01813 | 0.072316 | 0.018133 | 5.0761e-06 | 3.0302e-06 | 0.11078 | 0.11078 | 0.11078 | 0.97135 | -0.55218 | 0.97142 | -0.5507 | 7.6083
10 | 0.033279 | 0.0083436 | -0.033275 | -0.0083421 | 3.4055e-06 | 1.4878e-06 | 0.050986 | 0.050986 | 0.050986 | 0.97126 | -0.55383 | 0.97116 | -0.55598 | 3.5018
11 | 0.015959 | 0.0040009 | -0.015955 | -0.0039983 | 4.4464e-06 | 2.6008e-06 | 0.024463 | 0.024463 | 0.024463 | 0.97079 | -0.5633 | 0.97049 | -0.56915 | 6.7205
12 | -0.080422 | -0.020165 | 0.080436 | 0.020173 | 1.325e-05 | 8.0188e-06 | 0.12319 | 0.12319 | 0.12319 | 0.97142 | -0.5507 | 0.9716 | -0.54725 | 8.4611
13 | 0.030341 | 0.0076067 | -0.030338 | -0.0076055 | 3.0047e-06 | 1.1892e-06 | 0.04649 | 0.04649 | 0.04649 | 0.97116 | -0.55598 | 0.97105 | -0.55806 | 3.193
14 | 0.0080542 | 0.0020185 | -0.0080531 | -0.002018 | 1.1561e-06 | 4.9017e-07 | 0.012349 | 0.012349 | 0.012349 | 0.97049 | -0.56915 | 0.97034 | -0.57216 | 3.3927
15 | 0.0079005 | 0.0019798 | -0.0079003 | -0.0019797 | 2.1174e-07 | 8.7967e-08 | 0.012113 | 0.012113 | 0.012113 | 0.97049 | -0.56915 | 0.97046 | -0.56971 | 3.3279
16 | -0.084867 | -0.021284 | 0.084886 | 0.021295 | 1.9313e-05 | 1.1756e-05 | 0.12998 | 0.12998 | 0.12998 | 0.9716 | -0.54725 | 0.97184 | -0.54247 | 8.9272
17 | 0.030338 | 0.0076055 | -0.030337 | -0.0076049 | 1.5474e-06 | 6.1247e-07 | 0.04649 | 0.04649 | 0.04649 | 0.97105 | -0.55806 | 0.971 | -0.55913 | 3.193
18 | -0.0033458 | -0.0008383 | 0.0033458 | 0.00083826 | 5.1391e-08 | -3.1356e-08 | 0.0051319 | 0.0051319 | 0.0051319 | 0.9701 | -0.57684 | 0.97012 | -0.57652 | 1.4099
19 | 0.0033458 | 0.0008383 | -0.0033457 | -0.00083835 | 8.2841e-08 | -5.054e-08 | 0.0051319 | 0.005132 | 0.005132 | 0.9701 | -0.57684 | 0.97008 | -0.57736 | 1.4099
20 | -0.0050734 | -0.0012712 | 0.0050737 | 0.0012713 | 3.0675e-07 | 2.9519e-08 | 0.0077817 | 0.0077816 | 0.0077817 | 0.97012 | -0.57652 | 0.97018 | -0.57525 | 2.1378
21 | 0.0013892 | 0.00034801 | -0.0013892 | -0.00034817 | 2.3958e-08 | -1.5836e-07 | 0.0021309 | 0.002131 | 0.002131 | 0.97008 | -0.57736 | 0.97006 | -0.57772 | 0.58544
22 | 0.0066872 | 0.0016757 | -0.0066862 | -0.0016754 | 9.8281e-07 | 3.212e-07 | 0.010255 | 0.010255 | 0.010255 | 0.97034 | -0.57216 | 0.97018 | -0.57525 | 2.8173
23 | 0.0049444 | 0.001239 | -0.0049441 | -0.001239 | 2.6342e-07 | 1.7588e-08 | 0.0075812 | 0.0075812 | 0.0075812 | 0.97046 | -0.56971 | 0.97041 | -0.57083 | 2.0828
24 | 0.0029559 | 0.0007407 | -0.0029558 | -0.00074079 | 8.8291e-08 | -8.5108e-08 | 0.0045322 | 0.0045323 | 0.0045323 | 0.97046 | -0.56971 | 0.97043 | -0.57034 | 1.2451
25 | 0.34715 | 0.089483 | -0.34697 | -0.089365 | 0.00018503 | 0.00011804 | 0.51814 | 0.51814 | 0.51814 | 0.99867 | -0.024963 | 0.99809 | -0.035915 | 35.5864
26 | -0.3505 | -0.090322 | 0.35093 | 0.090594 | 0.00042653 | 0.00027211 | 0.52313 | 0.52313 | 0.52313 | 0.99867 | -0.024963 | 1 | 0 | 35.9289
27 | 0.34361 | 0.088522 | -0.34327 | -0.088306 | 0.00033911 | 0.00021631 | 0.51313 | 0.51313 | 0.51313 | 0.99809 | -0.035915 | 0.99701 | -0.056212 | 35.2422
28 | 0.096194 | 0.024165 | -0.096048 | -0.024072 | 0.00014649 | 9.3504e-05 | 0.14316 | 0.14316 | 0.14316 | 1 | 0 | 0.99834 | -0.031962 | 39.3292
29 | 0.33994 | 0.087473 | -0.33974 | -0.087341 | 0.00020631 | 0.00013159 | 0.50817 | 0.50817 | 0.50817 | 0.99701 | -0.056212 | 0.99635 | -0.068701 | 34.9015
30 | 0.33547 | 0.086272 | -0.33521 | -0.086106 | 0.00025983 | 0.00016572 | 0.50179 | 0.50179 | 0.50179 | 0.99635 | -0.068701 | 0.99551 | -0.08465 | 34.4638
31 | 0.24374 | 0.061909 | -0.24353 | -0.06178 | 0.0002039 | 0.00012969 | 0.36909 | 0.36909 | 0.36909 | 0.98342 | -0.316 | 0.98252 | -0.3334 | 25.3499
32 | -0.24374 | -0.061909 | 0.24396 | 0.062051 | 0.00022205 | 0.00014123 | 0.36909 | 0.36909 | 0.36909 | 0.98342 | -0.316 | 0.9844 | -0.29709 | 25.3499
33 | 0.24171 | 0.061324 | -0.2417 | -0.061313 | 1.6078e-05 | 1.0225e-05 | 0.36634 | 0.36634 | 0.36634 | 0.98252 | -0.3334 | 0.98245 | -0.33478 | 25.1606
34 | -0.24839 | -0.063161 | 0.24849 | 0.063227 | 0.00010435 | 6.6385e-05 | 0.37579 | 0.37579 | 0.37579 | 0.9844 | -0.29709 | 0.98485 | -0.28838 | 25.8098
35 | 0.33093 | 0.085034 | -0.33071 | -0.084893 | 0.00022087 | 0.00014086 | 0.4954 | 0.4954 | 0.4954 | 0.99551 | -0.08465 | 0.99479 | -0.0984 | 34.0246
36 | 0.23918 | 0.060684 | -0.23908 | -0.060618 | 0.00010364 | 6.5901e-05 | 0.36253 | 0.36253 | 0.36253 | 0.98245 | -0.33478 | 0.98198 | -0.3438 | 24.8993
37 | -0.25167 | -0.064025 | 0.25178 | 0.064091 | 0.00010445 | 6.6454e-05 | 0.3806 | 0.3806 | 0.3806 | 0.98485 | -0.28838 | 0.9853 | -0.27977 | 26.1399
38 | 0.32848 | 0.084333 | -0.3282 | -0.084157 | 0.00027663 | 0.00017641 | 0.49206 | 0.49206 | 0.49206 | 0.99479 | -0.0984 | 0.99387 | -0.11577 | 33.7952
39 | 0.013543 | 0.0033962 | -0.013539 | -0.0033936 | 4.6756e-06 | 2.618e-06 | 0.020523 | 0.020523 | 0.020523 | 0.98198 | -0.3438 | 0.98161 | -0.35104 | 5.6383
40 | 0.22554 | 0.057222 | -0.22536 | -0.057108 | 0.00017843 | 0.00011337 | 0.34201 | 0.34201 | 0.34201 | 0.98198 | -0.3438 | 0.98114 | -0.36026 | 23.4898
41 | -0.25496 | -0.064889 | 0.25506 | 0.064952 | 9.8877e-05 | 6.2919e-05 | 0.3854 | 0.3854 | 0.3854 | 0.9853 | -0.27977 | 0.98571 | -0.27173 | 26.4701
42 | 0.0075939 | 0.0019033 | -0.0075931 | -0.001903 | 8.0297e-07 | 3.1721e-07 | 0.01162 | 0.011621 | 0.011621 | 0.97242 | -0.53107 | 0.9723 | -0.53329 | 3.1925
43 | -0.015189 | -0.0038069 | 0.01519 | 0.0038073 | 7.7122e-07 | 4.4635e-07 | 0.023243 | 0.023243 | 0.023243 | 0.97242 | -0.53107 | 0.97247 | -0.53001 | 6.3854
44 | -0.017904 | -0.0044876 | 0.017909 | 0.0044906 | 4.9576e-06 | 2.9542e-06 | 0.027396 | 0.027396 | 0.027396 | 0.97247 | -0.53001 | 0.97276 | -0.5242 | 7.5265
45 | -0.02184 | -0.0054757 | 0.021841 | 0.0054764 | 1.1482e-06 | 7.0079e-07 | 0.033409 | 0.033409 | 0.033409 | 0.97276 | -0.5242 | 0.97282 | -0.52309 | 9.1783
46 | -0.028524 | -0.0071513 | 0.028537 | 0.0071592 | 1.2671e-05 | 7.8892e-06 | 0.043631 | 0.043631 | 0.043631 | 0.97282 | -0.52309 | 0.97329 | -0.51378 | 11.9866
47 | -0.035427 | -0.0088861 | 0.035429 | 0.0088872 | 1.7619e-06 | 1.1077e-06 | 0.054165 | 0.054165 | 0.054165 | 0.97329 | -0.51378 | 0.97335 | -0.51273 | 14.8805
48 | -0.0056392 | -0.0014133 | 0.0056402 | 0.0014135 | 1.068e-06 | 2.0157e-07 | 0.008596 | 0.0085958 | 0.008596 | 0.97617 | -0.45719 | 0.97637 | -0.45321 | 2.3615
49 | -0.19444 | -0.049008 | 0.19476 | 0.049207 | 0.00031456 | 0.0001994 | 0.29643 | 0.29643 | 0.29643 | 0.97637 | -0.45321 | 0.9781 | -0.41946 | 20.3593
50 | 0.012142 | 0.0030437 | -0.012139 | -0.0030421 | 2.8161e-06 | 1.5281e-06 | 0.018505 | 0.018505 | 0.018505 | 0.97637 | -0.45321 | 0.97613 | -0.45808 | 5.0837
51 | 0.17666 | 0.04455 | -0.17652 | -0.044461 | 0.00014099 | 8.9198e-05 | 0.26933 | 0.26933 | 0.26933 | 0.97637 | -0.45321 | 0.97552 | -0.4699 | 18.4981
52 | -0.039089 | -0.0098046 | 0.039111 | 0.0098183 | 2.1778e-05 | 1.3736e-05 | 0.059761 | 0.059761 | 0.059761 | 0.97335 | -0.51273 | 0.97394 | -0.50105 | 16.4179
53 | 0.0099975 | 0.0025038 | -0.0099968 | -0.0025035 | 6.5928e-07 | 3.2896e-07 | 0.015306 | 0.015306 | 0.015306 | 0.97187 | -0.54189 | 0.9718 | -0.54327 | 4.2051
54 | -0.011901 | -0.0029809 | 0.011902 | 0.0029814 | 8.8048e-07 | 4.7586e-07 | 0.018221 | 0.018221 | 0.018221 | 0.97187 | -0.54189 | 0.97195 | -0.54033 | 5.0058
55 | 0.0076433 | 0.0019137 | -0.007643 | -0.0019135 | 3.2546e-07 | 1.2978e-07 | 0.011703 | 0.011703 | 0.011703 | 0.9718 | -0.54327 | 0.97175 | -0.54416 | 3.2151
56 | -0.013848 | -0.0034692 | 0.013851 | 0.0034707 | 2.6044e-06 | 1.4753e-06 | 0.021201 | 0.021201 | 0.021201 | 0.97195 | -0.54033 | 0.97215 | -0.53638 | 5.8244
57 | 0.00544 | 0.0013614 | -0.0054398 | -0.0013614 | 2.3915e-07 | 3.9186e-08 | 0.0083294 | 0.0083295 | 0.0083295 | 0.97175 | -0.54416 | 0.97171 | -0.54509 | 2.2883
58 | -0.016516 | -0.0041387 | 0.01652 | 0.0041409 | 3.6885e-06 | 2.1698e-06 | 0.025281 | 0.02528 | 0.025281 | 0.97215 | -0.53638 | 0.97238 | -0.5317 | 6.9452
59 | 0.0027671 | 0.00069154 | -0.0027669 | -0.00069178 | 1.9903e-07 | -2.3886e-07 | 0.0042367 | 0.0042368 | 0.0042368 | 0.97171 | -0.54509 | 0.97163 | -0.5466 | 1.164
60 | -0.018796 | -0.0047114 | 0.018799 | 0.0047132 | 3.0461e-06 | 1.8277e-06 | 0.028764 | 0.028764 | 0.028764 | 0.97238 | -0.5317 | 0.97256 | -0.5283 | 7.9021
61 | 0.0027669 | 0.00069178 | -0.0027667 | -0.00069203 | 2.0265e-07 | -2.4312e-07 | 0.0042368 | 0.004237 | 0.004237 | 0.97163 | -0.5466 | 0.97155 | -0.54814 | 1.164
62 | -0.021437 | -0.0053742 | 0.021443 | 0.0053781 | 6.342e-06 | 3.8637e-06 | 0.032799 | 0.032799 | 0.032799 | 0.97256 | -0.5283 | 0.97287 | -0.52209 | 9.0108
63 | 0.0027667 | 0.00069203 | -0.0027662 | -0.0006927 | 5.6494e-07 | -6.7732e-07 | 0.004237 | 0.0042374 | 0.0042374 | 0.97155 | -0.54814 | 0.97134 | -0.55243 | 1.1641
64 | -0.026231 | -0.0065781 | 0.026237 | 0.0065814 | 5.357e-06 | 3.3183e-06 | 0.040123 | 0.040123 | 0.040123 | 0.97287 | -0.52209 | 0.97309 | -0.5178 | 11.0227
65 | -0.26775 | -0.068306 | 0.26787 | 0.068383 | 0.00011993 | 7.6357e-05 | 0.40387 | 0.40387 | 0.40387 | 0.98756 | -0.23631 | 0.98804 | -0.22704 | 27.7385
66 | 0.26524 | 0.067677 | -0.26501 | -0.067529 | 0.00023245 | 0.00014798 | 0.40009 | 0.40009 | 0.40009 | 0.98756 | -0.23631 | 0.98661 | -0.25447 | 27.4787
67 | -0.27121 | -0.06922 | 0.27145 | 0.069371 | 0.00023662 | 0.00015066 | 0.4089 | 0.4089 | 0.4089 | 0.98804 | -0.22704 | 0.98898 | -0.209 | 28.0841
68 | 0.26165 | 0.066686 | -0.26153 | -0.066612 | 0.00011533 | 7.3408e-05 | 0.39502 | 0.39502 | 0.39502 | 0.98661 | -0.25447 | 0.98614 | -0.26361 | 27.1302
69 | -0.27395 | -0.069997 | 0.27407 | 0.070069 | 0.00011262 | 7.1715e-05 | 0.41267 | 0.41267 | 0.41267 | 0.98898 | -0.209 | 0.98942 | -0.2005 | 28.3425
70 | 0.25836 | 0.065817 | -0.25826 | -0.065753 | 0.00010119 | 6.4398e-05 | 0.39023 | 0.39023 | 0.39023 | 0.98614 | -0.26361 | 0.98571 | -0.27173 | 26.8016
71 | -0.27544 | -0.070413 | 0.2756 | 0.070518 | 0.0001655 | 0.00010539 | 0.41473 | 0.41473 | 0.41473 | 0.98942 | -0.2005 | 0.99007 | -0.18809 | 28.4841
72 | -0.27703 | -0.070875 | 0.27727 | 0.071029 | 0.0002419 | 0.00015405 | 0.41687 | 0.41687 | 0.41687 | 0.99007 | -0.18809 | 0.99102 | -0.17007 | 28.6313
73 | -0.27727 | -0.071029 | 0.27748 | 0.071165 | 0.00021356 | 0.000136 | 0.41687 | 0.41687 | 0.41687 | 0.99102 | -0.17007 | 0.99185 | -0.15419 | 28.6312
74 | 0.22174 | 0.056201 | -0.22158 | -0.056098 | 0.00016214 | 0.000103 | 0.33652 | 0.33652 | 0.33652 | 0.98114 | -0.36026 | 0.98035 | -0.37549 | 23.1125
75 | 0.21794 | 0.055187 | -0.21788 | -0.055147 | 6.4351e-05 | 4.0869e-05 | 0.33101 | 0.33101 | 0.33101 | 0.98035 | -0.37549 | 0.98004 | -0.38164 | 22.7339
76 | 0.21118 | 0.053467 | -0.21093 | -0.053311 | 0.00024458 | 0.00015525 | 0.32083 | 0.32083 | 0.32083 | 0.98004 | -0.38164 | 0.9788 | -0.40579 | 22.035
77 | 0.013539 | 0.0033936 | -0.013539 | -0.0033934 | 2.9843e-07 | 1.6711e-07 | 0.020523 | 0.020523 | 0.020523 | 0.98161 | -0.35104 | 0.98159 | -0.35151 | 5.6383
78 | 0.20736 | 0.052415 | -0.20735 | -0.052409 | 9.6741e-06 | 6.1393e-06 | 0.31539 | 0.31539 | 0.31539 | 0.9788 | -0.40579 | 0.97875 | -0.40677 | 21.6617
79 | 0.010847 | 0.002719 | -0.010846 | -0.0027184 | 1.0866e-06 | 5.5996e-07 | 0.016444 | 0.016444 | 0.016444 | 0.98159 | -0.35151 | 0.98148 | -0.35361 | 4.5176
80 | 0.20329 | 0.051393 | -0.20329 | -0.051393 | 4.0667e-07 | 2.5799e-07 | 0.30923 | 0.30923 | 0.30923 | 0.97875 | -0.40677 | 0.97875 | -0.40681 | 21.2384
81 | 0.009665 | 0.0024223 | -0.0096645 | -0.0024221 | 5.0821e-07 | 2.4549e-07 | 0.014653 | 0.014653 | 0.014653 | 0.98148 | -0.35361 | 0.98143 | -0.35471 | 4.0256
82 | 0.19942 | 0.050423 | -0.1993 | -0.050346 | 0.00012091 | 7.668e-05 | 0.30334 | 0.30334 | 0.30334 | 0.97875 | -0.40681 | 0.9781 | -0.41946 | 20.8341
83 | 0.0084896 | 0.0021276 | -0.0084891 | -0.0021274 | 4.8905e-07 | 2.1353e-07 | 0.012872 | 0.012872 | 0.012872 | 0.98143 | -0.35471 | 0.98137 | -0.35592 | 3.5362
84 | -0.0013759 | -0.00034482 | 0.0013759 | 0.00034482 | 4.4837e-10 | -3.035e-09 | 0.0021097 | 0.0021097 | 0.0021097 | 0.97043 | -0.57035 | 0.97043 | -0.57034 | 0.57958
85 | 0.0033991 | 0.00085173 | -0.003399 | -0.00085177 | 7.1095e-08 | -4.0717e-08 | 0.005212 | 0.0052121 | 0.0052121 | 0.97041 | -0.57083 | 0.97038 | -0.57127 | 1.4319
86 | 0.0017738 | 0.00044445 | -0.0017737 | -0.00044454 | 2.3811e-08 | -9.0789e-08 | 0.0027199 | 0.0027199 | 0.0027199 | 0.97038 | -0.57127 | 0.97037 | -0.57155 | 0.74724
87 | 0.0039227 | 0.00098286 | -0.0039222 | -0.00098299 | 4.895e-07 | -1.3194e-07 | 0.0060164 | 0.0060166 | 0.0060166 | 0.97016 | -0.57567 | 0.97003 | -0.57829 | 1.6529
88 | -0.010341 | -0.0025915 | 0.010345 | 0.0025937 | 4.2965e-06 | 2.1871e-06 | 0.015861 | 0.015861 | 0.015861 | 0.97016 | -0.57567 | 0.9706 | -0.56695 | 4.3574
89 | 0.0052835 | 0.0013241 | -0.0052827 | -0.001324 | 7.936e-07 | 1.0933e-07 | 0.0081001 | 0.0081002 | 0.0081002 | 0.9706 | -0.56695 | 0.97044 | -0.5701 | 2.2253
90 | -0.022933 | -0.0057484 | 0.022936 | 0.0057496 | 2.1814e-06 | 1.1634e-06 | 0.035159 | 0.035159 | 0.035159 | 0.9706 | -0.56695 | 0.9707 | -0.56495 | 4.8296
91 | -0.022936 | -0.0057496 | 0.022937 | 0.0057499 | 1.2578e-06 | 2.6829e-07 | 0.035159 | 0.035159 | 0.035159 | 0.9707 | -0.56495 | 0.97076 | -0.5638 | 2.4148
92 | 0.0027662 | 0.0006927 | -0.0027658 | -0.00069317 | 3.8821e-07 | -4.6505e-07 | 0.0042374 | 0.0042376 | 0.0042376 | 0.97134 | -0.55243 | 0.97119 | -0.55538 | 1.1642
93 | 0.13341 | 0.033544 | -0.13337 | -0.033516 | 4.4565e-05 | 2.7952e-05 | 0.20387 | 0.20387 | 0.20387 | 0.97394 | -0.50105 | 0.97358 | -0.50805 | 14.0022
94 | -0.17252 | -0.043362 | 0.17278 | 0.043525 | 0.00025701 | 0.00016252 | 0.26363 | 0.26363 | 0.26363 | 0.97394 | -0.50105 | 0.97552 | -0.4699 | 18.1067
95 | 0.13096 | 0.032913 | -0.13096 | -0.032911 | 2.3791e-06 | 1.4912e-06 | 0.20019 | 0.20019 | 0.20019 | 0.97358 | -0.50805 | 0.97356 | -0.50843 | 13.7495
96 | 0.02605 | 0.0065301 | -0.026047 | -0.0065293 | 2.6757e-06 | 8.2692e-07 | 0.039926 | 0.039926 | 0.039926 | 0.97087 | -0.56165 | 0.97076 | -0.5638 | 2.7422
97 | -0.02812 | -0.007049 | 0.028123 | 0.0070502 | 3.373e-06 | 1.2005e-06 | 0.043099 | 0.043099 | 0.043099 | 0.97087 | -0.56165 | 0.971 | -0.55913 | 2.9601
98 | 0.0087678 | 0.0021972 | -0.0087676 | -0.0021971 | 2.2099e-07 | 1.002e-07 | 0.013366 | 0.013366 | 0.013366 | 0.97613 | -0.45808 | 0.9761 | -0.45861 | 3.6719
99 | 0.0062665 | 0.0015703 | -0.0062659 | -0.0015701 | 6.7496e-07 | 1.8548e-07 | 0.009553 | 0.0095531 | 0.0095531 | 0.9761 | -0.45861 | 0.97598 | -0.46087 | 2.6245
100 | 0.0026563 | 0.00066548 | -0.0026561 | -0.00066568 | 1.4948e-07 | -2.0805e-07 | 0.0040497 | 0.0040498 | 0.0040498 | 0.97598 | -0.46087 | 0.97592 | -0.46205 | 1.1126
101 | 0.12853 | 0.032302 | -0.12847 | -0.032266 | 5.7499e-05 | 3.6009e-05 | 0.19648 | 0.19648 | 0.19648 | 0.97356 | -0.50843 | 0.97309 | -0.5178 | 13.4944
102 | 0.015694 | 0.0039357 | -0.015692 | -0.0039345 | 1.9856e-06 | 1.1492e-06 | 0.023624 | 0.023624 | 0.023624 | 0.98853 | -0.21854 | 0.98839 | -0.2212 | 6.4902
103 | -0.017774 | -0.0044571 | 0.017779 | 0.0044601 | 5.0217e-06 | 2.974e-06 | 0.026756 | 0.026756 | 0.026756 | 0.98853 | -0.21854 | 0.98884 | -0.21262 | 7.3505
104 | 0.01361 | 0.0034129 | -0.013604 | -0.0034095 | 5.9941e-06 | 3.3486e-06 | 0.020491 | 0.020491 | 0.020491 | 0.98839 | -0.2212 | 0.98792 | -0.23044 | 5.6293
105 | -0.017779 | -0.0044601 | 0.01779 | 0.0044663 | 1.0423e-05 | 6.1726e-06 | 0.026756 | 0.026756 | 0.026756 | 0.98884 | -0.21262 | 0.98947 | -0.20033 | 7.3505
106 | 0.0012702 | 0.00031799 | -0.0012702 | -0.00031834 | 4.0096e-08 | -3.507e-07 | 0.0019101 | 0.0019103 | 0.0019103 | 0.98947 | -0.20033 | 0.98943 | -0.20099 | 0.5248
107 | -0.01906 | -0.0047843 | 0.019072 | 0.0047917 | 1.2356e-05 | 7.3926e-06 | 0.028666 | 0.028666 | 0.028666 | 0.98947 | -0.20033 | 0.99017 | -0.18674 | 7.8752
108 | 0.025253 | 0.0063383 | -0.025248 | -0.0063352 | 5.1703e-06 | 3.1859e-06 | 0.037954 | 0.037954 | 0.037954 | 0.99017 | -0.18674 | 0.98995 | -0.19104 | 10.4268
109 | -0.044325 | -0.01113 | 0.044394 | 0.011174 | 6.8962e-05 | 4.3602e-05 | 0.066619 | 0.066619 | 0.066619 | 0.99017 | -0.18674 | 0.99185 | -0.15419 | 18.302
110 | -0.32188 | -0.082339 | 0.32223 | 0.082566 | 0.00035534 | 0.00022658 | 0.48349 | 0.48349 | 0.48349 | 0.99185 | -0.15419 | 0.99305 | -0.13141 | 33.2067
111 | 0.022526 | 0.0056528 | -0.022524 | -0.0056521 | 1.1623e-06 | 7.0914e-07 | 0.033861 | 0.033861 | 0.033861 | 0.98995 | -0.19104 | 0.98989 | -0.19212 | 9.3026
112 | -0.3256 | -0.08341 | 0.32585 | 0.083568 | 0.00024695 | 0.00015748 | 0.48854 | 0.48854 | 0.48854 | 0.99305 | -0.13141 | 0.99387 | -0.11577 | 33.5535
113 | 0.019452 | 0.0048821 | -0.019433 | -0.0048707 | 1.8871e-05 | 1.1322e-05 | 0.029243 | 0.029243 | 0.029243 | 0.98989 | -0.19212 | 0.98884 | -0.21248 | 8.0338
114 | -0.007178 | -0.0017987 | 0.007179 | 0.0017991 | 9.8416e-07 | 3.5006e-07 | 0.010885 | 0.010885 | 0.010885 | 0.98122 | -0.3588 | 0.98137 | -0.35592 | 2.9905
115 | 0.0058404 | 0.0014635 | -0.00584 | -0.0014634 | 3.5746e-07 | 7.5295e-08 | 0.0088568 | 0.0088569 | 0.0088569 | 0.98122 | -0.3588 | 0.98115 | -0.36008 | 2.4332
116 | 0.0038819 | 0.00097265 | -0.0038817 | -0.00097271 | 1.7378e-07 | -5.7636e-08 | 0.0058871 | 0.0058872 | 0.0058872 | 0.98115 | -0.36008 | 0.98111 | -0.36102 | 1.6174
117 | 0.0019306 | 0.00048371 | -0.0019305 | -0.00048384 | 3.8765e-08 | -1.2745e-07 | 0.002928 | 0.0029281 | 0.0029281 | 0.98111 | -0.36102 | 0.98108 | -0.36145 | 0.80441
118 | -0.08931 | -0.022404 | 0.089343 | 0.022424 | 3.3049e-05 | 2.0217e-05 | 0.13675 | 0.13675 | 0.13675 | 0.97184 | -0.54247 | 0.97223 | -0.53471 | 9.3924
119 | 0.10223 | 0.025685 | -0.10217 | -0.025647 | 6.0545e-05 | 3.7437e-05 | 0.15636 | 0.15636 | 0.15636 | 0.97309 | -0.5178 | 0.97246 | -0.53022 | 10.7388
120 | 0.09193 | 0.02308 | -0.09191 | -0.023068 | 1.9697e-05 | 1.2079e-05 | 0.14068 | 0.14068 | 0.14068 | 0.97246 | -0.53022 | 0.97223 | -0.53471 | 9.6622
121 | -0.010317 | -0.0025857 | 0.010319 | 0.0025865 | 1.5859e-06 | 7.8999e-07 | 0.015528 | 0.015528 | 0.015528 | 0.98868 | -0.21571 | 0.98884 | -0.21248 | 4.2658

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44877 | 0.11476

## res_load
| p_mw | q_mvar
0 | 0.0018447 | 0.00046233
1 | 0.0034873 | 0.00087401
2 | 0.0016913 | 0.00042387
3 | 0.0015328 | 0.00038417
4 | 0.0025818 | 0.00064706
5 | 0.0080454 | 0.0020164
6 | 0.0022179 | 0.00055586
7 | 0.0016556 | 0.00041493
8 | 0.0081065 | 0.0020317
9 | 0.0029342 | 0.00073537
10 | 0.0044311 | 0.0011105
11 | 0.0017275 | 0.00043296
12 | 0.0019564 | 0.00049033
13 | 0.0013658 | 0.00034231
14 | 0.003348 | 0.00083908
15 | 0.0033613 | 0.00084243
16 | 0.0033239 | 0.00083304
17 | 0.096048 | 0.024072
18 | 0.0042673 | 0.0010695
19 | 0.0018198 | 0.00045607
20 | 0.0044305 | 0.0011104
21 | 0.0042787 | 0.0010723
22 | 0.0025116 | 0.00062946
23 | 0.003181 | 0.00079723
24 | 0.0022334 | 0.00055975
25 | 0.0031838 | 0.00079793
26 | 0.0075953 | 0.0019035
27 | 0.0075931 | 0.001903
28 | 0.0027145 | 0.00068031
29 | 0.0039306 | 0.0009851
30 | 0.006683 | 0.0016749
31 | 0.0068902 | 0.0017269
32 | 0.0056392 | 0.0014133
33 | 0.0036605 | 0.00091741
34 | 0.0019036 | 0.0004771
35 | 0.0023535 | 0.00058984
36 | 0.0019464 | 0.00048781
37 | 0.002203 | 0.00055212
38 | 0.0026654 | 0.00066801
39 | 0.0026727 | 0.00066983
40 | 0.0022763 | 0.00057049
41 | 0.0026375 | 0.00066102
42 | 0.0047882 | 0.0012
43 | 0.0025115 | 0.00062944
44 | 0.003341 | 0.00083733
45 | 0.0033637 | 0.00084302
46 | 0.002501 | 0.0006268
47 | 0.0031716 | 0.00079488
48 | 0.0013705 | 0.00034348
49 | 0.0031969 | 0.00080122
50 | 0.0014259 | 0.00035738
51 | 0.0036219 | 0.00090772
52 | 0.003632 | 0.00091026
53 | 0.0067026 | 0.0016798
54 | 0.0035752 | 0.00089602
55 | 0.0026911 | 0.00067444
56 | 0.0040537 | 0.001016
57 | 0.0011813 | 0.00029607
58 | 0.0038722 | 0.00097047
59 | 0.001175 | 0.00029447
60 | 0.0013759 | 0.00034482
61 | 0.0015799 | 0.00039597
62 | 0.0015451 | 0.00038723
63 | 0.0016252 | 0.00040732
64 | 0.0064185 | 0.0016086
65 | 0.0039222 | 0.00098299
66 | 0.0073045 | 0.0018307
67 | 0.0052827 | 0.001324
68 | 0.0017737 | 0.00044454
69 | 0.0016126 | 0.00040415
70 | 0.0013892 | 0.00034817
71 | 0.0027658 | 0.00069317
72 | 0.0024079 | 0.00060348
73 | 0.0037362 | 0.00093637
74 | 0.0020704 | 0.00051888
75 | 0.0031099 | 0.00077942
76 | 0.0022133 | 0.0005547
77 | 0.0045445 | 0.001139
78 | 0.0033712 | 0.0008449
79 | 0.002501 | 0.00062682
80 | 0.0036096 | 0.00090465
81 | 0.0026561 | 0.00066568
82 | 0.0024299 | 0.000609
83 | 0.0020805 | 0.00052143
84 | 0.0020814 | 0.00052166
85 | 0.013604 | 0.0034095
86 | 0.0012702 | 0.00031834
87 | 0.0027225 | 0.00068233
88 | 0.0033704 | 0.00084471
89 | 0.0030726 | 0.00077006
90 | 0.0013377 | 0.00033525
91 | 0.00131 | 0.00032833
92 | 0.0019582 | 0.00049076
93 | 0.0019511 | 0.00048899
94 | 0.0019305 | 0.00048384
95 | 0.0044239 | 0.0011087
96 | 0.010244 | 0.0025674
97 | 0.010317 | 0.0025857
98 | 0.0091143 | 0.0022843
99 | 0.0023502 | 0.00058902
100 | 0.0025671 | 0.00064337

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1