## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-27_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-27_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2581-27_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2581-27_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2581-27_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2581-27_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2581-27_0_6_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_2581-27_0_6_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_2581-27_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2581-27_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2581-27_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_2581-27_0_6_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_2581-27_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2581-27_0_6_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2581-27_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2581-27_0_6_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_2581-27_0_6_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_2581-27_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2581-27_0_6_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_2581-27_0_6_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_2581-27_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2581-27_0_6_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2581-27_0_6_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_2581-27_0_6_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_2581-27_0_6_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_2581-27_0_6_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_2581-27_0_6_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2581-27_0_6_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_2581-27_0_6_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_2581-27_0_6_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_2581-27_0_6_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_2581-27_0_6_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_2581-27_0_6_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2581-27_0_6_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2581-27_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2581-27_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_2581-27_0_6_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2581-27_0_6_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_2581-27_0_6_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_2581-27_0_6_node_44 | 0.4 | n |  | TRUE
40 | bus_MV_523_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-27_0_6_load_0 | 0 | 0.0079819 | 0.0020004 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-27_0_6_load_1 | 1 | 0.0072989 | 0.0018293 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-27_0_6_load_3 | 3 | 0.0038462 | 0.00096396 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-27_0_6_load_4 | 4 | 0.0047422 | 0.0011885 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-27_0_6_load_5 | 5 | 0.0021806 | 0.00054652 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-27_0_6_load_37 | 6 | 0.0064216 | 0.0016094 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-27_0_6_load_6 | 8 | 0.099079 | 0.024832 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-27_0_6_load_7 | 9 | 0.076015 | 0.019051 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-27_0_6_load_36 | 11 | 0.069933 | 0.017527 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-27_0_6_load_31 | 16 | 0.02011 | 0.00504 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-27_0_6_load_38 | 19 | 0.031946 | 0.0080063 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-27_0_6_load_46 | 22 | 0.013971 | 0.0035014 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-27_0_6_load_41 | 23 | 0.013516 | 0.0033874 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-27_0_6_load_26 | 24 | 0.036621 | 0.0091781 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-27_0_6_load_25 | 27 | 0.012857 | 0.0032222 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-27_0_6_load_32 | 29 | 0.0069258 | 0.0017358 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-27_0_6_load_45 | 30 | 0.049508 | 0.012408 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-27_0_6_load_28 | 32 | 0.00418 | 0.0010476 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-27_0_6_load_29 | 33 | 0.0042372 | 0.0010619 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-27_0_6_load_23 | 35 | 0.016715 | 0.0041892 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-27_0_6_load_39 | 37 | 0.0048784 | 0.0012226 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-27_0_6_load_40 | 38 | 0.0073345 | 0.0018382 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-27_0_6_load_44 | 39 | 0.012927 | 0.0032398 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-27_0_6_line_0 |  | 0 | 1 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2581-27_0_6_line_1 |  | 0 | 2 | 0.010931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2581-27_0_6_line_2 |  | 1 | 3 | 0.00982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2581-27_0_6_line_3 |  | 2 | 4 | 0.0055329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2581-27_0_6_line_4 |  | 2 | 5 | 0.046412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-27_0_6_line_5 |  | 3 | 6 | 0.010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2581-27_0_6_line_6 |  | 6 | 7 | 0.018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2581-27_0_6_line_7 |  | 7 | 28 | 0.019695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2581-27_0_6_line_8 |  | 7 | 14 | 0.04414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2581-27_0_6_line_9 |  | 8 | 9 | 0.027706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2581-27_0_6_line_10 |  | 9 | 10 | 0.037609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2581-27_0_6_line_11 |  | 10 | 11 | 0.0013704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2581-27_0_6_line_12 |  | 11 | 12 | 0.046066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2581-27_0_6_line_13 |  | 12 | 13 | 0.051374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2581-27_0_6_line_14 |  | 13 | 24 | 0.0060253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2581-27_0_6_line_15 |  | 14 | 15 | 0.049489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2581-27_0_6_line_16 |  | 14 | 16 | 0.029058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2581-27_0_6_line_17 |  | 15 | 19 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2581-27_0_6_line_18 |  | 16 | 29 | 0.033305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2581-27_0_6_line_19 |  | 17 | 18 | 0.088442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2581-27_0_6_line_20 |  | 17 | 19 | 0.013908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2581-27_0_6_line_21 |  | 18 | 25 | 0.01922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2581-27_0_6_line_22 |  | 20 | 21 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-27_0_6_line_23 |  | 20 | 22 | 0.048642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2581-27_0_6_line_24 |  | 21 | 23 | 0.019198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2581-27_0_6_line_25 |  | 23 | 31 | 0.016458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2581-27_0_6_line_26 |  | 24 | 34 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2581-27_0_6_line_27 |  | 25 | 26 | 0.016664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2581-27_0_6_line_28 |  | 25 | 30 | 0.005907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2581-27_0_6_line_29 |  | 26 | 27 | 0.012411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2581-27_0_6_line_30 |  | 27 | 34 | 0.015711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2581-27_0_6_line_31 |  | 28 | 39 | 0.0054856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2581-27_0_6_line_32 |  | 31 | 38 | 0.024939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2581-27_0_6_line_33 |  | 32 | 33 | 0.0089776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2581-27_0_6_line_34 |  | 33 | 36 | 0.0036214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2581-27_0_6_line_35 |  | 34 | 35 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2581-27_0_6_line_36 |  | 36 | 37 | 0.0060479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2581-27_0_6_line_37 |  | 36 | 38 | 0.012311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2581-27_0_6_line_38 |  | 37 | 39 | 0.018041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-27_0_6_trafo_36 | 0.63 MVA 20/0.4 kV | 40 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2635474.5391 | 1244494.4186 | 2635472.788 | 1244478.0398
1 | 2635475.7012 | 1244505.2878 | 2635474.5391 | 1244494.4186
2 | 2635472.788 | 1244478.0398 | 2635472.6026 | 1244476.306 | 2635471.7943 | 1244468.2702
3 | 2635475.7012 | 1244505.2878 | 2635476.2898 | 1244510.7892
4 | 2635475.7012 | 1244505.2878 | 2635471.2037 | 1244505.55 | 2635467.4592 | 1244502.4701 | 2635466.142 | 1244499.0933 | 2635464.4478 | 1244482.9172 | 2635461.1722 | 1244475.9709 | 2635459.5771 | 1244466.6163
5 | 2635470.7898 | 1244458.2838 | 2635471.7943 | 1244468.2702
6 | 2635468.9008 | 1244439.5045 | 2635470.7898 | 1244458.2838
7 | 2635468.9008 | 1244439.5045 | 2635488.6535 | 1244439.378
8 | 2635458.9785 | 1244400.4644 | 2635461.2161 | 1244415.4875 | 2635465.4126 | 1244415.0234 | 2635465.515 | 1244415.5799 | 2635466.0878 | 1244419.6304 | 2635468.9008 | 1244439.5045
9 | 2635342.1057 | 1244520.13 | 2635338.9171 | 1244503.3489 | 2635337.1592 | 1244492.8711
10 | 2635339.3771 | 1244457.7999 | 2635334.8981 | 1244462.5875 | 2635333.5576 | 1244464.3584 | 2635333.2834 | 1244467.2698 | 2635333.4546 | 1244470.2505 | 2635335.1079 | 1244480.6449 | 2635337.1592 | 1244492.8711
11 | 2635339.3771 | 1244457.7999 | 2635340.4295 | 1244456.9222
12 | 2635344.2429 | 1244413.4446 | 2635344.8347 | 1244419.3964 | 2635344.8481 | 1244419.6856 | 2635345.0042 | 1244423.9114 | 2635345.8623 | 1244452.3906 | 2635340.4295 | 1244456.9222
13 | 2635336.1525 | 1244363.553 | 2635339.5127 | 1244404.5662 | 2635340.7344 | 1244408.7873 | 2635344.2429 | 1244413.4446
14 | 2635336.1525 | 1244363.553 | 2635341.7387 | 1244361.2949
15 | 2635460.391 | 1244385.3742 | 2635463.4963 | 1244401.8701 | 2635465.4126 | 1244415.0234 | 2635461.2161 | 1244415.4875 | 2635458.9785 | 1244400.4644
16 | 2635458.9785 | 1244400.4644 | 2635487.99 | 1244398.8232
17 | 2635460.391 | 1244385.3742 | 2635459.3318 | 1244380.5425 | 2635458.1492 | 1244376.1215 | 2635456.5002 | 1244372.331
18 | 2635521.2417 | 1244396.9422 | 2635487.99 | 1244398.8232
19 | 2635391.5798 | 1244344.2149 | 2635449.4607 | 1244331.6297 | 2635452.4742 | 1244352.1165 | 2635451.5895 | 1244354.7462 | 2635449.7587 | 1244360.1722
20 | 2635449.7587 | 1244360.1722 | 2635456.0397 | 1244371.2724 | 2635456.5002 | 1244372.331
21 | 2635381.4104 | 1244356.6624 | 2635380.7298 | 1244351.6773 | 2635386.8184 | 1244350.7018 | 2635391.5798 | 1244344.2149
22 | 2635516.6942 | 1244511.4145 | 2635536.909 | 1244511.0352
23 | 2635536.909 | 1244511.0352 | 2635537.4118 | 1244462.3955
24 | 2635516.6942 | 1244511.4145 | 2635515.2794 | 1244506.6696 | 2635515.6976 | 1244492.4286
25 | 2635516.1808 | 1244475.9773 | 2635515.6976 | 1244492.4286
26 | 2635356.5355 | 1244355.3134 | 2635341.7387 | 1244361.2949
27 | 2635364.7769 | 1244358.2866 | 2635381.4104 | 1244356.6624
28 | 2635381.4104 | 1244356.6624 | 2635386.5998 | 1244359.484
29 | 2635364.7769 | 1244358.2866 | 2635363.8995 | 1244367.2983 | 2635360.5557 | 1244367.589
30 | 2635356.5355 | 1244355.3134 | 2635357.4356 | 1244367.8602 | 2635360.5557 | 1244367.589
31 | 2635488.6535 | 1244439.378 | 2635494.1336 | 1244439.1329
32 | 2635516.1808 | 1244475.9773 | 2635517.5949 | 1244464.4227 | 2635517.9178 | 1244451.1283
33 | 2635530.8155 | 1244438.7677 | 2635521.838 | 1244438.8057
34 | 2635518.2166 | 1244438.821 | 2635521.838 | 1244438.8057
35 | 2635356.5355 | 1244355.3134 | 2635372.4524 | 1244349.6036
36 | 2635518.2166 | 1244438.821 | 2635512.1688 | 1244438.8455
37 | 2635518.2166 | 1244438.821 | 2635517.9178 | 1244451.1283
38 | 2635512.1688 | 1244438.8455 | 2635499.4012 | 1244438.8974 | 2635494.1336 | 1244439.1329

## bus_geodata
| x | y | coords
0 | 2635474.5391 | 1244494.4186
1 | 2635472.788 | 1244478.0398
2 | 2635475.7012 | 1244505.2878
3 | 2635471.7943 | 1244468.2702
4 | 2635476.2898 | 1244510.7892
5 | 2635459.5771 | 1244466.6163
6 | 2635470.7898 | 1244458.2838
7 | 2635468.9008 | 1244439.5045
8 | 2635342.1057 | 1244520.13
9 | 2635337.1592 | 1244492.8711
10 | 2635339.3771 | 1244457.7999
11 | 2635340.4295 | 1244456.9222
12 | 2635344.2429 | 1244413.4446
13 | 2635336.1525 | 1244363.553
14 | 2635458.9785 | 1244400.4644
15 | 2635460.391 | 1244385.3742
16 | 2635487.99 | 1244398.8232
17 | 2635449.7587 | 1244360.1722
18 | 2635391.5798 | 1244344.2149
19 | 2635456.5002 | 1244372.331
20 | 2635536.909 | 1244511.0352
21 | 2635516.6942 | 1244511.4145
22 | 2635537.4118 | 1244462.3955
23 | 2635515.6976 | 1244492.4286
24 | 2635341.7387 | 1244361.2949
25 | 2635381.4104 | 1244356.6624
26 | 2635364.7769 | 1244358.2866
27 | 2635360.5557 | 1244367.589
28 | 2635488.6535 | 1244439.378
29 | 2635521.2417 | 1244396.9422
30 | 2635386.5998 | 1244359.484
31 | 2635516.1808 | 1244475.9773
32 | 2635530.8155 | 1244438.7677
33 | 2635521.838 | 1244438.8057
34 | 2635356.5355 | 1244355.3134
35 | 2635372.4524 | 1244349.6036
36 | 2635518.2166 | 1244438.821
37 | 2635512.1688 | 1244438.8455
38 | 2635517.9178 | 1244451.1283
39 | 2635494.1336 | 1244439.1329
40 | 2635340.4295 | 1244456.9222

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97525 | -0.47683 | 0.0079819 | 0.0020004
1 | 0.97548 | -0.47234 | 0.0072989 | 0.0018293
2 | 0.97518 | -0.47822 | 0 | 0
3 | 0.97568 | -0.46834 | 0.0038462 | 0.00096396
4 | 0.97516 | -0.4787 | 0.0047422 | 0.0011885
5 | 0.97509 | -0.48008 | 0.0021806 | 0.00054652
6 | 0.97593 | -0.46356 | 0.0064216 | 0.0016094
7 | 0.9765 | -0.45235 | 0 | 0
8 | 0.99442 | -0.10722 | 0.099079 | 0.024832
9 | 0.99693 | -0.058963 | 0.076015 | 0.019051
10 | 0.99993 | -0.0013941 | 0 | 0
11 | 1 | 0 | -0.45021 | -0.11445
12 | 0.99619 | -0.072066 | 0 | 0
13 | 0.99194 | -0.15309 | 0 | 0
14 | 0.97842 | -0.41469 | 0 | 0
15 | 0.98119 | -0.36053 | 0 | 0
16 | 0.97769 | -0.42901 | 0.02011 | 0.00504
17 | 0.98236 | -0.33782 | 0 | 0
18 | 0.98654 | -0.25695 | 0 | 0
19 | 0.9817 | -0.3506 | 0.031946 | 0.0080063
20 | 0.97204 | -0.54018 | 0 | 0
21 | 0.9723 | -0.53499 | 0 | 0
22 | 0.9714 | -0.55273 | 0.013971 | 0.0035014
23 | 0.97255 | -0.53005 | 0.013516 | 0.0033874
24 | 0.99145 | -0.16263 | 0.036621 | 0.0091781
25 | 0.98745 | -0.23947 | 0 | 0
26 | 0.98849 | -0.21943 | 0 | 0
27 | 0.98926 | -0.20453 | 0.012857 | 0.0032222
28 | 0.97538 | -0.47435 | 0 | 0
29 | 0.97748 | -0.43321 | 0.0069258 | 0.0017358
30 | 0.98718 | -0.2447 | 0.049508 | 0.012408
31 | 0.97297 | -0.52171 | 0 | 0
32 | 0.97395 | -0.50247 | 0.00418 | 0.0010476
33 | 0.97398 | -0.50178 | 0.0042372 | 0.0010619
34 | 0.99031 | -0.18451 | 0 | 0
35 | 0.99005 | -0.18953 | 0.016715 | 0.0041892
36 | 0.97401 | -0.50122 | 0 | 0
37 | 0.97426 | -0.49641 | 0.0048784 | 0.0012226
38 | 0.97361 | -0.5091 | 0.0073345 | 0.0018382
39 | 0.97506 | -0.48049 | 0.012927 | 0.0032398
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014905 | -0.0037352 | 0.014909 | 0.003737 | 3.1948e-06 | 1.8391e-06 | 0.022742 | 0.022742 | 0.022742 | 0.97525 | -0.47683 | 0.97548 | -0.47234 | 6.2479
1 | 0.0069236 | 0.0017347 | -0.0069231 | -0.0017346 | 4.5743e-07 | 1.5637e-07 | 0.010564 | 0.010564 | 0.010564 | 0.97525 | -0.47683 | 0.97518 | -0.47822 | 2.9021
2 | -0.022208 | -0.0055663 | 0.022212 | 0.0055689 | 4.226e-06 | 2.582e-06 | 0.033876 | 0.033876 | 0.033876 | 0.97548 | -0.47234 | 0.97568 | -0.46834 | 9.3066
3 | 0.0047423 | 0.0011885 | -0.0047422 | -0.0011885 | 1.0864e-07 | 5.0492e-10 | 0.0072362 | 0.0072362 | 0.0072362 | 0.97518 | -0.47822 | 0.97516 | -0.4787 | 1.988
4 | 0.0021808 | 0.00054606 | -0.0021806 | -0.00054652 | 1.9272e-07 | -4.5565e-07 | 0.0033275 | 0.0033277 | 0.0033277 | 0.97518 | -0.47822 | 0.97509 | -0.48008 | 0.9142
5 | -0.026058 | -0.0065328 | 0.026064 | 0.0065365 | 5.9446e-06 | 3.6792e-06 | 0.039742 | 0.039742 | 0.039742 | 0.97568 | -0.46834 | 0.97593 | -0.46356 | 10.9181
6 | -0.032486 | -0.0081459 | 0.032503 | 0.0081568 | 1.7365e-05 | 1.0878e-05 | 0.049533 | 0.049533 | 0.049533 | 0.97593 | -0.46356 | 0.9765 | -0.45235 | 13.6079
7 | 0.061228 | 0.015415 | -0.061164 | -0.015374 | 6.4328e-05 | 4.0924e-05 | 0.093327 | 0.093327 | 0.093327 | 0.9765 | -0.45235 | 0.97538 | -0.47435 | 25.6393
8 | -0.093731 | -0.023572 | 0.0939 | 0.023679 | 0.00016891 | 0.00010699 | 0.14286 | 0.14286 | 0.14286 | 0.9765 | -0.45235 | 0.97842 | -0.41469 | 19.6236
9 | -0.099079 | -0.024832 | 0.099308 | 0.024977 | 0.00022837 | 0.0001458 | 0.14826 | 0.14826 | 0.14826 | 0.99442 | -0.10722 | 0.99693 | -0.058963 | 40.7303
10 | -0.17532 | -0.044028 | 0.17581 | 0.044337 | 0.00048301 | 0.00030815 | 0.26172 | 0.26172 | 0.26172 | 0.99693 | -0.058963 | 0.99993 | -0.0013941 | 35.9502
11 | -0.17581 | -0.044337 | 0.17582 | 0.044344 | 1.1733e-05 | 7.4552e-06 | 0.26172 | 0.26172 | 0.26172 | 0.99993 | -0.0013941 | 1 | 0 | 23.9668
12 | 0.27275 | 0.070109 | -0.2718 | -0.069502 | 0.00095139 | 0.00060708 | 0.40647 | 0.40648 | 0.40648 | 1 | 0 | 0.99619 | -0.072066 | 37.223
13 | 0.2718 | 0.069502 | -0.27073 | -0.068825 | 0.001061 | 0.00067705 | 0.40648 | 0.40648 | 0.40648 | 0.99619 | -0.072066 | 0.99194 | -0.15309 | 37.2231
14 | 0.27073 | 0.068825 | -0.27061 | -0.068746 | 0.00012444 | 7.9408e-05 | 0.40648 | 0.40648 | 0.40648 | 0.99194 | -0.15309 | 0.99145 | -0.16263 | 37.2231
15 | -0.12096 | -0.030466 | 0.12127 | 0.030666 | 0.00031418 | 0.00019983 | 0.18401 | 0.18401 | 0.18401 | 0.97842 | -0.41469 | 0.98119 | -0.36053 | 25.276
16 | 0.027056 | 0.0067877 | -0.027037 | -0.0067763 | 1.8452e-05 | 1.1444e-05 | 0.04115 | 0.04115 | 0.04115 | 0.97842 | -0.41469 | 0.97769 | -0.42901 | 11.3049
17 | -0.12127 | -0.030666 | 0.12133 | 0.030703 | 5.78e-05 | 3.6474e-05 | 0.18401 | 0.18401 | 0.18401 | 0.98119 | -0.36053 | 0.9817 | -0.3506 | 16.8506
18 | 0.0069272 | 0.0017362 | -0.0069258 | -0.0017358 | 1.3883e-06 | 4.7094e-07 | 0.010543 | 0.010543 | 0.010543 | 0.97769 | -0.42901 | 0.97748 | -0.43321 | 2.8965
19 | -0.15337 | -0.038769 | 0.15396 | 0.039147 | 0.00059724 | 0.00037886 | 0.23243 | 0.23243 | 0.23243 | 0.98236 | -0.33782 | 0.98654 | -0.25695 | 21.2848
20 | 0.15337 | 0.038769 | -0.15327 | -0.038709 | 9.3923e-05 | 5.9583e-05 | 0.23243 | 0.23243 | 0.23243 | 0.98236 | -0.33782 | 0.9817 | -0.3506 | 21.2848
21 | -0.15396 | -0.039147 | 0.15409 | 0.03923 | 0.00012979 | 8.2329e-05 | 0.23243 | 0.23243 | 0.23243 | 0.98654 | -0.25695 | 0.98745 | -0.23947 | 21.2847
22 | -0.013979 | -0.0035062 | 0.013983 | 0.0035081 | 3.4622e-06 | 1.9658e-06 | 0.021401 | 0.021401 | 0.021401 | 0.97204 | -0.54018 | 0.9723 | -0.53499 | 5.8793
23 | 0.013979 | 0.0035062 | -0.013971 | -0.0035014 | 8.3541e-06 | 4.7441e-06 | 0.021401 | 0.021401 | 0.021401 | 0.97204 | -0.54018 | 0.9714 | -0.55273 | 5.8794
24 | -0.013983 | -0.0035081 | 0.013986 | 0.00351 | 3.2972e-06 | 1.872e-06 | 0.021401 | 0.0214 | 0.021401 | 0.9723 | -0.53499 | 0.97255 | -0.53005 | 5.8793
25 | -0.027502 | -0.0068974 | 0.027513 | 0.0069041 | 1.0929e-05 | 6.7899e-06 | 0.04208 | 0.04208 | 0.04208 | 0.97255 | -0.53005 | 0.97297 | -0.52171 | 11.5603
26 | 0.23399 | 0.059568 | -0.23374 | -0.059411 | 0.00024651 | 0.00015715 | 0.35151 | 0.35151 | 0.35151 | 0.99145 | -0.16263 | 0.99031 | -0.18451 | 32.1899
27 | -0.20361 | -0.051645 | 0.20381 | 0.05177 | 0.00019639 | 0.00012505 | 0.30705 | 0.30705 | 0.30705 | 0.98745 | -0.23947 | 0.98849 | -0.21943 | 28.1184
28 | 0.04952 | 0.012416 | -0.049508 | -0.012408 | 1.2336e-05 | 7.8194e-06 | 0.074625 | 0.074625 | 0.074625 | 0.98745 | -0.23947 | 0.98718 | -0.2447 | 20.5015
29 | -0.20381 | -0.05177 | 0.20396 | 0.051864 | 0.00014626 | 9.3131e-05 | 0.30705 | 0.30705 | 0.30705 | 0.98849 | -0.21943 | 0.98926 | -0.20453 | 28.1184
30 | -0.21681 | -0.055086 | 0.21702 | 0.055219 | 0.00020921 | 0.00013329 | 0.32639 | 0.32639 | 0.32639 | 0.98926 | -0.20453 | 0.99031 | -0.18451 | 29.8893
31 | 0.061164 | 0.015374 | -0.061146 | -0.015362 | 1.7917e-05 | 1.1398e-05 | 0.093327 | 0.093327 | 0.093327 | 0.97538 | -0.47435 | 0.97506 | -0.48049 | 25.6393
32 | -0.027513 | -0.0069041 | 0.027529 | 0.0069144 | 1.656e-05 | 1.0288e-05 | 0.04208 | 0.042079 | 0.04208 | 0.97297 | -0.52171 | 0.97361 | -0.5091 | 11.5603
33 | -0.00418 | -0.0010476 | 0.0041802 | 0.0010476 | 1.3731e-07 | -2.3851e-08 | 0.0063863 | 0.0063863 | 0.0063863 | 0.97395 | -0.50247 | 0.97398 | -0.50178 | 1.7545
34 | -0.0084174 | -0.0021095 | 0.0084176 | 0.0021096 | 2.2458e-07 | 9.866e-08 | 0.01286 | 0.01286 | 0.01286 | 0.97398 | -0.50178 | 0.97401 | -0.50122 | 3.5329
35 | 0.016719 | 0.0041915 | -0.016715 | -0.0041892 | 4.0021e-06 | 2.3439e-06 | 0.025122 | 0.025122 | 0.025122 | 0.99031 | -0.18451 | 0.99005 | -0.18953 | 6.9017
36 | -0.043294 | -0.010871 | 0.043304 | 0.010877 | 9.9238e-06 | 6.2759e-06 | 0.066149 | 0.066149 | 0.066149 | 0.97401 | -0.50122 | 0.97426 | -0.49641 | 18.1727
37 | 0.034877 | 0.0087609 | -0.034864 | -0.0087526 | 1.311e-05 | 8.2372e-06 | 0.053289 | 0.053289 | 0.053289 | 0.97401 | -0.50122 | 0.97361 | -0.5091 | 14.6399
38 | -0.048183 | -0.012099 | 0.048219 | 0.012123 | 3.6647e-05 | 2.3229e-05 | 0.0736 | 0.0736 | 0.0736 | 0.97426 | -0.49641 | 0.97506 | -0.48049 | 20.2197

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52015 | 0.13198

## res_load
| p_mw | q_mvar
0 | 0.0079819 | 0.0020004
1 | 0.0072989 | 0.0018293
2 | 0.0038462 | 0.00096396
3 | 0.0047422 | 0.0011885
4 | 0.0021806 | 0.00054652
5 | 0.0064216 | 0.0016094
6 | 0.099079 | 0.024832
7 | 0.076015 | 0.019051
8 | 0.069933 | 0.017527
9 | 0.02011 | 0.00504
10 | 0.031946 | 0.0080063
11 | 0.013971 | 0.0035014
12 | 0.013516 | 0.0033874
13 | 0.036621 | 0.0091781
14 | 0.012857 | 0.0032222
15 | 0.0069258 | 0.0017358
16 | 0.049508 | 0.012408
17 | 0.00418 | 0.0010476
18 | 0.0042372 | 0.0010619
19 | 0.016715 | 0.0041892
20 | 0.0048784 | 0.0012226
21 | 0.0073345 | 0.0018382
22 | 0.012927 | 0.0032398

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1