## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-28_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-28_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2581-28_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2581-28_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2581-28_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2581-28_0_5_node_107 | 0.4 | n |  | TRUE
6 | bus_LV_2581-28_0_5_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_2581-28_0_5_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_2581-28_0_5_node_93 | 0.4 | n |  | TRUE
9 | bus_LV_2581-28_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2581-28_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2581-28_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2581-28_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2581-28_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2581-28_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2581-28_0_5_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_2581-28_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2581-28_0_5_node_72 | 0.4 | n |  | TRUE
18 | bus_LV_2581-28_0_5_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_2581-28_0_5_node_91 | 0.4 | n |  | TRUE
20 | bus_LV_2581-28_0_5_node_133 | 0.4 | n |  | TRUE
21 | bus_LV_2581-28_0_5_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_2581-28_0_5_node_76 | 0.4 | n |  | TRUE
23 | bus_LV_2581-28_0_5_node_70 | 0.4 | n |  | TRUE
24 | bus_LV_2581-28_0_5_node_92 | 0.4 | n |  | TRUE
25 | bus_LV_2581-28_0_5_node_131 | 0.4 | n |  | TRUE
26 | bus_LV_2581-28_0_5_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2581-28_0_5_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2581-28_0_5_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2581-28_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2581-28_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2581-28_0_5_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2581-28_0_5_node_125 | 0.4 | n |  | TRUE
33 | bus_LV_2581-28_0_5_node_124 | 0.4 | n |  | TRUE
34 | bus_LV_2581-28_0_5_node_67 | 0.4 | n |  | TRUE
35 | bus_LV_2581-28_0_5_node_73 | 0.4 | n |  | TRUE
36 | bus_LV_2581-28_0_5_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2581-28_0_5_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2581-28_0_5_node_101 | 0.4 | n |  | TRUE
39 | bus_LV_2581-28_0_5_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2581-28_0_5_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2581-28_0_5_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2581-28_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2581-28_0_5_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2581-28_0_5_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_2581-28_0_5_node_108 | 0.4 | n |  | TRUE
46 | bus_LV_2581-28_0_5_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_2581-28_0_5_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_2581-28_0_5_node_130 | 0.4 | n |  | TRUE
49 | bus_LV_2581-28_0_5_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_2581-28_0_5_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_2581-28_0_5_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_2581-28_0_5_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_2581-28_0_5_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2581-28_0_5_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_2581-28_0_5_node_114 | 0.4 | n |  | TRUE
56 | bus_LV_2581-28_0_5_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2581-28_0_5_node_112 | 0.4 | n |  | TRUE
58 | bus_LV_2581-28_0_5_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_2581-28_0_5_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_2581-28_0_5_node_94 | 0.4 | n |  | TRUE
61 | bus_LV_2581-28_0_5_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_2581-28_0_5_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_2581-28_0_5_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2581-28_0_5_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2581-28_0_5_node_111 | 0.4 | n |  | TRUE
66 | bus_LV_2581-28_0_5_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_2581-28_0_5_node_134 | 0.4 | n |  | TRUE
68 | bus_LV_2581-28_0_5_node_110 | 0.4 | n |  | TRUE
69 | bus_LV_2581-28_0_5_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_2581-28_0_5_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_2581-28_0_5_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2581-28_0_5_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_2581-28_0_5_node_103 | 0.4 | n |  | TRUE
74 | bus_LV_2581-28_0_5_node_144 | 0.4 | n |  | TRUE
75 | bus_LV_2581-28_0_5_node_85 | 0.4 | n |  | TRUE
76 | bus_LV_2581-28_0_5_node_105 | 0.4 | n |  | TRUE
77 | bus_LV_2581-28_0_5_node_145 | 0.4 | n |  | TRUE
78 | bus_LV_2581-28_0_5_node_142 | 0.4 | n |  | TRUE
79 | bus_LV_2581-28_0_5_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_2581-28_0_5_node_46 | 0.4 | n |  | TRUE
81 | bus_LV_2581-28_0_5_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_2581-28_0_5_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_2581-28_0_5_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_2581-28_0_5_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_2581-28_0_5_node_109 | 0.4 | n |  | TRUE
86 | bus_LV_2581-28_0_5_node_95 | 0.4 | n |  | TRUE
87 | bus_LV_2581-28_0_5_node_96 | 0.4 | n |  | TRUE
88 | bus_LV_2581-28_0_5_node_54 | 0.4 | n |  | TRUE
89 | bus_LV_2581-28_0_5_node_55 | 0.4 | n |  | TRUE
90 | bus_LV_2581-28_0_5_node_56 | 0.4 | n |  | TRUE
91 | bus_LV_2581-28_0_5_node_57 | 0.4 | n |  | TRUE
92 | bus_LV_2581-28_0_5_node_58 | 0.4 | n |  | TRUE
93 | bus_LV_2581-28_0_5_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_2581-28_0_5_node_61 | 0.4 | n |  | TRUE
95 | bus_LV_2581-28_0_5_node_59 | 0.4 | n |  | TRUE
96 | bus_LV_2581-28_0_5_node_60 | 0.4 | n |  | TRUE
97 | bus_LV_2581-28_0_5_node_62 | 0.4 | n |  | TRUE
98 | bus_LV_2581-28_0_5_node_121 | 0.4 | n |  | TRUE
99 | bus_LV_2581-28_0_5_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_2581-28_0_5_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_2581-28_0_5_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_2581-28_0_5_node_119 | 0.4 | n |  | TRUE
103 | bus_LV_2581-28_0_5_node_117 | 0.4 | n |  | TRUE
104 | bus_LV_2581-28_0_5_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_2581-28_0_5_node_127 | 0.4 | n |  | TRUE
106 | bus_LV_2581-28_0_5_node_128 | 0.4 | n |  | TRUE
107 | bus_LV_2581-28_0_5_node_71 | 0.4 | n |  | TRUE
108 | bus_LV_2581-28_0_5_node_78 | 0.4 | n |  | TRUE
109 | bus_LV_2581-28_0_5_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_2581-28_0_5_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_2581-28_0_5_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2581-28_0_5_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2581-28_0_5_node_80 | 0.4 | n |  | TRUE
114 | bus_LV_2581-28_0_5_node_135 | 0.4 | n |  | TRUE
115 | bus_LV_2581-28_0_5_node_129 | 0.4 | n |  | TRUE
116 | bus_LV_2581-28_0_5_node_104 | 0.4 | n |  | TRUE
117 | bus_LV_2581-28_0_5_node_82 | 0.4 | n |  | TRUE
118 | bus_LV_2581-28_0_5_node_83 | 0.4 | n |  | TRUE
119 | bus_LV_2581-28_0_5_node_84 | 0.4 | n |  | TRUE
120 | bus_LV_2581-28_0_5_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_2581-28_0_5_node_141 | 0.4 | n |  | TRUE
122 | bus_LV_2581-28_0_5_node_86 | 0.4 | n |  | TRUE
123 | bus_LV_2581-28_0_5_node_87 | 0.4 | n |  | TRUE
124 | bus_LV_2581-28_0_5_node_89 | 0.4 | n |  | TRUE
125 | bus_LV_2581-28_0_5_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_2581-28_0_5_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_2581-28_0_5_node_106 | 0.4 | n |  | TRUE
128 | bus_LV_2581-28_0_5_node_102 | 0.4 | n |  | TRUE
129 | bus_LV_2581-28_0_5_node_98 | 0.4 | n |  | TRUE
130 | bus_LV_2581-28_0_5_node_113 | 0.4 | n |  | TRUE
131 | bus_LV_2581-28_0_5_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_2581-28_0_5_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_2581-28_0_5_node_143 | 0.4 | n |  | TRUE
134 | bus_LV_2581-28_0_5_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_2581-28_0_5_node_136 | 0.4 | n |  | TRUE
136 | bus_LV_2581-28_0_5_node_137 | 0.4 | n |  | TRUE
137 | bus_LV_2581-28_0_5_node_138 | 0.4 | n |  | TRUE
138 | bus_LV_2581-28_0_5_node_140 | 0.4 | n |  | TRUE
139 | bus_LV_2581-28_0_5_node_146 | 0.4 | n |  | TRUE
140 | bus_MV_523_0_node_155 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-28_0_5_load_0 | 0 | 0.0014914 | 0.00037378 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-28_0_5_load_1 | 1 | 0.0023683 | 0.00059354 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-28_0_5_load_2 | 2 | 0.0023 | 0.00057643 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-28_0_5_load_3 | 3 | 0.0069492 | 0.0017416 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-28_0_5_load_4 | 4 | 0.0023734 | 0.00059483 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-28_0_5_load_107 | 5 | 0.0066756 | 0.0016731 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-28_0_5_load_31 | 6 | 0.0014858 | 0.00037239 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-28_0_5_load_93 | 8 | 0.001482 | 0.00037143 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-28_0_5_load_5 | 9 | 0.0032589 | 0.00081676 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-28_0_5_load_6 | 10 | 0.0022284 | 0.00055848 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-28_0_5_load_8 | 12 | 0.0030072 | 0.00075368 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-28_0_5_load_10 | 13 | 0.0025404 | 0.00063669 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-28_0_5_load_11 | 14 | 0.0042926 | 0.0010758 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-28_0_5_load_64 | 15 | 0.0038203 | 0.00095747 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-28_0_5_load_72 | 17 | 0.0063261 | 0.0015855 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-28_0_5_load_69 | 18 | 0.0064678 | 0.001621 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-28_0_5_load_91 | 19 | 0.0024797 | 0.00062148 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-28_0_5_load_133 | 20 | 0.0032173 | 0.00080633 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-28_0_5_load_65 | 21 | 0.0032478 | 0.00081398 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-28_0_5_load_76 | 22 | 0.0084986 | 0.0021299 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-28_0_5_load_70 | 23 | 0.0021278 | 0.00053327 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-28_0_5_load_92 | 24 | 0.0068477 | 0.0017162 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-28_0_5_load_131 | 25 | 0.0090429 | 0.0022664 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2581-28_0_5_load_12 | 26 | 0.0024633 | 0.00061735 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2581-28_0_5_load_13 | 27 | 0.0034795 | 0.00087204 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2581-28_0_5_load_16 | 29 | 0.0017269 | 0.0004328 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2581-28_0_5_load_18 | 30 | 0.0017028 | 0.00042677 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2581-28_0_5_load_125 | 32 | 0.0020598 | 0.00051623 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2581-28_0_5_load_124 | 33 | 0.0024379 | 0.000611 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2581-28_0_5_load_67 | 34 | 0.0045107 | 0.0011305 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2581-28_0_5_load_19 | 36 | 0.0018663 | 0.00046775 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2581-28_0_5_load_20 | 37 | 0.0018943 | 0.00047476 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2581-28_0_5_load_101 | 38 | 0.0030486 | 0.00076406 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2581-28_0_5_load_21 | 39 | 0.0039504 | 0.00099005 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2581-28_0_5_load_22 | 40 | 0.0039636 | 0.00099338 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2581-28_0_5_load_23 | 41 | 0.0022544 | 0.000565 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2581-28_0_5_load_24 | 42 | 0.0029846 | 0.00074801 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2581-28_0_5_load_44 | 44 | 0.0063199 | 0.0015839 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2581-28_0_5_load_108 | 45 | 0.0024439 | 0.0006125 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2581-28_0_5_load_37 | 46 | 0.0026677 | 0.0006686 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2581-28_0_5_load_130 | 48 | 0.0021954 | 0.00055022 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2581-28_0_5_load_26 | 50 | 0.0020754 | 0.00052013 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2581-28_0_5_load_27 | 51 | 0.0050814 | 0.0012735 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2581-28_0_5_load_28 | 52 | 0.0093568 | 0.002345 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2581-28_0_5_load_29 | 53 | 0.0023257 | 0.00058287 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2581-28_0_5_load_30 | 54 | 0.010974 | 0.0027503 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2581-28_0_5_load_114 | 55 | 0.002282 | 0.00057193 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2581-28_0_5_load_112 | 57 | 0.004992 | 0.0012511 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2581-28_0_5_load_81 | 58 | 0.0051387 | 0.0012879 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2581-28_0_5_load_94 | 60 | 0.007082 | 0.0017749 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2581-28_0_5_load_32 | 61 | 0.0025443 | 0.00063766 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2581-28_0_5_load_33 | 62 | 0.0019424 | 0.00048681 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2581-28_0_5_load_35 | 63 | 0.0018741 | 0.00046969 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2581-28_0_5_load_36 | 64 | 0.0019986 | 0.00050089 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2581-28_0_5_load_52 | 66 | 0.0022868 | 0.00057313 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2581-28_0_5_load_134 | 67 | 0.0024528 | 0.00061473 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2581-28_0_5_load_110 | 68 | 0.0025274 | 0.00063343 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2581-28_0_5_load_53 | 69 | 0.0065269 | 0.0016358 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2581-28_0_5_load_38 | 70 | 0.0039225 | 0.00098308 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2581-28_0_5_load_39 | 71 | 0.004869 | 0.0012203 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2581-28_0_5_load_41 | 72 | 0.004847 | 0.0012148 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2581-28_0_5_load_103 | 73 | 0.00244 | 0.00061152 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2581-28_0_5_load_105 | 76 | 0.011456 | 0.002871 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2581-28_0_5_load_145 | 77 | 0.0080146 | 0.0020086 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2581-28_0_5_load_142 | 78 | 0.0069546 | 0.001743 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2581-28_0_5_load_75 | 79 | 0.0096759 | 0.002425 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2581-28_0_5_load_46 | 80 | 0.005807 | 0.0014554 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2581-28_0_5_load_47 | 81 | 0.0071735 | 0.0017979 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2581-28_0_5_load_49 | 82 | 0.0079145 | 0.0019836 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2581-28_0_5_load_63 | 83 | 0.0024678 | 0.0006185 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2581-28_0_5_load_126 | 84 | 0.0032744 | 0.00082065 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2581-28_0_5_load_109 | 85 | 0.0025396 | 0.00063649 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2581-28_0_5_load_95 | 86 | 0.0055895 | 0.0014009 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2581-28_0_5_load_96 | 87 | 0.0056685 | 0.0014207 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2581-28_0_5_load_54 | 88 | 0.010054 | 0.0025198 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2581-28_0_5_load_56 | 90 | 0.010842 | 0.0027173 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2581-28_0_5_load_58 | 92 | 0.0056295 | 0.0014109 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2581-28_0_5_load_90 | 93 | 0.0059506 | 0.0014914 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2581-28_0_5_load_61 | 94 | 0.013611 | 0.0034114 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2581-28_0_5_load_59 | 95 | 0.007001 | 0.0017546 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2581-28_0_5_load_60 | 96 | 0.007025 | 0.0017606 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2581-28_0_5_load_62 | 97 | 0.01134 | 0.002842 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2581-28_0_5_load_121 | 98 | 0.010812 | 0.0027096 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2581-28_0_5_load_122 | 99 | 0.011331 | 0.0028399 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2581-28_0_5_load_123 | 100 | 0.0023254 | 0.00058279 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2581-28_0_5_load_66 | 101 | 0.005077 | 0.0012724 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2581-28_0_5_load_119 | 102 | 0.0019189 | 0.00048092 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2581-28_0_5_load_117 | 103 | 0.0018373 | 0.00046046 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2581-28_0_5_load_74 | 104 | 0.002687 | 0.00067343 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2581-28_0_5_load_127 | 105 | 0.0034843 | 0.00087324 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2581-28_0_5_load_128 | 106 | 0.0033571 | 0.00084137 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2581-28_0_5_load_71 | 107 | 0.0058357 | 0.0014626 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2581-28_0_5_load_78 | 108 | 0.0018186 | 0.00045578 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2581-28_0_5_load_77 | 109 | 0.0020969 | 0.00052554 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2581-28_0_5_load_97 | 111 | 0.0023099 | 0.00057891 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2581-28_0_5_load_79 | 112 | 0.0026291 | 0.00065892 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2581-28_0_5_load_80 | 113 | 0.010361 | 0.0025968 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2581-28_0_5_load_135 | 114 | 0.0034902 | 0.00087473 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2581-28_0_5_load_129 | 115 | 0.0035543 | 0.0008908 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2581-28_0_5_load_82 | 117 | 0.0032358 | 0.00081096 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2581-28_0_5_load_83 | 118 | 0.0077812 | 0.0019501 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2581-28_0_5_load_84 | 119 | 0.022102 | 0.0055393 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2581-28_0_5_load_132 | 120 | 0.0027106 | 0.00067934 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2581-28_0_5_load_86 | 122 | 0.0034511 | 0.00086494 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2581-28_0_5_load_87 | 123 | 0.0019274 | 0.00048306 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2581-28_0_5_load_89 | 124 | 0.0039863 | 0.00099905 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2581-28_0_5_load_120 | 125 | 0.0036453 | 0.00091359 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2581-28_0_5_load_118 | 126 | 0.003907 | 0.00097919 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2581-28_0_5_load_106 | 127 | 0.0043656 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2581-28_0_5_load_102 | 128 | 0.0057258 | 0.001435 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2581-28_0_5_load_98 | 129 | 0.0023119 | 0.00057943 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2581-28_0_5_load_113 | 130 | 0.0025482 | 0.00063865 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2581-28_0_5_load_115 | 131 | 0.0022698 | 0.00056886 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2581-28_0_5_load_116 | 132 | 0.003542 | 0.00088772 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2581-28_0_5_load_143 | 133 | 0.0036078 | 0.0009042 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2581-28_0_5_load_139 | 134 | 0.0027134 | 0.00068003 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2581-28_0_5_load_136 | 135 | 0.004078 | 0.001022 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2581-28_0_5_load_140 | 138 | 0.0036314 | 0.00091011 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2581-28_0_5_load_146 | 139 | 0.0036401 | 0.0009123 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 116 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-28_0_5_line_0 |  | 0 | 1 | 0.00682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2581-28_0_5_line_1 |  | 0 | 2 | 0.0066668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2581-28_0_5_line_2 |  | 1 | 3 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2581-28_0_5_line_3 |  | 2 | 4 | 0.0098745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2581-28_0_5_line_4 |  | 3 | 5 | 0.021557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-28_0_5_line_5 |  | 4 | 6 | 0.0067539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2581-28_0_5_line_6 |  | 5 | 7 | 0.012055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2581-28_0_5_line_7 |  | 6 | 8 | 0.0050437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2581-28_0_5_line_8 |  | 7 | 74 | 0.006285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2581-28_0_5_line_9 |  | 7 | 59 | 0.029331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2581-28_0_5_line_10 |  | 8 | 60 | 0.0057424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2581-28_0_5_line_11 |  | 9 | 10 | 0.0017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2581-28_0_5_line_12 |  | 9 | 11 | 0.022435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2581-28_0_5_line_13 |  | 10 | 12 | 0.0074557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2581-28_0_5_line_14 |  | 11 | 13 | 0.020117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2581-28_0_5_line_15 |  | 11 | 14 | 0.022509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2581-28_0_5_line_16 |  | 12 | 15 | 0.0079447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2581-28_0_5_line_17 |  | 13 | 19 | 0.010133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2581-28_0_5_line_18 |  | 14 | 20 | 0.02038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2581-28_0_5_line_19 |  | 15 | 21 | 0.017781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2581-28_0_5_line_20 |  | 16 | 17 | 0.0084249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2581-28_0_5_line_21 |  | 16 | 18 | 0.018199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2581-28_0_5_line_22 |  | 17 | 22 | 0.010756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-28_0_5_line_23 |  | 18 | 23 | 0.01346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2581-28_0_5_line_24 |  | 19 | 24 | 0.024371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2581-28_0_5_line_25 |  | 20 | 25 | 0.011004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2581-28_0_5_line_26 |  | 21 | 101 | 0.0060854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2581-28_0_5_line_27 |  | 22 | 35 | 0.025487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2581-28_0_5_line_28 |  | 23 | 107 | 0.0031131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2581-28_0_5_line_29 |  | 24 | 116 | 0.017128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2581-28_0_5_line_30 |  | 25 | 48 | 0.0050118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2581-28_0_5_line_31 |  | 26 | 27 | 0.0011918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2581-28_0_5_line_32 |  | 26 | 28 | 0.015763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2581-28_0_5_line_33 |  | 28 | 29 | 0.018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2581-28_0_5_line_34 |  | 29 | 30 | 0.0066826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2581-28_0_5_line_35 |  | 30 | 36 | 0.0067575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2581-28_0_5_line_36 |  | 31 | 32 | 0.026872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2581-28_0_5_line_37 |  | 31 | 33 | 0.015753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2581-28_0_5_line_38 |  | 32 | 37 | 0.008002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2581-28_0_5_line_39 |  | 33 | 38 | 0.0093014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2581-28_0_5_line_40 |  | 34 | 35 | 0.011702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2581-28_0_5_line_41 |  | 35 | 104 | 0.014969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2581-28_0_5_line_42 |  | 35 | 79 | 0.022863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2581-28_0_5_line_43 |  | 36 | 37 | 0.015179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2581-28_0_5_line_44 |  | 38 | 110 | 0.0023769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2581-28_0_5_line_45 |  | 39 | 40 | 0.013018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2581-28_0_5_line_46 |  | 39 | 41 | 0.0053347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2581-28_0_5_line_47 |  | 40 | 42 | 0.00037638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2581-28_0_5_line_48 |  | 41 | 43 | 0.03325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2581-28_0_5_line_49 |  | 42 | 44 | 0.005688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2581-28_0_5_line_50 |  | 43 | 45 | 0.022843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2581-28_0_5_line_51 |  | 43 | 46 | 0.015096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2581-28_0_5_line_52 |  | 44 | 47 | 0.032726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2581-28_0_5_line_53 |  | 45 | 48 | 0.0093757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2581-28_0_5_line_54 |  | 46 | 49 | 0.0048639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2581-28_0_5_line_55 |  | 47 | 79 | 0.035367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_2581-28_0_5_line_56 |  | 49 | 64 | 0.021364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2581-28_0_5_line_57 |  | 49 | 61 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2581-28_0_5_line_58 |  | 50 | 51 | 0.021295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2581-28_0_5_line_59 |  | 50 | 52 | 0.005285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2581-28_0_5_line_60 |  | 51 | 53 | 0.014335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2581-28_0_5_line_61 |  | 52 | 54 | 0.02455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2581-28_0_5_line_62 |  | 53 | 55 | 0.0087802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2581-28_0_5_line_63 |  | 54 | 56 | 0.024981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2581-28_0_5_line_64 |  | 55 | 57 | 0.0036332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2581-28_0_5_line_65 |  | 56 | 58 | 0.0075138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_2581-28_0_5_line_66 |  | 56 | 59 | 0.049813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2581-28_0_5_line_67 |  | 57 | 130 | 0.0052539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2581-28_0_5_line_68 |  | 58 | 76 | 0.028789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2581-28_0_5_line_69 |  | 59 | 70 | 0.021744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2581-28_0_5_line_70 |  | 61 | 62 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2581-28_0_5_line_71 |  | 62 | 63 | 0.0085326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2581-28_0_5_line_72 |  | 63 | 65 | 0.0038301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2581-28_0_5_line_73 |  | 64 | 66 | 0.00065362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2581-28_0_5_line_74 |  | 65 | 67 | 0.013948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2581-28_0_5_line_75 |  | 65 | 68 | 0.0044283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2581-28_0_5_line_76 |  | 66 | 69 | 0.0019301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2581-28_0_5_line_77 |  | 68 | 85 | 0.013567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2581-28_0_5_line_78 |  | 69 | 86 | 0.027244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2581-28_0_5_line_79 |  | 70 | 71 | 0.02863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2581-28_0_5_line_80 |  | 71 | 72 | 0.017991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2581-28_0_5_line_81 |  | 72 | 73 | 0.026179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2581-28_0_5_line_82 |  | 73 | 75 | 0.018479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2581-28_0_5_line_83 |  | 74 | 77 | 0.024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2581-28_0_5_line_84 |  | 74 | 78 | 0.031388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2581-28_0_5_line_85 |  | 75 | 118 | 0.029043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2581-28_0_5_line_86 |  | 76 | 116 | 0.012712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2581-28_0_5_line_87 |  | 77 | 137 | 0.009563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2581-28_0_5_line_88 |  | 78 | 138 | 0.013901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2581-28_0_5_line_89 |  | 80 | 81 | 0.0034132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2581-28_0_5_line_90 |  | 81 | 82 | 0.0057602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2581-28_0_5_line_91 |  | 82 | 83 | 0.011212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2581-28_0_5_line_92 |  | 83 | 84 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2581-28_0_5_line_93 |  | 84 | 100 | 0.00065191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2581-28_0_5_line_94 |  | 86 | 87 | 0.0026171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2581-28_0_5_line_95 |  | 87 | 128 | 0.0095322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2581-28_0_5_line_96 |  | 88 | 89 | 0.05691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2581-28_0_5_line_97 |  | 88 | 90 | 0.00067047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2581-28_0_5_line_98 |  | 89 | 91 | 0.004774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2581-28_0_5_line_99 |  | 89 | 92 | 0.027715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2581-28_0_5_line_100 |  | 91 | 93 | 0.027731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2581-28_0_5_line_101 |  | 92 | 94 | 0.031876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2581-28_0_5_line_102 |  | 94 | 95 | 0.00081938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2581-28_0_5_line_103 |  | 95 | 96 | 0.018766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2581-28_0_5_line_104 |  | 96 | 97 | 0.01663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2581-28_0_5_line_105 |  | 97 | 98 | 0.014525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2581-28_0_5_line_106 |  | 98 | 99 | 0.018984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2581-28_0_5_line_107 |  | 99 | 127 | 0.0066634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2581-28_0_5_line_108 |  | 100 | 131 | 0.0081386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2581-28_0_5_line_109 |  | 101 | 102 | 0.00094377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2581-28_0_5_line_110 |  | 102 | 103 | 0.0039533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2581-28_0_5_line_111 |  | 103 | 132 | 0.0039105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2581-28_0_5_line_112 |  | 104 | 110 | 0.015337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2581-28_0_5_line_113 |  | 105 | 106 | 0.019551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2581-28_0_5_line_114 |  | 106 | 115 | 0.00031329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2581-28_0_5_line_115 |  | 107 | 108 | 0.0048962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2581-28_0_5_line_116 |  | 108 | 109 | 0.0074472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2581-28_0_5_line_117 |  | 109 | 112 | 0.0081168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2581-28_0_5_line_118 |  | 110 | 111 | 0.02864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2581-28_0_5_line_119 |  | 111 | 129 | 0.0079607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2581-28_0_5_line_120 |  | 112 | 113 | 0.0097858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2581-28_0_5_line_121 |  | 113 | 114 | 0.0062588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2581-28_0_5_line_122 |  | 114 | 115 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2581-28_0_5_line_123 |  | 116 | 127 | 0.041205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2581-28_0_5_line_124 |  | 117 | 118 | 0.0018316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2581-28_0_5_line_125 |  | 117 | 119 | 0.0004782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2581-28_0_5_line_126 |  | 120 | 121 | 0.018168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2581-28_0_5_line_127 |  | 121 | 133 | 0.020316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2581-28_0_5_line_128 |  | 121 | 134 | 0.0045774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2581-28_0_5_line_129 |  | 122 | 123 | 0.02445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2581-28_0_5_line_130 |  | 123 | 124 | 0.0049694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2581-28_0_5_line_131 |  | 124 | 125 | 0.011431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2581-28_0_5_line_132 |  | 125 | 126 | 0.011072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2581-28_0_5_line_133 |  | 126 | 132 | 0.0059562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2581-28_0_5_line_134 |  | 130 | 131 | 0.0089075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2581-28_0_5_line_135 |  | 133 | 139 | 0.010796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2581-28_0_5_line_136 |  | 134 | 138 | 0.028752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2581-28_0_5_line_137 |  | 135 | 136 | 0.035357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2581-28_0_5_line_138 |  | 136 | 137 | 0.061139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-28_0_5_trafo_104 | 0.63 MVA 20/0.4 kV | 140 | 116 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2634334.4401 | 1245057.2803 | 2634340.6515 | 1245060.0967
1 | 2634334.4401 | 1245057.2803 | 2634328.3683 | 1245054.5273
2 | 2634356.5919 | 1245067.3244 | 2634340.6515 | 1245060.0967
3 | 2634319.375 | 1245050.4495 | 2634328.3683 | 1245054.5273
4 | 2634356.5919 | 1245067.3244 | 2634376.2251 | 1245076.2265
5 | 2634319.375 | 1245050.4495 | 2634313.2239 | 1245047.6605
6 | 2634387.2039 | 1245081.2045 | 2634376.2251 | 1245076.2265
7 | 2634308.6303 | 1245045.5777 | 2634313.2239 | 1245047.6605
8 | 2634387.2039 | 1245081.2045 | 2634382.6155 | 1245085.514
9 | 2634387.2039 | 1245081.2045 | 2634410.1726 | 1245062.8812
10 | 2634303.4004 | 1245043.2064 | 2634308.6303 | 1245045.5777
11 | 2634565.8677 | 1244970.8164 | 2634567.4057 | 1244971.6423
12 | 2634546.1021 | 1244960.2036 | 2634565.8677 | 1244970.8164
13 | 2634567.4057 | 1244971.6423 | 2634573.9744 | 1244975.1693
14 | 2634546.1021 | 1244960.2036 | 2634534.9995 | 1244971.2017 | 2634531.4258 | 1244973.9186
15 | 2634546.1021 | 1244960.2036 | 2634528.1043 | 1244951.2042 | 2634525.9298 | 1244950.2207
16 | 2634580.9508 | 1244978.9702 | 2634575.7027 | 1244976.0972 | 2634573.9744 | 1244975.1693
17 | 2634523.3598 | 1244980.0511 | 2634531.4258 | 1244973.9186
18 | 2634507.3605 | 1244941.8225 | 2634525.9298 | 1244950.2207
19 | 2634580.9508 | 1244978.9702 | 2634596.5476 | 1244987.5085
20 | 2634561.3986 | 1244899.7978 | 2634559.1029 | 1244891.8015 | 2634559.0838 | 1244891.6976
21 | 2634561.3986 | 1244899.7978 | 2634568.7037 | 1244899.996 | 2634574.1988 | 1244900.9063 | 2634578.942 | 1244903.3174
22 | 2634559.0838 | 1244891.6976 | 2634557.1358 | 1244881.1198
23 | 2634578.942 | 1244903.3174 | 2634590.9413 | 1244909.4168
24 | 2634523.3598 | 1244980.0511 | 2634513.3024 | 1244987.6974 | 2634504.1934 | 1244995.0994
25 | 2634497.4541 | 1244937.0383 | 2634503.1008 | 1244939.896 | 2634507.3605 | 1244941.8225
26 | 2634601.8855 | 1244990.4307 | 2634596.5476 | 1244987.5085
27 | 2634557.8984 | 1244856.0046 | 2634557.2992 | 1244857.7022 | 2634555.6003 | 1244866.5981 | 2634556.1 | 1244875.4957 | 2634557.1358 | 1244881.1198
28 | 2634593.7054 | 1244910.8489 | 2634591.1035 | 1244909.4992 | 2634590.9413 | 1244909.4168
29 | 2634490.9005 | 1245005.9013 | 2634504.1934 | 1244995.0994
30 | 2634497.4541 | 1244937.0383 | 2634492.9823 | 1244934.7752
31 | 2634646.4969 | 1244862.3026 | 2634647.0104 | 1244861.2271
32 | 2634653.8018 | 1244847.0019 | 2634647.0104 | 1244861.2271
33 | 2634653.8018 | 1244847.0019 | 2634641.8013 | 1244839.6049 | 2634637.9719 | 1244837.1338
34 | 2634637.9719 | 1244837.1338 | 2634632.3569 | 1244833.5104
35 | 2634632.3569 | 1244833.5104 | 2634626.679 | 1244829.8464
36 | 2634583.6011 | 1244804.3985 | 2634593.0038 | 1244810.3015 | 2634606.7674 | 1244817.9985
37 | 2634583.6011 | 1244804.3985 | 2634580.6979 | 1244809.8963 | 2634576.2032 | 1244818.3061
38 | 2634613.7515 | 1244821.9042 | 2634606.7674 | 1244817.9985
39 | 2634576.2032 | 1244818.3061 | 2634571.8189 | 1244826.5094
40 | 2634557.8984 | 1244856.0046 | 2634568.1003 | 1244858.2988 | 2634569.2932 | 1244858.6572
41 | 2634557.8984 | 1244856.0046 | 2634560.0978 | 1244849.402 | 2634563.5734 | 1244842.1861
42 | 2634557.8984 | 1244856.0046 | 2634548.3969 | 1244852.8028 | 2634536.1356 | 1244849.0024
43 | 2634613.7515 | 1244821.9042 | 2634618.3988 | 1244824.5031 | 2634626.679 | 1244829.8464
44 | 2634570.6986 | 1244828.6057 | 2634571.8189 | 1244826.5094
45 | 2634479.9088 | 1244885.0628 | 2634483.4987 | 1244876.6967 | 2634485.2497 | 1244873.1958
46 | 2634477.8052 | 1244889.9652 | 2634479.9088 | 1244885.0628
47 | 2634485.2497 | 1244873.1958 | 2634485.418 | 1244872.8592
48 | 2634464.1978 | 1244920.3019 | 2634474.3995 | 1244897.9021 | 2634477.8052 | 1244889.9652
49 | 2634485.418 | 1244872.8592 | 2634487.9624 | 1244867.772
50 | 2634464.1978 | 1244920.3019 | 2634471.8975 | 1244924.1046 | 2634484.6169 | 1244930.5416
51 | 2634464.1978 | 1244920.3019 | 2634450.6072 | 1244913.7313
52 | 2634502.3987 | 1244838.4039 | 2634496.7006 | 1244850.3007 | 2634487.9624 | 1244867.772
53 | 2634484.6169 | 1244930.5416 | 2634492.9823 | 1244934.7752
54 | 2634446.2282 | 1244911.6142 | 2634450.6072 | 1244913.7313
55 | 2634502.3987 | 1244838.4039 | 2634505.2037 | 1244839.3986 | 2634514.4041 | 1244842.3984 | 2634521.6 | 1244844.4972 | 2634536.1356 | 1244849.0024
56 | 2634446.2282 | 1244911.6142 | 2634437.3618 | 1244931.0519
57 | 2634446.2282 | 1244911.6142 | 2634430.1319 | 1244903.7997
58 | 2634398.9683 | 1245013.3277 | 2634390.699 | 1245010.0007 | 2634379.3607 | 1245005.0252
59 | 2634398.9683 | 1245013.3277 | 2634403.8713 | 1245015.3004
60 | 2634366.1204 | 1244999.5383 | 2634373.5992 | 1245002.4969 | 2634379.3607 | 1245005.0252
61 | 2634426.7456 | 1245024.2094 | 2634423.4003 | 1245022.7985 | 2634407.1014 | 1245016.6 | 2634403.8713 | 1245015.3004
62 | 2634366.1204 | 1244999.5383 | 2634357.9558 | 1244996.3083
63 | 2634450.1024 | 1245033.0043 | 2634439.3033 | 1245029.5061 | 2634426.7456 | 1245024.2094
64 | 2634354.5706 | 1244994.9895 | 2634355.402 | 1244995.298 | 2634357.9558 | 1244996.3083
65 | 2634450.1024 | 1245033.0043 | 2634456.4295 | 1245028.9516
66 | 2634450.1024 | 1245033.0043 | 2634434.2031 | 1245043.897 | 2634425.2035 | 1245050.6047 | 2634410.1726 | 1245062.8812
67 | 2634354.5706 | 1244994.9895 | 2634349.645 | 1244993.1615
68 | 2634456.4295 | 1245028.9516 | 2634457.6026 | 1245028.2003 | 2634480.6313 | 1245013.3599
69 | 2634410.1726 | 1245062.8812 | 2634426.0879 | 1245077.6966
70 | 2634418.7747 | 1244898.2859 | 2634430.1319 | 1244903.7997
71 | 2634418.7747 | 1244898.2859 | 2634418.5997 | 1244898.2009 | 2634411.0614 | 1244894.6374
72 | 2634407.5987 | 1244893.0005 | 2634411.0614 | 1244894.6374
73 | 2634437.3618 | 1244931.0519 | 2634437.0905 | 1244931.6466
74 | 2634407.5987 | 1244893.0005 | 2634412.7026 | 1244880.5998 | 2634412.9326 | 1244880.1139
75 | 2634407.5987 | 1244893.0005 | 2634403.5981 | 1244891.1018
76 | 2634436.2895 | 1244933.4026 | 2634437.0905 | 1244931.6466
77 | 2634391.4085 | 1244885.153 | 2634394.1038 | 1244886.596 | 2634403.5981 | 1244891.1018
78 | 2634436.2895 | 1244933.4026 | 2634424.9828 | 1244958.19
79 | 2634446.8477 | 1245097.4086 | 2634445.3995 | 1245096.0958 | 2634434.7986 | 1245085.8054 | 2634426.0879 | 1245077.6966
80 | 2634446.8477 | 1245097.4086 | 2634457.1015 | 1245106.7039 | 2634460.4989 | 1245109.09
81 | 2634460.4989 | 1245109.09 | 2634469.2012 | 1245115.2018 | 2634482.0377 | 1245123.9684
82 | 2634497.6442 | 1245133.8568 | 2634485.9001 | 1245126.6061 | 2634482.0377 | 1245123.9684
83 | 2634382.6155 | 1245085.514 | 2634375.4974 | 1245092.1994 | 2634365.6031 | 1245103.488
84 | 2634382.6155 | 1245085.514 | 2634400.44 | 1245106.1306 | 2634403.3918 | 1245109.0261
85 | 2634497.6442 | 1245133.8568 | 2634508.899 | 1245140.8045 | 2634516.8171 | 1245127.1132
86 | 2634490.9005 | 1245005.9013 | 2634486.004 | 1245009.8977 | 2634480.6313 | 1245013.3599
87 | 2634358.8543 | 1245110.2481 | 2634363.397 | 1245106.005 | 2634365.6031 | 1245103.488
88 | 2634413.3153 | 1245118.7602 | 2634403.3918 | 1245109.0261
89 | 2634304.0027 | 1244974.4692 | 2634307.0987 | 1244975.9063 | 2634307.0987 | 1244975.9063
90 | 2634307.0987 | 1244975.9063 | 2634312.3901 | 1244978.1825
91 | 2634312.3901 | 1244978.1825 | 2634320.8004 | 1244981.8004 | 2634322.7032 | 1244982.5795
92 | 2634322.7032 | 1244982.5795 | 2634333.1155 | 1244986.8432
93 | 2634333.1155 | 1244986.8432 | 2634333.7188 | 1244987.0903
94 | 2634423.8966 | 1244960.5711 | 2634424.9828 | 1244958.19
95 | 2634419.9407 | 1244969.2437 | 2634423.8966 | 1244960.5711
96 | 2634636.0976 | 1245106.2002 | 2634630.8944 | 1245109.6721 | 2634601.2569 | 1245118.3939 | 2634591.536 | 1245117.9259 | 2634582.826 | 1245112.9562
97 | 2634582.826 | 1245112.9562 | 2634582.2436 | 1245112.6239
98 | 2634636.0976 | 1245106.2002 | 2634640.7527 | 1245107.3169
99 | 2634636.0976 | 1245106.2002 | 2634612.6101 | 1245091.487
100 | 2634640.7527 | 1245107.3169 | 2634645.6199 | 1245103.176 | 2634657.3001 | 1245085.3159
101 | 2634612.6101 | 1245091.487 | 2634602.8999 | 1245085.4043 | 2634585.6387 | 1245074.4977
102 | 2634584.946 | 1245074.06 | 2634585.6387 | 1245074.4977
103 | 2634584.946 | 1245074.06 | 2634569.0819 | 1245064.0361
104 | 2634555.0229 | 1245055.1527 | 2634569.0819 | 1245064.0361
105 | 2634542.7438 | 1245047.3941 | 2634555.0229 | 1245055.1527
106 | 2634542.7438 | 1245047.3941 | 2634528.5038 | 1245038.3964 | 2634526.7579 | 1245037.159
107 | 2634521.3215 | 1245033.3059 | 2634526.7579 | 1245037.159
108 | 2634341.2941 | 1244990.0622 | 2634337.9033 | 1244988.8038 | 2634333.7188 | 1244987.0903
109 | 2634601.8855 | 1244990.4307 | 2634602.7133 | 1244990.8839
110 | 2634602.7133 | 1244990.8839 | 2634606.181 | 1244992.7822
111 | 2634609.6003 | 1244994.6794 | 2634608.4042 | 1244993.9993 | 2634606.181 | 1244992.7822
112 | 2634570.6986 | 1244828.6057 | 2634564.0977 | 1244841.0977 | 2634563.5734 | 1244842.1861
113 | 2634653.2816 | 1244942.8549 | 2634652.9037 | 1244942.6031 | 2634641.8019 | 1244935.3003 | 2634636.6058 | 1244932.7035
114 | 2634636.3256 | 1244932.5635 | 2634636.6058 | 1244932.7035
115 | 2634593.7054 | 1244910.8489 | 2634598.0517 | 1244913.1033
116 | 2634604.6625 | 1244916.5323 | 2634598.0517 | 1244913.1033
117 | 2634604.6625 | 1244916.5323 | 2634611.8677 | 1244920.2697
118 | 2634570.6986 | 1244828.6057 | 2634562.6019 | 1244824.2002 | 2634545.2292 | 1244815.5148
119 | 2634545.2292 | 1244815.5148 | 2634538.1088 | 1244811.9549
120 | 2634620.5925 | 1244924.7007 | 2634615.6001 | 1244922.2057 | 2634611.8677 | 1244920.2697
121 | 2634620.5925 | 1244924.7007 | 2634626.1911 | 1244927.4987
122 | 2634636.3256 | 1244932.5635 | 2634626.1911 | 1244927.4987
123 | 2634490.9005 | 1245005.9013 | 2634493.0979 | 1245008.7048 | 2634498.7994 | 1245015.698 | 2634509.6025 | 1245025.0001 | 2634521.3215 | 1245033.3059
124 | 2634516.8171 | 1245127.1132 | 2634517.7341 | 1245125.5277
125 | 2634517.7341 | 1245125.5277 | 2634517.9735 | 1245125.1137
126 | 2634437.1088 | 1245142.0998 | 2634453.6718 | 1245149.5656
127 | 2634437.1088 | 1245142.0998 | 2634425.7688 | 1245158.9561
128 | 2634437.1088 | 1245142.0998 | 2634433.8411 | 1245138.8944
129 | 2634638.6586 | 1245011.2038 | 2634653.6021 | 1245019.7017 | 2634659.9599 | 1245023.2054
130 | 2634638.6586 | 1245011.2038 | 2634634.3387 | 1245008.7473
131 | 2634624.4024 | 1245003.0969 | 2634634.3387 | 1245008.7473
132 | 2634614.7778 | 1244997.6237 | 2634624.4024 | 1245003.0969
133 | 2634614.7778 | 1244997.6237 | 2634609.6003 | 1244994.6794
134 | 2634349.645 | 1244993.1615 | 2634341.2941 | 1244990.0622
135 | 2634434.3894 | 1245165.4547 | 2634425.7688 | 1245158.9561
136 | 2634413.3153 | 1245118.7602 | 2634433.8411 | 1245138.8944
137 | 2634320.1103 | 1245157.3547 | 2634304.0195 | 1245151.8026 | 2634293.2171 | 1245146.2922 | 2634288.623 | 1245142.1155
138 | 2634320.1103 | 1245157.3547 | 2634331.1843 | 1245143.3318 | 2634346.6319 | 1245121.6404 | 2634358.8543 | 1245110.2481

## bus_geodata
| x | y | coords
0 | 2634334.4401 | 1245057.2803
1 | 2634340.6515 | 1245060.0967
2 | 2634328.3683 | 1245054.5273
3 | 2634356.5919 | 1245067.3244
4 | 2634319.375 | 1245050.4495
5 | 2634376.2251 | 1245076.2265
6 | 2634313.2239 | 1245047.6605
7 | 2634387.2039 | 1245081.2045
8 | 2634308.6303 | 1245045.5777
9 | 2634565.8677 | 1244970.8164
10 | 2634567.4057 | 1244971.6423
11 | 2634546.1021 | 1244960.2036
12 | 2634573.9744 | 1244975.1693
13 | 2634531.4258 | 1244973.9186
14 | 2634525.9298 | 1244950.2207
15 | 2634580.9508 | 1244978.9702
16 | 2634561.3986 | 1244899.7978
17 | 2634559.0838 | 1244891.6976
18 | 2634578.942 | 1244903.3174
19 | 2634523.3598 | 1244980.0511
20 | 2634507.3605 | 1244941.8225
21 | 2634596.5476 | 1244987.5085
22 | 2634557.1358 | 1244881.1198
23 | 2634590.9413 | 1244909.4168
24 | 2634504.1934 | 1244995.0994
25 | 2634497.4541 | 1244937.0383
26 | 2634647.0104 | 1244861.2271
27 | 2634646.4969 | 1244862.3026
28 | 2634653.8018 | 1244847.0019
29 | 2634637.9719 | 1244837.1338
30 | 2634632.3569 | 1244833.5104
31 | 2634583.6011 | 1244804.3985
32 | 2634606.7674 | 1244817.9985
33 | 2634576.2033 | 1244818.3061
34 | 2634569.2932 | 1244858.6572
35 | 2634557.8984 | 1244856.0046
36 | 2634626.679 | 1244829.8464
37 | 2634613.7515 | 1244821.9042
38 | 2634571.8189 | 1244826.5094
39 | 2634479.9088 | 1244885.0628
40 | 2634485.2497 | 1244873.1958
41 | 2634477.8052 | 1244889.9652
42 | 2634485.418 | 1244872.8592
43 | 2634464.1978 | 1244920.3019
44 | 2634487.9624 | 1244867.772
45 | 2634484.6169 | 1244930.5416
46 | 2634450.6072 | 1244913.7313
47 | 2634502.3987 | 1244838.4039
48 | 2634492.9823 | 1244934.7752
49 | 2634446.2282 | 1244911.6142
50 | 2634398.9683 | 1245013.3277
51 | 2634379.3607 | 1245005.0252
52 | 2634403.8713 | 1245015.3004
53 | 2634366.1204 | 1244999.5383
54 | 2634426.7456 | 1245024.2094
55 | 2634357.9558 | 1244996.3083
56 | 2634450.1024 | 1245033.0043
57 | 2634354.5706 | 1244994.9895
58 | 2634456.4295 | 1245028.9516
59 | 2634410.1726 | 1245062.8812
60 | 2634303.4004 | 1245043.2064
61 | 2634430.1319 | 1244903.7997
62 | 2634418.7747 | 1244898.2859
63 | 2634411.0614 | 1244894.6374
64 | 2634437.3618 | 1244931.0519
65 | 2634407.5987 | 1244893.0005
66 | 2634437.0905 | 1244931.6466
67 | 2634412.9326 | 1244880.1139
68 | 2634403.5981 | 1244891.1018
69 | 2634436.2895 | 1244933.4026
70 | 2634426.0879 | 1245077.6966
71 | 2634446.8477 | 1245097.4086
72 | 2634460.4989 | 1245109.09
73 | 2634482.0377 | 1245123.9684
74 | 2634382.6155 | 1245085.514
75 | 2634497.6442 | 1245133.8568
76 | 2634480.6313 | 1245013.3599
77 | 2634365.6031 | 1245103.488
78 | 2634403.3918 | 1245109.0261
79 | 2634536.1356 | 1244849.0024
80 | 2634304.0027 | 1244974.4692
81 | 2634307.0987 | 1244975.9063
82 | 2634312.3901 | 1244978.1825
83 | 2634322.7032 | 1244982.5795
84 | 2634333.1155 | 1244986.8432
85 | 2634391.4085 | 1244885.153
86 | 2634424.9828 | 1244958.19
87 | 2634423.8966 | 1244960.5711
88 | 2634582.826 | 1245112.9562
89 | 2634636.0976 | 1245106.2002
90 | 2634582.2436 | 1245112.6239
91 | 2634640.7527 | 1245107.3169
92 | 2634612.6101 | 1245091.487
93 | 2634657.3001 | 1245085.3159
94 | 2634585.6387 | 1245074.4977
95 | 2634584.946 | 1245074.06
96 | 2634569.0819 | 1245064.0361
97 | 2634555.0229 | 1245055.1528
98 | 2634542.7438 | 1245047.3941
99 | 2634526.7579 | 1245037.159
100 | 2634333.7188 | 1244987.0903
101 | 2634601.8855 | 1244990.4307
102 | 2634602.7133 | 1244990.8839
103 | 2634606.181 | 1244992.7822
104 | 2634563.5734 | 1244842.1861
105 | 2634653.2816 | 1244942.8549
106 | 2634636.6058 | 1244932.7035
107 | 2634593.7054 | 1244910.8489
108 | 2634598.0517 | 1244913.1033
109 | 2634604.6625 | 1244916.5323
110 | 2634570.6986 | 1244828.6057
111 | 2634545.2292 | 1244815.5148
112 | 2634611.8677 | 1244920.2697
113 | 2634620.5925 | 1244924.7007
114 | 2634626.1911 | 1244927.4987
115 | 2634636.3256 | 1244932.5635
116 | 2634490.9005 | 1245005.9013
117 | 2634517.7341 | 1245125.5277
118 | 2634516.8171 | 1245127.1132
119 | 2634517.9735 | 1245125.1137
120 | 2634453.6718 | 1245149.5656
121 | 2634437.1088 | 1245142.0998
122 | 2634659.9599 | 1245023.2054
123 | 2634638.6586 | 1245011.2038
124 | 2634634.3387 | 1245008.7473
125 | 2634624.4024 | 1245003.0969
126 | 2634614.7778 | 1244997.6237
127 | 2634521.3215 | 1245033.3059
128 | 2634419.9407 | 1244969.2437
129 | 2634538.1088 | 1244811.9549
130 | 2634349.645 | 1244993.1615
131 | 2634341.2941 | 1244990.0622
132 | 2634609.6003 | 1244994.6794
133 | 2634425.7688 | 1245158.9561
134 | 2634433.8411 | 1245138.8944
135 | 2634288.623 | 1245142.1155
136 | 2634320.1103 | 1245157.3547
137 | 2634358.8543 | 1245110.2481
138 | 2634413.3153 | 1245118.7602
139 | 2634434.3894 | 1245165.4547
140 | 2634450.1024 | 1245033.0043

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98719 | -0.24632 | 0.0014914 | 0.00037378
1 | 0.98729 | -0.24435 | 0.0023683 | 0.00059354
2 | 0.9871 | -0.24808 | 0.0023 | 0.00057643
3 | 0.98759 | -0.23853 | 0.0069492 | 0.0017416
4 | 0.98698 | -0.25027 | 0.0023734 | 0.00059483
5 | 0.98809 | -0.2287 | 0.0066756 | 0.0016731
6 | 0.98692 | -0.25149 | 0.0014858 | 0.00037239
7 | 0.98845 | -0.22177 | 0 | 0
8 | 0.98688 | -0.25226 | 0.001482 | 0.00037143
9 | 0.99121 | -0.16722 | 0.0032589 | 0.00081676
10 | 0.99114 | -0.1685 | 0.0022284 | 0.00055848
11 | 0.99213 | -0.14938 | 0 | 0
12 | 0.99087 | -0.17371 | 0.0030072 | 0.00075368
13 | 0.99429 | -0.10813 | 0.0025404 | 0.00063669
14 | 0.99018 | -0.18677 | 0.0042926 | 0.0010758
15 | 0.99061 | -0.17884 | 0.0038203 | 0.00095747
16 | 0.97394 | -0.50223 | 0 | 0
17 | 0.9743 | -0.49523 | 0.0063261 | 0.0015855
18 | 0.97317 | -0.51736 | 0.0064678 | 0.001621
19 | 0.99539 | -0.08719 | 0.0024797 | 0.00062148
20 | 0.98845 | -0.21997 | 0.0032173 | 0.00080633
21 | 0.99008 | -0.18913 | 0.0032478 | 0.00081398
22 | 0.97481 | -0.48505 | 0.0084986 | 0.0021299
23 | 0.97269 | -0.52697 | 0.0021278 | 0.00053327
24 | 0.99807 | -0.036492 | 0.0068477 | 0.0017162
25 | 0.98753 | -0.23763 | 0.0090429 | 0.0022664
26 | 0.97414 | -0.4985 | 0.0024633 | 0.00061735
27 | 0.97413 | -0.49857 | 0.0034795 | 0.00087204
28 | 0.97422 | -0.49678 | 0 | 0
29 | 0.97433 | -0.49474 | 0.0017269 | 0.0004328
30 | 0.97437 | -0.4938 | 0.0017028 | 0.00042677
31 | 0.97507 | -0.48009 | 0 | 0
32 | 0.97469 | -0.48758 | 0.0020598 | 0.00051623
33 | 0.97529 | -0.4757 | 0.0024379 | 0.000611
34 | 0.97619 | -0.45799 | 0.0045107 | 0.0011305
35 | 0.97624 | -0.45702 | 0 | 0
36 | 0.97443 | -0.49264 | 0.0018663 | 0.00046775
37 | 0.97459 | -0.48951 | 0.0018943 | 0.00047476
38 | 0.97544 | -0.4727 | 0.0030486 | 0.00076406
39 | 0.98246 | -0.33566 | 0.0039504 | 0.00099005
40 | 0.98176 | -0.34924 | 0.0039636 | 0.00099338
41 | 0.98276 | -0.32991 | 0.0022544 | 0.000565
42 | 0.98174 | -0.34962 | 0.0029846 | 0.00074801
43 | 0.98464 | -0.29346 | 0 | 0
44 | 0.98145 | -0.35521 | 0.0063199 | 0.0015839
45 | 0.9864 | -0.25942 | 0.0024439 | 0.0006125
46 | 0.98402 | -0.3055 | 0.0026677 | 0.0006686
47 | 0.97989 | -0.38553 | 0 | 0
48 | 0.98713 | -0.24528 | 0.0021954 | 0.00055022
49 | 0.98383 | -0.30915 | 0 | 0
50 | 0.9924 | -0.14553 | 0.0020754 | 0.00052013
51 | 0.99146 | -0.16381 | 0.0050814 | 0.0012735
52 | 0.99265 | -0.14081 | 0.0093568 | 0.002345
53 | 0.99089 | -0.17485 | 0.0023257 | 0.00058287
54 | 0.99399 | -0.11483 | 0.010974 | 0.0027503
55 | 0.99056 | -0.18125 | 0.002282 | 0.00057193
56 | 0.99561 | -0.083649 | 0 | 0
57 | 0.99043 | -0.18375 | 0.004992 | 0.0012511
58 | 0.99626 | -0.071261 | 0.0051387 | 0.0012879
59 | 0.99027 | -0.18648 | 0 | 0
60 | 0.98684 | -0.25299 | 0.007082 | 0.0017749
61 | 0.9836 | -0.31363 | 0.0025443 | 0.00063766
62 | 0.98347 | -0.3162 | 0.0019424 | 0.00048681
63 | 0.9834 | -0.31765 | 0.0018741 | 0.00046969
64 | 0.98329 | -0.31985 | 0.0019986 | 0.00050089
65 | 0.98337 | -0.31817 | 0 | 0
66 | 0.98327 | -0.32015 | 0.0022868 | 0.00057313
67 | 0.98334 | -0.31878 | 0.0024528 | 0.00061473
68 | 0.98335 | -0.31857 | 0.0025274 | 0.00063343
69 | 0.98323 | -0.32097 | 0.0065269 | 0.0016358
70 | 0.98928 | -0.20551 | 0.0039225 | 0.00098308
71 | 0.98809 | -0.22863 | 0.004869 | 0.0012203
72 | 0.98742 | -0.24162 | 0.004847 | 0.0012148
73 | 0.98657 | -0.25827 | 0.00244 | 0.00061152
74 | 0.98824 | -0.22574 | 0 | 0
75 | 0.986 | -0.26924 | 0 | 0
76 | 0.99881 | -0.022653 | 0.011456 | 0.002871
77 | 0.98797 | -0.23109 | 0.0080146 | 0.0020086
78 | 0.98757 | -0.23878 | 0.0069546 | 0.001743
79 | 0.97821 | -0.4184 | 0.0096759 | 0.002425
80 | 0.98924 | -0.20689 | 0.005807 | 0.0014554
81 | 0.98926 | -0.20653 | 0.0071735 | 0.0017979
82 | 0.98932 | -0.2052 | 0.0079145 | 0.0019836
83 | 0.98954 | -0.20103 | 0.0024678 | 0.0006185
84 | 0.98978 | -0.19635 | 0.0032744 | 0.00082065
85 | 0.98332 | -0.31919 | 0.0025396 | 0.00063649
86 | 0.9828 | -0.32932 | 0.0055895 | 0.0014009
87 | 0.98277 | -0.32986 | 0.0056685 | 0.0014207
88 | 0.98878 | -0.21616 | 0.010054 | 0.0025198
89 | 0.98987 | -0.19498 | 0 | 0
90 | 0.98877 | -0.21629 | 0.010842 | 0.0027173
91 | 0.98984 | -0.19549 | 0 | 0
92 | 0.99055 | -0.18176 | 0.0056295 | 0.0014109
93 | 0.98969 | -0.19843 | 0.0059506 | 0.0014914
94 | 0.9915 | -0.16338 | 0.013611 | 0.0034114
95 | 0.99153 | -0.16271 | 0.007001 | 0.0017546
96 | 0.99244 | -0.14507 | 0.007025 | 0.0017606
97 | 0.99336 | -0.12739 | 0.01134 | 0.002842
98 | 0.99431 | -0.10907 | 0.010812 | 0.0027096
99 | 0.99574 | -0.081578 | 0.011331 | 0.0028399
100 | 0.9898 | -0.19604 | 0.0023254 | 0.00058279
101 | 0.98992 | -0.1923 | 0.005077 | 0.0012724
102 | 0.9899 | -0.1927 | 0.0019189 | 0.00048092
103 | 0.98981 | -0.19427 | 0.0018373 | 0.00046046
104 | 0.97585 | -0.46469 | 0.002687 | 0.00067343
105 | 0.97156 | -0.54931 | 0.0034843 | 0.00087324
106 | 0.97162 | -0.54805 | 0.0033571 | 0.00084137
107 | 0.97258 | -0.52907 | 0.0058357 | 0.0014626
108 | 0.97244 | -0.53185 | 0.0018186 | 0.00045578
109 | 0.97224 | -0.53583 | 0.0020969 | 0.00052554
110 | 0.97549 | -0.4718 | 0 | 0
111 | 0.97537 | -0.47422 | 0.0023099 | 0.00057891
112 | 0.97203 | -0.53985 | 0.0026291 | 0.00065892
113 | 0.97181 | -0.54423 | 0.010361 | 0.0025968
114 | 0.97173 | -0.54583 | 0.0034902 | 0.00087473
115 | 0.97162 | -0.54801 | 0.0035543 | 0.0008908
116 | 1 | 0 | -0.55476 | -0.14131
117 | 0.98508 | -0.28733 | 0.0032358 | 0.00081096
118 | 0.98512 | -0.2865 | 0.0077812 | 0.0019501
119 | 0.98507 | -0.28752 | 0.022102 | 0.0055393
120 | 0.98694 | -0.25104 | 0.0027106 | 0.00067934
121 | 0.98699 | -0.25016 | 0 | 0
122 | 0.98932 | -0.20394 | 0.0034511 | 0.00086494
123 | 0.98939 | -0.20243 | 0.0019274 | 0.00048306
124 | 0.98942 | -0.20196 | 0.0039863 | 0.00099905
125 | 0.98952 | -0.20005 | 0.0036453 | 0.00091359
126 | 0.98965 | -0.19749 | 0.003907 | 0.00097919
127 | 0.99631 | -0.07062 | 0.0043656 | 0.0010941
128 | 0.98272 | -0.33084 | 0.0057258 | 0.001435
129 | 0.97535 | -0.47456 | 0.0023119 | 0.00057943
130 | 0.99027 | -0.1869 | 0.0025482 | 0.00063865
131 | 0.99001 | -0.19185 | 0.0022698 | 0.00056886
132 | 0.98974 | -0.19569 | 0.003542 | 0.00088772
133 | 0.98685 | -0.2528 | 0.0036078 | 0.0009042
134 | 0.98703 | -0.24934 | 0.0027134 | 0.00068003
135 | 0.98757 | -0.23882 | 0.004078 | 0.001022
136 | 0.98771 | -0.23624 | 0 | 0
137 | 0.98793 | -0.23178 | 0 | 0
138 | 0.98737 | -0.24283 | 0.0036314 | 0.00091011
139 | 0.98682 | -0.2535 | 0.0036401 | 0.0009123
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016218 | -0.0040657 | 0.01622 | 0.0040666 | 1.5285e-06 | 8.9101e-07 | 0.024447 | 0.024447 | 0.024447 | 0.98719 | -0.24632 | 0.98729 | -0.24435 | 6.7161
1 | 0.014727 | 0.0036919 | -0.014726 | -0.0036912 | 1.232e-06 | 7.0323e-07 | 0.022199 | 0.022199 | 0.022199 | 0.98719 | -0.24632 | 0.9871 | -0.24808 | 6.0985
2 | -0.018588 | -0.0046601 | 0.018593 | 0.0046632 | 5.1516e-06 | 3.0731e-06 | 0.028016 | 0.028016 | 0.028016 | 0.98729 | -0.24435 | 0.98759 | -0.23853 | 7.6967
3 | 0.012426 | 0.0031148 | -0.012424 | -0.0031141 | 1.2993e-06 | 7.0531e-07 | 0.018731 | 0.018732 | 0.018732 | 0.9871 | -0.24808 | 0.98698 | -0.25027 | 5.146
4 | -0.025542 | -0.0064048 | 0.025554 | 0.0064122 | 1.1974e-05 | 7.3873e-06 | 0.038486 | 0.038486 | 0.038486 | 0.98759 | -0.23853 | 0.98809 | -0.2287 | 10.5732
5 | 0.010051 | 0.0025192 | -0.01005 | -0.0025189 | 5.8157e-07 | 2.8589e-07 | 0.015153 | 0.015153 | 0.015153 | 0.98698 | -0.25027 | 0.98692 | -0.25149 | 4.163
6 | -0.03223 | -0.0080852 | 0.032241 | 0.0080919 | 1.0651e-05 | 6.6619e-06 | 0.048539 | 0.048539 | 0.048539 | 0.98809 | -0.2287 | 0.98845 | -0.22177 | 13.335
7 | 0.0085645 | 0.0021466 | -0.0085642 | -0.0021464 | 3.1539e-07 | 1.374e-07 | 0.012913 | 0.012913 | 0.012913 | 0.98692 | -0.25149 | 0.98688 | -0.25226 | 3.5476
8 | 0.035385 | 0.0088783 | -0.035378 | -0.0088741 | 6.6886e-06 | 4.2002e-06 | 0.053272 | 0.053272 | 0.053272 | 0.98845 | -0.22177 | 0.98824 | -0.22574 | 14.6352
9 | -0.067625 | -0.01697 | 0.067739 | 0.017043 | 0.00011401 | 7.2591e-05 | 0.10181 | 0.10181 | 0.10181 | 0.98845 | -0.22177 | 0.99027 | -0.18648 | 27.9701
10 | 0.0070822 | 0.001775 | -0.007082 | -0.0017749 | 2.4555e-07 | 8.3785e-08 | 0.010679 | 0.010679 | 0.010679 | 0.98688 | -0.25226 | 0.98684 | -0.25299 | 2.9337
11 | 0.041646 | 0.010455 | -0.041643 | -0.010454 | 2.5593e-06 | 1.6154e-06 | 0.062525 | 0.062525 | 0.062525 | 0.99121 | -0.16722 | 0.99114 | -0.1685 | 17.1772
12 | -0.044904 | -0.011272 | 0.044943 | 0.011296 | 3.8238e-05 | 2.4183e-05 | 0.067417 | 0.067417 | 0.067417 | 0.99121 | -0.16722 | 0.99213 | -0.14938 | 18.5213
13 | 0.039415 | 0.0098951 | -0.039405 | -0.0098889 | 9.7919e-06 | 6.1707e-06 | 0.05918 | 0.05918 | 0.05918 | 0.99114 | -0.1685 | 0.99087 | -0.17371 | 16.2582
14 | -0.23455 | -0.059731 | 0.23502 | 0.060029 | 0.00046768 | 0.0002988 | 0.35212 | 0.35212 | 0.35212 | 0.99213 | -0.14938 | 0.99429 | -0.10813 | 48.3686
15 | 0.18961 | 0.048434 | -0.18927 | -0.048216 | 0.0003421 | 0.00021836 | 0.28471 | 0.28471 | 0.28471 | 0.99213 | -0.14938 | 0.99018 | -0.18677 | 39.1081
16 | 0.036398 | 0.0091353 | -0.036389 | -0.0091297 | 8.9024e-06 | 5.5952e-06 | 0.054664 | 0.054664 | 0.054664 | 0.99087 | -0.17371 | 0.99061 | -0.17884 | 15.0175
17 | -0.23756 | -0.060666 | 0.2378 | 0.06082 | 0.00024068 | 0.00015377 | 0.35593 | 0.35593 | 0.35593 | 0.99429 | -0.10813 | 0.99539 | -0.08719 | 48.8908
18 | 0.18498 | 0.04714 | -0.18468 | -0.046951 | 0.00029587 | 0.00018883 | 0.27826 | 0.27826 | 0.27826 | 0.99018 | -0.18677 | 0.98845 | -0.21997 | 38.222
19 | 0.032568 | 0.0081722 | -0.032552 | -0.0081622 | 1.5961e-05 | 9.986e-06 | 0.048925 | 0.048925 | 0.048925 | 0.99061 | -0.17884 | 0.99008 | -0.18913 | 13.441
20 | -0.045299 | -0.011382 | 0.045315 | 0.011391 | 1.5138e-05 | 9.5833e-06 | 0.06922 | 0.06922 | 0.06922 | 0.97394 | -0.50223 | 0.9743 | -0.49523 | 19.0165
21 | 0.045299 | 0.011382 | -0.045267 | -0.011361 | 3.2699e-05 | 2.0701e-05 | 0.06922 | 0.06922 | 0.06922 | 0.97394 | -0.50223 | 0.97317 | -0.51736 | 19.0165
22 | -0.051641 | -0.012977 | 0.051666 | 0.012993 | 2.5097e-05 | 1.5928e-05 | 0.078882 | 0.078882 | 0.078882 | 0.9743 | -0.49523 | 0.97481 | -0.48505 | 21.6708
23 | 0.038799 | 0.0097399 | -0.038781 | -0.0097286 | 1.7769e-05 | 1.1205e-05 | 0.059331 | 0.059331 | 0.059331 | 0.97317 | -0.51736 | 0.97269 | -0.52697 | 16.2996
24 | -0.24028 | -0.061441 | 0.24087 | 0.061819 | 0.00059101 | 0.00037761 | 0.35963 | 0.35963 | 0.35963 | 0.99539 | -0.08719 | 0.99807 | -0.036492 | 49.4
25 | 0.18146 | 0.046145 | -0.18131 | -0.046047 | 0.00015423 | 9.8428e-05 | 0.27341 | 0.27341 | 0.27341 | 0.98845 | -0.21997 | 0.98753 | -0.23763 | 37.5567
26 | 0.029305 | 0.0073482 | -0.0293 | -0.0073455 | 4.4268e-06 | 2.7549e-06 | 0.044044 | 0.044044 | 0.044044 | 0.99008 | -0.18913 | 0.98992 | -0.1923 | 12.1
27 | -0.060164 | -0.015122 | 0.060245 | 0.015174 | 8.064e-05 | 5.1292e-05 | 0.091854 | 0.091854 | 0.091854 | 0.97481 | -0.48505 | 0.97624 | -0.45702 | 25.2347
28 | 0.036653 | 0.0091954 | -0.03665 | -0.0091931 | 3.6709e-06 | 2.3107e-06 | 0.056076 | 0.056076 | 0.056076 | 0.97269 | -0.52697 | 0.97258 | -0.52907 | 15.4054
29 | -0.24772 | -0.063535 | 0.24816 | 0.063816 | 0.00043929 | 0.0002807 | 0.36984 | 0.36984 | 0.36984 | 0.99807 | -0.036492 | 1 | 0 | 50.8023
30 | 0.17226 | 0.04378 | -0.1722 | -0.04374 | 6.342e-05 | 4.0461e-05 | 0.25979 | 0.25979 | 0.25979 | 0.98753 | -0.23763 | 0.98713 | -0.24528 | 35.6851
31 | 0.0034795 | 0.00087203 | -0.0034795 | -0.00087204 | 1.2625e-08 | -6.757e-09 | 0.005315 | 0.005315 | 0.005315 | 0.97414 | -0.4985 | 0.97413 | -0.49857 | 1.4602
32 | -0.0059427 | -0.0014894 | 0.0059432 | 0.0014895 | 4.8711e-07 | 1.1549e-07 | 0.0090777 | 0.0090776 | 0.0090777 | 0.97414 | -0.4985 | 0.97422 | -0.49678 | 2.4939
33 | -0.0059432 | -0.0014895 | 0.0059438 | 0.0014896 | 5.7645e-07 | 1.3662e-07 | 0.0090776 | 0.0090775 | 0.0090776 | 0.97422 | -0.49678 | 0.97433 | -0.49474 | 2.4939
34 | -0.0076707 | -0.0019224 | 0.007671 | 0.0019226 | 3.4392e-07 | 1.3687e-07 | 0.011715 | 0.011715 | 0.011715 | 0.97433 | -0.49474 | 0.97437 | -0.4938 | 3.2184
35 | -0.0093738 | -0.0023493 | 0.0093744 | 0.0023496 | 5.193e-07 | 2.4818e-07 | 0.014315 | 0.014315 | 0.014315 | 0.97437 | -0.4938 | 0.97443 | -0.49264 | 3.9328
36 | 0.015203 | 0.003813 | -0.015198 | -0.0038099 | 5.4247e-06 | 3.1368e-06 | 0.023202 | 0.023202 | 0.023202 | 0.97507 | -0.48009 | 0.97469 | -0.48758 | 6.3742
37 | -0.015203 | -0.003813 | 0.015206 | 0.0038148 | 3.1801e-06 | 1.8387e-06 | 0.023202 | 0.023202 | 0.023202 | 0.97507 | -0.48009 | 0.97529 | -0.4757 | 6.3741
38 | 0.013138 | 0.0032936 | -0.013137 | -0.003293 | 1.2072e-06 | 6.7289e-07 | 0.020057 | 0.020057 | 0.020057 | 0.97469 | -0.48758 | 0.97459 | -0.48951 | 5.5103
39 | -0.017644 | -0.0044259 | 0.017647 | 0.0044274 | 2.528e-06 | 1.5018e-06 | 0.026921 | 0.026921 | 0.026921 | 0.97529 | -0.4757 | 0.97544 | -0.4727 | 7.396
40 | -0.0045107 | -0.0011305 | 0.0045109 | 0.0011305 | 2.0746e-07 | -1.3535e-08 | 0.0068757 | 0.0068757 | 0.0068757 | 0.97619 | -0.45799 | 0.97624 | -0.45702 | 1.8889
41 | 0.028025 | 0.0070353 | -0.028014 | -0.0070289 | 1.0244e-05 | 6.3692e-06 | 0.04272 | 0.04272 | 0.04272 | 0.97624 | -0.45702 | 0.97585 | -0.46469 | 11.7363
42 | -0.09278 | -0.02334 | 0.092952 | 0.023449 | 0.00017154 | 0.0001095 | 0.14145 | 0.14145 | 0.14145 | 0.97624 | -0.45702 | 0.97821 | -0.4184 | 38.8599
43 | -0.011241 | -0.0028173 | 0.011242 | 0.0028182 | 1.6772e-06 | 8.8427e-07 | 0.017165 | 0.017165 | 0.017165 | 0.97443 | -0.49264 | 0.97459 | -0.48951 | 4.7157
44 | -0.020695 | -0.0051914 | 0.020696 | 0.005192 | 8.8848e-07 | 5.3896e-07 | 0.031572 | 0.031572 | 0.031572 | 0.97544 | -0.4727 | 0.97549 | -0.4718 | 8.6736
45 | 0.11631 | 0.029465 | -0.11624 | -0.029417 | 7.5851e-05 | 4.8215e-05 | 0.17628 | 0.17628 | 0.17628 | 0.98246 | -0.33566 | 0.98176 | -0.34924 | 24.2144
46 | -0.12026 | -0.030455 | 0.1203 | 0.030476 | 3.3228e-05 | 2.1131e-05 | 0.18226 | 0.18226 | 0.18226 | 0.98246 | -0.33566 | 0.98276 | -0.32991 | 25.0362
47 | 0.11228 | 0.028423 | -0.11227 | -0.028422 | 2.0461e-06 | 1.3e-06 | 0.17027 | 0.17027 | 0.17027 | 0.98176 | -0.34924 | 0.98174 | -0.34962 | 23.3892
48 | -0.12255 | -0.031041 | 0.12277 | 0.031178 | 0.00021494 | 0.00013672 | 0.18568 | 0.18568 | 0.18568 | 0.98276 | -0.32991 | 0.98464 | -0.29346 | 25.5051
49 | 0.10929 | 0.027674 | -0.10926 | -0.027656 | 2.93e-05 | 1.8608e-05 | 0.16575 | 0.16575 | 0.16575 | 0.98174 | -0.34962 | 0.98145 | -0.35521 | 22.7678
50 | -0.16717 | -0.042329 | 0.16745 | 0.042503 | 0.0002737 | 0.00017459 | 0.25279 | 0.25279 | 0.25279 | 0.98464 | -0.29346 | 0.9864 | -0.25942 | 34.7241
51 | 0.044405 | 0.011151 | -0.04438 | -0.011135 | 2.5499e-05 | 1.6127e-05 | 0.067115 | 0.067115 | 0.067115 | 0.98464 | -0.29346 | 0.98402 | -0.3055 | 18.4381
52 | 0.10294 | 0.026072 | -0.10279 | -0.025977 | 0.00014965 | 9.495e-05 | 0.15617 | 0.15617 | 0.15617 | 0.98145 | -0.35521 | 0.97989 | -0.38553 | 21.4517
53 | -0.16989 | -0.043116 | 0.17001 | 0.04319 | 0.00011564 | 7.3769e-05 | 0.25648 | 0.25648 | 0.25648 | 0.9864 | -0.25942 | 0.98713 | -0.24528 | 35.2305
54 | 0.041712 | 0.010466 | -0.041705 | -0.010461 | 7.2578e-06 | 4.5832e-06 | 0.063081 | 0.063081 | 0.063081 | 0.98402 | -0.3055 | 0.98383 | -0.30915 | 17.3298
55 | 0.10279 | 0.025977 | -0.10263 | -0.025874 | 0.00016173 | 0.00010262 | 0.15617 | 0.15617 | 0.15617 | 0.97989 | -0.38553 | 0.97821 | -0.4184 | 21.4517
56 | 0.027819 | 0.0069801 | -0.027805 | -0.0069713 | 1.4185e-05 | 8.8073e-06 | 0.042078 | 0.042078 | 0.042078 | 0.98383 | -0.30915 | 0.98329 | -0.31985 | 11.5599
57 | 0.013886 | 0.0034813 | -0.013883 | -0.0034797 | 2.9598e-06 | 1.6671e-06 | 0.021003 | 0.021003 | 0.021003 | 0.98383 | -0.30915 | 0.9836 | -0.31363 | 5.77
58 | 0.048573 | 0.012216 | -0.048531 | -0.012189 | 4.2376e-05 | 2.6846e-05 | 0.072846 | 0.072846 | 0.072846 | 0.9924 | -0.14553 | 0.99146 | -0.16381 | 20.0126
59 | -0.050648 | -0.012736 | 0.05066 | 0.012743 | 1.1434e-05 | 7.2497e-06 | 0.075957 | 0.075957 | 0.075957 | 0.9924 | -0.14553 | 0.99265 | -0.14081 | 20.8674
60 | 0.043449 | 0.010915 | -0.043426 | -0.010901 | 2.2865e-05 | 1.4449e-05 | 0.065219 | 0.065219 | 0.065219 | 0.99146 | -0.16381 | 0.99089 | -0.17485 | 17.9174
61 | -0.060017 | -0.015088 | 0.060091 | 0.015135 | 7.4544e-05 | 4.739e-05 | 0.089984 | 0.089983 | 0.089984 | 0.99265 | -0.14081 | 0.99399 | -0.11483 | 24.7207
62 | 0.041101 | 0.010318 | -0.041088 | -0.01031 | 1.2546e-05 | 7.9161e-06 | 0.061727 | 0.061727 | 0.061727 | 0.99089 | -0.17485 | 0.99056 | -0.18125 | 16.958
63 | -0.071065 | -0.017886 | 0.071171 | 0.017953 | 0.00010607 | 6.7563e-05 | 0.10641 | 0.10641 | 0.10641 | 0.99399 | -0.11483 | 0.99561 | -0.083649 | 29.2338
64 | 0.038806 | 0.0097381 | -0.038802 | -0.0097351 | 4.6306e-06 | 2.9168e-06 | 0.058299 | 0.058299 | 0.058299 | 0.99056 | -0.18125 | 0.99043 | -0.18375 | 16.0162
65 | -0.18888 | -0.047818 | 0.18899 | 0.04789 | 0.00011241 | 7.1745e-05 | 0.28247 | 0.28247 | 0.28247 | 0.99561 | -0.083649 | 0.99626 | -0.071261 | 38.8003
66 | 0.11771 | 0.029865 | -0.11713 | -0.029495 | 0.00057899 | 0.00036991 | 0.17606 | 0.17606 | 0.17606 | 0.99561 | -0.083649 | 0.99027 | -0.18648 | 48.3669
67 | 0.03381 | 0.008484 | -0.033804 | -0.0084808 | 5.0842e-06 | 3.1863e-06 | 0.050799 | 0.050799 | 0.050799 | 0.99043 | -0.18375 | 0.99027 | -0.1869 | 13.9558
68 | -0.19413 | -0.049178 | 0.19459 | 0.049468 | 0.00045441 | 0.00029007 | 0.29014 | 0.29014 | 0.29014 | 0.99626 | -0.071261 | 0.99881 | -0.022653 | 39.8546
69 | 0.049392 | 0.012453 | -0.049347 | -0.012424 | 4.4946e-05 | 2.8486e-05 | 0.074244 | 0.074244 | 0.074244 | 0.99027 | -0.18648 | 0.98928 | -0.20551 | 20.3968
70 | 0.011339 | 0.002842 | -0.011337 | -0.0028413 | 1.3931e-06 | 7.3134e-07 | 0.017154 | 0.017154 | 0.017154 | 0.9836 | -0.31363 | 0.98347 | -0.3162 | 4.7126
71 | 0.009395 | 0.0023545 | -0.0093944 | -0.0023542 | 6.4654e-07 | 3.0552e-07 | 0.014215 | 0.014215 | 0.014215 | 0.98347 | -0.3162 | 0.9834 | -0.31765 | 3.9052
72 | 0.0075203 | 0.0018845 | -0.0075201 | -0.0018844 | 1.8598e-07 | 7.0433e-08 | 0.011379 | 0.011379 | 0.011379 | 0.9834 | -0.31765 | 0.98337 | -0.31817 | 3.1261
73 | 0.025806 | 0.0064704 | -0.025806 | -0.0064702 | 3.7383e-07 | 2.3096e-07 | 0.039054 | 0.039054 | 0.039054 | 0.98329 | -0.31985 | 0.98327 | -0.32015 | 10.729
74 | 0.0024529 | 0.0006146 | -0.0024528 | -0.00061473 | 7.2052e-08 | -1.3083e-07 | 0.0037116 | 0.0037116 | 0.0037116 | 0.98337 | -0.31817 | 0.98334 | -0.31878 | 1.0197
75 | 0.0050672 | 0.0012698 | -0.0050671 | -0.0012698 | 9.763e-08 | 6.3039e-09 | 0.0076675 | 0.0076676 | 0.0076676 | 0.98337 | -0.31817 | 0.98335 | -0.31857 | 2.1065
76 | 0.023519 | 0.0058971 | -0.023518 | -0.0058965 | 9.1692e-07 | 5.6235e-07 | 0.035593 | 0.035593 | 0.035593 | 0.98327 | -0.32015 | 0.98323 | -0.32097 | 9.7783
77 | 0.0025397 | 0.00063636 | -0.0025396 | -0.00063649 | 7.5138e-08 | -1.2401e-07 | 0.003843 | 0.0038431 | 0.0038431 | 0.98335 | -0.31857 | 0.98332 | -0.31919 | 1.0558
78 | 0.016991 | 0.0042607 | -0.016984 | -0.0042567 | 6.756e-06 | 3.9784e-06 | 0.025715 | 0.025715 | 0.025715 | 0.98323 | -0.32097 | 0.9828 | -0.32932 | 7.0646
79 | 0.045424 | 0.011441 | -0.045374 | -0.011409 | 5.0148e-05 | 3.1728e-05 | 0.068344 | 0.068345 | 0.068345 | 0.98928 | -0.20551 | 0.98809 | -0.22863 | 18.776
80 | 0.040505 | 0.010189 | -0.04048 | -0.010173 | 2.5115e-05 | 1.5843e-05 | 0.061012 | 0.061012 | 0.061012 | 0.98809 | -0.22863 | 0.98742 | -0.24162 | 16.7616
81 | 0.035633 | 0.0089584 | -0.035605 | -0.0089406 | 2.8318e-05 | 1.7789e-05 | 0.053708 | 0.053708 | 0.053708 | 0.98742 | -0.24162 | 0.98657 | -0.25827 | 14.755
82 | 0.033165 | 0.0083291 | -0.033147 | -0.0083182 | 1.7344e-05 | 1.0864e-05 | 0.050028 | 0.050028 | 0.050028 | 0.98657 | -0.25827 | 0.986 | -0.26924 | 13.744
83 | 0.012097 | 0.0030319 | -0.012094 | -0.0030303 | 3.0827e-06 | 1.6555e-06 | 0.018215 | 0.018215 | 0.018215 | 0.98824 | -0.22574 | 0.98797 | -0.23109 | 5.0041
84 | 0.023281 | 0.0058421 | -0.023266 | -0.0058333 | 1.4466e-05 | 8.8565e-06 | 0.035057 | 0.035057 | 0.035057 | 0.98824 | -0.22574 | 0.98757 | -0.23878 | 9.6311
85 | 0.033147 | 0.0083182 | -0.03312 | -0.0083012 | 2.7258e-05 | 1.7075e-05 | 0.050028 | 0.050028 | 0.050028 | 0.986 | -0.26924 | 0.98512 | -0.2865 | 13.744
86 | -0.20604 | -0.052339 | 0.20627 | 0.052483 | 0.00022494 | 0.00014363 | 0.30721 | 0.30721 | 0.30721 | 0.99881 | -0.022653 | 1 | 0 | 42.1988
87 | 0.0040795 | 0.0010216 | -0.0040794 | -0.0010217 | 1.3537e-07 | -3.5816e-08 | 0.006144 | 0.006144 | 0.006144 | 0.98797 | -0.23109 | 0.98793 | -0.23178 | 1.6879
88 | 0.016312 | 0.0040903 | -0.016309 | -0.0040884 | 3.149e-06 | 1.8376e-06 | 0.024578 | 0.024579 | 0.024579 | 0.98757 | -0.23878 | 0.98737 | -0.24283 | 6.7523
89 | -0.005807 | -0.0014554 | 0.0058071 | 0.0014554 | 9.7659e-08 | 1.868e-08 | 0.0087349 | 0.0087349 | 0.0087349 | 0.98924 | -0.20689 | 0.98926 | -0.20653 | 2.3997
90 | -0.012981 | -0.0032532 | 0.012981 | 0.0032537 | 8.2349e-07 | 4.5307e-07 | 0.019525 | 0.019525 | 0.019525 | 0.98926 | -0.20653 | 0.98932 | -0.2052 | 5.364
91 | -0.020896 | -0.0052372 | 0.0209 | 0.0052398 | 4.153e-06 | 2.5139e-06 | 0.031429 | 0.031429 | 0.031429 | 0.98932 | -0.2052 | 0.98954 | -0.20103 | 8.6344
92 | -0.023368 | -0.0058583 | 0.023373 | 0.0058615 | 5.21e-06 | 3.1899e-06 | 0.03514 | 0.03514 | 0.03514 | 0.98954 | -0.20103 | 0.98978 | -0.19635 | 9.6538
93 | -0.026648 | -0.0066821 | 0.026648 | 0.0066823 | 3.9237e-07 | 2.4274e-07 | 0.040063 | 0.040063 | 0.040063 | 0.98978 | -0.19635 | 0.9898 | -0.19604 | 11.0062
94 | 0.011395 | 0.0028559 | -0.011395 | -0.0028557 | 2.9212e-07 | 1.5379e-07 | 0.017252 | 0.017252 | 0.017252 | 0.9828 | -0.32932 | 0.98277 | -0.32986 | 4.7397
95 | 0.005726 | 0.0014351 | -0.0057258 | -0.001435 | 2.6868e-07 | 5.1179e-08 | 0.0086698 | 0.0086698 | 0.0086698 | 0.98277 | -0.32986 | 0.98272 | -0.33084 | 2.3818
96 | -0.020896 | -0.0052371 | 0.020917 | 0.0052499 | 2.1104e-05 | 1.2776e-05 | 0.031447 | 0.031447 | 0.031447 | 0.98878 | -0.21616 | 0.98987 | -0.19498 | 8.6392
97 | 0.010842 | 0.0027173 | -0.010842 | -0.0027173 | 6.6935e-08 | 3.4239e-08 | 0.016316 | 0.016316 | 0.016316 | 0.98878 | -0.21616 | 0.98877 | -0.21629 | 4.4825
98 | 0.0059515 | 0.0014916 | -0.0059514 | -0.0014915 | 1.433e-07 | 3.0343e-08 | 0.0089466 | 0.0089467 | 0.0089467 | 0.98987 | -0.19498 | 0.98984 | -0.19549 | 2.4579
99 | -0.026869 | -0.0067414 | 0.026886 | 0.0067519 | 1.6958e-05 | 1.0496e-05 | 0.040393 | 0.040393 | 0.040393 | 0.98987 | -0.19498 | 0.99055 | -0.18176 | 11.097
100 | 0.0059514 | 0.0014915 | -0.0059506 | -0.0014914 | 8.3238e-07 | 1.7632e-07 | 0.0089467 | 0.0089468 | 0.0089468 | 0.98984 | -0.19549 | 0.98969 | -0.19843 | 2.4579
101 | -0.032515 | -0.0081628 | 0.032544 | 0.0081806 | 2.8525e-05 | 1.7845e-05 | 0.04885 | 0.04885 | 0.04885 | 0.99055 | -0.18176 | 0.9915 | -0.16338 | 13.4202
102 | -0.046155 | -0.011592 | 0.046157 | 0.011593 | 1.4747e-06 | 9.3323e-07 | 0.069277 | 0.069277 | 0.069277 | 0.9915 | -0.16338 | 0.99153 | -0.16271 | 19.0322
103 | -0.053158 | -0.013348 | 0.053202 | 0.013376 | 4.4794e-05 | 2.8426e-05 | 0.079784 | 0.079784 | 0.079784 | 0.99153 | -0.16271 | 0.99244 | -0.14507 | 21.9186
104 | -0.060227 | -0.015137 | 0.060278 | 0.015169 | 5.0871e-05 | 3.2342e-05 | 0.090317 | 0.090317 | 0.090317 | 0.99244 | -0.14507 | 0.99336 | -0.12739 | 24.8123
105 | -0.071618 | -0.018011 | 0.071681 | 0.018051 | 6.2714e-05 | 3.9949e-05 | 0.1073 | 0.1073 | 0.1073 | 0.99336 | -0.12739 | 0.99431 | -0.10907 | 29.4788
106 | -0.082492 | -0.020761 | 0.082601 | 0.02083 | 0.00010855 | 6.9227e-05 | 0.12348 | 0.12348 | 0.12348 | 0.99431 | -0.10907 | 0.99574 | -0.081578 | 33.9238
107 | -0.093932 | -0.02367 | 0.093981 | 0.023701 | 4.9267e-05 | 3.1444e-05 | 0.14042 | 0.14042 | 0.14042 | 0.99574 | -0.081578 | 0.99631 | -0.07062 | 38.5758
108 | -0.028973 | -0.0072651 | 0.028979 | 0.0072687 | 5.7906e-06 | 3.6014e-06 | 0.043559 | 0.043558 | 0.043559 | 0.9898 | -0.19604 | 0.99001 | -0.19185 | 11.9666
109 | 0.024223 | 0.006073 | -0.024223 | -0.0060728 | 4.6924e-07 | 2.8818e-07 | 0.036412 | 0.036412 | 0.036412 | 0.98992 | -0.1923 | 0.9899 | -0.1927 | 10.0034
110 | 0.022304 | 0.0055918 | -0.022302 | -0.0055908 | 1.6665e-06 | 1.0157e-06 | 0.033528 | 0.033528 | 0.033528 | 0.9899 | -0.1927 | 0.98981 | -0.19427 | 9.2109
111 | 0.020465 | 0.0051304 | -0.020463 | -0.0051295 | 1.388e-06 | 8.3808e-07 | 0.030766 | 0.030766 | 0.030766 | 0.98981 | -0.19427 | 0.98974 | -0.19569 | 8.4521
112 | 0.025327 | 0.0063555 | -0.025319 | -0.0063502 | 8.5794e-06 | 5.2993e-06 | 0.038623 | 0.038623 | 0.038623 | 0.97585 | -0.46469 | 0.97549 | -0.4718 | 10.6107
113 | -0.0034843 | -0.00087324 | 0.0034845 | 0.00087313 | 2.0879e-07 | -1.0851e-07 | 0.0053364 | 0.0053363 | 0.0053364 | 0.97156 | -0.54931 | 0.97162 | -0.54805 | 1.4661
114 | -0.0068416 | -0.0017145 | 0.0068416 | 0.0017145 | 1.2898e-08 | 4.3744e-09 | 0.010478 | 0.010478 | 0.010478 | 0.97162 | -0.54805 | 0.97162 | -0.54801 | 2.8785
115 | 0.030814 | 0.0077305 | -0.03081 | -0.0077279 | 4.0813e-06 | 2.5513e-06 | 0.047147 | 0.047147 | 0.047147 | 0.97258 | -0.52907 | 0.97244 | -0.53185 | 12.9525
116 | 0.028991 | 0.0072722 | -0.028986 | -0.0072687 | 5.4966e-06 | 3.4255e-06 | 0.044364 | 0.044365 | 0.044365 | 0.97244 | -0.53185 | 0.97224 | -0.53583 | 12.1881
117 | 0.026889 | 0.0067432 | -0.026884 | -0.00674 | 5.1554e-06 | 3.1988e-06 | 0.041155 | 0.041155 | 0.041155 | 0.97224 | -0.53583 | 0.97203 | -0.53985 | 11.3064
118 | 0.0046224 | 0.0011582 | -0.0046219 | -0.0011583 | 5.3397e-07 | -1.5765e-08 | 0.007051 | 0.0070511 | 0.0070511 | 0.97549 | -0.4718 | 0.97537 | -0.47422 | 1.9371
119 | 0.002312 | 0.00057935 | -0.0023119 | -0.00057943 | 3.7138e-08 | -7.5586e-08 | 0.0035271 | 0.0035272 | 0.0035272 | 0.97537 | -0.47422 | 0.97535 | -0.47456 | 0.969
120 | 0.024255 | 0.0060811 | -0.02425 | -0.006078 | 5.0593e-06 | 3.1167e-06 | 0.03713 | 0.037131 | 0.037131 | 0.97203 | -0.53985 | 0.97181 | -0.54423 | 10.2007
121 | 0.013888 | 0.0034812 | -0.013887 | -0.0034806 | 1.0614e-06 | 6.0175e-07 | 0.021266 | 0.021266 | 0.021266 | 0.97181 | -0.54423 | 0.97173 | -0.54583 | 5.8422
122 | 0.010397 | 0.0026059 | -0.010396 | -0.0026053 | 1.0769e-06 | 5.489e-07 | 0.015921 | 0.015921 | 0.015921 | 0.97173 | -0.54583 | 0.97162 | -0.54801 | 4.3739
123 | 0.098681 | 0.025008 | -0.098347 | -0.024795 | 0.00033361 | 0.00021297 | 0.14694 | 0.14694 | 0.14694 | 1 | 0 | 0.99631 | -0.07062 | 40.367
124 | -0.025338 | -0.0063504 | 0.025339 | 0.006351 | 1.0062e-06 | 6.2066e-07 | 0.038275 | 0.038275 | 0.038275 | 0.98508 | -0.28733 | 0.98512 | -0.2865 | 10.515
125 | 0.022102 | 0.0055394 | -0.022102 | -0.0055393 | 1.9989e-07 | 1.2184e-07 | 0.033387 | 0.033387 | 0.033387 | 0.98508 | -0.28733 | 0.98507 | -0.28752 | 9.1722
126 | -0.0027106 | -0.00067934 | 0.0027107 | 0.00067918 | 1.1378e-07 | -1.5936e-07 | 0.0040867 | 0.0040867 | 0.0040867 | 0.98694 | -0.25104 | 0.98699 | -0.25016 | 1.1227
127 | 0.007249 | 0.0018168 | -0.007248 | -0.0018164 | 9.0993e-07 | 3.2275e-07 | 0.010929 | 0.010929 | 0.010929 | 0.98699 | -0.25016 | 0.98685 | -0.2528 | 3.0024
128 | -0.0099596 | -0.0024959 | 0.00996 | 0.0024961 | 3.8701e-07 | 1.8918e-07 | 0.015015 | 0.015015 | 0.015015 | 0.98699 | -0.25016 | 0.98703 | -0.24934 | 4.1251
129 | -0.0034511 | -0.00086494 | 0.0034514 | 0.00086478 | 2.4704e-07 | -1.5587e-07 | 0.0051908 | 0.0051907 | 0.0051908 | 0.98932 | -0.20394 | 0.98939 | -0.20243 | 1.426
130 | -0.0053788 | -0.0013478 | 0.0053789 | 0.0013479 | 1.2195e-07 | 1.4226e-08 | 0.0080895 | 0.0080895 | 0.0080895 | 0.98939 | -0.20243 | 0.98942 | -0.20196 | 2.2224
131 | -0.0093652 | -0.0023469 | 0.009366 | 0.0023473 | 8.5032e-07 | 3.9739e-07 | 0.014085 | 0.014084 | 0.014085 | 0.98942 | -0.20196 | 0.98952 | -0.20005 | 3.8694
132 | -0.013011 | -0.0032609 | 0.013013 | 0.0032618 | 1.5895e-06 | 8.7504e-07 | 0.019566 | 0.019566 | 0.019566 | 0.98952 | -0.20005 | 0.98965 | -0.19749 | 5.3753
133 | -0.01692 | -0.004241 | 0.016921 | 0.0042418 | 1.4456e-06 | 8.4865e-07 | 0.025441 | 0.025441 | 0.025441 | 0.98965 | -0.19749 | 0.98974 | -0.19569 | 6.9892
134 | 0.031256 | 0.0078422 | -0.031249 | -0.0078376 | 7.3693e-06 | 4.6018e-06 | 0.04697 | 0.04697 | 0.04697 | 0.99027 | -0.1869 | 0.99001 | -0.19185 | 12.9039
135 | 0.0036402 | 0.00091224 | -0.0036401 | -0.0009123 | 1.2197e-07 | -5.9867e-08 | 0.0054889 | 0.0054889 | 0.0054889 | 0.98685 | -0.2528 | 0.98682 | -0.2535 | 1.5079
136 | -0.012673 | -0.0031762 | 0.012677 | 0.0031783 | 3.9359e-06 | 2.1513e-06 | 0.019106 | 0.019106 | 0.019106 | 0.98703 | -0.24934 | 0.98737 | -0.24283 | 5.2489
137 | -0.004078 | -0.001022 | 0.0040785 | 0.0010219 | 5.0058e-07 | -1.321e-07 | 0.0061445 | 0.0061443 | 0.0061445 | 0.98757 | -0.23882 | 0.98771 | -0.23624 | 1.688
138 | -0.0040785 | -0.0010219 | 0.0040794 | 0.0010217 | 8.6552e-07 | -2.2874e-07 | 0.0061443 | 0.006144 | 0.0061443 | 0.98771 | -0.23624 | 0.98793 | -0.23178 | 1.688

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.55476 | 0.14131

## res_load
| p_mw | q_mvar
0 | 0.0014914 | 0.00037378
1 | 0.0023683 | 0.00059354
2 | 0.0023 | 0.00057643
3 | 0.0069492 | 0.0017416
4 | 0.0023734 | 0.00059483
5 | 0.0066756 | 0.0016731
6 | 0.0014858 | 0.00037239
7 | 0.001482 | 0.00037143
8 | 0.0032589 | 0.00081676
9 | 0.0022284 | 0.00055848
10 | 0.0030072 | 0.00075368
11 | 0.0025404 | 0.00063669
12 | 0.0042926 | 0.0010758
13 | 0.0038203 | 0.00095747
14 | 0.0063261 | 0.0015855
15 | 0.0064678 | 0.001621
16 | 0.0024797 | 0.00062148
17 | 0.0032173 | 0.00080633
18 | 0.0032478 | 0.00081398
19 | 0.0084986 | 0.0021299
20 | 0.0021278 | 0.00053327
21 | 0.0068477 | 0.0017162
22 | 0.0090429 | 0.0022664
23 | 0.0024633 | 0.00061735
24 | 0.0034795 | 0.00087204
25 | 0.0017269 | 0.0004328
26 | 0.0017028 | 0.00042677
27 | 0.0020598 | 0.00051623
28 | 0.0024379 | 0.000611
29 | 0.0045107 | 0.0011305
30 | 0.0018663 | 0.00046775
31 | 0.0018943 | 0.00047476
32 | 0.0030486 | 0.00076406
33 | 0.0039504 | 0.00099005
34 | 0.0039636 | 0.00099338
35 | 0.0022544 | 0.000565
36 | 0.0029846 | 0.00074801
37 | 0.0063199 | 0.0015839
38 | 0.0024439 | 0.0006125
39 | 0.0026677 | 0.0006686
40 | 0.0021954 | 0.00055022
41 | 0.0020754 | 0.00052013
42 | 0.0050814 | 0.0012735
43 | 0.0093568 | 0.002345
44 | 0.0023257 | 0.00058287
45 | 0.010974 | 0.0027503
46 | 0.002282 | 0.00057193
47 | 0.004992 | 0.0012511
48 | 0.0051387 | 0.0012879
49 | 0.007082 | 0.0017749
50 | 0.0025443 | 0.00063766
51 | 0.0019424 | 0.00048681
52 | 0.0018741 | 0.00046969
53 | 0.0019986 | 0.00050089
54 | 0.0022868 | 0.00057313
55 | 0.0024528 | 0.00061473
56 | 0.0025274 | 0.00063343
57 | 0.0065269 | 0.0016358
58 | 0.0039225 | 0.00098308
59 | 0.004869 | 0.0012203
60 | 0.004847 | 0.0012148
61 | 0.00244 | 0.00061152
62 | 0.011456 | 0.002871
63 | 0.0080146 | 0.0020086
64 | 0.0069546 | 0.001743
65 | 0.0096759 | 0.002425
66 | 0.005807 | 0.0014554
67 | 0.0071735 | 0.0017979
68 | 0.0079145 | 0.0019836
69 | 0.0024678 | 0.0006185
70 | 0.0032744 | 0.00082065
71 | 0.0025396 | 0.00063649
72 | 0.0055895 | 0.0014009
73 | 0.0056685 | 0.0014207
74 | 0.010054 | 0.0025198
75 | 0.010842 | 0.0027173
76 | 0.0056295 | 0.0014109
77 | 0.0059506 | 0.0014914
78 | 0.013611 | 0.0034114
79 | 0.007001 | 0.0017546
80 | 0.007025 | 0.0017606
81 | 0.01134 | 0.002842
82 | 0.010812 | 0.0027096
83 | 0.011331 | 0.0028399
84 | 0.0023254 | 0.00058279
85 | 0.005077 | 0.0012724
86 | 0.0019189 | 0.00048092
87 | 0.0018373 | 0.00046046
88 | 0.002687 | 0.00067343
89 | 0.0034843 | 0.00087324
90 | 0.0033571 | 0.00084137
91 | 0.0058357 | 0.0014626
92 | 0.0018186 | 0.00045578
93 | 0.0020969 | 0.00052554
94 | 0.0023099 | 0.00057891
95 | 0.0026291 | 0.00065892
96 | 0.010361 | 0.0025968
97 | 0.0034902 | 0.00087473
98 | 0.0035543 | 0.0008908
99 | 0.0032358 | 0.00081096
100 | 0.0077812 | 0.0019501
101 | 0.022102 | 0.0055393
102 | 0.0027106 | 0.00067934
103 | 0.0034511 | 0.00086494
104 | 0.0019274 | 0.00048306
105 | 0.0039863 | 0.00099905
106 | 0.0036453 | 0.00091359
107 | 0.003907 | 0.00097919
108 | 0.0043656 | 0.0010941
109 | 0.0057258 | 0.001435
110 | 0.0023119 | 0.00057943
111 | 0.0025482 | 0.00063865
112 | 0.0022698 | 0.00056886
113 | 0.003542 | 0.00088772
114 | 0.0036078 | 0.0009042
115 | 0.0027134 | 0.00068003
116 | 0.004078 | 0.001022
117 | 0.0036314 | 0.00091011
118 | 0.0036401 | 0.0009123

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1