## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-47_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-47_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2581-47_0_4_node_15 | 0.4 | n |  | TRUE
3 | bus_LV_2581-47_0_4_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_2581-47_0_4_node_55 | 0.4 | n |  | TRUE
5 | bus_LV_2581-47_0_4_node_56 | 0.4 | n |  | TRUE
6 | bus_LV_2581-47_0_4_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_2581-47_0_4_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_2581-47_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2581-47_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2581-47_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2581-47_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2581-47_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2581-47_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2581-47_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_2581-47_0_4_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_2581-47_0_4_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_2581-47_0_4_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_2581-47_0_4_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_2581-47_0_4_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_2581-47_0_4_node_54 | 0.4 | n |  | TRUE
21 | bus_LV_2581-47_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2581-47_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2581-47_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2581-47_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2581-47_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2581-47_0_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2581-47_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_2581-47_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2581-47_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2581-47_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2581-47_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2581-47_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2581-47_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2581-47_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2581-47_0_4_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_2581-47_0_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_2581-47_0_4_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_2581-47_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2581-47_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2581-47_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_2581-47_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_2581-47_0_4_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_2581-47_0_4_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_2581-47_0_4_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_2581-47_0_4_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_2581-47_0_4_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_2581-47_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_2581-47_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_2581-47_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2581-47_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2581-47_0_4_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2581-47_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2581-47_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_2581-47_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_2581-47_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2581-47_0_4_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_2581-47_0_4_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_2581-47_0_4_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_2581-47_0_4_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_2581-47_0_4_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_2581-47_0_4_node_63 | 0.4 | n |  | TRUE
62 | bus_MV_523_0_node_161 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-47_0_4_load_0 | 0 | 0.013133 | 0.0032914 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-47_0_4_load_15 | 2 | 0.010394 | 0.0026049 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-47_0_4_load_16 | 3 | 0.0095655 | 0.0023973 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-47_0_4_load_55 | 4 | 0.059795 | 0.014986 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-47_0_4_load_42 | 6 | 0.013398 | 0.0033579 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-47_0_4_load_35 | 7 | 0.0094418 | 0.0023663 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-47_0_4_load_4 | 8 | 0.0056561 | 0.0014176 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-47_0_4_load_5 | 9 | 0.0063938 | 0.0016024 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-47_0_4_load_6 | 10 | 0.010317 | 0.0025857 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-47_0_4_load_7 | 11 | 0.0058712 | 0.0014715 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-47_0_4_load_8 | 12 | 0.020184 | 0.0050586 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-47_0_4_load_31 | 14 | 0.0058182 | 0.0014582 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-47_0_4_load_53 | 16 | 0.015472 | 0.0038778 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-47_0_4_load_43 | 17 | 0.0053671 | 0.0013451 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-47_0_4_load_36 | 18 | 0.078325 | 0.01963 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-47_0_4_load_32 | 19 | 0.0094627 | 0.0023716 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-47_0_4_load_54 | 20 | 0.015445 | 0.003871 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-47_0_4_load_10 | 21 | 0.020918 | 0.0052425 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-47_0_4_load_11 | 22 | 0.0027806 | 0.0006969 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-47_0_4_load_12 | 23 | 0.0028153 | 0.00070558 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-47_0_4_load_13 | 24 | 0.014979 | 0.0037542 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-47_0_4_load_14 | 25 | 0.0020053 | 0.00050258 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-47_0_4_load_30 | 26 | 0.0028142 | 0.00070531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2581-47_0_4_load_29 | 27 | 0.005101 | 0.0012784 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2581-47_0_4_load_24 | 29 | 0.0018862 | 0.00047271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2581-47_0_4_load_18 | 30 | 0.009439 | 0.0023656 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2581-47_0_4_load_27 | 31 | 0.0095396 | 0.0023909 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2581-47_0_4_load_19 | 32 | 0.0093239 | 0.0023368 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2581-47_0_4_load_26 | 34 | 0.0093952 | 0.0023547 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2581-47_0_4_load_57 | 37 | 0.0078697 | 0.0019723 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2581-47_0_4_load_21 | 38 | 0.00071655 | 0.00017958 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2581-47_0_4_load_22 | 39 | 0.00071706 | 0.00017971 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2581-47_0_4_load_23 | 40 | 0.00076288 | 0.0001912 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2581-47_0_4_load_46 | 42 | 0.0007029 | 0.00017616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2581-47_0_4_load_47 | 43 | 0.0073849 | 0.0018508 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2581-47_0_4_load_49 | 45 | 0.002811 | 0.00070451 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2581-47_0_4_load_64 | 46 | 0.00080627 | 0.00020207 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2581-47_0_4_load_33 | 48 | 0.0093836 | 0.0023518 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2581-47_0_4_load_37 | 49 | 0.0075504 | 0.0018923 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2581-47_0_4_load_38 | 50 | 0.0012572 | 0.0003151 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2581-47_0_4_load_41 | 53 | 0.0034663 | 0.00086874 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2581-47_0_4_load_50 | 55 | 0.0032112 | 0.00080481 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2581-47_0_4_load_51 | 56 | 0.0014055 | 0.00035225 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2581-47_0_4_load_58 | 57 | 0.0017516 | 0.00043899 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2581-47_0_4_load_61 | 59 | 0.0018403 | 0.00046123 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2581-47_0_4_load_63 | 61 | 0.0042614 | 0.001068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-47_0_4_line_0 |  | 0 | 1 | 0.010795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2581-47_0_4_line_1 |  | 1 | 2 | 0.040831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2581-47_0_4_line_2 |  | 2 | 3 | 0.018037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2581-47_0_4_line_3 |  | 3 | 30 | 0.012598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2581-47_0_4_line_4 |  | 4 | 5 | 0.025258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-47_0_4_line_5 |  | 5 | 20 | 0.083631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2581-47_0_4_line_6 |  | 6 | 7 | 0.018088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2581-47_0_4_line_7 |  | 7 | 48 | 0.017354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2581-47_0_4_line_8 |  | 8 | 9 | 0.0060757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2581-47_0_4_line_9 |  | 8 | 10 | 0.0023348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2581-47_0_4_line_10 |  | 9 | 11 | 0.034824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2581-47_0_4_line_11 |  | 10 | 12 | 0.027396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2581-47_0_4_line_12 |  | 10 | 13 | 0.029687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2581-47_0_4_line_13 |  | 11 | 14 | 0.010099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2581-47_0_4_line_14 |  | 13 | 15 | 0.034472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2581-47_0_4_line_15 |  | 13 | 16 | 0.025655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2581-47_0_4_line_16 |  | 14 | 17 | 0.013776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2581-47_0_4_line_17 |  | 15 | 18 | 0.011021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2581-47_0_4_line_18 |  | 15 | 19 | 0.024411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2581-47_0_4_line_19 |  | 16 | 20 | 0.026183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2581-47_0_4_line_20 |  | 17 | 47 | 0.045532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2581-47_0_4_line_21 |  | 18 | 36 | 0.0050264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2581-47_0_4_line_22 |  | 19 | 48 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-47_0_4_line_23 |  | 21 | 22 | 0.015709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2581-47_0_4_line_24 |  | 21 | 23 | 0.0030084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2581-47_0_4_line_25 |  | 22 | 24 | 0.035639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2581-47_0_4_line_26 |  | 23 | 25 | 0.018515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2581-47_0_4_line_27 |  | 25 | 26 | 0.0012291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2581-47_0_4_line_28 |  | 26 | 29 | 0.0044348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2581-47_0_4_line_29 |  | 27 | 28 | 0.0138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2581-47_0_4_line_30 |  | 28 | 33 | 0.034496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2581-47_0_4_line_31 |  | 28 | 35 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2581-47_0_4_line_32 |  | 29 | 39 | 0.0059501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2581-47_0_4_line_33 |  | 30 | 31 | 0.0048537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2581-47_0_4_line_34 |  | 31 | 34 | 0.017309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2581-47_0_4_line_35 |  | 32 | 33 | 0.026588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2581-47_0_4_line_36 |  | 32 | 34 | 0.017173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2581-47_0_4_line_37 |  | 33 | 36 | 0.016282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2581-47_0_4_line_38 |  | 35 | 37 | 0.018309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2581-47_0_4_line_39 |  | 37 | 57 | 0.012676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2581-47_0_4_line_40 |  | 38 | 39 | 0.0054569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2581-47_0_4_line_41 |  | 38 | 40 | 0.0056473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2581-47_0_4_line_42 |  | 40 | 41 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2581-47_0_4_line_43 |  | 41 | 42 | 0.034211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2581-47_0_4_line_44 |  | 41 | 43 | 0.042091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2581-47_0_4_line_45 |  | 41 | 44 | 0.15872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2581-47_0_4_line_46 |  | 42 | 45 | 0.01507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2581-47_0_4_line_47 |  | 44 | 46 | 0.06303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2581-47_0_4_line_48 |  | 45 | 55 | 0.010072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2581-47_0_4_line_49 |  | 47 | 56 | 0.044659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2581-47_0_4_line_50 |  | 49 | 50 | 0.005676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2581-47_0_4_line_51 |  | 49 | 51 | 0.014152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2581-47_0_4_line_52 |  | 50 | 52 | 0.011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2581-47_0_4_line_53 |  | 51 | 53 | 0.0073223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2581-47_0_4_line_54 |  | 52 | 54 | 0.003267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2581-47_0_4_line_55 |  | 53 | 55 | 0.012587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2581-47_0_4_line_56 |  | 54 | 56 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2581-47_0_4_line_57 |  | 57 | 58 | 0.0063455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2581-47_0_4_line_58 |  | 58 | 59 | 0.0091667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2581-47_0_4_line_59 |  | 59 | 60 | 0.028374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2581-47_0_4_line_60 |  | 60 | 61 | 0.01241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-47_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 62 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2636258.6894 | 1243838.2167 | 2636248.5445 | 1243841.9073
1 | 2636258.6531 | 1243797.386 | 2636258.6894 | 1243838.2167
2 | 2636259.9674 | 1243779.3966 | 2636258.6531 | 1243797.386
3 | 2636260.8853 | 1243766.8322 | 2636259.9674 | 1243779.3966
4 | 2636149.3403 | 1243855.5726 | 2636167.9409 | 1243872.6603
5 | 2636183.4576 | 1243779.2172 | 2636149.3403 | 1243855.5726
6 | 2636222.5595 | 1243785.1909 | 2636220.8257 | 1243803.1959
7 | 2636224.2229 | 1243767.9169 | 2636222.5595 | 1243785.1909
8 | 2636162.3052 | 1243722.6652 | 2636158.0998 | 1243721.4057 | 2636156.4918 | 1243720.8998
9 | 2636164.5418 | 1243723.3351 | 2636162.3052 | 1243722.6652
10 | 2636156.4918 | 1243720.8998 | 2636149.1994 | 1243718.6053 | 2636130.6027 | 1243709.6975 | 2636124.7175 | 1243706.8009
11 | 2636164.5418 | 1243723.3351 | 2636158.3501 | 1243750.0221
12 | 2636193.7795 | 1243728.4164 | 2636189.7976 | 1243728.3032 | 2636178.803 | 1243726.902 | 2636167.0989 | 1243724.1067 | 2636164.5418 | 1243723.3351
13 | 2636115.6565 | 1243702.3411 | 2636124.7175 | 1243706.8009
14 | 2636228.2301 | 1243726.3028 | 2636223.201 | 1243726.9059 | 2636211.1993 | 1243728.3003 | 2636200.5042 | 1243728.602 | 2636193.7795 | 1243728.4164
15 | 2636193.7795 | 1243728.4164 | 2636188.6711 | 1243753.5581
16 | 2636115.6565 | 1243702.3411 | 2636103.2962 | 1243696.2574
17 | 2636228.2301 | 1243726.3028 | 2636234.1493 | 1243724.7379 | 2636238.8388 | 1243723.3234
18 | 2636228.2301 | 1243726.3028 | 2636225.8903 | 1243750.6012
19 | 2636188.6711 | 1243753.5581 | 2636183.4576 | 1243779.2172
20 | 2636062.4447 | 1243676.1505 | 2636103.2962 | 1243696.2574
21 | 2636243.651 | 1243721.8718 | 2636238.8388 | 1243723.3234
22 | 2636225.8903 | 1243750.6012 | 2636224.2229 | 1243767.9169
23 | 2636220.5229 | 1243614.5481 | 2636218.2033 | 1243612.1011 | 2636209.3075 | 1243603.5521
24 | 2636207.1384 | 1243601.4675 | 2636209.3075 | 1243603.5521
25 | 2636220.5229 | 1243614.5481 | 2636232.8006 | 1243627.5001 | 2636244.7507 | 1243640.6816
26 | 2636193.2175 | 1243589.285 | 2636198.5998 | 1243593.503 | 2636205.1979 | 1243599.6027 | 2636207.1384 | 1243601.4675
27 | 2636193.2175 | 1243589.285 | 2636192.2501 | 1243588.5268
28 | 2636188.7595 | 1243585.7913 | 2636192.2501 | 1243588.5268
29 | 2636291.3689 | 1243704.185 | 2636282.1371 | 1243693.9271
30 | 2636291.3689 | 1243704.185 | 2636286.937 | 1243705.9813 | 2636273.0435 | 1243711.5 | 2636267.8771 | 1243713.5476 | 2636259.1517 | 1243716.752
31 | 2636308.1913 | 1243697.9838 | 2636296.0859 | 1243702.7351 | 2636291.3689 | 1243704.185
32 | 2636188.7595 | 1243585.7913 | 2636186.6033 | 1243584.1016 | 2636184.025 | 1243582.1883
33 | 2636260.8853 | 1243766.8322 | 2636261.239 | 1243761.9914
34 | 2636262.5002 | 1243744.7281 | 2636261.239 | 1243761.9914
35 | 2636277.0094 | 1243736.496 | 2636259.1517 | 1243716.752
36 | 2636277.0094 | 1243736.496 | 2636262.5768 | 1243743.6792 | 2636262.5002 | 1243744.7281
37 | 2636259.1517 | 1243716.752 | 2636250.2686 | 1243719.7886 | 2636243.651 | 1243721.8718
38 | 2636308.1913 | 1243697.9838 | 2636307.1479 | 1243694.3528 | 2636306.5711 | 1243691.0583 | 2636306.3283 | 1243687.499 | 2636306.7663 | 1243683.8437 | 2636308.642 | 1243681.1201 | 2636309.0561 | 1243680.6443
39 | 2636309.0561 | 1243680.6443 | 2636317.3783 | 1243671.0823
40 | 2636184.025 | 1243582.1883 | 2636179.6429 | 1243578.9364
41 | 2636175.1078 | 1243575.5711 | 2636179.6429 | 1243578.9364
42 | 2636145.4989 | 1243555.5996 | 2636162.902 | 1243567.0017 | 2636173.3999 | 1243574.3037 | 2636175.1078 | 1243575.5711
43 | 2636145.4989 | 1243555.5996 | 2636140.8995 | 1243563.7991 | 2636131.1985 | 1243579.5058 | 2636127.9229 | 1243584.9437
44 | 2636145.4989 | 1243555.5996 | 2636141.4008 | 1243552.2058 | 2636136.1038 | 1243549.6052 | 2636128.4992 | 1243546.2012 | 2636107.4871 | 1243538.0518
45 | 2636145.4989 | 1243555.5996 | 2636145.403 | 1243551.4963 | 2636144.6974 | 1243529.6001 | 2636143.8011 | 1243508.0029 | 2636144.6988 | 1243490.8973 | 2636146.4031 | 1243476.5984 | 2636151.4996 | 1243453.8036 | 2636153.2007 | 1243444.9971 | 2636153.5014 | 1243434.103 | 2636151.2039 | 1243412.9976 | 2636150.9029 | 1243397.8972
46 | 2636119.7385 | 1243597.594 | 2636125.9003 | 1243588.3015 | 2636127.9229 | 1243584.9437
47 | 2636150.9029 | 1243397.8972 | 2636092.2022 | 1243374.5029
48 | 2636119.7385 | 1243597.594 | 2636119.6001 | 1243597.8027 | 2636113.2011 | 1243605.2536
49 | 2636062.4447 | 1243676.1505 | 2636065.1032 | 1243670.1962 | 2636063.6033 | 1243669.5422 | 2636058.2971 | 1243667.2196 | 2636055.5518 | 1243666.3134 | 2636054.1907 | 1243665.2045 | 2636054.1031 | 1243663.4472 | 2636055.1611 | 1243662.2195 | 2636056.3948 | 1243661.9046 | 2636058.6042 | 1243662.6963 | 2636066.9043 | 1243667.3052 | 2636068.0001 | 1243667.3008 | 2636069.1026 | 1243666.1956 | 2636072.4948 | 1243660.1739
50 | 2636091.0442 | 1243631.1176 | 2636087.2318 | 1243635.3228
51 | 2636100.3726 | 1243620.4782 | 2636096.4978 | 1243625.1021 | 2636091.0442 | 1243631.1176
52 | 2636079.2956 | 1243644.0766 | 2636087.2318 | 1243635.3228
53 | 2636100.3726 | 1243620.4782 | 2636105.0806 | 1243614.8701
54 | 2636077.0969 | 1243646.4981 | 2636079.2956 | 1243644.0766
55 | 2636105.0806 | 1243614.8701 | 2636111.0984 | 1243607.7018 | 2636113.2011 | 1243605.2536
56 | 2636077.0969 | 1243646.4981 | 2636077.6995 | 1243649.3036 | 2636077.4032 | 1243650.8027 | 2636076.1998 | 1243653.5972 | 2636072.4948 | 1243660.1739
57 | 2636321.6248 | 1243666.3677 | 2636318.6044 | 1243669.6736 | 2636317.3783 | 1243671.0823
58 | 2636321.6248 | 1243666.3677 | 2636327.6129 | 1243659.4271
59 | 2636346.1481 | 1243637.9437 | 2636327.6129 | 1243659.4271
60 | 2636346.1481 | 1243637.9437 | 2636335.1119 | 1243632.2058

## bus_geodata
| x | y | coords
0 | 2636248.5445 | 1243841.9073
1 | 2636258.6894 | 1243838.2167
2 | 2636258.6531 | 1243797.386
3 | 2636259.9674 | 1243779.3966
4 | 2636167.9409 | 1243872.6603
5 | 2636149.3403 | 1243855.5726
6 | 2636220.8257 | 1243803.1959
7 | 2636222.5595 | 1243785.1909
8 | 2636162.3052 | 1243722.6652
9 | 2636156.4918 | 1243720.8998
10 | 2636164.5418 | 1243723.3351
11 | 2636124.7175 | 1243706.8009
12 | 2636158.3501 | 1243750.0221
13 | 2636193.7795 | 1243728.4164
14 | 2636115.6565 | 1243702.3411
15 | 2636228.2301 | 1243726.3028
16 | 2636188.6711 | 1243753.5581
17 | 2636103.2962 | 1243696.2574
18 | 2636238.8388 | 1243723.3234
19 | 2636225.8903 | 1243750.6012
20 | 2636183.4576 | 1243779.2172
21 | 2636209.3075 | 1243603.5521
22 | 2636220.5229 | 1243614.5481
23 | 2636207.1384 | 1243601.4675
24 | 2636244.7507 | 1243640.6816
25 | 2636193.2175 | 1243589.285
26 | 2636192.2501 | 1243588.5268
27 | 2636282.1371 | 1243693.9271
28 | 2636291.3689 | 1243704.185
29 | 2636188.7595 | 1243585.7913
30 | 2636260.8853 | 1243766.8322
31 | 2636261.239 | 1243761.9914
32 | 2636277.0094 | 1243736.496
33 | 2636259.1517 | 1243716.752
34 | 2636262.5002 | 1243744.7281
35 | 2636308.1913 | 1243697.9838
36 | 2636243.651 | 1243721.8718
37 | 2636309.0561 | 1243680.6443
38 | 2636179.6429 | 1243578.9364
39 | 2636184.025 | 1243582.1883
40 | 2636175.1078 | 1243575.5711
41 | 2636145.4989 | 1243555.5996
42 | 2636127.9229 | 1243584.9437
43 | 2636107.4871 | 1243538.0518
44 | 2636150.9029 | 1243397.8972
45 | 2636119.7385 | 1243597.594
46 | 2636092.2022 | 1243374.5029
47 | 2636062.4447 | 1243676.1505
48 | 2636224.2229 | 1243767.9169
49 | 2636091.0442 | 1243631.1176
50 | 2636087.2318 | 1243635.3228
51 | 2636100.3726 | 1243620.4782
52 | 2636079.2956 | 1243644.0766
53 | 2636105.0806 | 1243614.8701
54 | 2636077.0969 | 1243646.4981
55 | 2636113.2011 | 1243605.2536
56 | 2636072.4948 | 1243660.1739
57 | 2636317.3783 | 1243671.0823
58 | 2636321.6248 | 1243666.3677
59 | 2636327.6129 | 1243659.4271
60 | 2636346.1481 | 1243637.9437
61 | 2636335.1119 | 1243632.2058
62 | 2636164.5418 | 1243723.3351

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98893 | -0.21328 | 0.013133 | 0.0032914
1 | 0.98906 | -0.21076 | 0 | 0
2 | 0.98955 | -0.20121 | 0.010394 | 0.0026049
3 | 0.98994 | -0.19366 | 0.0095655 | 0.0023973
4 | 0.99011 | -0.19027 | 0.059795 | 0.014986
5 | 0.99149 | -0.16346 | 0 | 0
6 | 0.99465 | -0.10277 | 0.013398 | 0.0033579
7 | 0.99487 | -0.098501 | 0.0094418 | 0.0023663
8 | 0.99597 | -0.076435 | 0.0056561 | 0.0014176
9 | 0.99539 | -0.08738 | 0.0063938 | 0.0016024
10 | 0.9962 | -0.072 | 0.010317 | 0.0025857
11 | 0.99228 | -0.14642 | 0.0058712 | 0.0014715
12 | 0.9957 | -0.081717 | 0.020184 | 0.0050586
13 | 1 | 0 | -0.44666 | -0.1131
14 | 0.99143 | -0.16255 | 0.0058182 | 0.0014582
15 | 0.99667 | -0.063792 | 0 | 0
16 | 0.99787 | -0.040652 | 0.015472 | 0.0038778
17 | 0.99035 | -0.18319 | 0.0053671 | 0.0013451
18 | 0.99581 | -0.080238 | 0.078325 | 0.01963
19 | 0.99574 | -0.081664 | 0.0094627 | 0.0023716
20 | 0.99607 | -0.075199 | 0.015445 | 0.003871
21 | 0.97219 | -0.53608 | 0.020918 | 0.0052425
22 | 0.97193 | -0.54123 | 0.0027806 | 0.0006969
23 | 0.9723 | -0.53394 | 0.0028153 | 0.00070558
24 | 0.97143 | -0.55109 | 0.014979 | 0.0037542
25 | 0.97301 | -0.51978 | 0.0020053 | 0.00050258
26 | 0.97306 | -0.5188 | 0.0028142 | 0.00070531
27 | 0.99331 | -0.12854 | 0.005101 | 0.0012784
28 | 0.99337 | -0.1273 | 0 | 0
29 | 0.97325 | -0.51502 | 0.0018862 | 0.00047271
30 | 0.99032 | -0.18625 | 0.009439 | 0.0023656
31 | 0.99051 | -0.18258 | 0.0095396 | 0.0023909
32 | 0.9923 | -0.14787 | 0.0093239 | 0.0023368
33 | 0.99403 | -0.11461 | 0 | 0
34 | 0.99134 | -0.16658 | 0.0093952 | 0.0023547
35 | 0.99312 | -0.13227 | 0 | 0
36 | 0.99539 | -0.088336 | 0 | 0
37 | 0.99285 | -0.13736 | 0.0078697 | 0.0019723
38 | 0.97377 | -0.50484 | 0.00071655 | 0.00017958
39 | 0.97352 | -0.50974 | 0.00071706 | 0.00017971
40 | 0.97403 | -0.49968 | 0.00076288 | 0.0001912
41 | 0.97571 | -0.46667 | 0 | 0
42 | 0.97758 | -0.43004 | 0.0007029 | 0.00017616
43 | 0.97542 | -0.47236 | 0.0073849 | 0.0018508
44 | 0.97559 | -0.46902 | 0 | 0
45 | 0.97841 | -0.41375 | 0.002811 | 0.00070451
46 | 0.97555 | -0.46996 | 0.00080627 | 0.00020207
47 | 0.987 | -0.24733 | 0 | 0
48 | 0.99523 | -0.091523 | 0.0093836 | 0.0023518
49 | 0.98114 | -0.36064 | 0.0075504 | 0.0018923
50 | 0.98154 | -0.3528 | 0.0012572 | 0.0003151
51 | 0.98023 | -0.37828 | 0 | 0
52 | 0.9824 | -0.33622 | 0 | 0
53 | 0.97976 | -0.38743 | 0.0034663 | 0.00086874
54 | 0.98263 | -0.33165 | 0 | 0
55 | 0.979 | -0.40237 | 0.0032112 | 0.00080481
56 | 0.98372 | -0.31067 | 0.0014055 | 0.00035225
57 | 0.99276 | -0.13912 | 0.0017516 | 0.00043899
58 | 0.99273 | -0.1398 | 0 | 0
59 | 0.99268 | -0.14079 | 0.0018403 | 0.00046123
60 | 0.99256 | -0.14293 | 0 | 0
61 | 0.99252 | -0.14387 | 0.0042614 | 0.001068
62 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013133 | -0.0032914 | 0.013134 | 0.0032922 | 1.5807e-06 | 8.7314e-07 | 0.01976 | 0.01976 | 0.01976 | 0.98893 | -0.21328 | 0.98906 | -0.21076 | 5.4287
1 | -0.013134 | -0.0032922 | 0.01314 | 0.0032955 | 5.9786e-06 | 3.302e-06 | 0.01976 | 0.01976 | 0.01976 | 0.98906 | -0.21076 | 0.98955 | -0.20121 | 5.4287
2 | -0.023534 | -0.0059004 | 0.023542 | 0.0059056 | 8.4713e-06 | 5.1898e-06 | 0.035389 | 0.035389 | 0.035389 | 0.98955 | -0.20121 | 0.98994 | -0.19366 | 9.7224
3 | -0.033108 | -0.008303 | 0.03312 | 0.0083103 | 1.1701e-05 | 7.3266e-06 | 0.049768 | 0.049767 | 0.049768 | 0.98994 | -0.19366 | 0.99032 | -0.18625 | 13.6724
4 | -0.059795 | -0.014986 | 0.059872 | 0.015035 | 7.6492e-05 | 4.863e-05 | 0.089865 | 0.089865 | 0.089865 | 0.99011 | -0.19027 | 0.99149 | -0.16346 | 24.6883
5 | -0.059872 | -0.015035 | 0.060125 | 0.015196 | 0.00025327 | 0.00016101 | 0.089865 | 0.089865 | 0.089865 | 0.99149 | -0.16346 | 0.99607 | -0.075199 | 24.6882
6 | -0.013398 | -0.0033579 | 0.013401 | 0.0033594 | 2.7251e-06 | 1.5093e-06 | 0.020044 | 0.020044 | 0.020044 | 0.99465 | -0.10277 | 0.99487 | -0.098501 | 5.5065
7 | -0.022843 | -0.0057257 | 0.02285 | 0.0057304 | 7.5964e-06 | 4.6363e-06 | 0.034166 | 0.034166 | 0.034166 | 0.99487 | -0.098501 | 0.99523 | -0.091523 | 9.3862
8 | 0.1041 | 0.026729 | -0.10405 | -0.026694 | 5.5278e-05 | 3.5299e-05 | 0.15576 | 0.15576 | 0.15576 | 0.99597 | -0.076435 | 0.99539 | -0.08738 | 42.7918
9 | -0.10976 | -0.028147 | 0.10978 | 0.028162 | 2.361e-05 | 1.508e-05 | 0.16421 | 0.16421 | 0.16421 | 0.99597 | -0.076435 | 0.9962 | -0.072 | 45.1133
10 | 0.097654 | 0.025091 | -0.097375 | -0.024913 | 0.00027915 | 0.0001782 | 0.1462 | 0.1462 | 0.1462 | 0.99539 | -0.08738 | 0.99228 | -0.14642 | 40.166
11 | 0.020193 | 0.0050642 | -0.020184 | -0.0050586 | 9.3473e-06 | 5.6258e-06 | 0.030164 | 0.030164 | 0.030164 | 0.9962 | -0.072 | 0.9957 | -0.081717 | 8.2868
12 | -0.14029 | -0.035812 | 0.14078 | 0.036125 | 0.00048995 | 0.00031318 | 0.20979 | 0.20979 | 0.20979 | 0.9962 | -0.072 | 1 | 0 | 57.6336
13 | 0.091504 | 0.023442 | -0.091432 | -0.023396 | 7.1497e-05 | 4.5627e-05 | 0.1374 | 0.1374 | 0.1374 | 0.99228 | -0.14642 | 0.99143 | -0.16255 | 37.7472
14 | 0.21289 | 0.053839 | -0.21224 | -0.053424 | 0.0006493 | 0.00041465 | 0.31695 | 0.31695 | 0.31695 | 1 | 0 | 0.99667 | -0.063792 | 43.5368
15 | 0.091346 | 0.023138 | -0.091168 | -0.023024 | 0.00017797 | 0.00011357 | 0.13601 | 0.13601 | 0.13601 | 1 | 0 | 0.99787 | -0.040652 | 37.3655
16 | 0.085614 | 0.021938 | -0.085528 | -0.021883 | 8.5528e-05 | 5.456e-05 | 0.12867 | 0.12867 | 0.12867 | 0.99143 | -0.16255 | 0.99035 | -0.18319 | 35.3483
17 | 0.17049 | 0.042938 | -0.17035 | -0.042853 | 0.00013396 | 8.5446e-05 | 0.25461 | 0.25461 | 0.25461 | 0.99667 | -0.063792 | 0.99581 | -0.080238 | 34.9741
18 | 0.041747 | 0.010486 | -0.041712 | -0.010463 | 3.5571e-05 | 2.2447e-05 | 0.062336 | 0.062336 | 0.062336 | 0.99667 | -0.063792 | 0.99574 | -0.081664 | 17.1253
19 | 0.075696 | 0.019146 | -0.07557 | -0.019067 | 0.00012524 | 7.9812e-05 | 0.11294 | 0.11294 | 0.11294 | 0.99787 | -0.040652 | 0.99607 | -0.075199 | 31.027
20 | 0.080161 | 0.020538 | -0.079913 | -0.02038 | 0.00024835 | 0.00015836 | 0.1206 | 0.1206 | 0.1206 | 0.99035 | -0.18319 | 0.987 | -0.24733 | 33.1329
21 | 0.09203 | 0.023223 | -0.091994 | -0.0232 | 3.5674e-05 | 2.2766e-05 | 0.13757 | 0.13757 | 0.13757 | 0.99581 | -0.080238 | 0.99539 | -0.088336 | 37.7948
22 | 0.032249 | 0.0080916 | -0.032234 | -0.0080821 | 1.5153e-05 | 9.4716e-06 | 0.048195 | 0.048196 | 0.048196 | 0.99574 | -0.081664 | 0.99523 | -0.091523 | 13.2405
23 | 0.017771 | 0.0044577 | -0.017767 | -0.0044551 | 4.359e-06 | 2.595e-06 | 0.027202 | 0.027202 | 0.027202 | 0.97219 | -0.53608 | 0.97193 | -0.54123 | 7.4731
24 | -0.038689 | -0.0097002 | 0.038693 | 0.0097027 | 3.9562e-06 | 2.4947e-06 | 0.059218 | 0.059218 | 0.059218 | 0.97219 | -0.53608 | 0.9723 | -0.53394 | 16.2687
25 | 0.014986 | 0.0037582 | -0.014979 | -0.0037542 | 7.0359e-06 | 4.0616e-06 | 0.022945 | 0.022945 | 0.022945 | 0.97193 | -0.54123 | 0.97143 | -0.55109 | 6.3036
26 | -0.041508 | -0.010408 | 0.041536 | 0.010426 | 2.802e-05 | 1.7703e-05 | 0.063527 | 0.063527 | 0.063527 | 0.9723 | -0.53394 | 0.97301 | -0.51978 | 17.4524
27 | -0.043542 | -0.010929 | 0.043544 | 0.01093 | 2.044e-06 | 1.2929e-06 | 0.066593 | 0.066593 | 0.066593 | 0.97301 | -0.51978 | 0.97306 | -0.5188 | 18.2949
28 | -0.046358 | -0.011635 | 0.046366 | 0.01164 | 8.3591e-06 | 5.2947e-06 | 0.070897 | 0.070897 | 0.070897 | 0.97306 | -0.5188 | 0.97325 | -0.51502 | 19.4772
29 | -0.005101 | -0.0012784 | 0.0051013 | 0.0012784 | 3.0219e-07 | 1.4753e-08 | 0.0076415 | 0.0076415 | 0.0076415 | 0.99331 | -0.12854 | 0.99337 | -0.1273 | 2.0993
30 | -0.020834 | -0.0052236 | 0.020846 | 0.0052312 | 1.2599e-05 | 7.6166e-06 | 0.031208 | 0.031208 | 0.031208 | 0.99337 | -0.1273 | 0.99403 | -0.11461 | 8.5737
31 | 0.015732 | 0.0039452 | -0.015729 | -0.003943 | 3.7267e-06 | 2.1535e-06 | 0.023567 | 0.023567 | 0.023567 | 0.99337 | -0.1273 | 0.99312 | -0.13227 | 6.4745
32 | -0.048252 | -0.012113 | 0.048265 | 0.012121 | 1.2146e-05 | 7.6996e-06 | 0.073781 | 0.073781 | 0.073781 | 0.97325 | -0.51502 | 0.97352 | -0.50974 | 20.2694
33 | -0.042559 | -0.010676 | 0.042566 | 0.010681 | 7.4436e-06 | 4.7015e-06 | 0.06395 | 0.06395 | 0.06395 | 0.99032 | -0.18625 | 0.99051 | -0.18258 | 17.5687
34 | -0.052106 | -0.013071 | 0.052145 | 0.013097 | 3.9777e-05 | 2.5234e-05 | 0.078281 | 0.078281 | 0.078281 | 0.99051 | -0.18258 | 0.99134 | -0.16658 | 21.5058
35 | -0.070919 | -0.017823 | 0.071032 | 0.017895 | 0.0001128 | 7.1849e-05 | 0.10637 | 0.10636 | 0.10637 | 0.9923 | -0.14787 | 0.99403 | -0.11461 | 29.2212
36 | 0.061596 | 0.015486 | -0.061541 | -0.015451 | 5.4962e-05 | 3.4954e-05 | 0.092383 | 0.092383 | 0.092383 | 0.9923 | -0.14787 | 0.99134 | -0.16658 | 25.3801
37 | -0.091879 | -0.023126 | 0.091994 | 0.0232 | 0.00011556 | 7.3747e-05 | 0.13757 | 0.13757 | 0.13757 | 0.99403 | -0.11461 | 0.99539 | -0.088336 | 37.7948
38 | 0.015729 | 0.003943 | -0.015725 | -0.0039408 | 3.8134e-06 | 2.2037e-06 | 0.023567 | 0.023567 | 0.023567 | 0.99312 | -0.13227 | 0.99285 | -0.13736 | 6.4745
39 | 0.0078551 | 0.0019685 | -0.0078544 | -0.0019682 | 6.5883e-07 | 2.5773e-07 | 0.011773 | 0.011773 | 0.011773 | 0.99285 | -0.13736 | 0.99276 | -0.13912 | 3.2342
40 | 0.048993 | 0.012308 | -0.048982 | -0.012301 | 1.1473e-05 | 7.2747e-06 | 0.074877 | 0.074877 | 0.074877 | 0.97377 | -0.50484 | 0.97352 | -0.50974 | 20.5705
41 | -0.04971 | -0.012487 | 0.049722 | 0.012495 | 1.2223e-05 | 7.7524e-06 | 0.075972 | 0.075972 | 0.075972 | 0.97377 | -0.50484 | 0.97403 | -0.49968 | 20.8713
42 | -0.050485 | -0.012686 | 0.050564 | 0.012737 | 7.9702e-05 | 5.0564e-05 | 0.077137 | 0.077137 | 0.077137 | 0.97403 | -0.49968 | 0.97571 | -0.46667 | 21.1915
43 | -0.058758 | -0.014788 | 0.058861 | 0.014853 | 0.00010307 | 6.5534e-05 | 0.089631 | 0.089631 | 0.089631 | 0.97571 | -0.46667 | 0.97758 | -0.43004 | 24.624
44 | 0.0073869 | 0.0018516 | -0.0073849 | -0.0018508 | 2.0032e-06 | 7.5651e-07 | 0.011266 | 0.011266 | 0.011266 | 0.97571 | -0.46667 | 0.97542 | -0.47236 | 3.095
45 | 0.00080639 | 0.00019938 | -0.0008063 | -0.00020131 | 8.9924e-08 | -1.9245e-06 | 0.0012288 | 0.0012295 | 0.0012295 | 0.97571 | -0.46667 | 0.97559 | -0.46902 | 0.33778
46 | -0.059564 | -0.01503 | 0.05961 | 0.015059 | 4.649e-05 | 2.9565e-05 | 0.090701 | 0.090701 | 0.090701 | 0.97758 | -0.43004 | 0.97841 | -0.41375 | 24.9179
47 | 0.0008063 | 0.00020131 | -0.00080627 | -0.00020207 | 3.574e-08 | -7.6412e-07 | 0.0012295 | 0.0012298 | 0.0012298 | 0.97559 | -0.46902 | 0.97555 | -0.46996 | 0.33786
48 | -0.062421 | -0.015764 | 0.062455 | 0.015785 | 3.407e-05 | 2.1678e-05 | 0.094976 | 0.094976 | 0.094976 | 0.97841 | -0.41375 | 0.979 | -0.40237 | 26.0923
49 | 0.079913 | 0.02038 | -0.079669 | -0.020225 | 0.00024359 | 0.00015533 | 0.1206 | 0.1206 | 0.1206 | 0.987 | -0.24733 | 0.98372 | -0.31067 | 33.133
50 | -0.076819 | -0.019438 | 0.076848 | 0.019456 | 2.8924e-05 | 1.844e-05 | 0.11657 | 0.11657 | 0.11657 | 0.98114 | -0.36064 | 0.98154 | -0.3528 | 32.0253
51 | 0.069269 | 0.017546 | -0.06921 | -0.017508 | 5.8646e-05 | 3.7355e-05 | 0.10512 | 0.10512 | 0.10512 | 0.98114 | -0.36064 | 0.98023 | -0.37828 | 28.8795
52 | -0.078105 | -0.019771 | 0.078168 | 0.019811 | 6.2197e-05 | 3.9657e-05 | 0.11848 | 0.11848 | 0.11848 | 0.98154 | -0.3528 | 0.9824 | -0.33622 | 32.5489
53 | 0.06921 | 0.017508 | -0.06918 | -0.017489 | 3.0343e-05 | 1.9327e-05 | 0.10512 | 0.10512 | 0.10512 | 0.98023 | -0.37828 | 0.97976 | -0.38743 | 28.8795
54 | -0.078168 | -0.019811 | 0.078185 | 0.019822 | 1.7197e-05 | 1.0965e-05 | 0.11848 | 0.11848 | 0.11848 | 0.9824 | -0.33622 | 0.98263 | -0.33165 | 32.5489
55 | 0.065714 | 0.01662 | -0.065667 | -0.01659 | 4.7065e-05 | 2.9963e-05 | 0.099857 | 0.099857 | 0.099857 | 0.97976 | -0.38743 | 0.979 | -0.40237 | 27.4332
56 | -0.078185 | -0.019822 | 0.078264 | 0.019872 | 7.8899e-05 | 5.0305e-05 | 0.11848 | 0.11848 | 0.11848 | 0.98263 | -0.33165 | 0.98372 | -0.31067 | 32.5489
57 | 0.0061028 | 0.0015292 | -0.0061026 | -0.0015292 | 1.991e-07 | 4.5381e-08 | 0.0091472 | 0.0091473 | 0.0091473 | 0.99276 | -0.13912 | 0.99273 | -0.1398 | 2.513
58 | 0.0061026 | 0.0015292 | -0.0061024 | -0.0015291 | 2.8763e-07 | 6.557e-08 | 0.0091473 | 0.0091473 | 0.0091473 | 0.99273 | -0.1398 | 0.99268 | -0.14079 | 2.513
59 | 0.004262 | 0.0010679 | -0.0042616 | -0.001068 | 4.3429e-07 | -8.8828e-08 | 0.0063887 | 0.0063888 | 0.0063888 | 0.99268 | -0.14079 | 0.99256 | -0.14293 | 1.7552
60 | 0.0042616 | 0.001068 | -0.0042614 | -0.001068 | 1.8995e-07 | -3.8821e-08 | 0.0063888 | 0.0063888 | 0.0063888 | 0.99256 | -0.14293 | 0.99252 | -0.14387 | 1.7552

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44666 | 0.1131

## res_load
| p_mw | q_mvar
0 | 0.013133 | 0.0032914
1 | 0.010394 | 0.0026049
2 | 0.0095655 | 0.0023973
3 | 0.059795 | 0.014986
4 | 0.013398 | 0.0033579
5 | 0.0094418 | 0.0023663
6 | 0.0056561 | 0.0014176
7 | 0.0063938 | 0.0016024
8 | 0.010317 | 0.0025857
9 | 0.0058712 | 0.0014715
10 | 0.020184 | 0.0050586
11 | 0.0058182 | 0.0014582
12 | 0.015472 | 0.0038778
13 | 0.0053671 | 0.0013451
14 | 0.078325 | 0.01963
15 | 0.0094627 | 0.0023716
16 | 0.015445 | 0.003871
17 | 0.020918 | 0.0052425
18 | 0.0027806 | 0.0006969
19 | 0.0028153 | 0.00070558
20 | 0.014979 | 0.0037542
21 | 0.0020053 | 0.00050258
22 | 0.0028142 | 0.00070531
23 | 0.005101 | 0.0012784
24 | 0.0018862 | 0.00047271
25 | 0.009439 | 0.0023656
26 | 0.0095396 | 0.0023909
27 | 0.0093239 | 0.0023368
28 | 0.0093952 | 0.0023547
29 | 0.0078697 | 0.0019723
30 | 0.00071655 | 0.00017958
31 | 0.00071706 | 0.00017971
32 | 0.00076288 | 0.0001912
33 | 0.0007029 | 0.00017616
34 | 0.0073849 | 0.0018508
35 | 0.002811 | 0.00070451
36 | 0.00080627 | 0.00020207
37 | 0.0093836 | 0.0023518
38 | 0.0075504 | 0.0018923
39 | 0.0012572 | 0.0003151
40 | 0.0034663 | 0.00086874
41 | 0.0032112 | 0.00080481
42 | 0.0014055 | 0.00035225
43 | 0.0017516 | 0.00043899
44 | 0.0018403 | 0.00046123
45 | 0.0042614 | 0.001068

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1