## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-51_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-51_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2581-51_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2581-51_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2581-51_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2581-51_0_4_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_2581-51_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_2581-51_0_4_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_2581-51_0_4_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2581-51_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2581-51_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2581-51_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2581-51_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2581-51_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2581-51_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2581-51_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2581-51_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2581-51_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2581-51_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2581-51_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_2581-51_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_2581-51_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_2581-51_0_4_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_2581-51_0_4_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_2581-51_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2581-51_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2581-51_0_4_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_2581-51_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2581-51_0_4_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_2581-51_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2581-51_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2581-51_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2581-51_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2581-51_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2581-51_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_2581-51_0_4_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_2581-51_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2581-51_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_2581-51_0_4_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_2581-51_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_MV_523_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-51_0_4_load_0 | 0 | 0.0043628 | 0.0010934 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-51_0_4_load_1 | 1 | 0.026871 | 0.0067345 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-51_0_4_load_2 | 2 | 0.01724 | 0.0043207 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-51_0_4_load_4 | 4 | 0.01749 | 0.0043833 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-51_0_4_load_36 | 5 | 0.0059813 | 0.001499 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-51_0_4_load_37 | 7 | 0.088398 | 0.022155 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-51_0_4_load_14 | 8 | 0.0095048 | 0.0023821 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-51_0_4_load_10 | 9 | 0.018652 | 0.0046746 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-51_0_4_load_5 | 10 | 0.022966 | 0.0057557 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-51_0_4_load_6 | 11 | 0.0041363 | 0.0010367 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-51_0_4_load_7 | 12 | 0.023305 | 0.0058409 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-51_0_4_load_15 | 15 | 0.0012599 | 0.00031576 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-51_0_4_load_16 | 16 | 0.041512 | 0.010404 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-51_0_4_load_22 | 19 | 0.030858 | 0.0077337 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-51_0_4_load_40 | 21 | 0.0021127 | 0.00052948 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-51_0_4_load_31 | 22 | 0.014809 | 0.0037114 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-51_0_4_load_11 | 24 | 0.0033627 | 0.00084277 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-51_0_4_load_13 | 25 | 0.012221 | 0.0030628 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-51_0_4_load_29 | 26 | 0.015042 | 0.0037699 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-51_0_4_load_23 | 27 | 0.0073112 | 0.0018324 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-51_0_4_load_17 | 31 | 0.034878 | 0.0087413 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-51_0_4_load_24 | 33 | 0.0039673 | 0.00099431 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-51_0_4_load_39 | 34 | 0.0019961 | 0.00050028 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2581-51_0_4_load_35 | 35 | 0.017416 | 0.0043649 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2581-51_0_4_load_25 | 36 | 0.0024806 | 0.0006217 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2581-51_0_4_load_38 | 37 | 0.0061807 | 0.001549 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2581-51_0_4_load_41 | 38 | 0.0033887 | 0.00084929 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2581-51_0_4_load_42 | 39 | 0.0041322 | 0.0010356 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-51_0_4_line_0 |  | 0 | 1 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2581-51_0_4_line_1 |  | 0 | 2 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2581-51_0_4_line_2 |  | 1 | 3 | 0.039367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2581-51_0_4_line_3 |  | 2 | 4 | 0.0054208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2581-51_0_4_line_4 |  | 3 | 5 | 0.060882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-51_0_4_line_5 |  | 4 | 6 | 0.022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2581-51_0_4_line_6 |  | 5 | 7 | 0.016093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2581-51_0_4_line_7 |  | 6 | 8 | 0.025925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2581-51_0_4_line_8 |  | 6 | 9 | 0.0013929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2581-51_0_4_line_9 |  | 8 | 27 | 0.004926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2581-51_0_4_line_10 |  | 9 | 24 | 0.01679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2581-51_0_4_line_11 |  | 10 | 11 | 0.012603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2581-51_0_4_line_12 |  | 10 | 12 | 0.032257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2581-51_0_4_line_13 |  | 11 | 13 | 0.026644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2581-51_0_4_line_14 |  | 12 | 14 | 0.025754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2581-51_0_4_line_15 |  | 13 | 15 | 0.024883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2581-51_0_4_line_16 |  | 13 | 16 | 0.0020062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2581-51_0_4_line_17 |  | 14 | 17 | 0.033397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2581-51_0_4_line_18 |  | 14 | 18 | 0.018355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2581-51_0_4_line_19 |  | 14 | 19 | 0.032265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2581-51_0_4_line_20 |  | 16 | 20 | 0.049233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2581-51_0_4_line_21 |  | 17 | 21 | 0.043211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2581-51_0_4_line_22 |  | 18 | 22 | 0.019251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-51_0_4_line_23 |  | 19 | 23 | 0.0025693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2581-51_0_4_line_24 |  | 20 | 30 | 0.10589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2581-51_0_4_line_25 |  | 21 | 34 | 0.0080836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2581-51_0_4_line_26 |  | 23 | 35 | 0.015559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_2581-51_0_4_line_27 |  | 24 | 25 | 0.01097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_2581-51_0_4_line_28 |  | 25 | 26 | 0.016236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2581-51_0_4_line_29 |  | 26 | 28 | 0.036108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2581-51_0_4_line_30 |  | 27 | 29 | 0.025723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2581-51_0_4_line_31 |  | 28 | 35 | 0.01953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_2581-51_0_4_line_32 |  | 28 | 37 | 0.050756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2581-51_0_4_line_33 |  | 29 | 33 | 0.11786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2581-51_0_4_line_34 |  | 29 | 32 | 0.08899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2581-51_0_4_line_35 |  | 30 | 36 | 0.025293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2581-51_0_4_line_36 |  | 31 | 32 | 0.10368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2581-51_0_4_line_37 |  | 34 | 38 | 0.011776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2581-51_0_4_line_38 |  | 38 | 39 | 0.00066383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-51_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 40 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2634566.1992 | 1244467.5254 | 2634569.1916 | 1244465.8842 | 2634580.3497 | 1244461.2228
1 | 2634566.1992 | 1244467.5254 | 2634555.4725 | 1244473.4088
2 | 2634618.0021 | 1244452.0039 | 2634613.5986 | 1244451.7003 | 2634606.1 | 1244452.2013 | 2634599.7622 | 1244453.1762 | 2634596.113 | 1244454.4113 | 2634584.7043 | 1244459.4036 | 2634580.3497 | 1244461.2228
3 | 2634550.7196 | 1244476.0156 | 2634555.4725 | 1244473.4088
4 | 2634618.0021 | 1244452.0039 | 2634618.0933 | 1244460.988 | 2634617.9983 | 1244466.9024 | 2634617.4018 | 1244475.9048 | 2634615.3986 | 1244489.0016 | 2634612.6001 | 1244511.4998 | 2634612.5389 | 1244512.5378
5 | 2634530.597 | 1244486.3063 | 2634534.7876 | 1244484.2293 | 2634545.1013 | 1244479.097 | 2634550.7196 | 1244476.0156
6 | 2634612.5389 | 1244512.5378 | 2634611.6024 | 1244528.405 | 2634611.6024 | 1244528.6027
7 | 2634530.597 | 1244486.3063 | 2634524.4016 | 1244479.6993 | 2634511.2441 | 1244469.1452
8 | 2634530.597 | 1244486.3063 | 2634529.3731 | 1244486.9713
9 | 2634511.2441 | 1244469.1452 | 2634507.4015 | 1244466.0629
10 | 2634514.6203 | 1244494.9874 | 2634529.3731 | 1244486.9713
11 | 2634532.9612 | 1244597.1609 | 2634545.5283 | 1244598.108
12 | 2634532.9612 | 1244597.1609 | 2634500.7949 | 1244594.7368
13 | 2634572.0973 | 1244600.1102 | 2634545.5283 | 1244598.108
14 | 2634475.1136 | 1244592.7974 | 2634486.4048 | 1244593.6524 | 2634500.7949 | 1244594.7368
15 | 2634572.0973 | 1244600.1102 | 2634572.0355 | 1244624.9927
16 | 2634572.0973 | 1244600.1102 | 2634574.0978 | 1244600.2612
17 | 2634475.1136 | 1244592.7974 | 2634475.8277 | 1244603.842 | 2634474.158 | 1244615.5177 | 2634473.2021 | 1244625.2962 | 2634473.0998 | 1244625.9961
18 | 2634475.1136 | 1244592.7974 | 2634456.7609 | 1244591.3567
19 | 2634475.1136 | 1244592.7974 | 2634473.9784 | 1244583.9962 | 2634470.9882 | 1244560.7974
20 | 2634623.1909 | 1244603.9659 | 2634574.0978 | 1244600.2612
21 | 2634473.0998 | 1244625.9961 | 2634497.1009 | 1244635.7974 | 2634513.0959 | 1244642.3507
22 | 2634456.7609 | 1244591.3567 | 2634437.5694 | 1244589.8463
23 | 2634470.6597 | 1244558.2492 | 2634470.9882 | 1244560.7974
24 | 2634623.1909 | 1244603.9659 | 2634631.8022 | 1244604.4053 | 2634643.1018 | 1244606.4058 | 2634657.8027 | 1244609.5047 | 2634670.7994 | 1244613.3052 | 2634683.0992 | 1244618.7027 | 2634685.3998 | 1244609.0321 | 2634685.8428 | 1244606.9222 | 2634687.0999 | 1244596.1003 | 2634687.4036 | 1244586.7961 | 2634687.297 | 1244575.2991
25 | 2634520.5761 | 1244645.4154 | 2634513.0959 | 1244642.3507
26 | 2634470.6597 | 1244558.2492 | 2634466.6788 | 1244545.0397 | 2634466.1139 | 1244543.3703
27 | 2634504.9815 | 1244500.2248 | 2634514.6203 | 1244494.9874
28 | 2634504.9815 | 1244500.2248 | 2634490.7155 | 1244507.9763
29 | 2634458.9885 | 1244525.2156 | 2634490.7155 | 1244507.9763
30 | 2634487.0028 | 1244450.3964 | 2634491.1711 | 1244453.4559 | 2634503.2072 | 1244462.6985 | 2634507.4015 | 1244466.0629
31 | 2634458.9885 | 1244525.2156 | 2634462.6525 | 1244533.142 | 2634466.1139 | 1244543.3703
32 | 2634458.9885 | 1244525.2156 | 2634446.9818 | 1244531.7391 | 2634414.5197 | 1244549.6832
33 | 2634487.0028 | 1244450.3964 | 2634477.1789 | 1244447.9378 | 2634452.2624 | 1244447.304 | 2634399.7433 | 1244447.9556 | 2634369.4637 | 1244448.438
34 | 2634487.0028 | 1244450.3964 | 2634484.6617 | 1244433.2495 | 2634485.5182 | 1244408.0938 | 2634483.1808 | 1244391.614 | 2634475.5883 | 1244362.729
35 | 2634687.297 | 1244575.2991 | 2634666.4172 | 1244569.2733 | 2634667.6773 | 1244565.9426
36 | 2634475.5883 | 1244362.729 | 2634429.2167 | 1244363.8163 | 2634396.4321 | 1244358.245 | 2634378.0054 | 1244355.1141 | 2634372.7764 | 1244353.9839
37 | 2634520.5761 | 1244645.4154 | 2634528.097 | 1244648.4968 | 2634531.4361 | 1244649.9669
38 | 2634531.4361 | 1244649.9669 | 2634532.0436 | 1244650.2344

## bus_geodata
| x | y | coords
0 | 2634566.1992 | 1244467.5254
1 | 2634580.3497 | 1244461.2228
2 | 2634555.4725 | 1244473.4088
3 | 2634618.0021 | 1244452.0039
4 | 2634550.7196 | 1244476.0156
5 | 2634612.5389 | 1244512.5378
6 | 2634530.597 | 1244486.3063
7 | 2634611.6024 | 1244528.6027
8 | 2634511.2441 | 1244469.1452
9 | 2634529.3731 | 1244486.9713
10 | 2634532.9612 | 1244597.1609
11 | 2634545.5283 | 1244598.108
12 | 2634500.7949 | 1244594.7368
13 | 2634572.0973 | 1244600.1102
14 | 2634475.1136 | 1244592.7974
15 | 2634572.0355 | 1244624.9927
16 | 2634574.0978 | 1244600.2612
17 | 2634473.0998 | 1244625.9961
18 | 2634456.7609 | 1244591.3567
19 | 2634470.9882 | 1244560.7974
20 | 2634623.1909 | 1244603.9659
21 | 2634513.0959 | 1244642.3507
22 | 2634437.5694 | 1244589.8463
23 | 2634470.6597 | 1244558.2492
24 | 2634514.6203 | 1244494.9874
25 | 2634504.9815 | 1244500.2248
26 | 2634490.7155 | 1244507.9763
27 | 2634507.4015 | 1244466.0629
28 | 2634458.9885 | 1244525.2156
29 | 2634487.0028 | 1244450.3964
30 | 2634687.297 | 1244575.2991
31 | 2634372.7764 | 1244353.9839
32 | 2634475.5883 | 1244362.729
33 | 2634369.4637 | 1244448.438
34 | 2634520.5761 | 1244645.4154
35 | 2634466.1139 | 1244543.3703
36 | 2634667.6773 | 1244565.9426
37 | 2634414.5197 | 1244549.6832
38 | 2634531.4361 | 1244649.9669
39 | 2634532.0436 | 1244650.2344
40 | 2634530.597 | 1244486.3063

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99462 | -0.10263 | 0.0043628 | 0.0010934
1 | 0.99289 | -0.13582 | 0.026871 | 0.0067345
2 | 0.99603 | -0.075596 | 0.01724 | 0.0043207
3 | 0.98946 | -0.20174 | 0 | 0
4 | 0.99639 | -0.068796 | 0.01749 | 0.0043833
5 | 0.98416 | -0.30458 | 0.0059813 | 0.001499
6 | 0.99806 | -0.037032 | 0 | 0
7 | 0.98284 | -0.33022 | 0.088398 | 0.022155
8 | 0.99674 | -0.062319 | 0.0095048 | 0.0023821
9 | 0.99819 | -0.0344 | 0.018652 | 0.0046746
10 | 0.98375 | -0.31271 | 0.022966 | 0.0057557
11 | 0.98318 | -0.32392 | 0.0041363 | 0.0010367
12 | 0.9859 | -0.27076 | 0.023305 | 0.0058409
13 | 0.98206 | -0.34569 | 0 | 0
14 | 0.98818 | -0.22668 | 0 | 0
15 | 0.98203 | -0.34626 | 0.0012599 | 0.00031576
16 | 0.98198 | -0.34729 | 0.041512 | 0.010404
17 | 0.98782 | -0.23362 | 0 | 0
18 | 0.98793 | -0.23153 | 0 | 0
19 | 0.99181 | -0.15661 | 0.030858 | 0.0077337
20 | 0.98187 | -0.3495 | 0 | 0
21 | 0.98736 | -0.2426 | 0.0021127 | 0.00052948
22 | 0.98766 | -0.23662 | 0.014809 | 0.0037114
23 | 0.99199 | -0.15313 | 0 | 0
24 | 1 | 0 | -0.44459 | -0.11273
25 | 0.99897 | -0.019507 | 0.012221 | 0.0030628
26 | 0.99754 | -0.046714 | 0.015042 | 0.0037699
27 | 0.99653 | -0.06631 | 0.0073112 | 0.0018324
28 | 0.99461 | -0.10271 | 0 | 0
29 | 0.99561 | -0.083868 | 0 | 0
30 | 0.98163 | -0.35426 | 0 | 0
31 | 0.98945 | -0.20277 | 0.034878 | 0.0087413
32 | 0.99277 | -0.13861 | 0 | 0
33 | 0.99519 | -0.092098 | 0.0039673 | 0.00099431
34 | 0.98729 | -0.24397 | 0.0019961 | 0.00050028
35 | 0.99308 | -0.13208 | 0.017416 | 0.0043649
36 | 0.98157 | -0.35539 | 0.0024806 | 0.0006217
37 | 0.99433 | -0.10824 | 0.0061807 | 0.001549
38 | 0.98721 | -0.24556 | 0.0033887 | 0.00084929
39 | 0.9872 | -0.24561 | 0.0041322 | 0.0010356
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12232 | 0.031072 | -0.12213 | -0.030947 | 0.00019504 | 0.00012462 | 0.18315 | 0.18315 | 0.18315 | 0.99462 | -0.10263 | 0.99289 | -0.13582 | 50.3154
1 | -0.12668 | -0.032165 | 0.12685 | 0.032271 | 0.00016505 | 0.00010548 | 0.18967 | 0.18967 | 0.18967 | 0.99462 | -0.10263 | 0.99603 | -0.075596 | 52.1085
2 | 0.095255 | 0.024213 | -0.094954 | -0.02402 | 0.00030136 | 0.00019236 | 0.14288 | 0.14288 | 0.14288 | 0.99289 | -0.13582 | 0.98946 | -0.20174 | 39.2521
3 | -0.14409 | -0.036591 | 0.14414 | 0.036621 | 4.7171e-05 | 3.0048e-05 | 0.21543 | 0.21543 | 0.21543 | 0.99603 | -0.075596 | 0.99639 | -0.068796 | 29.592
4 | 0.094954 | 0.02402 | -0.094488 | -0.023723 | 0.00046607 | 0.00029751 | 0.14288 | 0.14288 | 0.14288 | 0.98946 | -0.20174 | 0.98416 | -0.30458 | 39.2522
5 | -0.16163 | -0.041005 | 0.16187 | 0.041162 | 0.0002473 | 0.00015768 | 0.24155 | 0.24155 | 0.24155 | 0.99639 | -0.068796 | 0.99806 | -0.037032 | 33.1798
6 | 0.088506 | 0.022224 | -0.088398 | -0.022155 | 0.00010809 | 6.8974e-05 | 0.13383 | 0.13383 | 0.13383 | 0.98416 | -0.30458 | 0.98284 | -0.33022 | 36.7677
7 | 0.055971 | 0.014144 | -0.055903 | -0.014101 | 6.7765e-05 | 4.3031e-05 | 0.083489 | 0.083489 | 0.083489 | 0.99806 | -0.037032 | 0.99674 | -0.062319 | 22.9367
8 | -0.21784 | -0.055306 | 0.21787 | 0.055324 | 2.7592e-05 | 1.7622e-05 | 0.32504 | 0.32504 | 0.32504 | 0.99806 | -0.037032 | 0.99819 | -0.0344 | 44.648
9 | 0.046399 | 0.011718 | -0.04639 | -0.011713 | 8.8714e-06 | 5.6135e-06 | 0.0693 | 0.0693 | 0.0693 | 0.99674 | -0.062319 | 0.99653 | -0.06631 | 19.0384
10 | -0.23652 | -0.059998 | 0.23692 | 0.060249 | 0.00039193 | 0.0002504 | 0.35284 | 0.35284 | 0.35284 | 0.99819 | -0.0344 | 1 | 0 | 48.4673
11 | 0.049467 | 0.012425 | -0.04944 | -0.012408 | 2.6466e-05 | 1.6778e-05 | 0.074833 | 0.074833 | 0.074833 | 0.98375 | -0.31271 | 0.98318 | -0.32392 | 20.5586
12 | -0.072433 | -0.01818 | 0.072578 | 0.018273 | 0.00014523 | 9.2536e-05 | 0.10957 | 0.10957 | 0.10957 | 0.98375 | -0.31271 | 0.9859 | -0.27076 | 30.1019
13 | 0.045304 | 0.011371 | -0.045257 | -0.011342 | 4.6983e-05 | 2.9732e-05 | 0.068573 | 0.068573 | 0.068573 | 0.98318 | -0.32392 | 0.98206 | -0.34569 | 18.8388
14 | -0.095883 | -0.024114 | 0.096086 | 0.024243 | 0.00020235 | 0.00012917 | 0.14475 | 0.14475 | 0.14475 | 0.9859 | -0.27076 | 0.98818 | -0.22668 | 39.7652
15 | 0.0012599 | 0.00031546 | -0.0012599 | -0.00031576 | 3.4004e-08 | -2.9306e-07 | 0.0019089 | 0.001909 | 0.001909 | 0.98206 | -0.34569 | 0.98203 | -0.34626 | 0.52446
16 | 0.043997 | 0.011026 | -0.043994 | -0.011024 | 3.3434e-06 | 2.1144e-06 | 0.066664 | 0.066664 | 0.066664 | 0.98206 | -0.34569 | 0.98198 | -0.34729 | 18.3143
17 | 0.01164 | 0.0029198 | -0.011636 | -0.0029178 | 3.8479e-06 | 2.0349e-06 | 0.017528 | 0.017528 | 0.017528 | 0.98818 | -0.22668 | 0.98782 | -0.23362 | 4.8155
18 | 0.014816 | 0.0037154 | -0.014812 | -0.0037135 | 3.4262e-06 | 1.9577e-06 | 0.022311 | 0.022311 | 0.022311 | 0.98818 | -0.22668 | 0.98793 | -0.23153 | 6.1293
19 | -0.12254 | -0.030878 | 0.12295 | 0.031142 | 0.00041224 | 0.00026342 | 0.18458 | 0.18458 | 0.18458 | 0.98818 | -0.22668 | 0.99181 | -0.15661 | 50.7099
20 | 0.0024816 | 0.00062003 | -0.0024813 | -0.00062049 | 2.6099e-07 | -4.5573e-07 | 0.0037597 | 0.0037599 | 0.0037599 | 0.98198 | -0.34729 | 0.98187 | -0.3495 | 1.0329
21 | 0.011636 | 0.0029178 | -0.011631 | -0.0029152 | 4.9787e-06 | 2.6334e-06 | 0.017528 | 0.017529 | 0.017529 | 0.98782 | -0.23362 | 0.98736 | -0.2426 | 4.8156
22 | 0.014812 | 0.0037135 | -0.014809 | -0.0037114 | 3.5934e-06 | 2.0534e-06 | 0.022311 | 0.022311 | 0.022311 | 0.98793 | -0.23153 | 0.98766 | -0.23662 | 6.1294
23 | -0.15381 | -0.038875 | 0.15384 | 0.038892 | 2.568e-05 | 1.6369e-05 | 0.23088 | 0.23088 | 0.23088 | 0.99181 | -0.15661 | 0.99199 | -0.15313 | 31.7143
24 | 0.0024813 | 0.00062049 | -0.0024808 | -0.00062147 | 5.6145e-07 | -9.7965e-07 | 0.0037599 | 0.0037604 | 0.0037604 | 0.98187 | -0.3495 | 0.98163 | -0.35426 | 1.0331
25 | 0.0095182 | 0.0023857 | -0.0095176 | -0.0023854 | 6.2377e-07 | 2.9583e-07 | 0.014345 | 0.014345 | 0.014345 | 0.98736 | -0.2426 | 0.98729 | -0.24397 | 3.9409
26 | -0.15384 | -0.038892 | 0.15399 | 0.038991 | 0.00015551 | 9.9122e-05 | 0.23088 | 0.23088 | 0.23088 | 0.99199 | -0.15313 | 0.99308 | -0.13208 | 31.7143
27 | 0.20602 | 0.052484 | -0.20583 | -0.05236 | 0.00019368 | 0.00012367 | 0.30687 | 0.30687 | 0.30687 | 1 | 0 | 0.99897 | -0.019507 | 42.1519
28 | 0.19361 | 0.049298 | -0.19335 | -0.049136 | 0.00025366 | 0.00016192 | 0.28866 | 0.28866 | 0.28866 | 0.99897 | -0.019507 | 0.99754 | -0.046714 | 39.6515
29 | 0.17831 | 0.045366 | -0.17783 | -0.04506 | 0.00047985 | 0.00030616 | 0.26622 | 0.26622 | 0.26622 | 0.99754 | -0.046714 | 0.99461 | -0.10271 | 36.5694
30 | 0.039079 | 0.0098805 | -0.039046 | -0.0098597 | 3.2879e-05 | 2.0708e-05 | 0.058383 | 0.058383 | 0.058383 | 0.99653 | -0.06631 | 0.99561 | -0.083868 | 16.0392
31 | 0.17165 | 0.04351 | -0.17141 | -0.043356 | 0.00024182 | 0.00015426 | 0.25698 | 0.25698 | 0.25698 | 0.99461 | -0.10271 | 0.99308 | -0.13208 | 35.2989
32 | 0.0061823 | 0.0015494 | -0.0061807 | -0.001549 | 1.6283e-06 | 3.8358e-07 | 0.0092492 | 0.0092494 | 0.0092494 | 0.99461 | -0.10271 | 0.99433 | -0.10824 | 2.541
33 | 0.0039689 | 0.00099377 | -0.0039673 | -0.00099431 | 1.5551e-06 | -5.3676e-07 | 0.0059315 | 0.005932 | 0.005932 | 0.99561 | -0.083868 | 0.99519 | -0.092098 | 1.6297
34 | 0.035077 | 0.008866 | -0.034985 | -0.0088084 | 9.181e-05 | 5.7604e-05 | 0.052451 | 0.052452 | 0.052452 | 0.99561 | -0.083868 | 0.99277 | -0.13861 | 14.4098
35 | 0.0024808 | 0.00062147 | -0.0024806 | -0.0006217 | 1.3413e-07 | -2.3388e-07 | 0.0037604 | 0.0037605 | 0.0037605 | 0.98163 | -0.35426 | 0.98157 | -0.35539 | 1.0331
36 | -0.034878 | -0.0087413 | 0.034985 | 0.0088084 | 0.00010697 | 6.7122e-05 | 0.052452 | 0.052452 | 0.052452 | 0.98945 | -0.20277 | 0.99277 | -0.13861 | 14.41
37 | 0.0075215 | 0.0018851 | -0.0075209 | -0.0018849 | 5.675e-07 | 2.1262e-07 | 0.011336 | 0.011336 | 0.011336 | 0.98729 | -0.24397 | 0.98721 | -0.24556 | 3.1144
38 | 0.0041322 | 0.0010356 | -0.0041322 | -0.0010356 | 9.6571e-09 | -2.307e-09 | 0.0062284 | 0.0062284 | 0.0062284 | 0.98721 | -0.24556 | 0.9872 | -0.24561 | 1.7111

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44795 | 0.11358

## res_load
| p_mw | q_mvar
0 | 0.0043628 | 0.0010934
1 | 0.026871 | 0.0067345
2 | 0.01724 | 0.0043207
3 | 0.01749 | 0.0043833
4 | 0.0059813 | 0.001499
5 | 0.088398 | 0.022155
6 | 0.0095048 | 0.0023821
7 | 0.018652 | 0.0046746
8 | 0.022966 | 0.0057557
9 | 0.0041363 | 0.0010367
10 | 0.023305 | 0.0058409
11 | 0.0012599 | 0.00031576
12 | 0.041512 | 0.010404
13 | 0.030858 | 0.0077337
14 | 0.0021127 | 0.00052948
15 | 0.014809 | 0.0037114
16 | 0.0033627 | 0.00084277
17 | 0.012221 | 0.0030628
18 | 0.015042 | 0.0037699
19 | 0.0073112 | 0.0018324
20 | 0.034878 | 0.0087413
21 | 0.0039673 | 0.00099431
22 | 0.0019961 | 0.00050028
23 | 0.017416 | 0.0043649
24 | 0.0024806 | 0.0006217
25 | 0.0061807 | 0.001549
26 | 0.0033887 | 0.00084929
27 | 0.0041322 | 0.0010356

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1