## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2581-52_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2581-52_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2581-52_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2581-52_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2581-52_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2581-52_0_6_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2581-52_0_6_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2581-52_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2581-52_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2581-52_0_6_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2581-52_0_6_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_2581-52_0_6_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_2581-52_0_6_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_2581-52_0_6_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_2581-52_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2581-52_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2581-52_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2581-52_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2581-52_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2581-52_0_6_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2581-52_0_6_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2581-52_0_6_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_2581-52_0_6_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_2581-52_0_6_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_2581-52_0_6_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_2581-52_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2581-52_0_6_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2581-52_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2581-52_0_6_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2581-52_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_2581-52_0_6_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_2581-52_0_6_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_2581-52_0_6_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_2581-52_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2581-52_0_6_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_2581-52_0_6_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_2581-52_0_6_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2581-52_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2581-52_0_6_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_2581-52_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_MV_290_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2581-52_0_6_load_0 | 0 | 0.0041071 | 0.0010293 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2581-52_0_6_load_1 | 1 | 0.01066 | 0.0026717 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2581-52_0_6_load_2 | 2 | 0.01357 | 0.003401 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2581-52_0_6_load_4 | 4 | 0.087548 | 0.021942 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2581-52_0_6_load_7 | 5 | 0.029635 | 0.0074272 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2581-52_0_6_load_9 | 6 | 0.014585 | 0.0036553 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2581-52_0_6_load_5 | 7 | 0.030399 | 0.0076187 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2581-52_0_6_load_6 | 8 | 0.027835 | 0.0069761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2581-52_0_6_load_8 | 9 | 0.0050365 | 0.0012623 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2581-52_0_6_load_41 | 10 | 0.039568 | 0.0099166 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2581-52_0_6_load_38 | 11 | 0.009893 | 0.0024794 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2581-52_0_6_load_27 | 12 | 0.012846 | 0.0032194 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2581-52_0_6_load_10 | 14 | 0.0067488 | 0.0016914 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2581-52_0_6_load_11 | 15 | 0.0067316 | 0.0016871 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2581-52_0_6_load_13 | 17 | 0.0067042 | 0.0016802 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2581-52_0_6_load_15 | 19 | 0.0067538 | 0.0016927 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2581-52_0_6_load_16 | 20 | 0.0067538 | 0.0016927 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2581-52_0_6_load_33 | 21 | 0.099228 | 0.024869 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2581-52_0_6_load_40 | 22 | 0.006776 | 0.0016982 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2581-52_0_6_load_32 | 23 | 0.021246 | 0.0053248 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2581-52_0_6_load_37 | 24 | 0.006724 | 0.0016852 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2581-52_0_6_load_17 | 25 | 0.0011494 | 0.00028808 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2581-52_0_6_load_18 | 26 | 0.00072183 | 0.00018091 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2581-52_0_6_load_19 | 27 | 0.00081948 | 0.00020538 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2581-52_0_6_load_20 | 28 | 0.00079949 | 0.00020037 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2581-52_0_6_load_21 | 29 | 0.0070767 | 0.0017736 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2581-52_0_6_load_34 | 31 | 0.011346 | 0.0028436 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2581-52_0_6_load_23 | 33 | 0.0091198 | 0.0022856 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2581-52_0_6_load_36 | 34 | 0.0067569 | 0.0016934 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2581-52_0_6_load_24 | 35 | 0.0033876 | 0.00084901 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2581-52_0_6_load_25 | 36 | 0.0050057 | 0.0012545 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2581-52_0_6_load_26 | 37 | 0.0033766 | 0.00084624 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2581-52_0_6_load_28 | 38 | 0.00071044 | 0.00017805 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2581-52_0_6_load_31 | 39 | 0.0052239 | 0.0013092 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2581-52_0_6_line_0 |  | 0 | 1 | 0.020261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2581-52_0_6_line_1 |  | 0 | 2 | 0.034556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2581-52_0_6_line_2 |  | 1 | 3 | 0.024074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2581-52_0_6_line_3 |  | 2 | 4 | 0.033662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2581-52_0_6_line_4 |  | 3 | 5 | 0.004205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2581-52_0_6_line_5 |  | 5 | 6 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2581-52_0_6_line_6 |  | 5 | 7 | 0.0023586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2581-52_0_6_line_7 |  | 6 | 11 | 0.0023872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2581-52_0_6_line_8 |  | 7 | 8 | 0.021942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2581-52_0_6_line_9 |  | 8 | 9 | 0.0081792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2581-52_0_6_line_10 |  | 9 | 10 | 0.0056251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2581-52_0_6_line_11 |  | 10 | 12 | 0.001335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2581-52_0_6_line_12 |  | 11 | 13 | 0.046882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2581-52_0_6_line_13 |  | 12 | 36 | 0.015305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2581-52_0_6_line_14 |  | 13 | 18 | 0.03202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2581-52_0_6_line_15 |  | 14 | 15 | 0.0016102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2581-52_0_6_line_16 |  | 14 | 16 | 0.008191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2581-52_0_6_line_17 |  | 15 | 17 | 0.02583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2581-52_0_6_line_18 |  | 16 | 18 | 0.013639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2581-52_0_6_line_19 |  | 16 | 19 | 0.014921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2581-52_0_6_line_20 |  | 17 | 20 | 0.012566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2581-52_0_6_line_21 |  | 18 | 21 | 0.022768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2581-52_0_6_line_22 |  | 19 | 22 | 0.002518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2581-52_0_6_line_23 |  | 21 | 23 | 0.0093968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2581-52_0_6_line_24 |  | 22 | 24 | 0.020419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2581-52_0_6_line_25 |  | 23 | 39 | 0.028789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2581-52_0_6_line_26 |  | 24 | 34 | 0.0010899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2581-52_0_6_line_27 |  | 25 | 26 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2581-52_0_6_line_28 |  | 25 | 27 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2581-52_0_6_line_29 |  | 26 | 28 | 0.0073711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2581-52_0_6_line_30 |  | 27 | 29 | 0.073943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2581-52_0_6_line_31 |  | 28 | 30 | 0.069039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2581-52_0_6_line_32 |  | 30 | 31 | 0.01685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2581-52_0_6_line_33 |  | 30 | 32 | 0.039723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2581-52_0_6_line_34 |  | 32 | 38 | 0.046194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2581-52_0_6_line_35 |  | 33 | 34 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2581-52_0_6_line_36 |  | 35 | 36 | 0.035223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2581-52_0_6_line_37 |  | 35 | 37 | 0.03568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2581-52_0_6_line_38 |  | 37 | 38 | 0.027864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2581-52_0_6_trafo_38 | 0.63 MVA 20/0.4 kV | 40 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2636259.9941 | 1246421.459 | 2636263.6016 | 1246404.0723 | 2636264.0642 | 1246401.6116
1 | 2636259.9941 | 1246421.459 | 2636258.1457 | 1246430.3673 | 2636258.5801 | 1246435.918 | 2636262.6326 | 1246441.4909 | 2636268.3738 | 1246445.1283 | 2636274.2792 | 1246447.0265
2 | 2636268.5125 | 1246377.9519 | 2636264.0642 | 1246401.6116
3 | 2636306.3263 | 1246457.3275 | 2636274.2792 | 1246447.0265
4 | 2636264.4169 | 1246376.9484 | 2636268.5125 | 1246377.9519
5 | 2636264.4169 | 1246376.9484 | 2636259.8965 | 1246397.1426
6 | 2636264.4169 | 1246376.9484 | 2636264.9322 | 1246374.6468
7 | 2636259.8965 | 1246397.1426 | 2636259.3751 | 1246399.4721
8 | 2636264.9322 | 1246374.6468 | 2636269.7259 | 1246353.2351
9 | 2636269.7259 | 1246353.2351 | 2636271.5128 | 1246345.2535
10 | 2636271.5128 | 1246345.2535 | 2636272.7417 | 1246339.7643
11 | 2636273.0334 | 1246338.4616 | 2636272.7417 | 1246339.7643
12 | 2636249.1341 | 1246445.222 | 2636259.3751 | 1246399.4721
13 | 2636276.377 | 1246323.5265 | 2636273.0334 | 1246338.4616
14 | 2636249.1341 | 1246445.222 | 2636218.5717 | 1246435.3846
15 | 2636219.8536 | 1246443.0071 | 2636218.3271 | 1246442.4947
16 | 2636227.619 | 1246445.6132 | 2636219.8536 | 1246443.0071
17 | 2636193.839 | 1246434.2764 | 2636218.3271 | 1246442.4947
18 | 2636227.619 | 1246445.6132 | 2636218.5717 | 1246435.3846
19 | 2636227.619 | 1246445.6132 | 2636241.3771 | 1246451.3888
20 | 2636193.839 | 1246434.2764 | 2636181.9264 | 1246430.2785
21 | 2636218.5717 | 1246435.3846 | 2636197.0116 | 1246428.0658
22 | 2636243.6988 | 1246452.3635 | 2636241.3771 | 1246451.3888
23 | 2636188.104 | 1246425.0735 | 2636192.4901 | 1246426.5309 | 2636197.0116 | 1246428.0658
24 | 2636243.6988 | 1246452.3635 | 2636246.4322 | 1246453.5109 | 2636263.1943 | 1246458.3786
25 | 2636188.104 | 1246425.0735 | 2636160.7835 | 1246415.9959
26 | 2636264.2409 | 1246458.6825 | 2636263.1943 | 1246458.3786
27 | 2636343.2127 | 1246252.7618 | 2636345.329 | 1246265.2923 | 2636347.9869 | 1246272.907
28 | 2636354.0603 | 1246289.2844 | 2636352.0844 | 1246284.6463 | 2636347.9869 | 1246272.907
29 | 2636341.9852 | 1246245.4936 | 2636343.2127 | 1246252.7618
30 | 2636354.0603 | 1246289.2844 | 2636361.0503 | 1246305.6928 | 2636365.5628 | 1246318.7845 | 2636367.3098 | 1246327.0784 | 2636367.9455 | 1246336.7331 | 2636367.3198 | 1246345.1681 | 2636365.014 | 1246360.648
31 | 2636325.4902 | 1246179.2924 | 2636324.9548 | 1246189.0066 | 2636326.6628 | 1246197.5115 | 2636336.3412 | 1246219.4295 | 2636341.0865 | 1246240.1721 | 2636341.9852 | 1246245.4936
32 | 2636325.4902 | 1246179.2924 | 2636328.8339 | 1246168.6281 | 2636330.2548 | 1246163.1348
33 | 2636325.4902 | 1246179.2924 | 2636317.7056 | 1246178.7 | 2636298.6866 | 1246178.3946 | 2636291.7924 | 1246180.4427 | 2636286.4379 | 1246182.7115
34 | 2636286.4379 | 1246182.7115 | 2636291.2254 | 1246192.8585 | 2636294.3756 | 1246201.4834 | 2636296.5619 | 1246209.602 | 2636297.2516 | 1246217.8783 | 2636297.0121 | 1246222.4465 | 2636296.802 | 1246225.9253 | 2636296.717 | 1246226.9416
35 | 2636280.7929 | 1246463.6291 | 2636276.1558 | 1246462.1425 | 2636264.2409 | 1246458.6825
36 | 2636276.377 | 1246323.5265 | 2636284.0723 | 1246289.1543
37 | 2636291.868 | 1246254.3366 | 2636291.6984 | 1246255.0909 | 2636284.0723 | 1246289.1543
38 | 2636291.868 | 1246254.3366 | 2636294.6414 | 1246242.0004 | 2636296.1255 | 1246234.0153 | 2636296.717 | 1246226.9416

## bus_geodata
| x | y | coords
0 | 2636259.9941 | 1246421.459
1 | 2636264.0642 | 1246401.6116
2 | 2636274.2792 | 1246447.0265
3 | 2636268.5125 | 1246377.9519
4 | 2636306.3263 | 1246457.3275
5 | 2636264.4169 | 1246376.9484
6 | 2636259.8965 | 1246397.1426
7 | 2636264.9322 | 1246374.6468
8 | 2636269.7259 | 1246353.2351
9 | 2636271.5128 | 1246345.2535
10 | 2636272.7417 | 1246339.7643
11 | 2636259.3751 | 1246399.4721
12 | 2636273.0334 | 1246338.4616
13 | 2636249.1341 | 1246445.222
14 | 2636219.8536 | 1246443.0071
15 | 2636218.3271 | 1246442.4947
16 | 2636227.619 | 1246445.6132
17 | 2636193.839 | 1246434.2764
18 | 2636218.5717 | 1246435.3846
19 | 2636241.3771 | 1246451.3888
20 | 2636181.9264 | 1246430.2785
21 | 2636197.0116 | 1246428.0658
22 | 2636243.6988 | 1246452.3635
23 | 2636188.104 | 1246425.0735
24 | 2636263.1943 | 1246458.3786
25 | 2636347.9869 | 1246272.907
26 | 2636343.2127 | 1246252.7618
27 | 2636354.0603 | 1246289.2844
28 | 2636341.9852 | 1246245.4936
29 | 2636365.014 | 1246360.648
30 | 2636325.4902 | 1246179.2924
31 | 2636330.2548 | 1246163.1348
32 | 2636286.4379 | 1246182.7115
33 | 2636280.7929 | 1246463.6291
34 | 2636264.2409 | 1246458.6825
35 | 2636284.0723 | 1246289.1543
36 | 2636276.377 | 1246323.5265
37 | 2636291.868 | 1246254.3366
38 | 2636296.717 | 1246226.9416
39 | 2636160.7835 | 1246415.9959
40 | 2636264.4169 | 1246376.9484

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99294 | -0.13508 | 0.0041071 | 0.0010293
1 | 0.9949 | -0.097461 | 0.01066 | 0.0026717
2 | 0.98973 | -0.19705 | 0.01357 | 0.003401
3 | 0.99746 | -0.04846 | 0 | 0
4 | 0.98703 | -0.24963 | 0.087548 | 0.021942
5 | 0.99791 | -0.039927 | 0.029635 | 0.0074272
6 | 0.99977 | -0.0043031 | 0.014585 | 0.0036553
7 | 0.99775 | -0.043025 | 0.030399 | 0.0076187
8 | 0.99535 | -0.089117 | 0.027835 | 0.0069761
9 | 0.99467 | -0.10234 | 0.0050365 | 0.0012623
10 | 0.99422 | -0.11095 | 0.039568 | 0.0099166
11 | 1 | 0 | -0.50406 | -0.12725
12 | 0.99416 | -0.11206 | 0.012846 | 0.0032194
13 | 0.9973 | -0.051557 | 0 | 0
14 | 0.99355 | -0.12373 | 0.0067488 | 0.0016914
15 | 0.99352 | -0.12431 | 0.0067316 | 0.0016871
16 | 0.99376 | -0.11984 | 0 | 0
17 | 0.99321 | -0.13045 | 0.0067042 | 0.0016802
18 | 0.99454 | -0.10467 | 0 | 0
19 | 0.99326 | -0.12936 | 0.0067538 | 0.0016927
20 | 0.99313 | -0.13195 | 0.0067538 | 0.0016927
21 | 0.99192 | -0.15523 | 0.099228 | 0.024869
22 | 0.9932 | -0.13066 | 0.006776 | 0.0016982
23 | 0.9917 | -0.15964 | 0.021246 | 0.0053248
24 | 0.99277 | -0.13882 | 0.006724 | 0.0016852
25 | 0.98867 | -0.21836 | 0.0011494 | 0.00028808
26 | 0.98884 | -0.215 | 0.00072183 | 0.00018091
27 | 0.98854 | -0.22082 | 0.00081948 | 0.00020538
28 | 0.98891 | -0.21372 | 0.00079949 | 0.00020037
29 | 0.98806 | -0.23016 | 0.0070767 | 0.0017736
30 | 0.98958 | -0.20072 | 0 | 0
31 | 0.9894 | -0.20412 | 0.011346 | 0.0028436
32 | 0.99037 | -0.18524 | 0 | 0
33 | 0.99261 | -0.14191 | 0.0091198 | 0.0022856
34 | 0.99276 | -0.13913 | 0.0067569 | 0.0016934
35 | 0.99273 | -0.13965 | 0.0033876 | 0.00084901
36 | 0.99368 | -0.12135 | 0.0050057 | 0.0012545
37 | 0.99188 | -0.15608 | 0.0033766 | 0.00084624
38 | 0.9913 | -0.16726 | 0.00071044 | 0.00017805
39 | 0.99156 | -0.1623 | 0.0052239 | 0.0013092
40 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.10575 | -0.026704 | 0.10594 | 0.026826 | 0.00019098 | 0.00012196 | 0.15854 | 0.15854 | 0.15854 | 0.99294 | -0.13508 | 0.9949 | -0.097461 | 43.5556
1 | 0.10164 | 0.025675 | -0.10134 | -0.025483 | 0.00030092 | 0.00019214 | 0.15239 | 0.15239 | 0.15239 | 0.99294 | -0.13508 | 0.98973 | -0.19705 | 41.8647
2 | -0.1166 | -0.029498 | 0.11687 | 0.029674 | 0.00027486 | 0.00017559 | 0.17449 | 0.17449 | 0.17449 | 0.9949 | -0.097461 | 0.99746 | -0.04846 | 47.9358
3 | 0.087768 | 0.022082 | -0.087548 | -0.021942 | 0.0002199 | 0.0001403 | 0.13199 | 0.13199 | 0.13199 | 0.98973 | -0.19705 | 0.98703 | -0.24963 | 36.2598
4 | -0.11687 | -0.029674 | 0.11692 | 0.029704 | 4.8009e-05 | 3.0671e-05 | 0.17449 | 0.17449 | 0.17449 | 0.99746 | -0.04846 | 0.99791 | -0.039927 | 47.9358
5 | -0.29714 | -0.075063 | 0.29765 | 0.075387 | 0.00050829 | 0.00032449 | 0.44328 | 0.44328 | 0.44328 | 0.99791 | -0.039927 | 0.99977 | -0.0043031 | 40.5936
6 | 0.15058 | 0.037931 | -0.15056 | -0.037917 | 2.231e-05 | 1.4217e-05 | 0.22461 | 0.22461 | 0.22461 | 0.99791 | -0.039927 | 0.99775 | -0.043025 | 30.8526
7 | -0.31223 | -0.079042 | 0.3123 | 0.079084 | 6.4517e-05 | 4.1197e-05 | 0.46499 | 0.46499 | 0.46499 | 0.99977 | -0.0043031 | 1 | 0 | 42.5814
8 | 0.12016 | 0.030298 | -0.1199 | -0.030129 | 0.00026444 | 0.00016895 | 0.17927 | 0.17927 | 0.17927 | 0.99775 | -0.043025 | 0.99535 | -0.089117 | 49.2502
9 | 0.092063 | 0.023153 | -0.092004 | -0.023116 | 5.8123e-05 | 3.7093e-05 | 0.13766 | 0.13766 | 0.13766 | 0.99535 | -0.089117 | 0.99467 | -0.10234 | 37.8183
10 | 0.086968 | 0.021854 | -0.086932 | -0.021831 | 3.5717e-05 | 2.2786e-05 | 0.13012 | 0.13012 | 0.13012 | 0.99467 | -0.10234 | 0.99422 | -0.11095 | 35.7484
11 | 0.047364 | 0.011914 | -0.047362 | -0.011913 | 2.5168e-06 | 1.5934e-06 | 0.070904 | 0.070904 | 0.070904 | 0.99422 | -0.11095 | 0.99416 | -0.11206 | 19.4792
12 | 0.19011 | 0.048165 | -0.18964 | -0.047866 | 0.00046958 | 0.00029869 | 0.28307 | 0.28307 | 0.28307 | 1 | 0 | 0.9973 | -0.051557 | 25.9224
13 | 0.034516 | 0.0086934 | -0.034501 | -0.0086838 | 1.5327e-05 | 9.611e-06 | 0.051678 | 0.051678 | 0.051678 | 0.99416 | -0.11206 | 0.99368 | -0.12135 | 14.1972
14 | 0.18964 | 0.047866 | -0.18916 | -0.047559 | 0.00048108 | 0.00030706 | 0.28307 | 0.28307 | 0.28307 | 0.9973 | -0.051557 | 0.99454 | -0.10467 | 38.8836
15 | 0.020195 | 0.0050627 | -0.020194 | -0.0050623 | 5.5238e-07 | 3.3267e-07 | 0.030245 | 0.030245 | 0.030245 | 0.99355 | -0.12373 | 0.99352 | -0.12431 | 8.3092
16 | -0.026943 | -0.0067541 | 0.026948 | 0.0067572 | 5.0017e-06 | 3.095e-06 | 0.040353 | 0.040353 | 0.040353 | 0.99355 | -0.12373 | 0.99376 | -0.11984 | 11.086
17 | 0.013462 | 0.0033752 | -0.013458 | -0.003373 | 3.9381e-06 | 2.186e-06 | 0.020163 | 0.020163 | 0.020163 | 0.99352 | -0.12431 | 0.99321 | -0.13045 | 5.5394
18 | -0.063108 | -0.01583 | 0.063153 | 0.015859 | 4.5675e-05 | 2.9055e-05 | 0.0945 | 0.0945 | 0.0945 | 0.99376 | -0.11984 | 0.99454 | -0.10467 | 25.9615
19 | 0.036159 | 0.0090727 | -0.036143 | -0.0090624 | 1.6405e-05 | 1.0306e-05 | 0.054147 | 0.054147 | 0.054147 | 0.99376 | -0.11984 | 0.99326 | -0.12936 | 14.8756
20 | 0.0067543 | 0.0016928 | -0.0067538 | -0.0016927 | 4.8252e-07 | 1.4621e-07 | 0.010119 | 0.010119 | 0.010119 | 0.99321 | -0.13045 | 0.99313 | -0.13195 | 2.78
21 | 0.12601 | 0.0317 | -0.1257 | -0.031506 | 0.00030362 | 0.00019402 | 0.18857 | 0.18857 | 0.18857 | 0.99454 | -0.10467 | 0.99192 | -0.15523 | 51.8058
22 | 0.029389 | 0.0073697 | -0.029387 | -0.0073686 | 1.8305e-06 | 1.1389e-06 | 0.044029 | 0.044029 | 0.044029 | 0.99326 | -0.12936 | 0.9932 | -0.13066 | 12.0959
23 | 0.026476 | 0.0066375 | -0.026471 | -0.0066341 | 5.559e-06 | 3.4365e-06 | 0.039718 | 0.039719 | 0.039719 | 0.99192 | -0.15523 | 0.9917 | -0.15964 | 10.9117
24 | 0.022611 | 0.0056703 | -0.022602 | -0.005665 | 8.7879e-06 | 5.3601e-06 | 0.033877 | 0.033877 | 0.033877 | 0.9932 | -0.13066 | 0.99277 | -0.13882 | 9.307
25 | 0.0052246 | 0.0013093 | -0.0052239 | -0.0013092 | 6.6347e-07 | 5.3224e-08 | 0.0078393 | 0.0078394 | 0.0078394 | 0.9917 | -0.15964 | 0.99156 | -0.1623 | 2.1537
26 | 0.015878 | 0.0039798 | -0.015878 | -0.0039796 | 2.3148e-07 | 1.3406e-07 | 0.023799 | 0.023799 | 0.023799 | 0.99277 | -0.13882 | 0.99276 | -0.13913 | 6.5382
27 | -0.0090497 | -0.0022685 | 0.0090511 | 0.0022691 | 1.4452e-06 | 6.5848e-07 | 0.013621 | 0.01362 | 0.013621 | 0.98867 | -0.21836 | 0.98884 | -0.215 | 3.7419
28 | 0.0079003 | 0.0019804 | -0.0078993 | -0.00198 | 9.2654e-07 | 3.6892e-07 | 0.011891 | 0.011891 | 0.011891 | 0.98867 | -0.21836 | 0.98854 | -0.22082 | 3.2667
29 | -0.009773 | -0.00245 | 0.0097736 | 0.0024503 | 5.9785e-07 | 2.8806e-07 | 0.014707 | 0.014707 | 0.014707 | 0.98884 | -0.215 | 0.98891 | -0.21372 | 4.0403
30 | 0.0070798 | 0.0017747 | -0.0070767 | -0.0017736 | 3.1494e-06 | 1.0681e-06 | 0.010657 | 0.010657 | 0.010657 | 0.98854 | -0.22082 | 0.98806 | -0.23016 | 2.9279
31 | -0.010573 | -0.0026507 | 0.01058 | 0.002654 | 6.5529e-06 | 3.3075e-06 | 0.01591 | 0.015909 | 0.01591 | 0.98891 | -0.21372 | 0.98958 | -0.20072 | 4.3708
32 | 0.011348 | 0.0028445 | -0.011346 | -0.0028436 | 1.8399e-06 | 9.6108e-07 | 0.017064 | 0.017064 | 0.017064 | 0.98958 | -0.20072 | 0.9894 | -0.20412 | 4.6879
33 | -0.021927 | -0.0054985 | 0.021944 | 0.0055084 | 1.6195e-05 | 9.8543e-06 | 0.032973 | 0.032973 | 0.032973 | 0.98958 | -0.20072 | 0.99037 | -0.18524 | 9.0585
34 | -0.021944 | -0.0055084 | 0.021962 | 0.0055198 | 1.8833e-05 | 1.1458e-05 | 0.032973 | 0.032973 | 0.032973 | 0.99037 | -0.18524 | 0.9913 | -0.16726 | 9.0585
35 | -0.0091198 | -0.0022856 | 0.009121 | 0.0022862 | 1.2109e-06 | 5.5163e-07 | 0.013671 | 0.013671 | 0.013671 | 0.99261 | -0.14191 | 0.99276 | -0.13913 | 3.7559
36 | -0.02947 | -0.0074132 | 0.029495 | 0.0074292 | 2.5784e-05 | 1.6046e-05 | 0.044182 | 0.044182 | 0.044182 | 0.99273 | -0.13965 | 0.99368 | -0.12135 | 12.1379
37 | 0.026082 | 0.0065642 | -0.026062 | -0.0065515 | 2.046e-05 | 1.2633e-05 | 0.039104 | 0.039104 | 0.039104 | 0.99273 | -0.13965 | 0.99188 | -0.15608 | 10.743
38 | 0.022685 | 0.0057053 | -0.022673 | -0.0056979 | 1.2107e-05 | 7.389e-06 | 0.034039 | 0.034039 | 0.034039 | 0.99188 | -0.15608 | 0.9913 | -0.16726 | 9.3514

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51395 | 0.12973

## res_load
| p_mw | q_mvar
0 | 0.0041071 | 0.0010293
1 | 0.01066 | 0.0026717
2 | 0.01357 | 0.003401
3 | 0.087548 | 0.021942
4 | 0.029635 | 0.0074272
5 | 0.014585 | 0.0036553
6 | 0.030399 | 0.0076187
7 | 0.027835 | 0.0069761
8 | 0.0050365 | 0.0012623
9 | 0.039568 | 0.0099166
10 | 0.009893 | 0.0024794
11 | 0.012846 | 0.0032194
12 | 0.0067488 | 0.0016914
13 | 0.0067316 | 0.0016871
14 | 0.0067042 | 0.0016802
15 | 0.0067538 | 0.0016927
16 | 0.0067538 | 0.0016927
17 | 0.099228 | 0.024869
18 | 0.006776 | 0.0016982
19 | 0.021246 | 0.0053248
20 | 0.006724 | 0.0016852
21 | 0.0011494 | 0.00028808
22 | 0.00072183 | 0.00018091
23 | 0.00081948 | 0.00020538
24 | 0.00079949 | 0.00020037
25 | 0.0070767 | 0.0017736
26 | 0.011346 | 0.0028436
27 | 0.0091198 | 0.0022856
28 | 0.0067569 | 0.0016934
29 | 0.0033876 | 0.00084901
30 | 0.0050057 | 0.0012545
31 | 0.0033766 | 0.00084624
32 | 0.00071044 | 0.00017805
33 | 0.0052239 | 0.0013092

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1