## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2583-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2583-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2583-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2583-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2583-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2583-5_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2583-5_0_4_node_81 | 0.4 | n |  | TRUE
7 | bus_LV_2583-5_0_4_node_181 | 0.4 | n |  | TRUE
8 | bus_LV_2583-5_0_4_node_125 | 0.4 | n |  | TRUE
9 | bus_LV_2583-5_0_4_node_82 | 0.4 | n |  | TRUE
10 | bus_LV_2583-5_0_4_node_192 | 0.4 | n |  | TRUE
11 | bus_LV_2583-5_0_4_node_227 | 0.4 | n |  | TRUE
12 | bus_LV_2583-5_0_4_node_183 | 0.4 | n |  | TRUE
13 | bus_LV_2583-5_0_4_node_180 | 0.4 | n |  | TRUE
14 | bus_LV_2583-5_0_4_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_2583-5_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_2583-5_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2583-5_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2583-5_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2583-5_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2583-5_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2583-5_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2583-5_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2583-5_0_4_node_83 | 0.4 | n |  | TRUE
24 | bus_LV_2583-5_0_4_node_95 | 0.4 | n |  | TRUE
25 | bus_LV_2583-5_0_4_node_199 | 0.4 | n |  | TRUE
26 | bus_LV_2583-5_0_4_node_131 | 0.4 | n |  | TRUE
27 | bus_LV_2583-5_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2583-5_0_4_node_84 | 0.4 | n |  | TRUE
29 | bus_LV_2583-5_0_4_node_197 | 0.4 | n |  | TRUE
30 | bus_LV_2583-5_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2583-5_0_4_node_129 | 0.4 | n |  | TRUE
32 | bus_LV_2583-5_0_4_node_157 | 0.4 | n |  | TRUE
33 | bus_LV_2583-5_0_4_node_155 | 0.4 | n |  | TRUE
34 | bus_LV_2583-5_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2583-5_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2583-5_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2583-5_0_4_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_2583-5_0_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_2583-5_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_2583-5_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2583-5_0_4_node_169 | 0.4 | n |  | TRUE
42 | bus_LV_2583-5_0_4_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_2583-5_0_4_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2583-5_0_4_node_102 | 0.4 | n |  | TRUE
45 | bus_LV_2583-5_0_4_node_207 | 0.4 | n |  | TRUE
46 | bus_LV_2583-5_0_4_node_171 | 0.4 | n |  | TRUE
47 | bus_LV_2583-5_0_4_node_161 | 0.4 | n |  | TRUE
48 | bus_LV_2583-5_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_2583-5_0_4_node_103 | 0.4 | n |  | TRUE
50 | bus_LV_2583-5_0_4_node_208 | 0.4 | n |  | TRUE
51 | bus_LV_2583-5_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2583-5_0_4_node_165 | 0.4 | n |  | TRUE
53 | bus_LV_2583-5_0_4_node_145 | 0.4 | n |  | TRUE
54 | bus_LV_2583-5_0_4_node_159 | 0.4 | n |  | TRUE
55 | bus_LV_2583-5_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_2583-5_0_4_node_173 | 0.4 | n |  | TRUE
57 | bus_LV_2583-5_0_4_node_172 | 0.4 | n |  | TRUE
58 | bus_LV_2583-5_0_4_node_63 | 0.4 | n |  | TRUE
59 | bus_LV_2583-5_0_4_node_232 | 0.4 | n |  | TRUE
60 | bus_LV_2583-5_0_4_node_220 | 0.4 | n |  | TRUE
61 | bus_LV_2583-5_0_4_node_230 | 0.4 | n |  | TRUE
62 | bus_LV_2583-5_0_4_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_2583-5_0_4_node_233 | 0.4 | n |  | TRUE
64 | bus_LV_2583-5_0_4_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_2583-5_0_4_node_70 | 0.4 | n |  | TRUE
66 | bus_LV_2583-5_0_4_node_71 | 0.4 | n |  | TRUE
67 | bus_LV_2583-5_0_4_node_72 | 0.4 | n |  | TRUE
68 | bus_LV_2583-5_0_4_node_73 | 0.4 | n |  | TRUE
69 | bus_LV_2583-5_0_4_node_198 | 0.4 | n |  | TRUE
70 | bus_LV_2583-5_0_4_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2583-5_0_4_node_196 | 0.4 | n |  | TRUE
72 | bus_LV_2583-5_0_4_node_80 | 0.4 | n |  | TRUE
73 | bus_LV_2583-5_0_4_node_79 | 0.4 | n |  | TRUE
74 | bus_LV_2583-5_0_4_node_150 | 0.4 | n |  | TRUE
75 | bus_LV_2583-5_0_4_node_148 | 0.4 | n |  | TRUE
76 | bus_LV_2583-5_0_4_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_2583-5_0_4_node_184 | 0.4 | n |  | TRUE
78 | bus_LV_2583-5_0_4_node_99 | 0.4 | n |  | TRUE
79 | bus_LV_2583-5_0_4_node_179 | 0.4 | n |  | TRUE
80 | bus_LV_2583-5_0_4_node_191 | 0.4 | n |  | TRUE
81 | bus_LV_2583-5_0_4_node_178 | 0.4 | n |  | TRUE
82 | bus_LV_2583-5_0_4_node_93 | 0.4 | n |  | TRUE
83 | bus_LV_2583-5_0_4_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_2583-5_0_4_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_2583-5_0_4_node_92 | 0.4 | n |  | TRUE
86 | bus_LV_2583-5_0_4_node_94 | 0.4 | n |  | TRUE
87 | bus_LV_2583-5_0_4_node_228 | 0.4 | n |  | TRUE
88 | bus_LV_2583-5_0_4_node_97 | 0.4 | n |  | TRUE
89 | bus_LV_2583-5_0_4_node_98 | 0.4 | n |  | TRUE
90 | bus_LV_2583-5_0_4_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_2583-5_0_4_node_110 | 0.4 | n |  | TRUE
92 | bus_LV_2583-5_0_4_node_189 | 0.4 | n |  | TRUE
93 | bus_LV_2583-5_0_4_node_209 | 0.4 | n |  | TRUE
94 | bus_LV_2583-5_0_4_node_104 | 0.4 | n |  | TRUE
95 | bus_LV_2583-5_0_4_node_190 | 0.4 | n |  | TRUE
96 | bus_LV_2583-5_0_4_node_111 | 0.4 | n |  | TRUE
97 | bus_LV_2583-5_0_4_node_112 | 0.4 | n |  | TRUE
98 | bus_LV_2583-5_0_4_node_113 | 0.4 | n |  | TRUE
99 | bus_LV_2583-5_0_4_node_114 | 0.4 | n |  | TRUE
100 | bus_LV_2583-5_0_4_node_115 | 0.4 | n |  | TRUE
101 | bus_LV_2583-5_0_4_node_170 | 0.4 | n |  | TRUE
102 | bus_LV_2583-5_0_4_node_215 | 0.4 | n |  | TRUE
103 | bus_LV_2583-5_0_4_node_146 | 0.4 | n |  | TRUE
104 | bus_LV_2583-5_0_4_node_126 | 0.4 | n |  | TRUE
105 | bus_LV_2583-5_0_4_node_127 | 0.4 | n |  | TRUE
106 | bus_LV_2583-5_0_4_node_128 | 0.4 | n |  | TRUE
107 | bus_LV_2583-5_0_4_node_130 | 0.4 | n |  | TRUE
108 | bus_LV_2583-5_0_4_node_142 | 0.4 | n |  | TRUE
109 | bus_LV_2583-5_0_4_node_143 | 0.4 | n |  | TRUE
110 | bus_LV_2583-5_0_4_node_147 | 0.4 | n |  | TRUE
111 | bus_LV_2583-5_0_4_node_149 | 0.4 | n |  | TRUE
112 | bus_LV_2583-5_0_4_node_154 | 0.4 | n |  | TRUE
113 | bus_LV_2583-5_0_4_node_156 | 0.4 | n |  | TRUE
114 | bus_LV_2583-5_0_4_node_158 | 0.4 | n |  | TRUE
115 | bus_LV_2583-5_0_4_node_237 | 0.4 | n |  | TRUE
116 | bus_LV_2583-5_0_4_node_236 | 0.4 | n |  | TRUE
117 | bus_LV_2583-5_0_4_node_160 | 0.4 | n |  | TRUE
118 | bus_LV_2583-5_0_4_node_182 | 0.4 | n |  | TRUE
119 | bus_LV_2583-5_0_4_node_210 | 0.4 | n |  | TRUE
120 | bus_LV_2583-5_0_4_node_221 | 0.4 | n |  | TRUE
121 | bus_LV_2583-5_0_4_node_226 | 0.4 | n |  | TRUE
122 | bus_LV_2583-5_0_4_node_234 | 0.4 | n |  | TRUE
123 | bus_LV_2583-5_0_4_node_235 | 0.4 | n |  | TRUE
124 | bus_MV_390_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2583-5_0_4_load_0 | 0 | 0.0020729 | 0.00051951 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2583-5_0_4_load_1 | 1 | 0.00090633 | 0.00022715 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2583-5_0_4_load_3 | 3 | 0.0010212 | 0.00025593 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2583-5_0_4_load_5 | 5 | 0.0010062 | 0.00025217 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2583-5_0_4_load_81 | 6 | 0.00097246 | 0.00024372 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2583-5_0_4_load_181 | 7 | 0.0013031 | 0.00032659 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2583-5_0_4_load_125 | 8 | 0.00084913 | 0.00021281 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2583-5_0_4_load_82 | 9 | 0.001103 | 0.00027643 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2583-5_0_4_load_227 | 11 | 0.0066351 | 0.0016629 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2583-5_0_4_load_183 | 12 | 0.0010091 | 0.0002529 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2583-5_0_4_load_180 | 13 | 0.0043312 | 0.0010855 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2583-5_0_4_load_124 | 14 | 0.0011201 | 0.00028073 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2583-5_0_4_load_6 | 15 | 0.0011678 | 0.00029268 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2583-5_0_4_load_7 | 16 | 0.00089627 | 0.00022463 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2583-5_0_4_load_10 | 19 | 0.0028099 | 0.00070423 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2583-5_0_4_load_11 | 20 | 0.0012546 | 0.00031444 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2583-5_0_4_load_12 | 21 | 0.0011137 | 0.00027912 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2583-5_0_4_load_83 | 23 | 0.0018602 | 0.00046621 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2583-5_0_4_load_95 | 24 | 0.0012898 | 0.00032325 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2583-5_0_4_load_199 | 25 | 0.0011017 | 0.00027611 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2583-5_0_4_load_131 | 26 | 0.0043282 | 0.0010848 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2583-5_0_4_load_197 | 29 | 0.00089115 | 0.00022334 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2583-5_0_4_load_23 | 30 | 0.0077873 | 0.0019517 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2583-5_0_4_load_129 | 31 | 0.01328 | 0.0033282 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2583-5_0_4_load_157 | 32 | 0.00090878 | 0.00022776 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2583-5_0_4_load_155 | 33 | 0.00040101 | 0.0001005 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2583-5_0_4_load_33 | 34 | 0.014132 | 0.0035419 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2583-5_0_4_load_40 | 40 | 0.00097072 | 0.00024329 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2583-5_0_4_load_169 | 41 | 0.011798 | 0.0029567 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2583-5_0_4_load_44 | 42 | 0.0014374 | 0.00036024 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2583-5_0_4_load_41 | 43 | 0.0028715 | 0.00071968 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2583-5_0_4_load_102 | 44 | 0.0025681 | 0.00064362 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2583-5_0_4_load_207 | 45 | 0.016793 | 0.0042086 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2583-5_0_4_load_171 | 46 | 0.015737 | 0.003944 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2583-5_0_4_load_103 | 49 | 0.00096294 | 0.00024134 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2583-5_0_4_load_208 | 50 | 0.015928 | 0.0039919 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2583-5_0_4_load_165 | 52 | 0.0010964 | 0.00027479 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2583-5_0_4_load_159 | 54 | 0.0018766 | 0.00047033 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2583-5_0_4_load_173 | 56 | 0.0077754 | 0.0019487 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2583-5_0_4_load_172 | 57 | 0.0034186 | 0.00085678 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2583-5_0_4_load_63 | 58 | 0.0049178 | 0.0012325 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2583-5_0_4_load_232 | 59 | 0.0040219 | 0.001008 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2583-5_0_4_load_220 | 60 | 0.0025113 | 0.0006294 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2583-5_0_4_load_230 | 61 | 0.0035414 | 0.00088756 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2583-5_0_4_load_78 | 62 | 0.0042541 | 0.0010662 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2583-5_0_4_load_233 | 63 | 0.0043007 | 0.0010779 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2583-5_0_4_load_69 | 64 | 0.0018866 | 0.00047283 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2583-5_0_4_load_70 | 65 | 0.0018288 | 0.00045835 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2583-5_0_4_load_71 | 66 | 0.0014915 | 0.00037379 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2583-5_0_4_load_72 | 67 | 0.0018281 | 0.00045816 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2583-5_0_4_load_73 | 68 | 0.0014958 | 0.00037489 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2583-5_0_4_load_198 | 69 | 0.0010835 | 0.00027156 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2583-5_0_4_load_196 | 71 | 0.0020136 | 0.00050467 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2583-5_0_4_load_80 | 72 | 0.0018636 | 0.00046707 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2583-5_0_4_load_79 | 73 | 0.0032475 | 0.00081389 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2583-5_0_4_load_150 | 74 | 0.0043568 | 0.0010919 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2583-5_0_4_load_184 | 77 | 0.00090483 | 0.00022677 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2583-5_0_4_load_99 | 78 | 0.00080028 | 0.00020057 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2583-5_0_4_load_191 | 80 | 0.0018534 | 0.0004645 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2583-5_0_4_load_178 | 81 | 0.0007966 | 0.00019965 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2583-5_0_4_load_93 | 82 | 0.0018781 | 0.0004707 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2583-5_0_4_load_90 | 83 | 0.0018701 | 0.00046868 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2583-5_0_4_load_91 | 84 | 0.0017452 | 0.0004374 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2583-5_0_4_load_92 | 85 | 0.00095586 | 0.00023956 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2583-5_0_4_load_97 | 88 | 0.00091654 | 0.00022971 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2583-5_0_4_load_98 | 89 | 0.00076164 | 0.00019088 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2583-5_0_4_load_100 | 90 | 0.0027972 | 0.00070106 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2583-5_0_4_load_110 | 91 | 0.0013369 | 0.00033505 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2583-5_0_4_load_189 | 92 | 0.0017977 | 0.00045054 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2583-5_0_4_load_209 | 93 | 0.0028462 | 0.00071333 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2583-5_0_4_load_104 | 94 | 0.0064618 | 0.0016195 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2583-5_0_4_load_190 | 95 | 0.00098567 | 0.00024703 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2583-5_0_4_load_111 | 96 | 0.0084673 | 0.0021221 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2583-5_0_4_load_112 | 97 | 0.0088303 | 0.0022131 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2583-5_0_4_load_170 | 101 | 0.0067521 | 0.0016922 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2583-5_0_4_load_215 | 102 | 0.0066733 | 0.0016725 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2583-5_0_4_load_146 | 103 | 0.0035215 | 0.00088256 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2583-5_0_4_load_126 | 104 | 0.0018317 | 0.00045908 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2583-5_0_4_load_127 | 105 | 0.00075883 | 0.00019018 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2583-5_0_4_load_128 | 106 | 0.00076107 | 0.00019074 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2583-5_0_4_load_130 | 107 | 0.0012033 | 0.00030158 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2583-5_0_4_load_142 | 108 | 0.0013288 | 0.00033302 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2583-5_0_4_load_143 | 109 | 0.0012574 | 0.00031513 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2583-5_0_4_load_147 | 110 | 0.0034052 | 0.00085344 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2583-5_0_4_load_149 | 111 | 0.0038526 | 0.00096556 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2583-5_0_4_load_154 | 112 | 0.00040093 | 0.00010048 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2583-5_0_4_load_156 | 113 | 0.00040101 | 0.0001005 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2583-5_0_4_load_237 | 115 | 0.00040101 | 0.0001005 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2583-5_0_4_load_236 | 116 | 0.00040088 | 0.00010047 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2583-5_0_4_load_160 | 117 | 0.0048402 | 0.0012131 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2583-5_0_4_load_182 | 118 | 0.0019277 | 0.00048312 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2583-5_0_4_load_210 | 119 | 0.011521 | 0.0028873 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2583-5_0_4_load_221 | 120 | 0.0074243 | 0.0018607 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2583-5_0_4_load_226 | 121 | 0.00040101 | 0.0001005 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2583-5_0_4_load_234 | 122 | 0.00040128 | 0.00010057 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2583-5_0_4_load_235 | 123 | 0.00040128 | 0.00010057 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 103 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2583-5_0_4_line_0 |  | 0 | 1 | 0.015406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2583-5_0_4_line_1 |  | 0 | 2 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2583-5_0_4_line_2 |  | 1 | 3 | 0.0077673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2583-5_0_4_line_3 |  | 2 | 4 | 0.028941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2583-5_0_4_line_4 |  | 2 | 5 | 0.03783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2583-5_0_4_line_5 |  | 3 | 6 | 9.3037e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2583-5_0_4_line_6 |  | 4 | 7 | 0.012535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2583-5_0_4_line_7 |  | 5 | 8 | 0.0066076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2583-5_0_4_line_8 |  | 6 | 9 | 0.017935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2583-5_0_4_line_9 |  | 7 | 13 | 0.015411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2583-5_0_4_line_10 |  | 8 | 14 | 0.0011084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2583-5_0_4_line_11 |  | 9 | 79 | 0.037375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2583-5_0_4_line_12 |  | 10 | 11 | 0.035696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2583-5_0_4_line_13 |  | 10 | 12 | 0.010882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2583-5_0_4_line_14 |  | 11 | 87 | 0.018005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2583-5_0_4_line_15 |  | 12 | 118 | 0.024892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2583-5_0_4_line_16 |  | 14 | 104 | 0.0097105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2583-5_0_4_line_17 |  | 15 | 16 | 0.015101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2583-5_0_4_line_18 |  | 15 | 17 | 0.016134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2583-5_0_4_line_19 |  | 16 | 18 | 0.0074675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2583-5_0_4_line_20 |  | 17 | 19 | 0.041918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2583-5_0_4_line_21 |  | 17 | 20 | 0.014115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2583-5_0_4_line_22 |  | 17 | 21 | 0.016685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2583-5_0_4_line_23 |  | 18 | 22 | 0.024156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2583-5_0_4_line_24 |  | 19 | 23 | 0.0007173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2583-5_0_4_line_25 |  | 20 | 24 | 0.0076836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2583-5_0_4_line_26 |  | 21 | 25 | 0.0069044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2583-5_0_4_line_27 |  | 22 | 26 | 0.021114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2583-5_0_4_line_28 |  | 22 | 27 | 0.027767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2583-5_0_4_line_29 |  | 23 | 28 | 0.014921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2583-5_0_4_line_30 |  | 25 | 29 | 0.023485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2583-5_0_4_line_31 |  | 26 | 31 | 0.011488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2583-5_0_4_line_32 |  | 27 | 30 | 0.027703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2583-5_0_4_line_33 |  | 28 | 81 | 0.016121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2583-5_0_4_line_34 |  | 28 | 79 | 0.005544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2583-5_0_4_line_35 |  | 29 | 71 | 0.0047853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2583-5_0_4_line_36 |  | 31 | 105 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2583-5_0_4_line_37 |  | 32 | 33 | 0.034476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2583-5_0_4_line_38 |  | 33 | 112 | 0.00028582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2583-5_0_4_line_39 |  | 34 | 35 | 0.0094211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2583-5_0_4_line_40 |  | 34 | 36 | 0.02 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2583-5_0_4_line_41 |  | 35 | 37 | 0.011322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2583-5_0_4_line_42 |  | 35 | 38 | 0.088875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2583-5_0_4_line_43 |  | 36 | 39 | 0.028903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2583-5_0_4_line_44 |  | 36 | 40 | 0.0097765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2583-5_0_4_line_45 |  | 37 | 41 | 0.025331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2583-5_0_4_line_46 |  | 38 | 42 | 0.018608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2583-5_0_4_line_47 |  | 38 | 43 | 0.0020451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2583-5_0_4_line_48 |  | 39 | 44 | 0.025221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2583-5_0_4_line_49 |  | 40 | 45 | 0.0073361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2583-5_0_4_line_50 |  | 41 | 46 | 0.015893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2583-5_0_4_line_51 |  | 42 | 47 | 0.017608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2583-5_0_4_line_52 |  | 43 | 48 | 0.0089569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2583-5_0_4_line_53 |  | 44 | 49 | 0.0043398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2583-5_0_4_line_54 |  | 45 | 50 | 0.0088458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2583-5_0_4_line_55 |  | 46 | 99 | 0.018027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2583-5_0_4_line_56 |  | 47 | 53 | 0.10204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2583-5_0_4_line_57 |  | 47 | 54 | 0.047747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2583-5_0_4_line_58 |  | 48 | 51 | 0.015484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2583-5_0_4_line_59 |  | 49 | 94 | 0.0057477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2583-5_0_4_line_60 |  | 51 | 52 | 0.041674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2583-5_0_4_line_61 |  | 53 | 109 | 0.018424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2583-5_0_4_line_62 |  | 54 | 117 | 0.0046893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2583-5_0_4_line_63 |  | 55 | 56 | 0.025417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2583-5_0_4_line_64 |  | 55 | 57 | 0.015345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2583-5_0_4_line_65 |  | 56 | 61 | 0.012866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2583-5_0_4_line_66 |  | 57 | 62 | 0.017806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2583-5_0_4_line_67 |  | 58 | 59 | 0.029606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2583-5_0_4_line_68 |  | 58 | 60 | 0.030645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2583-5_0_4_line_69 |  | 59 | 63 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2583-5_0_4_line_70 |  | 60 | 120 | 0.0070976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2583-5_0_4_line_71 |  | 62 | 70 | 0.020553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2583-5_0_4_line_72 |  | 63 | 100 | 0.0206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2583-5_0_4_line_73 |  | 64 | 65 | 0.0061015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2583-5_0_4_line_74 |  | 64 | 66 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2583-5_0_4_line_75 |  | 65 | 67 | 0.020291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2583-5_0_4_line_76 |  | 66 | 68 | 0.0073122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2583-5_0_4_line_77 |  | 67 | 69 | 0.003577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2583-5_0_4_line_78 |  | 68 | 70 | 0.01589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2583-5_0_4_line_79 |  | 69 | 71 | 0.011119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2583-5_0_4_line_80 |  | 70 | 72 | 0.019689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2583-5_0_4_line_81 |  | 73 | 74 | 0.0025428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2583-5_0_4_line_82 |  | 74 | 75 | 0.017126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2583-5_0_4_line_83 |  | 75 | 103 | 0.034669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_2583-5_0_4_line_84 |  | 75 | 100 | 0.007472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_2583-5_0_4_line_85 |  | 76 | 77 | 0.020271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2583-5_0_4_line_86 |  | 76 | 78 | 0.01588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2583-5_0_4_line_87 |  | 77 | 93 | 0.040246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2583-5_0_4_line_88 |  | 78 | 88 | 0.014901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2583-5_0_4_line_89 |  | 79 | 80 | 0.033934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2583-5_0_4_line_90 |  | 80 | 111 | 0.020947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2583-5_0_4_line_91 |  | 81 | 82 | 0.012103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2583-5_0_4_line_92 |  | 82 | 84 | 0.015421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2583-5_0_4_line_93 |  | 83 | 84 | 0.027014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2583-5_0_4_line_94 |  | 83 | 85 | 0.01701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2583-5_0_4_line_95 |  | 85 | 86 | 0.022025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2583-5_0_4_line_96 |  | 86 | 87 | 0.019518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2583-5_0_4_line_97 |  | 88 | 89 | 0.0025428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2583-5_0_4_line_98 |  | 89 | 90 | 0.0044574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2583-5_0_4_line_99 |  | 90 | 91 | 0.0095728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2583-5_0_4_line_100 |  | 91 | 92 | 0.0035178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2583-5_0_4_line_101 |  | 92 | 95 | 0.013427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2583-5_0_4_line_102 |  | 93 | 119 | 0.025685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2583-5_0_4_line_103 |  | 95 | 107 | 0.0046412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2583-5_0_4_line_104 |  | 96 | 97 | 0.00054797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2583-5_0_4_line_105 |  | 96 | 98 | 0.024009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2583-5_0_4_line_106 |  | 97 | 99 | 0.022782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2583-5_0_4_line_107 |  | 98 | 100 | 0.008683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2583-5_0_4_line_108 |  | 99 | 101 | 0.032242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2583-5_0_4_line_109 |  | 101 | 102 | 0.017649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2583-5_0_4_line_110 |  | 103 | 110 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_2583-5_0_4_line_111 |  | 105 | 106 | 0.0064318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2583-5_0_4_line_112 |  | 106 | 107 | 0.012039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2583-5_0_4_line_113 |  | 108 | 109 | 0.023088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2583-5_0_4_line_114 |  | 110 | 111 | 0.020366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_2583-5_0_4_line_115 |  | 112 | 113 | 0.012897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2583-5_0_4_line_116 |  | 113 | 114 | 0.036356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2583-5_0_4_line_117 |  | 114 | 115 | 0.02402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2583-5_0_4_line_118 |  | 115 | 116 | 0.0002474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2583-5_0_4_line_119 |  | 116 | 123 | 0.02499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2583-5_0_4_line_120 |  | 119 | 121 | 0.004009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2583-5_0_4_line_121 |  | 121 | 122 | 7.6255e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2583-5_0_4_line_122 |  | 122 | 123 | 5.1936e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2583-5_0_4_trafo_146 | 0.63 MVA 20/0.4 kV | 124 | 103 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2642976.5248 | 1247613.8235 | 2642973.3033 | 1247620.5001 | 2642969.8099 | 1247627.6893
1 | 2642984.4978 | 1247597.2991 | 2642976.5248 | 1247613.8235
2 | 2642969.8099 | 1247627.6893 | 2642966.4151 | 1247634.6754
3 | 2642998.0584 | 1247571.7137 | 2642984.4978 | 1247597.2991
4 | 2642984.4978 | 1247597.2991 | 2643016.266 | 1247617.8382
5 | 2642966.4151 | 1247634.6754 | 2642966.3744 | 1247634.7591
6 | 2642998.0584 | 1247571.7137 | 2643009.0479 | 1247577.7424
7 | 2643021.8149 | 1247621.4258 | 2643016.266 | 1247617.8382
8 | 2642966.3744 | 1247634.7591 | 2642958.5357 | 1247650.8901
9 | 2643022.5283 | 1247585.2074 | 2643021.3702 | 1247584.5022 | 2643009.0479 | 1247577.7424
10 | 2643022.7458 | 1247622.0276 | 2643021.8149 | 1247621.4258
11 | 2642942.2004 | 1247684.5065 | 2642958.5357 | 1247650.8901
12 | 2643085.2007 | 1247624.225 | 2643080.6007 | 1247631.5965 | 2643068.7991 | 1247651.0016 | 2643066.4732 | 1247654.6124
13 | 2643085.2007 | 1247624.225 | 2643077.2472 | 1247619.1639 | 2643076.0167 | 1247618.387
14 | 2643056.723 | 1247669.7486 | 2643066.4732 | 1247654.6124
15 | 2643076.0167 | 1247618.387 | 2643054.9684 | 1247605.098
16 | 2643030.9004 | 1247627.2998 | 2643022.7458 | 1247622.0276
17 | 2642908.2149 | 1247756.0525 | 2642901.49 | 1247769.574
18 | 2642915.3999 | 1247741.6062 | 2642908.2149 | 1247756.0525
19 | 2642898.1646 | 1247776.2602 | 2642901.49 | 1247769.574
20 | 2642915.3999 | 1247741.6062 | 2642925.0022 | 1247719.2051 | 2642932.8267 | 1247703.5003
21 | 2642915.3999 | 1247741.6062 | 2642922.8037 | 1247745.4067 | 2642928.0432 | 1247747.8779
22 | 2642915.3999 | 1247741.6062 | 2642900.6039 | 1247733.8955
23 | 2642887.3975 | 1247797.8967 | 2642898.1646 | 1247776.2602
24 | 2642932.8267 | 1247703.5003 | 2642933.1466 | 1247702.8583
25 | 2642934.9926 | 1247751.1556 | 2642928.0432 | 1247747.8779
26 | 2642894.4148 | 1247730.8368 | 2642898.6972 | 1247732.9018 | 2642900.6039 | 1247733.8955
27 | 2642887.3975 | 1247797.8967 | 2642868.4685 | 1247788.5432
28 | 2642887.3975 | 1247797.8967 | 2642874.976 | 1247822.7458
29 | 2642939.8004 | 1247689.5035 | 2642933.1466 | 1247702.8583
30 | 2642894.4148 | 1247730.8368 | 2642873.2611 | 1247720.6364
31 | 2642858.1696 | 1247783.4541 | 2642868.4685 | 1247788.5432
32 | 2642874.976 | 1247822.7458 | 2642862.5855 | 1247847.5231
33 | 2642939.8004 | 1247689.5035 | 2642947.9012 | 1247692.9978 | 2642954.7842 | 1247695.4262
34 | 2642942.2004 | 1247684.5065 | 2642940.8035 | 1247687.5984 | 2642939.8004 | 1247689.5035
35 | 2642868.9507 | 1247718.5579 | 2642873.2611 | 1247720.6364
36 | 2642858.1696 | 1247783.4541 | 2642845.5624 | 1247777.2243
37 | 2642780.6512 | 1247900.2905 | 2642749.7023 | 1247885.1005
38 | 2642749.4457 | 1247884.9746 | 2642749.7023 | 1247885.1005
39 | 2642882.2709 | 1247505.2539 | 2642874.7261 | 1247499.612
40 | 2642859.9307 | 1247486.4801 | 2642863.0587 | 1247488.3817 | 2642868.3425 | 1247492.9674 | 2642870.9206 | 1247496.7663 | 2642874.7261 | 1247499.612
41 | 2642882.2709 | 1247505.2539 | 2642881.7914 | 1247510.9987 | 2642880.0916 | 1247516.29
42 | 2642882.2709 | 1247505.2539 | 2642879.6973 | 1247499.7984 | 2642877.9597 | 1247495.6831 | 2642884.4484 | 1247494.4847 | 2642896.3899 | 1247500.5973 | 2642904.5189 | 1247478.3079 | 2642912.6432 | 1247455.6405 | 2642909.6274 | 1247445.5231
43 | 2642835.2684 | 1247471.2919 | 2642848.0422 | 1247479.2895 | 2642859.9307 | 1247486.4801
44 | 2642859.9307 | 1247486.4801 | 2642855.6206 | 1247495.2552
45 | 2642880.0916 | 1247516.29 | 2642868.8932 | 1247539.0242
46 | 2642909.6274 | 1247445.5231 | 2642908.6042 | 1247448.1063 | 2642903.0233 | 1247462.9195
47 | 2642909.6274 | 1247445.5231 | 2642910.3838 | 1247443.623
48 | 2642835.2684 | 1247471.2919 | 2642822.2676 | 1247492.9034
49 | 2642852.3864 | 1247501.8398 | 2642855.6206 | 1247495.2552
50 | 2642868.8932 | 1247539.0242 | 2642861.869 | 1247553.2809
51 | 2642897.1013 | 1247479.4996 | 2642900.2032 | 1247470.4048 | 2642903.0233 | 1247462.9195
52 | 2642913.6966 | 1247435.3013 | 2642910.3838 | 1247443.623
53 | 2642820.0305 | 1247496.6222 | 2642822.2676 | 1247492.9034
54 | 2642848.4866 | 1247509.7796 | 2642852.3864 | 1247501.8398
55 | 2642853.8031 | 1247569.4021 | 2642859.2969 | 1247558.5012 | 2642861.869 | 1247553.2809
56 | 2642897.1013 | 1247479.4996 | 2642949.9034 | 1247513.504 | 2642977.9006 | 1247530.1066 | 2642983.5971 | 1247534.006
57 | 2642897.1013 | 1247479.4996 | 2642866.1676 | 1247462.6315 | 2642869.6592 | 1247450.6149
58 | 2642919.3972 | 1247420.8996 | 2642916.2043 | 1247429.0041 | 2642913.6966 | 1247435.3013
59 | 2642817.0676 | 1247501.5474 | 2642820.0305 | 1247496.6222
60 | 2642919.3972 | 1247420.8996 | 2642880.5988 | 1247405.3977
61 | 2642983.5971 | 1247534.006 | 2642996.003 | 1247542.7017 | 2642998.7598 | 1247544.467
62 | 2642869.6592 | 1247450.6149 | 2642870.9676 | 1247446.1118
63 | 2642748.6985 | 1247657.2803 | 2642759.6641 | 1247634.3503
64 | 2642748.6985 | 1247657.2803 | 2642762.3781 | 1247664.2338
65 | 2642765.215 | 1247622.743 | 2642759.6641 | 1247634.3503
66 | 2642762.3781 | 1247664.2338 | 2642768.6011 | 1247667.3971 | 2642778.089 | 1247672.6093
67 | 2642793.9469 | 1247602.4282 | 2642785.8493 | 1247598.4533 | 2642774.3082 | 1247597.5695 | 2642766.3902 | 1247593.2689
68 | 2642766.3902 | 1247593.2689 | 2642784.5847 | 1247568.6091
69 | 2642793.9469 | 1247602.4282 | 2642810.2076 | 1247610.4101
70 | 2642790.905 | 1247571.8387 | 2642784.5847 | 1247568.6091
71 | 2642796.1029 | 1247682.5054 | 2642778.089 | 1247672.6093
72 | 2642828.7001 | 1247619.4875 | 2642810.2076 | 1247610.4101
73 | 2642832.0678 | 1247700.4515 | 2642837.5273 | 1247703.1758
74 | 2642816.8639 | 1247692.8649 | 2642832.0678 | 1247700.4515
75 | 2642837.5273 | 1247703.1758 | 2642851.2013 | 1247709.999 | 2642855.7133 | 1247712.1747
76 | 2642816.8639 | 1247692.8649 | 2642810.321 | 1247689.6001
77 | 2642858.9353 | 1247713.7284 | 2642855.7133 | 1247712.1747
78 | 2642796.1029 | 1247682.5054 | 2642810.321 | 1247689.6001
79 | 2642858.9353 | 1247713.7284 | 2642868.9507 | 1247718.5579
80 | 2642796.1029 | 1247682.5054 | 2642790.4015 | 1247692.9045 | 2642786.8372 | 1247699.8751
81 | 2642816.4855 | 1247643.7277 | 2642817.6528 | 1247641.4686
82 | 2642825.4117 | 1247626.2016 | 2642822.5989 | 1247631.8962 | 2642817.6528 | 1247641.4686
83 | 2642825.4117 | 1247626.2016 | 2642844.2999 | 1247635.5997 | 2642856.4362 | 1247641.6745
84 | 2642825.4117 | 1247626.2016 | 2642826.8601 | 1247623.2879 | 2642828.7001 | 1247619.4875
85 | 2642767.1972 | 1247738.5009 | 2642758.1325 | 1247756.6321
86 | 2642767.1972 | 1247738.5009 | 2642781.4335 | 1247745.5356
87 | 2642740.1514 | 1247792.6375 | 2642741.0986 | 1247790.7032 | 2642758.1325 | 1247756.6321
88 | 2642794.7927 | 1247752.137 | 2642781.4335 | 1247745.5356
89 | 2642942.2004 | 1247684.5065 | 2642932.4022 | 1247679.6991 | 2642911.8174 | 1247669.3954
90 | 2642911.8174 | 1247669.3954 | 2642893.0857 | 1247660.0193
91 | 2642954.7842 | 1247695.4262 | 2642958.1008 | 1247696.5963 | 2642963.4034 | 1247697.5019 | 2642965.9032 | 1247697.4978 | 2642966.5993 | 1247697.3748
92 | 2642966.5993 | 1247697.3748 | 2642981.7852 | 1247694.6923
93 | 2643008.3538 | 1247689.8119 | 2642994.1996 | 1247692.4994 | 2642981.7852 | 1247694.6923
94 | 2643025.0651 | 1247686.639 | 2643008.3538 | 1247689.8119
95 | 2643046.9036 | 1247686.5997 | 2643043.1977 | 1247686.306 | 2643036.1023 | 1247685.7986 | 2643032.1032 | 1247685.3026 | 2643025.0651 | 1247686.639
96 | 2643046.9036 | 1247686.5997 | 2643048.998 | 1247682.1008 | 2643056.1043 | 1247670.7003 | 2643056.723 | 1247669.7486
97 | 2642794.7927 | 1247752.137 | 2642797.0725 | 1247753.2635
98 | 2642801.0686 | 1247755.2381 | 2642797.0725 | 1247753.2635
99 | 2642801.0686 | 1247755.2381 | 2642809.6508 | 1247759.4789
100 | 2642812.8045 | 1247761.0373 | 2642809.6508 | 1247759.4789
101 | 2642824.8419 | 1247766.9855 | 2642812.8045 | 1247761.0373
102 | 2642740.1514 | 1247792.6375 | 2642728.8557 | 1247815.7058
103 | 2642824.8419 | 1247766.9855 | 2642829.0028 | 1247769.0416
104 | 2642843.4194 | 1247589.6797 | 2642843.1696 | 1247590.1674
105 | 2642832.525 | 1247611.6877 | 2642837.1164 | 1247602.3257 | 2642841.1022 | 1247594.2046 | 2642843.1696 | 1247590.1674
106 | 2642853.8031 | 1247569.4021 | 2642843.4194 | 1247589.6797
107 | 2642832.525 | 1247611.6877 | 2642828.7001 | 1247619.4875
108 | 2642853.8031 | 1247569.4021 | 2642837.9036 | 1247561.3041 | 2642825.1558 | 1247554.6099
109 | 2642809.3683 | 1247546.7277 | 2642817.7022 | 1247550.6957 | 2642825.1558 | 1247554.6099
110 | 2642856.4362 | 1247641.6745 | 2642874.8742 | 1247650.9036
111 | 2642839.7962 | 1247774.375 | 2642845.5624 | 1247777.2243
112 | 2642839.7962 | 1247774.375 | 2642829.0028 | 1247769.0416
113 | 2642998.7598 | 1247544.467 | 2643018.2037 | 1247556.9174
114 | 2642893.0857 | 1247660.0193 | 2642874.8742 | 1247650.9036
115 | 2642737.8677 | 1247879.292 | 2642749.4457 | 1247884.9746
116 | 2642705.1098 | 1247863.5259 | 2642718.5373 | 1247869.8045 | 2642737.8677 | 1247879.292
117 | 2642705.1098 | 1247863.5259 | 2642710.8151 | 1247852.5485 | 2642715.9377 | 1247842.087
118 | 2642715.9377 | 1247842.087 | 2642716.0465 | 1247841.8648
119 | 2642727.0363 | 1247819.4214 | 2642716.0465 | 1247841.8648
120 | 2642728.8557 | 1247815.7058 | 2642727.0926 | 1247819.3063
121 | 2642727.0591 | 1247819.3748 | 2642727.0926 | 1247819.3063
122 | 2642727.0363 | 1247819.4214 | 2642727.0591 | 1247819.3748

## bus_geodata
| x | y | coords
0 | 2642976.5248 | 1247613.8235
1 | 2642969.8099 | 1247627.6893
2 | 2642984.4978 | 1247597.2991
3 | 2642966.4151 | 1247634.6754
4 | 2642998.0584 | 1247571.7137
5 | 2643016.266 | 1247617.8382
6 | 2642966.3744 | 1247634.7591
7 | 2643009.0479 | 1247577.7424
8 | 2643021.8149 | 1247621.4258
9 | 2642958.5357 | 1247650.8901
10 | 2643085.2007 | 1247624.225
11 | 2643066.4732 | 1247654.6124
12 | 2643076.0167 | 1247618.387
13 | 2643022.5283 | 1247585.2074
14 | 2643022.7458 | 1247622.0276
15 | 2642908.2149 | 1247756.0525
16 | 2642901.49 | 1247769.574
17 | 2642915.3999 | 1247741.6062
18 | 2642898.1646 | 1247776.2602
19 | 2642932.8267 | 1247703.5003
20 | 2642928.0432 | 1247747.8779
21 | 2642900.6039 | 1247733.8955
22 | 2642887.3975 | 1247797.8967
23 | 2642933.1466 | 1247702.8583
24 | 2642934.9926 | 1247751.1556
25 | 2642894.4148 | 1247730.8368
26 | 2642868.4685 | 1247788.5432
27 | 2642874.976 | 1247822.7458
28 | 2642939.8004 | 1247689.5035
29 | 2642873.2611 | 1247720.6364
30 | 2642862.5855 | 1247847.5231
31 | 2642858.1696 | 1247783.4541
32 | 2642780.6512 | 1247900.2905
33 | 2642749.7023 | 1247885.1005
34 | 2642874.7261 | 1247499.612
35 | 2642882.2709 | 1247505.2539
36 | 2642859.9307 | 1247486.4801
37 | 2642880.0916 | 1247516.29
38 | 2642909.6274 | 1247445.5231
39 | 2642835.2684 | 1247471.2919
40 | 2642855.6206 | 1247495.2552
41 | 2642868.8932 | 1247539.0242
42 | 2642903.0233 | 1247462.9195
43 | 2642910.3838 | 1247443.623
44 | 2642822.2676 | 1247492.9034
45 | 2642852.3864 | 1247501.8398
46 | 2642861.869 | 1247553.2809
47 | 2642897.1013 | 1247479.4996
48 | 2642913.6966 | 1247435.3013
49 | 2642820.0305 | 1247496.6222
50 | 2642848.4866 | 1247509.7796
51 | 2642919.3972 | 1247420.8996
52 | 2642880.5988 | 1247405.3977
53 | 2642983.5971 | 1247534.0061
54 | 2642869.6592 | 1247450.6149
55 | 2642748.6985 | 1247657.2803
56 | 2642759.6641 | 1247634.3503
57 | 2642762.3781 | 1247664.2338
58 | 2642766.3902 | 1247593.2689
59 | 2642793.9469 | 1247602.4282
60 | 2642784.5847 | 1247568.6091
61 | 2642765.215 | 1247622.743
62 | 2642778.089 | 1247672.6093
63 | 2642810.2076 | 1247610.4101
64 | 2642832.0678 | 1247700.4515
65 | 2642837.5273 | 1247703.1758
66 | 2642816.8639 | 1247692.8649
67 | 2642855.7133 | 1247712.1747
68 | 2642810.321 | 1247689.6001
69 | 2642858.9353 | 1247713.7284
70 | 2642796.1029 | 1247682.5054
71 | 2642868.9507 | 1247718.5579
72 | 2642786.8372 | 1247699.8751
73 | 2642816.4855 | 1247643.7277
74 | 2642817.6528 | 1247641.4686
75 | 2642825.4117 | 1247626.2016
76 | 2642767.1972 | 1247738.5009
77 | 2642758.1325 | 1247756.6321
78 | 2642781.4335 | 1247745.5356
79 | 2642942.2004 | 1247684.5065
80 | 2642911.8174 | 1247669.3954
81 | 2642954.7842 | 1247695.4262
82 | 2642966.5993 | 1247697.3748
83 | 2643008.3538 | 1247689.8119
84 | 2642981.7852 | 1247694.6923
85 | 2643025.0651 | 1247686.639
86 | 2643046.9036 | 1247686.5997
87 | 2643056.723 | 1247669.7486
88 | 2642794.7927 | 1247752.137
89 | 2642797.0725 | 1247753.2635
90 | 2642801.0686 | 1247755.2381
91 | 2642809.6508 | 1247759.4789
92 | 2642812.8045 | 1247761.0373
93 | 2642740.1514 | 1247792.6375
94 | 2642817.0676 | 1247501.5474
95 | 2642824.8419 | 1247766.9855
96 | 2642843.1696 | 1247590.1674
97 | 2642843.4194 | 1247589.6797
98 | 2642832.525 | 1247611.6877
99 | 2642853.8031 | 1247569.4021
100 | 2642828.7001 | 1247619.4875
101 | 2642825.1558 | 1247554.6099
102 | 2642809.3683 | 1247546.7277
103 | 2642856.4362 | 1247641.6745
104 | 2643030.9004 | 1247627.2998
105 | 2642845.5624 | 1247777.2243
106 | 2642839.7962 | 1247774.375
107 | 2642829.0028 | 1247769.0416
108 | 2643018.2037 | 1247556.9174
109 | 2642998.7598 | 1247544.467
110 | 2642874.8742 | 1247650.9036
111 | 2642893.0857 | 1247660.0193
112 | 2642749.4457 | 1247884.9746
113 | 2642737.8677 | 1247879.292
114 | 2642705.1098 | 1247863.5259
115 | 2642715.9377 | 1247842.087
116 | 2642716.0465 | 1247841.8648
117 | 2642870.9676 | 1247446.1118
118 | 2643054.9684 | 1247605.098
119 | 2642728.8557 | 1247815.7058
120 | 2642790.905 | 1247571.8387
121 | 2642727.0926 | 1247819.3063
122 | 2642727.0591 | 1247819.3748
123 | 2642727.0363 | 1247819.4214
124 | 2642825.4117 | 1247626.2016

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98932 | -0.20383 | 0.0020729 | 0.00051951
1 | 0.9895 | -0.2004 | 0.00090633 | 0.00022715
2 | 0.98915 | -0.20725 | 0 | 0
3 | 0.98959 | -0.19854 | 0.0010212 | 0.00025593
4 | 0.989 | -0.21015 | 0 | 0
5 | 0.98898 | -0.21049 | 0.0010062 | 0.00025217
6 | 0.9896 | -0.19852 | 0.00097246 | 0.00024372
7 | 0.98893 | -0.21141 | 0.0013031 | 0.00032659
8 | 0.98896 | -0.21094 | 0.00084913 | 0.00021281
9 | 0.98985 | -0.1936 | 0.001103 | 0.00027643
10 | 0.98809 | -0.22768 | 0 | 0
11 | 0.98819 | -0.22581 | 0.0066351 | 0.0016629
12 | 0.98806 | -0.22826 | 0.0010091 | 0.0002529
13 | 0.98887 | -0.2126 | 0.0043312 | 0.0010855
14 | 0.98895 | -0.21099 | 0.0011201 | 0.00028073
15 | 0.98368 | -0.3127 | 0.0011678 | 0.00029268
16 | 0.98287 | -0.32844 | 0.00089627 | 0.00022463
17 | 0.98456 | -0.29557 | 0 | 0
18 | 0.98248 | -0.33611 | 0 | 0
19 | 0.98833 | -0.22265 | 0.0028099 | 0.00070423
20 | 0.98453 | -0.29622 | 0.0012546 | 0.00031444
21 | 0.98402 | -0.30626 | 0.0011137 | 0.00027912
22 | 0.98121 | -0.36097 | 0 | 0
23 | 0.9884 | -0.22137 | 0.0018602 | 0.00046621
24 | 0.98452 | -0.2964 | 0.0012898 | 0.00032325
25 | 0.9838 | -0.31054 | 0.0011017 | 0.00027611
26 | 0.98024 | -0.37976 | 0.0043282 | 0.0010848
27 | 0.98101 | -0.36488 | 0 | 0
28 | 0.98981 | -0.19431 | 0 | 0
29 | 0.98307 | -0.32467 | 0.00089115 | 0.00022334
30 | 0.98081 | -0.36879 | 0.0077873 | 0.0019517
31 | 0.97977 | -0.3891 | 0.01328 | 0.0033282
32 | 0.97567 | -0.46948 | 0.00090878 | 0.00022776
33 | 0.9757 | -0.4689 | 0.00040101 | 0.0001005
34 | 0.98468 | -0.29478 | 0.014132 | 0.0035419
35 | 0.98518 | -0.28499 | 0 | 0
36 | 0.98387 | -0.3105 | 0 | 0
37 | 0.98594 | -0.27025 | 0 | 0
38 | 0.98397 | -0.30851 | 0 | 0
39 | 0.9836 | -0.3157 | 0 | 0
40 | 0.98357 | -0.31643 | 0.00097072 | 0.00024329
41 | 0.98763 | -0.23736 | 0.011798 | 0.0029567
42 | 0.98379 | -0.31211 | 0.0014374 | 0.00036024
43 | 0.98397 | -0.30866 | 0.0028715 | 0.00071968
44 | 0.98337 | -0.32024 | 0.0025681 | 0.00064362
45 | 0.98335 | -0.32075 | 0.016793 | 0.0042086
46 | 0.98886 | -0.21344 | 0.015737 | 0.003944
47 | 0.98364 | -0.31506 | 0 | 0
48 | 0.98396 | -0.30883 | 0 | 0
49 | 0.98334 | -0.32082 | 0.00096294 | 0.00024134
50 | 0.98322 | -0.32329 | 0.015928 | 0.0039919
51 | 0.98394 | -0.30914 | 0 | 0
52 | 0.9839 | -0.30996 | 0.0010964 | 0.00027479
53 | 0.9834 | -0.31982 | 0 | 0
54 | 0.98334 | -0.32084 | 0.0018766 | 0.00047033
55 | 0.98026 | -0.37969 | 0 | 0
56 | 0.97999 | -0.38491 | 0.0077754 | 0.0019487
57 | 0.98042 | -0.37654 | 0.0034186 | 0.00085678
58 | 0.99575 | -0.081141 | 0.0049178 | 0.0012325
59 | 0.99615 | -0.073413 | 0.0040219 | 0.001008
60 | 0.99548 | -0.086496 | 0.0025113 | 0.0006294
61 | 0.97995 | -0.38574 | 0.0035414 | 0.00088756
62 | 0.98066 | -0.37179 | 0.0042541 | 0.0010662
63 | 0.99647 | -0.067409 | 0.0043007 | 0.0010779
64 | 0.98186 | -0.34843 | 0.0018866 | 0.00047283
65 | 0.982 | -0.34559 | 0.0018288 | 0.00045835
66 | 0.98148 | -0.35576 | 0.0014915 | 0.00037379
67 | 0.98252 | -0.33549 | 0.0018281 | 0.00045816
68 | 0.98133 | -0.35871 | 0.0014958 | 0.00037489
69 | 0.98261 | -0.33359 | 0.0010835 | 0.00027156
70 | 0.98102 | -0.36471 | 0 | 0
71 | 0.98293 | -0.32747 | 0.0020136 | 0.00050467
72 | 0.98099 | -0.36538 | 0.0018636 | 0.00046707
73 | 0.9973 | -0.051374 | 0.0032475 | 0.00081389
74 | 0.99731 | -0.051229 | 0.0043568 | 0.0010919
75 | 0.99743 | -0.048947 | 0 | 0
76 | 0.97736 | -0.43637 | 0 | 0
77 | 0.97699 | -0.44355 | 0.00090483 | 0.00022677
78 | 0.97764 | -0.43076 | 0.00080028 | 0.00020057
79 | 0.99041 | -0.18262 | 0 | 0
80 | 0.99465 | -0.10148 | 0.0018534 | 0.0004645
81 | 0.98956 | -0.19914 | 0.0007966 | 0.00019965
82 | 0.98938 | -0.20259 | 0.0018781 | 0.0004707
83 | 0.98887 | -0.21245 | 0.0018701 | 0.00046868
84 | 0.98918 | -0.20648 | 0.0017452 | 0.0004374
85 | 0.98871 | -0.21564 | 0.00095586 | 0.00023956
86 | 0.98851 | -0.2194 | 0 | 0
87 | 0.98834 | -0.22274 | 0 | 0
88 | 0.97792 | -0.42527 | 0.00091654 | 0.00022971
89 | 0.97797 | -0.42429 | 0.00076164 | 0.00019088
90 | 0.97806 | -0.42251 | 0.0027972 | 0.00070106
91 | 0.97828 | -0.41821 | 0.0013369 | 0.00033505
92 | 0.97837 | -0.41654 | 0.0017977 | 0.00045054
93 | 0.9763 | -0.45715 | 0.0028462 | 0.00071333
94 | 0.98331 | -0.32149 | 0.0064618 | 0.0016195
95 | 0.97871 | -0.40975 | 0.00098567 | 0.00024703
96 | 0.99297 | -0.13433 | 0.0084673 | 0.0021221
97 | 0.99291 | -0.13551 | 0.0088303 | 0.0022131
98 | 0.99586 | -0.078971 | 0 | 0
99 | 0.99053 | -0.18134 | 0 | 0
100 | 0.9969 | -0.059031 | 0 | 0
101 | 0.99013 | -0.18903 | 0.0067521 | 0.0016922
102 | 0.99002 | -0.19112 | 0.0066733 | 0.0016725
103 | 1 | 0 | -0.31144 | -0.079172
104 | 0.98894 | -0.21131 | 0.0018317 | 0.00045908
105 | 0.97936 | -0.39715 | 0.00075883 | 0.00019018
106 | 0.97917 | -0.40075 | 0.00076107 | 0.00019074
107 | 0.97884 | -0.40732 | 0.0012033 | 0.00030158
108 | 0.98332 | -0.32124 | 0.0013288 | 0.00033302
109 | 0.98335 | -0.32068 | 0.0012574 | 0.00031513
110 | 0.99863 | -0.025957 | 0.0034052 | 0.00085344
111 | 0.9973 | -0.051058 | 0.0038526 | 0.00096556
112 | 0.9757 | -0.46889 | 0.00040093 | 0.00010048
113 | 0.97572 | -0.46849 | 0.00040101 | 0.0001005
114 | 0.9758 | -0.46708 | 0 | 0
115 | 0.97584 | -0.46615 | 0.00040101 | 0.0001005
116 | 0.97584 | -0.46614 | 0.00040088 | 0.00010047
117 | 0.98332 | -0.32125 | 0.0048402 | 0.0012131
118 | 0.98802 | -0.22911 | 0.0019277 | 0.00048312
119 | 0.97593 | -0.4645 | 0.011521 | 0.0028873
120 | 0.99543 | -0.087422 | 0.0074243 | 0.0018607
121 | 0.97591 | -0.4648 | 0.00040101 | 0.0001005
122 | 0.97591 | -0.46481 | 0.00040128 | 0.00010057
123 | 0.97591 | -0.46481 | 0.00040128 | 0.00010057
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012518 | -0.0031372 | 0.01252 | 0.0031383 | 2.0481e-06 | 1.1129e-06 | 0.018828 | 0.018828 | 0.018828 | 0.98932 | -0.20383 | 0.9895 | -0.2004 | 5.1726
1 | 0.010445 | 0.0026177 | -0.010444 | -0.0026169 | 1.6982e-06 | 8.5131e-07 | 0.015711 | 0.015711 | 0.015711 | 0.98932 | -0.20383 | 0.98915 | -0.20725 | 4.3161
2 | -0.013427 | -0.0033655 | 0.013428 | 0.0033661 | 1.1875e-06 | 6.602e-07 | 0.020191 | 0.020191 | 0.020191 | 0.9895 | -0.2004 | 0.98959 | -0.19854 | 5.547
3 | 0.0056357 | 0.0014122 | -0.0056349 | -0.0014121 | 7.8006e-07 | 1.2781e-07 | 0.0084779 | 0.008478 | 0.008478 | 0.98915 | -0.20725 | 0.989 | -0.21015 | 2.3291
4 | 0.004808 | 0.0012046 | -0.0048073 | -0.0012046 | 7.4213e-07 | -1.0535e-08 | 0.0072328 | 0.0072329 | 0.0072329 | 0.98915 | -0.20725 | 0.98898 | -0.21049 | 1.9871
5 | -0.014449 | -0.0036221 | 0.014449 | 0.0036221 | 1.6469e-08 | 9.345e-09 | 0.021727 | 0.021727 | 0.021727 | 0.98959 | -0.19854 | 0.9896 | -0.19852 | 5.9689
6 | 0.0056349 | 0.0014121 | -0.0056345 | -0.001412 | 3.3786e-07 | 5.5394e-08 | 0.008478 | 0.0084781 | 0.0084781 | 0.989 | -0.21015 | 0.98893 | -0.21141 | 2.3291
7 | 0.0038011 | 0.00095247 | -0.003801 | -0.0009525 | 8.1045e-08 | -3.2916e-08 | 0.0057191 | 0.0057191 | 0.0057191 | 0.98898 | -0.21049 | 0.98896 | -0.21094 | 1.5712
8 | -0.015421 | -0.0038658 | 0.015425 | 0.0038679 | 3.6165e-06 | 2.0841e-06 | 0.023189 | 0.023189 | 0.023189 | 0.9896 | -0.19852 | 0.98985 | -0.1936 | 6.3706
9 | 0.0043314 | 0.0010855 | -0.0043312 | -0.0010855 | 2.4547e-07 | -4.0614e-08 | 0.0065173 | 0.0065174 | 0.0065174 | 0.98893 | -0.21141 | 0.98887 | -0.2126 | 1.7905
10 | 0.0029519 | 0.00073969 | -0.0029519 | -0.0007397 | 8.1996e-09 | -8.9747e-09 | 0.0044415 | 0.0044415 | 0.0044415 | 0.98896 | -0.21094 | 0.98895 | -0.21099 | 1.2202
11 | -0.016528 | -0.0041443 | 0.016537 | 0.0041494 | 8.6528e-06 | 5.0571e-06 | 0.024847 | 0.024847 | 0.024847 | 0.98985 | -0.1936 | 0.99041 | -0.18262 | 6.8261
12 | -0.0029369 | -0.00073567 | 0.0029372 | 0.00073538 | 2.6183e-07 | -2.8969e-07 | 0.0044227 | 0.0044226 | 0.0044227 | 0.98809 | -0.22768 | 0.98819 | -0.22581 | 1.215
13 | 0.0029369 | 0.00073567 | -0.0029369 | -0.00073576 | 7.9827e-08 | -8.8297e-08 | 0.0044227 | 0.0044228 | 0.0044228 | 0.98809 | -0.22768 | 0.98806 | -0.22826 | 1.2151
14 | -0.0095723 | -0.0023983 | 0.0095737 | 0.002399 | 1.4027e-06 | 6.6704e-07 | 0.014414 | 0.014414 | 0.014414 | 0.98819 | -0.22581 | 0.98834 | -0.22274 | 3.9598
15 | 0.0019278 | 0.00048285 | -0.0019277 | -0.00048312 | 7.8675e-08 | -2.6845e-07 | 0.0029031 | 0.0029032 | 0.0029032 | 0.98806 | -0.22826 | 0.98802 | -0.22911 | 0.79759
16 | 0.0018318 | 0.00045897 | -0.0018317 | -0.00045908 | 2.7661e-08 | -1.0689e-07 | 0.0027561 | 0.0027561 | 0.0027561 | 0.98895 | -0.21099 | 0.98894 | -0.21131 | 0.75718
17 | 0.058083 | 0.014662 | -0.05804 | -0.014634 | 4.3756e-05 | 2.7812e-05 | 0.0879 | 0.0879 | 0.0879 | 0.98368 | -0.3127 | 0.98287 | -0.32844 | 24.1485
18 | -0.059251 | -0.014955 | 0.0593 | 0.014986 | 4.8646e-05 | 3.0929e-05 | 0.089667 | 0.089667 | 0.089667 | 0.98368 | -0.3127 | 0.98456 | -0.29557 | 24.6338
19 | 0.057143 | 0.014409 | -0.057122 | -0.014396 | 2.0974e-05 | 1.3329e-05 | 0.086544 | 0.086544 | 0.086544 | 0.98287 | -0.32844 | 0.98248 | -0.33611 | 23.7757
20 | -0.097545 | -0.024611 | 0.097887 | 0.024829 | 0.00034191 | 0.00021829 | 0.14748 | 0.14748 | 0.14748 | 0.98456 | -0.29557 | 0.98833 | -0.22265 | 40.5171
21 | 0.0025445 | 0.00063747 | -0.0025444 | -0.0006376 | 7.8278e-08 | -1.2941e-07 | 0.0038455 | 0.0038456 | 0.0038456 | 0.98456 | -0.29557 | 0.98453 | -0.29622 | 1.0565
22 | 0.0357 | 0.008988 | -0.035682 | -0.0089766 | 1.8224e-05 | 1.1451e-05 | 0.05397 | 0.05397 | 0.05397 | 0.98456 | -0.29557 | 0.98402 | -0.30626 | 14.8269
23 | 0.057122 | 0.014396 | -0.057055 | -0.014353 | 6.7846e-05 | 4.3116e-05 | 0.086544 | 0.086544 | 0.086544 | 0.98248 | -0.33611 | 0.98121 | -0.36097 | 23.7757
24 | -0.1007 | -0.025534 | 0.1007 | 0.025538 | 6.1912e-06 | 3.9532e-06 | 0.15171 | 0.15171 | 0.15171 | 0.98833 | -0.22265 | 0.9884 | -0.22137 | 41.6793
25 | 0.0012898 | 0.00032316 | -0.0012898 | -0.00032325 | 1.0949e-08 | -9.0701e-08 | 0.0019493 | 0.0019494 | 0.0019494 | 0.98453 | -0.29622 | 0.98452 | -0.2964 | 0.53554
26 | 0.034568 | 0.0086975 | -0.034561 | -0.008693 | 7.0782e-06 | 4.4424e-06 | 0.052286 | 0.052286 | 0.052286 | 0.98402 | -0.30626 | 0.9838 | -0.31054 | 14.3642
27 | 0.049264 | 0.0124 | -0.04922 | -0.012372 | 4.4216e-05 | 2.8032e-05 | 0.074729 | 0.07473 | 0.07473 | 0.98121 | -0.36097 | 0.98024 | -0.37976 | 20.5301
28 | 0.0077902 | 0.0019529 | -0.0077888 | -0.0019523 | 1.4534e-06 | 5.795e-07 | 0.011814 | 0.011814 | 0.011814 | 0.98121 | -0.36097 | 0.98101 | -0.36488 | 3.2457
29 | -0.10256 | -0.026004 | 0.1027 | 0.026089 | 0.00013358 | 8.53e-05 | 0.15451 | 0.15451 | 0.15451 | 0.9884 | -0.22137 | 0.98981 | -0.19431 | 42.4486
30 | 0.033459 | 0.0084169 | -0.033437 | -0.0084028 | 2.2566e-05 | 1.4144e-05 | 0.050619 | 0.05062 | 0.05062 | 0.9838 | -0.31054 | 0.98307 | -0.32467 | 13.9065
31 | 0.044892 | 0.011287 | -0.044872 | -0.011275 | 2.0013e-05 | 1.2664e-05 | 0.068159 | 0.068159 | 0.068159 | 0.98024 | -0.37976 | 0.97977 | -0.3891 | 18.7251
32 | 0.0077888 | 0.0019523 | -0.0077873 | -0.0019517 | 1.45e-06 | 5.7832e-07 | 0.011814 | 0.011814 | 0.011814 | 0.98101 | -0.36488 | 0.98081 | -0.36879 | 3.2457
33 | 0.016837 | 0.0042245 | -0.016833 | -0.0042222 | 3.8737e-06 | 2.272e-06 | 0.025313 | 0.025314 | 0.025314 | 0.98981 | -0.19431 | 0.98956 | -0.19914 | 6.9543
34 | -0.11953 | -0.030314 | 0.1196 | 0.030356 | 6.723e-05 | 4.2956e-05 | 0.17983 | 0.17983 | 0.17983 | 0.98981 | -0.19431 | 0.99041 | -0.18262 | 49.4028
35 | 0.032546 | 0.0081794 | -0.032541 | -0.0081767 | 4.3563e-06 | 2.7274e-06 | 0.049271 | 0.049271 | 0.049271 | 0.98307 | -0.32467 | 0.98293 | -0.32747 | 13.5359
36 | 0.031592 | 0.0079466 | -0.03158 | -0.007939 | 1.2145e-05 | 7.5961e-06 | 0.047991 | 0.047991 | 0.047991 | 0.97977 | -0.3891 | 0.97936 | -0.39715 | 13.1844
37 | -0.00090878 | -0.00022776 | 0.0009088 | 0.00022735 | 2.4832e-08 | -4.1468e-07 | 0.001386 | 0.0013858 | 0.001386 | 0.97567 | -0.46948 | 0.9757 | -0.4689 | 0.38077
38 | -0.0013098 | -0.00032785 | 0.0013098 | 0.00032785 | 4.2769e-10 | -3.2962e-09 | 0.0019974 | 0.0019974 | 0.0019974 | 0.9757 | -0.4689 | 0.9757 | -0.46889 | 0.54874
39 | -0.057872 | -0.014525 | 0.057899 | 0.014542 | 2.7026e-05 | 1.7177e-05 | 0.087462 | 0.087462 | 0.087462 | 0.98468 | -0.29478 | 0.98518 | -0.28499 | 24.0281
40 | 0.04374 | 0.010983 | -0.043707 | -0.010962 | 3.2775e-05 | 2.0722e-05 | 0.066106 | 0.066106 | 0.066106 | 0.98468 | -0.29478 | 0.98387 | -0.3105 | 18.161
41 | -0.07263 | -0.018237 | 0.072681 | 0.01827 | 5.1106e-05 | 3.2563e-05 | 0.10971 | 0.10971 | 0.10971 | 0.98518 | -0.28499 | 0.98594 | -0.27025 | 30.141
42 | 0.014731 | 0.0036957 | -0.014714 | -0.0036862 | 1.6501e-05 | 9.4302e-06 | 0.022251 | 0.022251 | 0.022251 | 0.98518 | -0.28499 | 0.98397 | -0.30851 | 6.1129
43 | 0.0099978 | 0.0025068 | -0.0099953 | -0.0025056 | 2.4783e-06 | 1.2191e-06 | 0.015121 | 0.015121 | 0.015121 | 0.98387 | -0.3105 | 0.9836 | -0.3157 | 4.1542
44 | 0.033709 | 0.0084551 | -0.0337 | -0.0084491 | 9.53e-06 | 5.9751e-06 | 0.050985 | 0.050985 | 0.050985 | 0.98387 | -0.3105 | 0.98357 | -0.31643 | 14.0068
45 | -0.072681 | -0.01827 | 0.072796 | 0.018343 | 0.00011434 | 7.2854e-05 | 0.10971 | 0.10971 | 0.10971 | 0.98594 | -0.27025 | 0.98763 | -0.23736 | 30.1409
46 | 0.010746 | 0.0026926 | -0.010744 | -0.0026916 | 1.8428e-06 | 9.4307e-07 | 0.016251 | 0.016251 | 0.016251 | 0.98397 | -0.30851 | 0.98379 | -0.31211 | 4.4645
47 | 0.0039681 | 0.00099366 | -0.003968 | -0.00099367 | 2.7612e-08 | -8.3047e-09 | 0.0060004 | 0.0060004 | 0.0060004 | 0.98397 | -0.30851 | 0.98397 | -0.30866 | 1.6485
48 | 0.0099953 | 0.0025056 | -0.0099932 | -0.0025046 | 2.1626e-06 | 1.064e-06 | 0.015121 | 0.015121 | 0.015121 | 0.9836 | -0.3157 | 0.98337 | -0.32024 | 4.1542
49 | 0.032729 | 0.0082059 | -0.032722 | -0.0082016 | 6.7451e-06 | 4.2238e-06 | 0.049516 | 0.049516 | 0.049516 | 0.98357 | -0.31643 | 0.98335 | -0.32075 | 13.6034
50 | -0.084593 | -0.0213 | 0.08469 | 0.021361 | 9.6868e-05 | 6.1792e-05 | 0.12749 | 0.12749 | 0.12749 | 0.98763 | -0.23736 | 0.98886 | -0.21344 | 35.0241
51 | 0.009307 | 0.0023314 | -0.0093056 | -0.0023308 | 1.3084e-06 | 6.1385e-07 | 0.014077 | 0.014077 | 0.014077 | 0.98379 | -0.31211 | 0.98364 | -0.31506 | 3.8672
52 | 0.0010965 | 0.00027399 | -0.0010965 | -0.0002741 | 9.2324e-09 | -1.0786e-07 | 0.0016579 | 0.0016579 | 0.0016579 | 0.98397 | -0.30866 | 0.98396 | -0.30883 | 0.45548
53 | 0.0074251 | 0.0018609 | -0.0074249 | -0.0018609 | 2.0544e-07 | 7.6427e-08 | 0.011236 | 0.011236 | 0.011236 | 0.98337 | -0.32024 | 0.98334 | -0.32082 | 3.0867
54 | 0.01593 | 0.003993 | -0.015928 | -0.0039919 | 1.9275e-06 | 1.1214e-06 | 0.024105 | 0.024105 | 0.024105 | 0.98335 | -0.32075 | 0.98322 | -0.32329 | 6.6224
55 | -0.10043 | -0.025305 | 0.10058 | 0.025404 | 0.00015448 | 9.8633e-05 | 0.15117 | 0.15117 | 0.15117 | 0.98886 | -0.21344 | 0.99053 | -0.18134 | 41.5296
56 | 0.0025869 | 0.00064679 | -0.0025863 | -0.00064771 | 5.8591e-07 | -9.1996e-07 | 0.0039128 | 0.0039133 | 0.0039133 | 0.98364 | -0.31506 | 0.9834 | -0.31982 | 1.0751
57 | 0.0067188 | 0.001684 | -0.0067169 | -0.0016834 | 1.8498e-06 | 5.7795e-07 | 0.010164 | 0.010164 | 0.010164 | 0.98364 | -0.31506 | 0.98334 | -0.32084 | 2.7924
58 | 0.0010965 | 0.0002741 | -0.0010965 | -0.00027429 | 1.5961e-08 | -1.8646e-07 | 0.0016579 | 0.001658 | 0.001658 | 0.98396 | -0.30883 | 0.98394 | -0.30914 | 0.4555
59 | 0.006462 | 0.0016195 | -0.0064618 | -0.0016195 | 2.0609e-07 | 5.8988e-08 | 0.0097784 | 0.0097784 | 0.0097784 | 0.98334 | -0.32082 | 0.98331 | -0.32149 | 2.6864
60 | 0.0010965 | 0.00027429 | -0.0010964 | -0.00027479 | 4.2965e-08 | -5.0179e-07 | 0.001658 | 0.0016582 | 0.0016582 | 0.98394 | -0.30914 | 0.9839 | -0.30996 | 0.45555
61 | 0.0025863 | 0.00064771 | -0.0025862 | -0.00064788 | 1.058e-07 | -1.6602e-07 | 0.0039133 | 0.0039133 | 0.0039133 | 0.9834 | -0.31982 | 0.98335 | -0.32068 | 1.0751
62 | 0.0048403 | 0.0012131 | -0.0048402 | -0.0012131 | 9.4338e-08 | 8.9e-10 | 0.0073244 | 0.0073245 | 0.0073245 | 0.98334 | -0.32084 | 0.98332 | -0.32125 | 2.0122
63 | 0.01132 | 0.0028377 | -0.011317 | -0.0028362 | 2.8144e-06 | 1.4809e-06 | 0.017183 | 0.017184 | 0.017184 | 0.98026 | -0.37969 | 0.97999 | -0.38491 | 4.7208
64 | -0.01132 | -0.0028377 | 0.011321 | 0.0028386 | 1.6992e-06 | 8.9398e-07 | 0.017183 | 0.017183 | 0.017183 | 0.98026 | -0.37969 | 0.98042 | -0.37654 | 4.7207
65 | 0.0035415 | 0.00088748 | -0.0035414 | -0.00088756 | 1.3952e-07 | -7.2811e-08 | 0.0053774 | 0.0053775 | 0.0053775 | 0.97999 | -0.38491 | 0.97995 | -0.38574 | 1.4773
66 | -0.01474 | -0.0036953 | 0.014743 | 0.0036973 | 3.342e-06 | 1.9143e-06 | 0.022372 | 0.022372 | 0.022372 | 0.98042 | -0.37654 | 0.98066 | -0.37179 | 6.1461
67 | -0.014856 | -0.003724 | 0.014862 | 0.0037271 | 5.472e-06 | 3.1168e-06 | 0.022201 | 0.022201 | 0.022201 | 0.99575 | -0.081141 | 0.99615 | -0.073413 | 6.0991
68 | 0.0099385 | 0.0024914 | -0.0099359 | -0.0024902 | 2.5349e-06 | 1.2238e-06 | 0.014852 | 0.014852 | 0.014852 | 0.99575 | -0.081141 | 0.99548 | -0.086496 | 4.0802
69 | -0.018884 | -0.0047351 | 0.018889 | 0.0047383 | 5.4051e-06 | 3.2234e-06 | 0.028209 | 0.028208 | 0.028209 | 0.99615 | -0.073413 | 0.99647 | -0.067409 | 7.7496
70 | 0.0074246 | 0.0018608 | -0.0074243 | -0.0018607 | 3.2783e-07 | 1.1754e-07 | 0.011098 | 0.011098 | 0.011098 | 0.99548 | -0.086496 | 0.99543 | -0.087422 | 3.0489
71 | -0.018998 | -0.0047634 | 0.019004 | 0.0047673 | 6.4048e-06 | 3.8396e-06 | 0.028827 | 0.028827 | 0.028827 | 0.98066 | -0.37179 | 0.98102 | -0.36471 | 7.9195
72 | -0.02319 | -0.0058162 | 0.023199 | 0.0058218 | 9.2646e-06 | 5.6609e-06 | 0.034631 | 0.034631 | 0.034631 | 0.99647 | -0.067409 | 0.9969 | -0.059031 | 9.5139
73 | -0.025759 | -0.0064663 | 0.025762 | 0.0064685 | 3.4876e-06 | 2.1549e-06 | 0.039042 | 0.039042 | 0.039042 | 0.98186 | -0.34843 | 0.982 | -0.34559 | 10.7258
74 | 0.023872 | 0.0059935 | -0.023864 | -0.0059884 | 8.3419e-06 | 5.124e-06 | 0.036183 | 0.036183 | 0.036183 | 0.98186 | -0.34843 | 0.98148 | -0.35576 | 9.9403
75 | -0.027591 | -0.0069268 | 0.027605 | 0.0069351 | 1.3303e-05 | 8.2573e-06 | 0.041813 | 0.041813 | 0.041813 | 0.982 | -0.34559 | 0.98252 | -0.33549 | 11.4871
76 | 0.022373 | 0.0056146 | -0.022369 | -0.0056126 | 3.1552e-06 | 1.927e-06 | 0.033922 | 0.033922 | 0.033922 | 0.98148 | -0.35576 | 0.98133 | -0.35871 | 9.3191
77 | -0.029433 | -0.0073932 | 0.029435 | 0.0073949 | 2.666e-06 | 1.6609e-06 | 0.044582 | 0.044582 | 0.044582 | 0.98252 | -0.33549 | 0.98261 | -0.33359 | 12.2477
78 | 0.020874 | 0.0052378 | -0.020868 | -0.0052341 | 5.9703e-06 | 3.6203e-06 | 0.031653 | 0.031653 | 0.031653 | 0.98133 | -0.35871 | 0.98102 | -0.36471 | 8.696
79 | -0.030519 | -0.0076665 | 0.030528 | 0.007672 | 8.9085e-06 | 5.5605e-06 | 0.046222 | 0.046222 | 0.046222 | 0.98261 | -0.33359 | 0.98293 | -0.32747 | 12.6985
80 | 0.0018637 | 0.00046686 | -0.0018636 | -0.00046707 | 5.8998e-08 | -2.1082e-07 | 0.0028268 | 0.0028268 | 0.0028268 | 0.98102 | -0.36471 | 0.98099 | -0.36538 | 0.77661
81 | -0.0032475 | -0.00081389 | 0.0032475 | 0.00081388 | 2.2387e-08 | -1.8853e-08 | 0.0048454 | 0.0048454 | 0.0048454 | 0.9973 | -0.051374 | 0.99731 | -0.051229 | 1.3311
82 | -0.0076043 | -0.0019058 | 0.0076051 | 0.0019061 | 8.2673e-07 | 3.056e-07 | 0.011346 | 0.011346 | 0.011346 | 0.99731 | -0.051229 | 0.99743 | -0.048947 | 3.117
83 | -0.16292 | -0.041352 | 0.16331 | 0.041598 | 0.00038461 | 0.00024524 | 0.24324 | 0.24324 | 0.24324 | 0.99743 | -0.048947 | 1 | 0 | 33.4125
84 | 0.15532 | 0.039446 | -0.15524 | -0.039398 | 7.5341e-05 | 4.8023e-05 | 0.2319 | 0.2319 | 0.2319 | 0.99743 | -0.048947 | 0.9969 | -0.059031 | 31.854
85 | 0.019414 | 0.0048723 | -0.019407 | -0.0048683 | 6.642e-06 | 3.9969e-06 | 0.029559 | 0.029559 | 0.029559 | 0.97736 | -0.43637 | 0.97699 | -0.44355 | 8.1207
86 | -0.019414 | -0.0048723 | 0.019419 | 0.0048754 | 5.203e-06 | 3.1309e-06 | 0.029559 | 0.029559 | 0.029559 | 0.97736 | -0.43637 | 0.97764 | -0.43076 | 8.1207
87 | 0.018502 | 0.0046415 | -0.01849 | -0.0046344 | 1.1986e-05 | 7.1675e-06 | 0.028181 | 0.028182 | 0.028182 | 0.97699 | -0.44355 | 0.9763 | -0.45715 | 7.7422
88 | -0.020219 | -0.005076 | 0.020224 | 0.0050792 | 5.2932e-06 | 3.2007e-06 | 0.030777 | 0.030777 | 0.030777 | 0.97764 | -0.43076 | 0.97792 | -0.42527 | 8.4553
89 | -0.13614 | -0.034506 | 0.13667 | 0.034847 | 0.00053307 | 0.00034072 | 0.20467 | 0.20467 | 0.20467 | 0.99041 | -0.18262 | 0.99465 | -0.10148 | 56.2288
90 | -0.13852 | -0.035311 | 0.13886 | 0.035527 | 0.00033804 | 0.00021607 | 0.20745 | 0.20745 | 0.20745 | 0.99465 | -0.10148 | 0.9973 | -0.051058 | 56.9905
91 | 0.016037 | 0.0040226 | -0.016034 | -0.004021 | 2.6395e-06 | 1.5338e-06 | 0.024116 | 0.024116 | 0.024116 | 0.98956 | -0.19914 | 0.98938 | -0.20259 | 6.6252
92 | 0.014156 | 0.0035503 | -0.014153 | -0.0035488 | 2.6215e-06 | 1.4797e-06 | 0.021291 | 0.021291 | 0.021291 | 0.98938 | -0.20259 | 0.98918 | -0.20648 | 5.8492
93 | -0.012404 | -0.0031095 | 0.012408 | 0.0031115 | 3.5295e-06 | 1.9122e-06 | 0.018666 | 0.018666 | 0.018666 | 0.98887 | -0.21245 | 0.98918 | -0.20648 | 5.128
94 | 0.010534 | 0.0026409 | -0.010533 | -0.0026401 | 1.6029e-06 | 8.0765e-07 | 0.015852 | 0.015852 | 0.015852 | 0.98887 | -0.21245 | 0.98871 | -0.21564 | 4.355
95 | 0.0095769 | 0.0024005 | -0.0095752 | -0.0023997 | 1.7159e-06 | 8.1574e-07 | 0.014413 | 0.014414 | 0.014414 | 0.98871 | -0.21564 | 0.98851 | -0.2194 | 3.9598
96 | 0.0095752 | 0.0023997 | -0.0095737 | -0.002399 | 1.5206e-06 | 7.2301e-07 | 0.014414 | 0.014414 | 0.014414 | 0.98851 | -0.2194 | 0.98834 | -0.22274 | 3.9598
97 | -0.021141 | -0.0053089 | 0.021142 | 0.0053095 | 9.8697e-07 | 5.9976e-07 | 0.032172 | 0.032172 | 0.032172 | 0.97792 | -0.42527 | 0.97797 | -0.42429 | 8.8384
98 | -0.021903 | -0.0055004 | 0.021905 | 0.0055015 | 1.857e-06 | 1.1325e-06 | 0.033331 | 0.033331 | 0.033331 | 0.97797 | -0.42429 | 0.97806 | -0.42251 | 9.1568
99 | -0.024703 | -0.0062026 | 0.024708 | 0.0062057 | 5.0714e-06 | 3.1256e-06 | 0.037586 | 0.037586 | 0.037586 | 0.97806 | -0.42251 | 0.97828 | -0.41821 | 10.3259
100 | -0.026045 | -0.0065407 | 0.026047 | 0.006542 | 2.0707e-06 | 1.2811e-06 | 0.03962 | 0.03962 | 0.03962 | 0.97828 | -0.41821 | 0.97837 | -0.41654 | 10.8846
101 | -0.027844 | -0.0069926 | 0.027853 | 0.0069982 | 9.0321e-06 | 5.6119e-06 | 0.042354 | 0.042354 | 0.042354 | 0.97837 | -0.41654 | 0.97871 | -0.40975 | 11.6357
102 | 0.015644 | 0.003921 | -0.015638 | -0.0039178 | 5.4759e-06 | 3.1835e-06 | 0.023843 | 0.023844 | 0.023844 | 0.9763 | -0.45715 | 0.97593 | -0.4645 | 6.5504
103 | -0.028839 | -0.0072452 | 0.028842 | 0.0072473 | 3.347e-06 | 2.0837e-06 | 0.043852 | 0.043852 | 0.043852 | 0.97871 | -0.40975 | 0.97884 | -0.40732 | 12.0474
104 | 0.1231 | 0.031149 | -0.12309 | -0.031145 | 7.0008e-06 | 4.4734e-06 | 0.18458 | 0.18458 | 0.18458 | 0.99297 | -0.13433 | 0.99291 | -0.13551 | 50.7083
105 | -0.13157 | -0.033272 | 0.13192 | 0.033495 | 0.00035037 | 0.00022392 | 0.19727 | 0.19727 | 0.19727 | 0.99297 | -0.13433 | 0.99586 | -0.078971 | 54.1942
106 | 0.11426 | 0.028932 | -0.11401 | -0.028772 | 0.00025082 | 0.00016023 | 0.17134 | 0.17134 | 0.17134 | 0.99291 | -0.13551 | 0.99053 | -0.18134 | 47.0728
107 | -0.13192 | -0.033495 | 0.13204 | 0.033576 | 0.00012671 | 8.0981e-05 | 0.19727 | 0.19727 | 0.19727 | 0.99586 | -0.078971 | 0.9969 | -0.059031 | 54.1942
108 | 0.013431 | 0.0033676 | -0.013426 | -0.0033649 | 4.9223e-06 | 2.7355e-06 | 0.020177 | 0.020177 | 0.020177 | 0.99053 | -0.18134 | 0.99013 | -0.18903 | 5.5432
109 | 0.0066739 | 0.0016727 | -0.0066733 | -0.0016725 | 6.6581e-07 | 1.9915e-07 | 0.01003 | 0.01003 | 0.01003 | 0.99013 | -0.18903 | 0.99002 | -0.19112 | 2.7555
110 | 0.14648 | 0.037574 | -0.14629 | -0.037457 | 0.00018418 | 0.00011733 | 0.21827 | 0.21827 | 0.21827 | 1 | 0 | 0.99863 | -0.025957 | 29.9818
111 | 0.030821 | 0.0077488 | -0.030816 | -0.0077455 | 5.2913e-06 | 3.3055e-06 | 0.046838 | 0.046838 | 0.046838 | 0.97936 | -0.39715 | 0.97917 | -0.40075 | 12.8676
112 | 0.030055 | 0.0075548 | -0.030046 | -0.0075489 | 9.4214e-06 | 5.8783e-06 | 0.045682 | 0.045682 | 0.045682 | 0.97917 | -0.40075 | 0.97884 | -0.40732 | 12.5499
113 | -0.0013288 | -0.00033302 | 0.0013288 | 0.00033275 | 3.5004e-08 | -2.7049e-07 | 0.0020108 | 0.0020106 | 0.0020108 | 0.98332 | -0.32124 | 0.98335 | -0.32068 | 0.5524
114 | 0.14289 | 0.036603 | -0.14271 | -0.036493 | 0.00017356 | 0.00011055 | 0.21319 | 0.21319 | 0.21319 | 0.99863 | -0.025957 | 0.9973 | -0.051058 | 29.2848
115 | -0.0017107 | -0.00042833 | 0.0017108 | 0.00042819 | 3.2917e-08 | -1.4002e-07 | 0.0026089 | 0.0026088 | 0.0026089 | 0.9757 | -0.46889 | 0.97572 | -0.46849 | 0.71672
116 | -0.0021118 | -0.00052869 | 0.0021119 | 0.00052833 | 1.4138e-07 | -3.6364e-07 | 0.0032203 | 0.0032202 | 0.0032203 | 0.97572 | -0.46849 | 0.9758 | -0.46708 | 0.88471
117 | -0.0021119 | -0.00052833 | 0.002112 | 0.00052809 | 9.34e-08 | -2.4029e-07 | 0.0032202 | 0.0032201 | 0.0032202 | 0.9758 | -0.46708 | 0.97584 | -0.46615 | 0.88467
118 | -0.002513 | -0.00062859 | 0.002513 | 0.00062859 | 1.3622e-09 | -2.2197e-09 | 0.0038316 | 0.0038316 | 0.0038316 | 0.97584 | -0.46615 | 0.97584 | -0.46614 | 1.0526
119 | -0.0029139 | -0.00072906 | 0.0029141 | 0.00072886 | 1.8497e-07 | -1.9384e-07 | 0.0044428 | 0.0044427 | 0.0044428 | 0.97584 | -0.46614 | 0.97591 | -0.46481 | 1.2206
120 | 0.0041177 | 0.0010305 | -0.0041177 | -0.0010305 | 5.9251e-08 | -1.2172e-08 | 0.0062779 | 0.0062779 | 0.0062779 | 0.97593 | -0.4645 | 0.97591 | -0.4648 | 1.7247
121 | 0.0037167 | 0.00093001 | -0.0037167 | -0.00093001 | 9.1753e-10 | -3.6567e-10 | 0.0056664 | 0.0056664 | 0.0056664 | 0.97591 | -0.4648 | 0.97591 | -0.46481 | 1.5567
122 | 0.0033154 | 0.00082943 | -0.0033154 | -0.00082944 | 4.9943e-10 | -3.2952e-10 | 0.0050546 | 0.0050546 | 0.0050546 | 0.97591 | -0.46481 | 0.97591 | -0.46481 | 1.3886

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31496 | 0.080054

## res_load
| p_mw | q_mvar
0 | 0.0020729 | 0.00051951
1 | 0.00090633 | 0.00022715
2 | 0.0010212 | 0.00025593
3 | 0.0010062 | 0.00025217
4 | 0.00097246 | 0.00024372
5 | 0.0013031 | 0.00032659
6 | 0.00084913 | 0.00021281
7 | 0.001103 | 0.00027643
8 | 0.0066351 | 0.0016629
9 | 0.0010091 | 0.0002529
10 | 0.0043312 | 0.0010855
11 | 0.0011201 | 0.00028073
12 | 0.0011678 | 0.00029268
13 | 0.00089627 | 0.00022463
14 | 0.0028099 | 0.00070423
15 | 0.0012546 | 0.00031444
16 | 0.0011137 | 0.00027912
17 | 0.0018602 | 0.00046621
18 | 0.0012898 | 0.00032325
19 | 0.0011017 | 0.00027611
20 | 0.0043282 | 0.0010848
21 | 0.00089115 | 0.00022334
22 | 0.0077873 | 0.0019517
23 | 0.01328 | 0.0033282
24 | 0.00090878 | 0.00022776
25 | 0.00040101 | 0.0001005
26 | 0.014132 | 0.0035419
27 | 0.00097072 | 0.00024329
28 | 0.011798 | 0.0029567
29 | 0.0014374 | 0.00036024
30 | 0.0028715 | 0.00071968
31 | 0.0025681 | 0.00064362
32 | 0.016793 | 0.0042086
33 | 0.015737 | 0.003944
34 | 0.00096294 | 0.00024134
35 | 0.015928 | 0.0039919
36 | 0.0010964 | 0.00027479
37 | 0.0018766 | 0.00047033
38 | 0.0077754 | 0.0019487
39 | 0.0034186 | 0.00085678
40 | 0.0049178 | 0.0012325
41 | 0.0040219 | 0.001008
42 | 0.0025113 | 0.0006294
43 | 0.0035414 | 0.00088756
44 | 0.0042541 | 0.0010662
45 | 0.0043007 | 0.0010779
46 | 0.0018866 | 0.00047283
47 | 0.0018288 | 0.00045835
48 | 0.0014915 | 0.00037379
49 | 0.0018281 | 0.00045816
50 | 0.0014958 | 0.00037489
51 | 0.0010835 | 0.00027156
52 | 0.0020136 | 0.00050467
53 | 0.0018636 | 0.00046707
54 | 0.0032475 | 0.00081389
55 | 0.0043568 | 0.0010919
56 | 0.00090483 | 0.00022677
57 | 0.00080028 | 0.00020057
58 | 0.0018534 | 0.0004645
59 | 0.0007966 | 0.00019965
60 | 0.0018781 | 0.0004707
61 | 0.0018701 | 0.00046868
62 | 0.0017452 | 0.0004374
63 | 0.00095586 | 0.00023956
64 | 0.00091654 | 0.00022971
65 | 0.00076164 | 0.00019088
66 | 0.0027972 | 0.00070106
67 | 0.0013369 | 0.00033505
68 | 0.0017977 | 0.00045054
69 | 0.0028462 | 0.00071333
70 | 0.0064618 | 0.0016195
71 | 0.00098567 | 0.00024703
72 | 0.0084673 | 0.0021221
73 | 0.0088303 | 0.0022131
74 | 0.0067521 | 0.0016922
75 | 0.0066733 | 0.0016725
76 | 0.0035215 | 0.00088256
77 | 0.0018317 | 0.00045908
78 | 0.00075883 | 0.00019018
79 | 0.00076107 | 0.00019074
80 | 0.0012033 | 0.00030158
81 | 0.0013288 | 0.00033302
82 | 0.0012574 | 0.00031513
83 | 0.0034052 | 0.00085344
84 | 0.0038526 | 0.00096556
85 | 0.00040093 | 0.00010048
86 | 0.00040101 | 0.0001005
87 | 0.00040101 | 0.0001005
88 | 0.00040088 | 0.00010047
89 | 0.0048402 | 0.0012131
90 | 0.0019277 | 0.00048312
91 | 0.011521 | 0.0028873
92 | 0.0074243 | 0.0018607
93 | 0.00040101 | 0.0001005
94 | 0.00040128 | 0.00010057
95 | 0.00040128 | 0.00010057

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1