## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2583-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2583-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2583-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2583-9_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2583-9_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2583-9_0_4_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_2583-9_0_4_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2583-9_0_4_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_2583-9_0_4_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2583-9_0_4_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_2583-9_0_4_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_2583-9_0_4_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_2583-9_0_4_node_95 | 0.4 | n |  | TRUE
13 | bus_LV_2583-9_0_4_node_112 | 0.4 | n |  | TRUE
14 | bus_LV_2583-9_0_4_node_107 | 0.4 | n |  | TRUE
15 | bus_LV_2583-9_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_2583-9_0_4_node_83 | 0.4 | n |  | TRUE
17 | bus_LV_2583-9_0_4_node_111 | 0.4 | n |  | TRUE
18 | bus_LV_2583-9_0_4_node_82 | 0.4 | n |  | TRUE
19 | bus_LV_2583-9_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2583-9_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2583-9_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2583-9_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2583-9_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2583-9_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2583-9_0_4_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_2583-9_0_4_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_2583-9_0_4_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_2583-9_0_4_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_2583-9_0_4_node_131 | 0.4 | n |  | TRUE
30 | bus_LV_2583-9_0_4_node_130 | 0.4 | n |  | TRUE
31 | bus_LV_2583-9_0_4_node_93 | 0.4 | n |  | TRUE
32 | bus_LV_2583-9_0_4_node_122 | 0.4 | n |  | TRUE
33 | bus_LV_2583-9_0_4_node_118 | 0.4 | n |  | TRUE
34 | bus_LV_2583-9_0_4_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_2583-9_0_4_node_127 | 0.4 | n |  | TRUE
36 | bus_LV_2583-9_0_4_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_2583-9_0_4_node_132 | 0.4 | n |  | TRUE
38 | bus_LV_2583-9_0_4_node_119 | 0.4 | n |  | TRUE
39 | bus_LV_2583-9_0_4_node_96 | 0.4 | n |  | TRUE
40 | bus_LV_2583-9_0_4_node_97 | 0.4 | n |  | TRUE
41 | bus_LV_2583-9_0_4_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_2583-9_0_4_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_2583-9_0_4_node_70 | 0.4 | n |  | TRUE
44 | bus_LV_2583-9_0_4_node_84 | 0.4 | n |  | TRUE
45 | bus_LV_2583-9_0_4_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_2583-9_0_4_node_81 | 0.4 | n |  | TRUE
47 | bus_LV_2583-9_0_4_node_109 | 0.4 | n |  | TRUE
48 | bus_LV_2583-9_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_2583-9_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_2583-9_0_4_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_2583-9_0_4_node_121 | 0.4 | n |  | TRUE
52 | bus_LV_2583-9_0_4_node_115 | 0.4 | n |  | TRUE
53 | bus_LV_2583-9_0_4_node_128 | 0.4 | n |  | TRUE
54 | bus_LV_2583-9_0_4_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_2583-9_0_4_node_116 | 0.4 | n |  | TRUE
56 | bus_LV_2583-9_0_4_node_105 | 0.4 | n |  | TRUE
57 | bus_LV_2583-9_0_4_node_76 | 0.4 | n |  | TRUE
58 | bus_LV_2583-9_0_4_node_129 | 0.4 | n |  | TRUE
59 | bus_LV_2583-9_0_4_node_88 | 0.4 | n |  | TRUE
60 | bus_LV_2583-9_0_4_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_2583-9_0_4_node_92 | 0.4 | n |  | TRUE
62 | bus_LV_2583-9_0_4_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_2583-9_0_4_node_125 | 0.4 | n |  | TRUE
64 | bus_LV_2583-9_0_4_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_2583-9_0_4_node_114 | 0.4 | n |  | TRUE
66 | bus_LV_2583-9_0_4_node_113 | 0.4 | n |  | TRUE
67 | bus_LV_2583-9_0_4_node_133 | 0.4 | n |  | TRUE
68 | bus_LV_2583-9_0_4_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_2583-9_0_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_2583-9_0_4_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_2583-9_0_4_node_103 | 0.4 | n |  | TRUE
72 | bus_LV_2583-9_0_4_node_108 | 0.4 | n |  | TRUE
73 | bus_LV_2583-9_0_4_node_110 | 0.4 | n |  | TRUE
74 | bus_MV_390_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2583-9_0_4_load_0 | 0 | 0.0019198 | 0.00048114 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2583-9_0_4_load_1 | 1 | 0.0019266 | 0.00048286 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2583-9_0_4_load_2 | 2 | 0.0019278 | 0.00048316 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2583-9_0_4_load_3 | 4 | 0.0019249 | 0.00048244 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2583-9_0_4_load_47 | 5 | 0.0019195 | 0.00048107 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2583-9_0_4_load_26 | 6 | 0.0023137 | 0.00057986 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2583-9_0_4_load_27 | 7 | 0.0023204 | 0.00058155 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2583-9_0_4_load_28 | 8 | 0.0019208 | 0.0004814 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2583-9_0_4_load_45 | 11 | 0.0019243 | 0.00048226 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2583-9_0_4_load_95 | 12 | 0.0019233 | 0.00048201 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2583-9_0_4_load_112 | 13 | 0.0019187 | 0.00048087 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2583-9_0_4_load_107 | 14 | 0.0078896 | 0.0019773 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2583-9_0_4_load_111 | 17 | 0.0023187 | 0.00058111 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2583-9_0_4_load_82 | 18 | 0.01466 | 0.003674 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2583-9_0_4_load_15 | 19 | 0.0015905 | 0.00039861 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2583-9_0_4_load_16 | 20 | 0.0029444 | 0.00073793 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2583-9_0_4_load_62 | 26 | 0.0042551 | 0.0010664 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2583-9_0_4_load_63 | 27 | 0.0077337 | 0.0019382 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2583-9_0_4_load_59 | 28 | 0.0057888 | 0.0014508 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2583-9_0_4_load_130 | 30 | 0.004951 | 0.0012408 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2583-9_0_4_load_122 | 32 | 0.010584 | 0.0026526 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2583-9_0_4_load_118 | 33 | 0.0015518 | 0.00038891 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2583-9_0_4_load_127 | 35 | 0.0070145 | 0.001758 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2583-9_0_4_load_60 | 36 | 0.001299 | 0.00032556 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2583-9_0_4_load_132 | 37 | 0.0049165 | 0.0012322 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2583-9_0_4_load_96 | 39 | 0.001917 | 0.00048044 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2583-9_0_4_load_97 | 40 | 0.0019198 | 0.00048115 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2583-9_0_4_load_98 | 41 | 0.0019215 | 0.00048158 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2583-9_0_4_load_48 | 42 | 0.001917 | 0.00048045 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2583-9_0_4_load_84 | 44 | 0.0012201 | 0.00030578 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2583-9_0_4_load_85 | 45 | 0.0012908 | 0.0003235 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2583-9_0_4_load_81 | 46 | 0.0092901 | 0.0023283 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2583-9_0_4_load_109 | 47 | 0.0011803 | 0.00029581 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2583-9_0_4_load_44 | 48 | 0.0019203 | 0.00048128 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2583-9_0_4_load_46 | 49 | 0.0019218 | 0.00048166 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2583-9_0_4_load_121 | 51 | 0.0050466 | 0.0012648 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2583-9_0_4_load_115 | 52 | 0.0049894 | 0.0012505 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2583-9_0_4_load_106 | 54 | 0.0046324 | 0.001161 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2583-9_0_4_load_116 | 55 | 0.0038044 | 0.00095347 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2583-9_0_4_load_105 | 56 | 0.076253 | 0.019111 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2583-9_0_4_load_129 | 58 | 0.0013345 | 0.00033445 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2583-9_0_4_load_88 | 59 | 0.0032311 | 0.0008098 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2583-9_0_4_load_92 | 61 | 0.0038082 | 0.00095443 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2583-9_0_4_load_126 | 62 | 0.0012207 | 0.00030595 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2583-9_0_4_load_125 | 63 | 0.0012201 | 0.00030578 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2583-9_0_4_load_114 | 65 | 0.0062869 | 0.0015756 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2583-9_0_4_load_113 | 66 | 0.0065069 | 0.0016308 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2583-9_0_4_load_133 | 67 | 0.0049273 | 0.0012349 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2583-9_0_4_load_99 | 68 | 0.0019203 | 0.00048126 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2583-9_0_4_load_100 | 69 | 0.0023168 | 0.00058063 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2583-9_0_4_load_101 | 70 | 0.092325 | 0.023139 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2583-9_0_4_load_108 | 72 | 0.0023181 | 0.00058096 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2583-9_0_4_load_110 | 73 | 0.0011864 | 0.00029734 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2583-9_0_4_line_0 |  | 0 | 1 | 0.04789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2583-9_0_4_line_1 |  | 0 | 2 | 0.0087096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2583-9_0_4_line_2 |  | 2 | 3 | 0.0023473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2583-9_0_4_line_3 |  | 3 | 6 | 0.025167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2583-9_0_4_line_4 |  | 3 | 7 | 0.014617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2583-9_0_4_line_5 |  | 3 | 8 | 0.012525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2583-9_0_4_line_6 |  | 3 | 9 | 0.10741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2583-9_0_4_line_7 |  | 3 | 10 | 0.10825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2583-9_0_4_line_8 |  | 4 | 5 | 0.0087096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2583-9_0_4_line_9 |  | 5 | 11 | 0.039256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2583-9_0_4_line_10 |  | 6 | 12 | 0.020674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2583-9_0_4_line_11 |  | 8 | 13 | 0.014896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2583-9_0_4_line_12 |  | 9 | 14 | 0.025719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2583-9_0_4_line_13 |  | 10 | 18 | 0.027377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2583-9_0_4_line_14 |  | 11 | 48 | 0.00014868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2583-9_0_4_line_15 |  | 12 | 39 | 0.033498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2583-9_0_4_line_16 |  | 13 | 42 | 0.013114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2583-9_0_4_line_17 |  | 14 | 43 | 0.02649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2583-9_0_4_line_18 |  | 15 | 16 | 0.03164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2583-9_0_4_line_19 |  | 15 | 17 | 0.017082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2583-9_0_4_line_20 |  | 16 | 44 | 0.012167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2583-9_0_4_line_21 |  | 16 | 45 | 0.02556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2583-9_0_4_line_22 |  | 16 | 46 | 0.023092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2583-9_0_4_line_23 |  | 17 | 47 | 0.014712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2583-9_0_4_line_24 |  | 18 | 46 | 0.038131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2583-9_0_4_line_25 |  | 19 | 20 | 0.018578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2583-9_0_4_line_26 |  | 20 | 21 | 0.01593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2583-9_0_4_line_27 |  | 21 | 25 | 0.027767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2583-9_0_4_line_28 |  | 22 | 23 | 0.009225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2583-9_0_4_line_29 |  | 22 | 24 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2583-9_0_4_line_30 |  | 23 | 26 | 0.039306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2583-9_0_4_line_31 |  | 23 | 27 | 0.021193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2583-9_0_4_line_32 |  | 23 | 28 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2583-9_0_4_line_33 |  | 24 | 29 | 0.015983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2583-9_0_4_line_34 |  | 24 | 30 | 0.00611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2583-9_0_4_line_35 |  | 25 | 33 | 0.016722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2583-9_0_4_line_36 |  | 25 | 34 | 0.024156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2583-9_0_4_line_37 |  | 26 | 31 | 0.020515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2583-9_0_4_line_38 |  | 27 | 35 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2583-9_0_4_line_39 |  | 28 | 36 | 0.03083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2583-9_0_4_line_40 |  | 29 | 37 | 0.006064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2583-9_0_4_line_41 |  | 29 | 38 | 0.02042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2583-9_0_4_line_42 |  | 31 | 32 | 0.028739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2583-9_0_4_line_43 |  | 34 | 55 | 0.020817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2583-9_0_4_line_44 |  | 35 | 53 | 0.015919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2583-9_0_4_line_45 |  | 36 | 50 | 0.008137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2583-9_0_4_line_46 |  | 38 | 67 | 0.006016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2583-9_0_4_line_47 |  | 38 | 64 | 0.01292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2583-9_0_4_line_48 |  | 39 | 68 | 0.030285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2583-9_0_4_line_49 |  | 40 | 41 | 0.011327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2583-9_0_4_line_50 |  | 41 | 69 | 0.037724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2583-9_0_4_line_51 |  | 42 | 49 | 0.00011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2583-9_0_4_line_52 |  | 43 | 54 | 0.018258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2583-9_0_4_line_53 |  | 44 | 62 | 0.012588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2583-9_0_4_line_54 |  | 45 | 50 | 0.0076343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2583-9_0_4_line_55 |  | 47 | 72 | 0.0032787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2583-9_0_4_line_56 |  | 48 | 49 | 0.02024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2583-9_0_4_line_57 |  | 50 | 51 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2583-9_0_4_line_58 |  | 51 | 52 | 0.020107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2583-9_0_4_line_59 |  | 53 | 57 | 0.017884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2583-9_0_4_line_60 |  | 54 | 56 | 0.052949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2583-9_0_4_line_61 |  | 55 | 61 | 0.020138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2583-9_0_4_line_62 |  | 56 | 71 | 0.055652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2583-9_0_4_line_63 |  | 57 | 58 | 0.050019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2583-9_0_4_line_64 |  | 59 | 60 | 0.00505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2583-9_0_4_line_65 |  | 60 | 64 | 0.023396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2583-9_0_4_line_66 |  | 60 | 61 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2583-9_0_4_line_67 |  | 62 | 63 | 0.012182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2583-9_0_4_line_68 |  | 64 | 65 | 0.018571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2583-9_0_4_line_69 |  | 65 | 66 | 0.020217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2583-9_0_4_line_70 |  | 68 | 69 | 0.00179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2583-9_0_4_line_71 |  | 70 | 71 | 0.081359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2583-9_0_4_line_72 |  | 72 | 73 | 0.0012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2583-9_0_4_trafo_46 | 0.63 MVA 20/0.4 kV | 74 | 49 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2643079.7692 | 1247930.6877 | 2643098.5214 | 1247940.3433 | 2643100.1826 | 1247943.5019 | 2643099.3031 | 1247948.132 | 2643091.0153 | 1247964.6896
1 | 2643079.7692 | 1247930.6877 | 2643072.0258 | 1247926.7006
2 | 2643069.9388 | 1247925.626 | 2643072.0258 | 1247926.7006
3 | 2643069.9388 | 1247925.626 | 2643092.3136 | 1247937.1469
4 | 2643069.9388 | 1247925.626 | 2643056.9071 | 1247919.0048
5 | 2643069.9388 | 1247925.626 | 2643058.7722 | 1247919.9524
6 | 2643069.9388 | 1247925.626 | 2643085.1655 | 1247896.2281 | 2643151.2007 | 1247930.2972
7 | 2643022.0609 | 1247856.7995 | 2643030.2279 | 1247865.698 | 2643036.0966 | 1247870.7884 | 2643047.2035 | 1247877.3066 | 2643085.1655 | 1247896.2281 | 2643069.9388 | 1247925.626
8 | 2643041.4325 | 1247987.7756 | 2643049.2688 | 1247991.5768
9 | 2643041.4325 | 1247987.7756 | 2643027.5559 | 1247981.0444 | 2643026.1048 | 1247978.0874 | 2643035.2022 | 1247959.673
10 | 2643092.3136 | 1247937.1469 | 2643098.5214 | 1247940.3433 | 2643100.1826 | 1247943.5019 | 2643099.3031 | 1247948.132 | 2643096.8818 | 1247952.9693
11 | 2643058.7722 | 1247919.9524 | 2643056.9071 | 1247919.0048 | 2643054.3635 | 1247920.8876 | 2643050.094 | 1247929.5298
12 | 2643151.2007 | 1247930.2972 | 2643174.3554 | 1247941.4913
13 | 2643022.0609 | 1247856.7995 | 2643009.8796 | 1247881.3167
14 | 2643035.2022 | 1247959.673 | 2643035.268 | 1247959.5397
15 | 2643081.8883 | 1247982.9241 | 2643096.8818 | 1247952.9693
16 | 2643044.2853 | 1247941.2874 | 2643050.094 | 1247929.5298
17 | 2643198.2042 | 1247953.021 | 2643174.3554 | 1247941.4913
18 | 2643011.1978 | 1247949.9384 | 2642982.6385 | 1247936.1445
19 | 2643011.1978 | 1247949.9384 | 2643003.6119 | 1247965.2436
20 | 2642982.6385 | 1247936.1445 | 2642981.0086 | 1247942.2256 | 2642978.367 | 1247947.4692
21 | 2642982.6385 | 1247936.1445 | 2642959.6179 | 1247925.0371
22 | 2642982.6385 | 1247936.1445 | 2642992.9132 | 1247915.4648
23 | 2642997.0785 | 1247978.4256 | 2643003.6119 | 1247965.2436
24 | 2642992.9132 | 1247915.4648 | 2643009.8796 | 1247881.3167
25 | 2642889.0599 | 1247830.1886 | 2642894.1527 | 1247832.88 | 2642895.9639 | 1247834.105 | 2642892.229 | 1247844.0588
26 | 2642874.976 | 1247822.7458 | 2642889.0599 | 1247830.1886
27 | 2642887.3975 | 1247797.8967 | 2642874.976 | 1247822.7458
28 | 2642908.3243 | 1247889.7314 | 2642912.3642 | 1247881.4328
29 | 2642918.9262 | 1247867.9491 | 2642912.3642 | 1247881.4328
30 | 2642908.3243 | 1247889.7314 | 2642872.6015 | 1247873.335
31 | 2642908.3243 | 1247889.7314 | 2642898.8348 | 1247908.6812
32 | 2642908.3243 | 1247889.7314 | 2642910.5111 | 1247895.3954 | 2642922.1783 | 1247900.9641
33 | 2642918.9262 | 1247867.9491 | 2642925.9177 | 1247853.5679
34 | 2642913.3792 | 1247865.3517 | 2642918.9262 | 1247867.9491
35 | 2642887.3975 | 1247797.8967 | 2642902.6608 | 1247804.7262
36 | 2642887.3975 | 1247797.8967 | 2642898.1646 | 1247776.2602
37 | 2642853.9571 | 1247864.7775 | 2642872.6015 | 1247873.335
38 | 2642898.8348 | 1247908.6812 | 2642892.9072 | 1247920.5182
39 | 2642922.1783 | 1247900.9641 | 2642950.0013 | 1247914.2441
40 | 2642920.4542 | 1247850.9043 | 2642925.9177 | 1247853.5679
41 | 2642925.9177 | 1247853.5679 | 2642934.8562 | 1247835.1981
42 | 2642853.9571 | 1247864.7775 | 2642841.1074 | 1247890.4836
43 | 2642898.1646 | 1247776.2602 | 2642916.7693 | 1247785.5991
44 | 2642884.9364 | 1247932.4908 | 2642891.3339 | 1247919.8175 | 2642892.9072 | 1247920.5182
45 | 2642957.3447 | 1247917.7491 | 2642950.0013 | 1247914.2441
46 | 2642929.2845 | 1247832.8896 | 2642934.8562 | 1247835.1981
47 | 2642934.8562 | 1247835.1981 | 2642940.5138 | 1247823.5757
48 | 2643081.8883 | 1247982.9241 | 2643072.9806 | 1248000.7203 | 2643070.2318 | 1248001.7455 | 2643063.5285 | 1247998.4938
49 | 2643029.4563 | 1247971.3036 | 2643026.1048 | 1247978.0874 | 2643027.5559 | 1247981.0444 | 2643027.976 | 1247981.2481
50 | 2643061.9179 | 1247997.7126 | 2643027.976 | 1247981.2481
51 | 2643044.233 | 1247941.3934 | 2643044.2853 | 1247941.2874
52 | 2643198.2042 | 1247953.021 | 2643189.7521 | 1247969.2051
53 | 2642972.7038 | 1247958.7111 | 2642978.367 | 1247947.4692
54 | 2642957.3447 | 1247917.7491 | 2642959.6179 | 1247925.0371
55 | 2642995.6225 | 1247981.3632 | 2642997.0785 | 1247978.4256
56 | 2643044.233 | 1247941.3934 | 2643035.268 | 1247959.5397
57 | 2642957.3447 | 1247917.7491 | 2642968.0332 | 1247896.1282
58 | 2642968.0332 | 1247896.1282 | 2642976.9437 | 1247878.1039
59 | 2642877.2225 | 1247948.6347 | 2642884.9364 | 1247932.4908
60 | 2643189.7521 | 1247969.2051 | 2643165.241 | 1248016.1389
61 | 2642916.7693 | 1247785.5991 | 2642918.391 | 1247786.4132 | 2642934.7932 | 1247794.5803
62 | 2643139.4787 | 1248065.4687 | 2643165.241 | 1248016.1389
63 | 2642877.2225 | 1247948.6347 | 2642882.0681 | 1247951.1047 | 2642921.8484 | 1247971.2266
64 | 2642950.8384 | 1247802.5698 | 2642953.1019 | 1247798.0554
65 | 2642950.8384 | 1247802.5698 | 2642947.3903 | 1247809.4383 | 2642940.5138 | 1247823.5757
66 | 2642950.8384 | 1247802.5698 | 2642934.7932 | 1247794.5803
67 | 2642967.223 | 1247969.5909 | 2642972.7038 | 1247958.7111
68 | 2642940.5138 | 1247823.5757 | 2642957.1535 | 1247831.8214
69 | 2642975.2688 | 1247840.7982 | 2642957.1535 | 1247831.8214
70 | 2643061.9179 | 1247997.7126 | 2643063.5285 | 1247998.4938
71 | 2643139.4787 | 1248065.4687 | 2643107.9942 | 1248050.0964 | 2643107.4133 | 1248045.856 | 2643125.3156 | 1248007.8163
72 | 2642995.0652 | 1247982.4876 | 2642995.6225 | 1247981.3632

## bus_geodata
| x | y | coords
0 | 2643079.7692 | 1247930.6877
1 | 2643091.0153 | 1247964.6896
2 | 2643072.0258 | 1247926.7006
3 | 2643069.9388 | 1247925.626
4 | 2643049.2688 | 1247991.5768
5 | 2643041.4325 | 1247987.7756
6 | 2643092.3136 | 1247937.1469
7 | 2643056.9071 | 1247919.0048
8 | 2643058.7722 | 1247919.9524
9 | 2643151.2007 | 1247930.2972
10 | 2643022.0609 | 1247856.7995
11 | 2643035.2022 | 1247959.673
12 | 2643096.8818 | 1247952.9693
13 | 2643050.094 | 1247929.5298
14 | 2643174.3554 | 1247941.4913
15 | 2643011.1978 | 1247949.9384
16 | 2642982.6385 | 1247936.1445
17 | 2643003.6119 | 1247965.2436
18 | 2643009.8796 | 1247881.3167
19 | 2642892.229 | 1247844.0588
20 | 2642889.0599 | 1247830.1886
21 | 2642874.976 | 1247822.7458
22 | 2642912.3642 | 1247881.4328
23 | 2642908.3243 | 1247889.7314
24 | 2642918.9262 | 1247867.9491
25 | 2642887.3975 | 1247797.8967
26 | 2642872.6015 | 1247873.335
27 | 2642898.8348 | 1247908.6812
28 | 2642922.1783 | 1247900.9641
29 | 2642925.9177 | 1247853.5679
30 | 2642913.3792 | 1247865.3517
31 | 2642853.9571 | 1247864.7775
32 | 2642841.1074 | 1247890.4836
33 | 2642902.6608 | 1247804.7262
34 | 2642898.1646 | 1247776.2602
35 | 2642892.9072 | 1247920.5182
36 | 2642950.0013 | 1247914.2441
37 | 2642920.4542 | 1247850.9043
38 | 2642934.8562 | 1247835.1981
39 | 2643081.8883 | 1247982.9241
40 | 2643029.4563 | 1247971.3036
41 | 2643027.976 | 1247981.2481
42 | 2643044.2853 | 1247941.2874
43 | 2643198.2042 | 1247953.021
44 | 2642978.367 | 1247947.4692
45 | 2642959.6179 | 1247925.0371
46 | 2642992.9132 | 1247915.4648
47 | 2642997.0785 | 1247978.4256
48 | 2643035.268 | 1247959.5397
49 | 2643044.233 | 1247941.3934
50 | 2642957.3447 | 1247917.7491
51 | 2642968.0332 | 1247896.1282
52 | 2642976.9437 | 1247878.1039
53 | 2642884.9364 | 1247932.4908
54 | 2643189.7521 | 1247969.2051
55 | 2642916.7693 | 1247785.5991
56 | 2643165.241 | 1248016.1389
57 | 2642877.2225 | 1247948.6347
58 | 2642921.8484 | 1247971.2266
59 | 2642953.1019 | 1247798.0554
60 | 2642950.8384 | 1247802.5698
61 | 2642934.7932 | 1247794.5803
62 | 2642972.7038 | 1247958.7111
63 | 2642967.223 | 1247969.5909
64 | 2642940.5138 | 1247823.5757
65 | 2642957.1535 | 1247831.8214
66 | 2642975.2688 | 1247840.7982
67 | 2642929.2845 | 1247832.8896
68 | 2643063.5285 | 1247998.4938
69 | 2643061.9179 | 1247997.7126
70 | 2643125.3156 | 1248007.8163
71 | 2643139.4787 | 1248065.4687
72 | 2642995.6225 | 1247981.3632
73 | 2642995.0652 | 1247982.4876
74 | 2643069.9388 | 1247925.626

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99576 | -0.080031 | 0.0019198 | 0.00048114
1 | 0.99567 | -0.081653 | 0.0019266 | 0.00048286
2 | 0.99579 | -0.079442 | 0.0019278 | 0.00048316
3 | 0.9958 | -0.079203 | 0 | 0
4 | 0.99971 | -0.0056531 | 0.0019249 | 0.00048244
5 | 0.99972 | -0.0053607 | 0.0019195 | 0.00048107
6 | 0.99547 | -0.085503 | 0.0023137 | 0.00057986
7 | 0.99577 | -0.0798 | 0.0023204 | 0.00058155
8 | 0.99709 | -0.054873 | 0.0019208 | 0.0004814
9 | 0.98978 | -0.19388 | 0 | 0
10 | 0.99149 | -0.16106 | 0 | 0
11 | 0.99986 | -0.0027285 | 0.0019243 | 0.00048226
12 | 0.99525 | -0.089839 | 0.0019233 | 0.00048201
13 | 0.99862 | -0.025853 | 0.0019187 | 0.00048087
14 | 0.98833 | -0.22155 | 0.0078896 | 0.0019773
15 | 0.98173 | -0.34896 | 0 | 0
16 | 0.98194 | -0.34496 | 0 | 0
17 | 0.98162 | -0.35113 | 0.0023187 | 0.00058111
18 | 0.98822 | -0.22363 | 0.01466 | 0.003674
19 | 0.97088 | -0.56182 | 0.0015905 | 0.00039861
20 | 0.97091 | -0.56127 | 0.0029444 | 0.00073793
21 | 0.97098 | -0.55994 | 0 | 0
22 | 0.97436 | -0.49301 | 0 | 0
23 | 0.97475 | -0.48547 | 0 | 0
24 | 0.97374 | -0.50527 | 0 | 0
25 | 0.97109 | -0.55761 | 0 | 0
26 | 0.97421 | -0.49618 | 0.0042551 | 0.0010664
27 | 0.97443 | -0.49173 | 0.0077337 | 0.0019382
28 | 0.97608 | -0.45921 | 0.0057888 | 0.0014508
29 | 0.97315 | -0.51691 | 0 | 0
30 | 0.97371 | -0.50583 | 0.004951 | 0.0012408
31 | 0.974 | -0.50017 | 0 | 0
32 | 0.97372 | -0.50576 | 0.010584 | 0.0026526
33 | 0.97107 | -0.55809 | 0.0015518 | 0.00038891
34 | 0.97123 | -0.55489 | 0 | 0
35 | 0.97433 | -0.49376 | 0.0070145 | 0.001758
36 | 0.97842 | -0.4135 | 0.001299 | 0.00032556
37 | 0.97312 | -0.51746 | 0.0049165 | 0.0012322
38 | 0.97249 | -0.52994 | 0 | 0
39 | 0.99494 | -0.095735 | 0.001917 | 0.00048044
40 | 0.99456 | -0.10318 | 0.0019198 | 0.00048115
41 | 0.99458 | -0.10279 | 0.0019215 | 0.00048158
42 | 0.99999 | -0.00023185 | 0.001917 | 0.00048045
43 | 0.98691 | -0.24888 | 0 | 0
44 | 0.9819 | -0.34576 | 0.0012201 | 0.00030578
45 | 0.9797 | -0.38843 | 0.0012908 | 0.0003235
46 | 0.98418 | -0.30142 | 0.0092901 | 0.0023283
47 | 0.98156 | -0.35238 | 0.0011803 | 0.00029581
48 | 0.99986 | -0.0027135 | 0.0019203 | 0.00048128
49 | 1 | 0 | -0.35371 | -0.090818
50 | 0.97904 | -0.40127 | 0 | 0
51 | 0.97882 | -0.40568 | 0.0050466 | 0.0012648
52 | 0.97873 | -0.4075 | 0.0049894 | 0.0012505
53 | 0.97431 | -0.49415 | 0 | 0
54 | 0.98593 | -0.26776 | 0.0046324 | 0.001161
55 | 0.97135 | -0.55255 | 0.0038044 | 0.00095347
56 | 0.98317 | -0.32126 | 0.076253 | 0.019111
57 | 0.97429 | -0.49459 | 0 | 0
58 | 0.97422 | -0.49581 | 0.0013345 | 0.00033445
59 | 0.97175 | -0.54464 | 0.0032311 | 0.0008098
60 | 0.97176 | -0.54433 | 0 | 0
61 | 0.97153 | -0.54887 | 0.0038082 | 0.00095443
62 | 0.98187 | -0.34632 | 0.0012207 | 0.00030595
63 | 0.98185 | -0.34659 | 0.0012201 | 0.00030578
64 | 0.97213 | -0.53702 | 0 | 0
65 | 0.97191 | -0.54141 | 0.0062869 | 0.0015756
66 | 0.97179 | -0.54383 | 0.0065069 | 0.0016308
67 | 0.97246 | -0.53049 | 0.0049273 | 0.0012349
68 | 0.99472 | -0.10004 | 0.0019203 | 0.00048126
69 | 0.99471 | -0.10024 | 0.0023168 | 0.00058063
70 | 0.97136 | -0.55213 | 0.092325 | 0.023139
71 | 0.97837 | -0.41436 | 0 | 0
72 | 0.98155 | -0.35258 | 0.0023181 | 0.00058096
73 | 0.98155 | -0.35261 | 0.0011864 | 0.00029734
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0019268 | 0.00048234 | -0.0019266 | -0.00048286 | 1.4888e-07 | -5.2763e-07 | 0.0028791 | 0.0028793 | 0.0028793 | 0.99576 | -0.080031 | 0.99567 | -0.081653 | 0.79103
1 | -0.0038466 | -0.00096348 | 0.0038467 | 0.00096343 | 1.0791e-07 | -4.4238e-08 | 0.005748 | 0.0057479 | 0.005748 | 0.99576 | -0.080031 | 0.99579 | -0.079442 | 1.5791
2 | -0.0057745 | -0.0014466 | 0.0057746 | 0.0014466 | 6.5539e-08 | 1.1408e-08 | 0.0086287 | 0.0086287 | 0.0086287 | 0.99579 | -0.079442 | 0.9958 | -0.079203 | 2.3705
3 | 0.014244 | 0.0035724 | -0.01424 | -0.00357 | 4.2759e-06 | 2.4093e-06 | 0.021286 | 0.021286 | 0.021286 | 0.9958 | -0.079203 | 0.99547 | -0.085503 | 5.8477
4 | 0.0023205 | 0.0005814 | -0.0023204 | -0.00058155 | 6.5904e-08 | -1.4798e-07 | 0.0034674 | 0.0034675 | 0.0034675 | 0.9958 | -0.079203 | 0.99577 | -0.0798 | 0.9526
5 | -0.3373 | -0.086612 | 0.3377 | 0.086866 | 0.00039891 | 0.00025482 | 0.50477 | 0.50477 | 0.50477 | 0.9958 | -0.079203 | 0.99709 | -0.054873 | 46.224
6 | 0.18422 | 0.047373 | -0.1832 | -0.046724 | 0.0010206 | 0.00064902 | 0.2757 | 0.27571 | 0.27571 | 0.9958 | -0.079203 | 0.98978 | -0.19388 | 25.2478
7 | 0.13074 | 0.033638 | -0.13023 | -0.033311 | 0.00051812 | 0.00032739 | 0.19568 | 0.19568 | 0.19568 | 0.9958 | -0.079203 | 0.99149 | -0.16106 | 17.9195
8 | -0.0019249 | -0.00048244 | 0.001925 | 0.00048234 | 2.6812e-08 | -9.7038e-08 | 0.0028652 | 0.0028651 | 0.0028652 | 0.99971 | -0.0056531 | 0.99972 | -0.0053607 | 0.78714
9 | -0.0038445 | -0.00096341 | 0.0038449 | 0.0009632 | 4.82e-07 | -2.0631e-07 | 0.0057222 | 0.005722 | 0.0057222 | 0.99972 | -0.0053607 | 0.99986 | -0.0027285 | 1.572
10 | 0.011926 | 0.0029901 | -0.011924 | -0.0029888 | 2.4639e-06 | 1.3082e-06 | 0.017827 | 0.017827 | 0.017827 | 0.99547 | -0.085503 | 0.99525 | -0.089839 | 4.8976
11 | -0.33962 | -0.087348 | 0.3401 | 0.087654 | 0.00047982 | 0.0003065 | 0.50763 | 0.50763 | 0.50763 | 0.99709 | -0.054873 | 0.99862 | -0.025853 | 46.4865
12 | 0.1832 | 0.046724 | -0.18295 | -0.046569 | 0.00024437 | 0.00015541 | 0.27571 | 0.27571 | 0.27571 | 0.98978 | -0.19388 | 0.98833 | -0.22155 | 25.2479
13 | 0.13023 | 0.033311 | -0.12983 | -0.03306 | 0.00039311 | 0.00025124 | 0.19568 | 0.19568 | 0.19568 | 0.99149 | -0.16106 | 0.98822 | -0.22363 | 53.7587
14 | -0.0057692 | -0.0014455 | 0.0057692 | 0.0014455 | 4.1099e-09 | 6.807e-10 | 0.0085857 | 0.0085857 | 0.0085857 | 0.99986 | -0.0027285 | 0.99986 | -0.0027135 | 2.3587
15 | 0.01 | 0.0025068 | -0.0099976 | -0.0025054 | 2.8083e-06 | 1.3621e-06 | 0.014952 | 0.014952 | 0.014952 | 0.99525 | -0.089839 | 0.99494 | -0.095735 | 4.1077
16 | -0.34202 | -0.088135 | 0.34245 | 0.088408 | 0.0004272 | 0.00027289 | 0.51049 | 0.51049 | 0.51049 | 0.99862 | -0.025853 | 0.99999 | -0.00023185 | 46.7482
17 | 0.17506 | 0.044591 | -0.17483 | -0.044445 | 0.00023048 | 0.00014649 | 0.26383 | 0.26383 | 0.26383 | 0.98833 | -0.22155 | 0.98691 | -0.24888 | 24.1601
18 | -0.0070045 | -0.0017554 | 0.0070058 | 0.0017559 | 1.3373e-06 | 4.5575e-07 | 0.010617 | 0.010617 | 0.010617 | 0.98173 | -0.34896 | 0.98194 | -0.34496 | 2.9167
19 | 0.0070045 | 0.0017554 | -0.0070038 | -0.0017552 | 7.2203e-07 | 2.4613e-07 | 0.010617 | 0.010617 | 0.010617 | 0.98173 | -0.34896 | 0.98162 | -0.35113 | 2.9167
20 | 0.0036612 | 0.00091719 | -0.003661 | -0.00091725 | 1.4044e-07 | -6.4023e-08 | 0.0055479 | 0.005548 | 0.005548 | 0.98194 | -0.34496 | 0.9819 | -0.34576 | 1.5242
21 | 0.094564 | 0.023968 | -0.094367 | -0.023842 | 0.0001971 | 0.00012582 | 0.1434 | 0.1434 | 0.1434 | 0.98194 | -0.34496 | 0.9797 | -0.38843 | 39.3951
22 | -0.10523 | -0.026641 | 0.10545 | 0.026782 | 0.00022047 | 0.00014081 | 0.15956 | 0.15956 | 0.15956 | 0.98194 | -0.34496 | 0.98418 | -0.30142 | 43.8359
23 | 0.0046851 | 0.0011741 | -0.0046848 | -0.0011741 | 2.7828e-07 | -7.8762e-09 | 0.007102 | 0.0071021 | 0.0071021 | 0.98162 | -0.35113 | 0.98156 | -0.35238 | 1.9511
24 | 0.11517 | 0.029386 | -0.11474 | -0.02911 | 0.00043097 | 0.00027533 | 0.17361 | 0.17361 | 0.17361 | 0.98822 | -0.22363 | 0.98418 | -0.30142 | 47.6946
25 | -0.0015905 | -0.00039861 | 0.0015905 | 0.0003984 | 4.1396e-08 | -2.0326e-07 | 0.0024376 | 0.0024375 | 0.0024376 | 0.97088 | -0.56182 | 0.97091 | -0.56127 | 0.66968
26 | -0.0045349 | -0.0011363 | 0.0045352 | 0.0011363 | 2.8855e-07 | -1.2347e-08 | 0.0069501 | 0.00695 | 0.0069501 | 0.97091 | -0.56127 | 0.97098 | -0.55994 | 1.9094
27 | -0.0045352 | -0.0011363 | 0.0045357 | 0.0011363 | 5.0295e-07 | -2.1597e-08 | 0.00695 | 0.0069499 | 0.00695 | 0.97098 | -0.55994 | 0.97109 | -0.55761 | 1.9093
28 | -0.044615 | -0.011215 | 0.044631 | 0.011226 | 1.6065e-05 | 1.0167e-05 | 0.068147 | 0.068147 | 0.068147 | 0.97436 | -0.49301 | 0.97475 | -0.48547 | 18.7217
29 | 0.044615 | 0.011215 | -0.044589 | -0.011199 | 2.6104e-05 | 1.652e-05 | 0.068147 | 0.068147 | 0.068147 | 0.97436 | -0.49301 | 0.97374 | -0.50527 | 18.7218
30 | 0.014851 | 0.0037258 | -0.014844 | -0.0037215 | 7.5771e-06 | 4.3597e-06 | 0.022673 | 0.022673 | 0.022673 | 0.97475 | -0.48547 | 0.97421 | -0.49618 | 6.2289
31 | 0.016088 | 0.0040329 | -0.016084 | -0.0040301 | 4.7939e-06 | 2.804e-06 | 0.02456 | 0.02456 | 0.02456 | 0.97475 | -0.48547 | 0.97443 | -0.49173 | 6.7473
32 | -0.075571 | -0.018984 | 0.075666 | 0.019045 | 9.485e-05 | 6.0467e-05 | 0.11538 | 0.11538 | 0.11538 | 0.97475 | -0.48547 | 0.97608 | -0.45921 | 31.6978
33 | 0.039638 | 0.009958 | -0.039616 | -0.0099441 | 2.1997e-05 | 1.3879e-05 | 0.060581 | 0.060581 | 0.060581 | 0.97374 | -0.50527 | 0.97315 | -0.51691 | 16.6432
34 | 0.0049511 | 0.0012408 | -0.004951 | -0.0012408 | 1.3116e-07 | 7.9404e-09 | 0.007566 | 0.007566 | 0.007566 | 0.97374 | -0.50527 | 0.97371 | -0.50583 | 2.0786
35 | 0.0015518 | 0.00038872 | -0.0015518 | -0.00038891 | 3.5454e-08 | -1.8418e-07 | 0.0023778 | 0.0023778 | 0.0023778 | 0.97109 | -0.55761 | 0.97107 | -0.55809 | 0.65325
36 | -0.0060875 | -0.001525 | 0.0060883 | 0.0015252 | 7.8813e-07 | 2.0551e-07 | 0.0093277 | 0.0093276 | 0.0093277 | 0.97109 | -0.55761 | 0.97123 | -0.55489 | 2.5625
37 | 0.010589 | 0.002655 | -0.010587 | -0.002654 | 2.0124e-06 | 1.0326e-06 | 0.016174 | 0.016174 | 0.016174 | 0.97421 | -0.49618 | 0.974 | -0.50017 | 4.4433
38 | 0.0083499 | 0.0020918 | -0.0083491 | -0.0020915 | 8.0708e-07 | 3.5164e-07 | 0.01275 | 0.012751 | 0.012751 | 0.97443 | -0.49173 | 0.97433 | -0.49376 | 3.5029
39 | -0.081455 | -0.020496 | 0.081633 | 0.020609 | 0.00017835 | 0.00011376 | 0.1242 | 0.1242 | 0.1242 | 0.97608 | -0.45921 | 0.97842 | -0.4135 | 34.1222
40 | 0.0049166 | 0.0012322 | -0.0049165 | -0.0012322 | 1.2852e-07 | 6.9153e-09 | 0.0075178 | 0.0075179 | 0.0075179 | 0.97315 | -0.51691 | 0.97312 | -0.51746 | 2.0653
41 | 0.0347 | 0.0087119 | -0.034678 | -0.0086984 | 2.1562e-05 | 1.3546e-05 | 0.053063 | 0.053064 | 0.053064 | 0.97315 | -0.51691 | 0.97249 | -0.52994 | 14.5779
42 | 0.010587 | 0.002654 | -0.010584 | -0.0026526 | 2.8192e-06 | 1.4467e-06 | 0.016174 | 0.016174 | 0.016174 | 0.974 | -0.50017 | 0.97372 | -0.50576 | 4.4434
43 | -0.0060883 | -0.0015252 | 0.0060889 | 0.0015254 | 6.7918e-07 | 1.7703e-07 | 0.0093276 | 0.0093275 | 0.0093276 | 0.97123 | -0.55489 | 0.97135 | -0.55255 | 2.5625
44 | 0.0013346 | 0.00033349 | -0.0013346 | -0.00033367 | 2.4792e-08 | -1.8239e-07 | 0.0020379 | 0.0020379 | 0.0020379 | 0.97433 | -0.49376 | 0.97431 | -0.49415 | 0.55987
45 | -0.082932 | -0.020935 | 0.082981 | 0.020966 | 4.8582e-05 | 3.099e-05 | 0.12618 | 0.12618 | 0.12618 | 0.97842 | -0.4135 | 0.97904 | -0.40127 | 34.6649
46 | 0.0049274 | 0.0012349 | -0.0049273 | -0.0012349 | 1.2824e-07 | 7.4322e-09 | 0.0075395 | 0.0075395 | 0.0075395 | 0.97249 | -0.52994 | 0.97246 | -0.53049 | 2.0713
47 | 0.029751 | 0.0074635 | -0.029741 | -0.0074572 | 1.0041e-05 | 6.266e-06 | 0.045524 | 0.045524 | 0.045524 | 0.97249 | -0.52994 | 0.97213 | -0.53702 | 12.5066
48 | 0.0080806 | 0.002025 | -0.0080789 | -0.0020243 | 1.6587e-06 | 6.6833e-07 | 0.012085 | 0.012085 | 0.012085 | 0.99494 | -0.095735 | 0.99472 | -0.10004 | 3.3201
49 | -0.0019198 | -0.00048115 | 0.0019198 | 0.00048103 | 3.5045e-08 | -1.2457e-07 | 0.0028723 | 0.0028723 | 0.0028723 | 0.99456 | -0.10318 | 0.99458 | -0.10279 | 0.7891
50 | -0.0038414 | -0.0009626 | 0.0038418 | 0.00096241 | 4.6724e-07 | -1.906e-07 | 0.0057471 | 0.005747 | 0.0057471 | 0.99458 | -0.10279 | 0.99471 | -0.10024 | 1.5789
51 | -0.34436 | -0.088889 | 0.34437 | 0.088891 | 3.8923e-06 | 2.4864e-06 | 0.51334 | 0.51334 | 0.51334 | 0.99999 | -0.00023185 | 1 | 0 | 47.0094
52 | 0.17483 | 0.044445 | -0.17467 | -0.044344 | 0.00015886 | 0.00010097 | 0.26383 | 0.26383 | 0.26383 | 0.98691 | -0.24888 | 0.98593 | -0.26776 | 24.1601
53 | 0.0024409 | 0.00061147 | -0.0024408 | -0.00061159 | 6.4588e-08 | -1.1788e-07 | 0.003699 | 0.003699 | 0.003699 | 0.9819 | -0.34576 | 0.98187 | -0.34632 | 1.0162
54 | 0.093076 | 0.023519 | -0.093019 | -0.023482 | 5.727e-05 | 3.6557e-05 | 0.14144 | 0.14144 | 0.14144 | 0.9797 | -0.38843 | 0.97904 | -0.40127 | 38.8565
55 | 0.0035045 | 0.00087827 | -0.0035045 | -0.00087829 | 3.4703e-08 | -1.9232e-08 | 0.0053127 | 0.0053128 | 0.0053128 | 0.98156 | -0.35238 | 0.98155 | -0.35258 | 1.4596
56 | -0.0076895 | -0.0019268 | 0.0076905 | 0.0019271 | 9.9396e-07 | 3.7063e-07 | 0.011444 | 0.011444 | 0.011444 | 0.99986 | -0.0027135 | 1 | 0 | 3.1439
57 | 0.010039 | 0.0025163 | -0.010036 | -0.0025153 | 2.1055e-06 | 1.0443e-06 | 0.015257 | 0.015258 | 0.015258 | 0.97904 | -0.40127 | 0.97882 | -0.40568 | 4.1916
58 | 0.0049899 | 0.0012505 | -0.0049894 | -0.0012505 | 4.3387e-07 | 2.4972e-08 | 0.0075856 | 0.0075857 | 0.0075857 | 0.97882 | -0.40568 | 0.97873 | -0.4075 | 2.084
59 | 0.0013346 | 0.00033367 | -0.0013345 | -0.00033387 | 2.7854e-08 | -2.0489e-07 | 0.0020379 | 0.002038 | 0.002038 | 0.97431 | -0.49415 | 0.97429 | -0.49459 | 0.55989
60 | 0.17004 | 0.043183 | -0.1696 | -0.042905 | 0.0004366 | 0.0002774 | 0.25684 | 0.25684 | 0.25684 | 0.98593 | -0.26776 | 0.98317 | -0.32126 | 23.52
61 | -0.0098933 | -0.0024789 | 0.0098951 | 0.0024797 | 1.7345e-06 | 8.6076e-07 | 0.015155 | 0.015155 | 0.015155 | 0.97135 | -0.55255 | 0.97153 | -0.54887 | 4.1636
62 | 0.093352 | 0.023795 | -0.092935 | -0.023528 | 0.00041745 | 0.00026646 | 0.14143 | 0.14143 | 0.14143 | 0.98317 | -0.32126 | 0.97837 | -0.41436 | 38.8547
63 | 0.0013345 | 0.00033387 | -0.0013345 | -0.00033445 | 7.7916e-08 | -5.7299e-07 | 0.002038 | 0.0020382 | 0.0020382 | 0.97429 | -0.49459 | 0.97422 | -0.49581 | 0.55996
64 | -0.0032311 | -0.0008098 | 0.0032312 | 0.00080977 | 4.636e-08 | -3.2893e-08 | 0.0049478 | 0.0049477 | 0.0049478 | 0.97175 | -0.54464 | 0.97176 | -0.54433 | 1.3593
65 | -0.016937 | -0.0042456 | 0.016943 | 0.0042491 | 5.9016e-06 | 3.487e-06 | 0.025936 | 0.025936 | 0.025936 | 0.97176 | -0.54433 | 0.97213 | -0.53702 | 7.1252
66 | 0.013706 | 0.0034358 | -0.013703 | -0.0034342 | 2.9608e-06 | 1.6729e-06 | 0.020988 | 0.020988 | 0.020988 | 0.97176 | -0.54433 | 0.97153 | -0.54887 | 5.7659
67 | 0.0012201 | 0.00030564 | -0.0012201 | -0.00030578 | 1.5619e-08 | -1.4408e-07 | 0.001849 | 0.0018491 | 0.0018491 | 0.98187 | -0.34632 | 0.98185 | -0.34659 | 0.50799
68 | 0.012797 | 0.0032081 | -0.012795 | -0.0032066 | 2.6722e-06 | 1.48e-06 | 0.019589 | 0.019589 | 0.019589 | 0.97213 | -0.53702 | 0.97191 | -0.54141 | 5.3815
69 | 0.0065076 | 0.001631 | -0.0065069 | -0.0016308 | 7.5261e-07 | 2.3116e-07 | 0.0099633 | 0.0099634 | 0.0099634 | 0.97191 | -0.54141 | 0.97179 | -0.54383 | 2.7372
70 | 0.0061586 | 0.0015431 | -0.0061586 | -0.001543 | 5.6971e-08 | 1.3225e-08 | 0.0092127 | 0.0092127 | 0.0092127 | 0.99472 | -0.10004 | 0.99471 | -0.10024 | 2.531
71 | -0.092325 | -0.023139 | 0.092935 | 0.023528 | 0.00061028 | 0.00038956 | 0.14143 | 0.14143 | 0.14143 | 0.97136 | -0.55213 | 0.97837 | -0.41436 | 38.8548
72 | 0.0011864 | 0.00029733 | -0.0011864 | -0.00029734 | 1.5223e-09 | -1.4887e-08 | 0.0017986 | 0.0017986 | 0.0017986 | 0.98155 | -0.35258 | 0.98155 | -0.35261 | 0.49412

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35563 | 0.0913

## res_load
| p_mw | q_mvar
0 | 0.0019198 | 0.00048114
1 | 0.0019266 | 0.00048286
2 | 0.0019278 | 0.00048316
3 | 0.0019249 | 0.00048244
4 | 0.0019195 | 0.00048107
5 | 0.0023137 | 0.00057986
6 | 0.0023204 | 0.00058155
7 | 0.0019208 | 0.0004814
8 | 0.0019243 | 0.00048226
9 | 0.0019233 | 0.00048201
10 | 0.0019187 | 0.00048087
11 | 0.0078896 | 0.0019773
12 | 0.0023187 | 0.00058111
13 | 0.01466 | 0.003674
14 | 0.0015905 | 0.00039861
15 | 0.0029444 | 0.00073793
16 | 0.0042551 | 0.0010664
17 | 0.0077337 | 0.0019382
18 | 0.0057888 | 0.0014508
19 | 0.004951 | 0.0012408
20 | 0.010584 | 0.0026526
21 | 0.0015518 | 0.00038891
22 | 0.0070145 | 0.001758
23 | 0.001299 | 0.00032556
24 | 0.0049165 | 0.0012322
25 | 0.001917 | 0.00048044
26 | 0.0019198 | 0.00048115
27 | 0.0019215 | 0.00048158
28 | 0.001917 | 0.00048045
29 | 0.0012201 | 0.00030578
30 | 0.0012908 | 0.0003235
31 | 0.0092901 | 0.0023283
32 | 0.0011803 | 0.00029581
33 | 0.0019203 | 0.00048128
34 | 0.0019218 | 0.00048166
35 | 0.0050466 | 0.0012648
36 | 0.0049894 | 0.0012505
37 | 0.0046324 | 0.001161
38 | 0.0038044 | 0.00095347
39 | 0.076253 | 0.019111
40 | 0.0013345 | 0.00033445
41 | 0.0032311 | 0.0008098
42 | 0.0038082 | 0.00095443
43 | 0.0012207 | 0.00030595
44 | 0.0012201 | 0.00030578
45 | 0.0062869 | 0.0015756
46 | 0.0065069 | 0.0016308
47 | 0.0049273 | 0.0012349
48 | 0.0019203 | 0.00048126
49 | 0.0023168 | 0.00058063
50 | 0.092325 | 0.023139
51 | 0.0023181 | 0.00058096
52 | 0.0011864 | 0.00029734

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1