## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2584-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2584-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2584-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2584-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2584-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2584-1_0_4_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_2584-1_0_4_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_2584-1_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2584-1_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_2584-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2584-1_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2584-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2584-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2584-1_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2584-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2584-1_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2584-1_0_4_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_2584-1_0_4_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_2584-1_0_4_node_68 | 0.4 | n |  | TRUE
19 | bus_LV_2584-1_0_4_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_2584-1_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_2584-1_0_4_node_69 | 0.4 | n |  | TRUE
22 | bus_LV_2584-1_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2584-1_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2584-1_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2584-1_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2584-1_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2584-1_0_4_node_91 | 0.4 | n |  | TRUE
28 | bus_LV_2584-1_0_4_node_70 | 0.4 | n |  | TRUE
29 | bus_LV_2584-1_0_4_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_2584-1_0_4_node_62 | 0.4 | n |  | TRUE
31 | bus_LV_2584-1_0_4_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_2584-1_0_4_node_123 | 0.4 | n |  | TRUE
33 | bus_LV_2584-1_0_4_node_105 | 0.4 | n |  | TRUE
34 | bus_LV_2584-1_0_4_node_104 | 0.4 | n |  | TRUE
35 | bus_LV_2584-1_0_4_node_106 | 0.4 | n |  | TRUE
36 | bus_LV_2584-1_0_4_node_78 | 0.4 | n |  | TRUE
37 | bus_LV_2584-1_0_4_node_121 | 0.4 | n |  | TRUE
38 | bus_LV_2584-1_0_4_node_77 | 0.4 | n |  | TRUE
39 | bus_LV_2584-1_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2584-1_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_2584-1_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_2584-1_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2584-1_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2584-1_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_2584-1_0_4_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_2584-1_0_4_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_2584-1_0_4_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_2584-1_0_4_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_2584-1_0_4_node_113 | 0.4 | n |  | TRUE
50 | bus_LV_2584-1_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_2584-1_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_2584-1_0_4_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_2584-1_0_4_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_2584-1_0_4_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_2584-1_0_4_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_2584-1_0_4_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_2584-1_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_2584-1_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_2584-1_0_4_node_80 | 0.4 | n |  | TRUE
60 | bus_LV_2584-1_0_4_node_65 | 0.4 | n |  | TRUE
61 | bus_LV_2584-1_0_4_node_81 | 0.4 | n |  | TRUE
62 | bus_LV_2584-1_0_4_node_107 | 0.4 | n |  | TRUE
63 | bus_LV_2584-1_0_4_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_2584-1_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_2584-1_0_4_node_33 | 0.4 | n |  | TRUE
66 | bus_LV_2584-1_0_4_node_34 | 0.4 | n |  | TRUE
67 | bus_LV_2584-1_0_4_node_35 | 0.4 | n |  | TRUE
68 | bus_LV_2584-1_0_4_node_37 | 0.4 | n |  | TRUE
69 | bus_LV_2584-1_0_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_2584-1_0_4_node_74 | 0.4 | n |  | TRUE
71 | bus_LV_2584-1_0_4_node_38 | 0.4 | n |  | TRUE
72 | bus_LV_2584-1_0_4_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2584-1_0_4_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_2584-1_0_4_node_48 | 0.4 | n |  | TRUE
75 | bus_LV_2584-1_0_4_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_2584-1_0_4_node_43 | 0.4 | n |  | TRUE
77 | bus_LV_2584-1_0_4_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_2584-1_0_4_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_2584-1_0_4_node_46 | 0.4 | n |  | TRUE
80 | bus_LV_2584-1_0_4_node_47 | 0.4 | n |  | TRUE
81 | bus_LV_2584-1_0_4_node_99 | 0.4 | n |  | TRUE
82 | bus_LV_2584-1_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_2584-1_0_4_node_83 | 0.4 | n |  | TRUE
84 | bus_LV_2584-1_0_4_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_2584-1_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_2584-1_0_4_node_51 | 0.4 | n |  | TRUE
87 | bus_LV_2584-1_0_4_node_52 | 0.4 | n |  | TRUE
88 | bus_LV_2584-1_0_4_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_2584-1_0_4_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_2584-1_0_4_node_101 | 0.4 | n |  | TRUE
91 | bus_LV_2584-1_0_4_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_2584-1_0_4_node_55 | 0.4 | n |  | TRUE
93 | bus_LV_2584-1_0_4_node_60 | 0.4 | n |  | TRUE
94 | bus_LV_2584-1_0_4_node_111 | 0.4 | n |  | TRUE
95 | bus_LV_2584-1_0_4_node_110 | 0.4 | n |  | TRUE
96 | bus_LV_2584-1_0_4_node_64 | 0.4 | n |  | TRUE
97 | bus_LV_2584-1_0_4_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_2584-1_0_4_node_108 | 0.4 | n |  | TRUE
99 | bus_LV_2584-1_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_2584-1_0_4_node_124 | 0.4 | n |  | TRUE
101 | bus_LV_2584-1_0_4_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_2584-1_0_4_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_2584-1_0_4_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_2584-1_0_4_node_76 | 0.4 | n |  | TRUE
105 | bus_LV_2584-1_0_4_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_2584-1_0_4_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_2584-1_0_4_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_2584-1_0_4_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_2584-1_0_4_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_2584-1_0_4_node_115 | 0.4 | n |  | TRUE
111 | bus_LV_2584-1_0_4_node_114 | 0.4 | n |  | TRUE
112 | bus_LV_2584-1_0_4_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_2584-1_0_4_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_2584-1_0_4_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_2584-1_0_4_node_126 | 0.4 | n |  | TRUE
116 | bus_LV_2584-1_0_4_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_2584-1_0_4_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_2584-1_0_4_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_2584-1_0_4_node_118 | 0.4 | n |  | TRUE
120 | bus_LV_2584-1_0_4_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2584-1_0_4_node_120 | 0.4 | n |  | TRUE
122 | bus_MV_398_1_node_189 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2584-1_0_4_load_0 | 0 | 0.0039078 | 0.00097939 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2584-1_0_4_load_1 | 1 | 0.002674 | 0.00067017 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2584-1_0_4_load_2 | 2 | 0.0061718 | 0.0015468 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2584-1_0_4_load_3 | 3 | 0.0049134 | 0.0012314 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2584-1_0_4_load_4 | 4 | 0.0047291 | 0.0011852 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2584-1_0_4_load_17 | 5 | 0.0031654 | 0.00079333 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2584-1_0_4_load_66 | 6 | 0.0059227 | 0.0014844 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2584-1_0_4_load_18 | 7 | 0.0038206 | 0.00095753 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2584-1_0_4_load_5 | 9 | 0.0012186 | 0.00030541 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2584-1_0_4_load_6 | 10 | 0.0039946 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2584-1_0_4_load_8 | 12 | 0.0063545 | 0.0015926 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2584-1_0_4_load_9 | 13 | 0.0011073 | 0.00027752 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2584-1_0_4_load_10 | 14 | 0.0015793 | 0.00039582 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2584-1_0_4_load_11 | 15 | 0.0016259 | 0.00040748 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2584-1_0_4_load_58 | 16 | 0.00079441 | 0.0001991 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2584-1_0_4_load_19 | 17 | 0.0060652 | 0.0015201 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2584-1_0_4_load_68 | 18 | 0.0013617 | 0.00034126 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2584-1_0_4_load_56 | 19 | 0.0021808 | 0.00054657 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2584-1_0_4_load_12 | 22 | 0.0016195 | 0.00040588 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2584-1_0_4_load_13 | 23 | 0.0016165 | 0.00040513 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2584-1_0_4_load_14 | 24 | 0.0016128 | 0.00040419 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2584-1_0_4_load_15 | 25 | 0.00125 | 0.00031327 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2584-1_0_4_load_16 | 26 | 0.0015832 | 0.00039679 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2584-1_0_4_load_91 | 27 | 0.0016244 | 0.0004071 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2584-1_0_4_load_70 | 28 | 0.001753 | 0.00043933 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2584-1_0_4_load_61 | 29 | 0.0016595 | 0.00041591 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2584-1_0_4_load_62 | 30 | 0.0015394 | 0.0003858 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2584-1_0_4_load_90 | 31 | 0.0015943 | 0.00039957 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2584-1_0_4_load_123 | 32 | 0.0013611 | 0.00034113 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2584-1_0_4_load_105 | 33 | 0.0038939 | 0.00097591 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2584-1_0_4_load_106 | 35 | 0.0015099 | 0.00037841 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2584-1_0_4_load_78 | 36 | 0.0030194 | 0.00075674 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2584-1_0_4_load_121 | 37 | 0.0015077 | 0.00037786 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2584-1_0_4_load_77 | 38 | 0.0022461 | 0.00056291 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2584-1_0_4_load_21 | 39 | 0.0029494 | 0.00073918 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2584-1_0_4_load_24 | 42 | 0.011658 | 0.0029217 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2584-1_0_4_load_26 | 43 | 0.0062303 | 0.0015615 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2584-1_0_4_load_27 | 44 | 0.0018741 | 0.0004697 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2584-1_0_4_load_112 | 45 | 0.018546 | 0.0046481 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2584-1_0_4_load_59 | 47 | 0.0040206 | 0.0010077 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2584-1_0_4_load_97 | 48 | 0.00058822 | 0.00014742 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2584-1_0_4_load_113 | 49 | 0.0035256 | 0.00088361 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2584-1_0_4_load_36 | 50 | 0.0038076 | 0.00095427 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2584-1_0_4_load_50 | 51 | 0.0053384 | 0.0013379 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2584-1_0_4_load_95 | 53 | 0.00059793 | 0.00014986 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2584-1_0_4_load_28 | 54 | 0.0020459 | 0.00051275 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2584-1_0_4_load_29 | 55 | 0.0020887 | 0.00052347 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2584-1_0_4_load_30 | 56 | 0.002219 | 0.00055613 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2584-1_0_4_load_31 | 57 | 0.005131 | 0.0012859 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2584-1_0_4_load_80 | 59 | 0.0017999 | 0.00045111 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2584-1_0_4_load_65 | 60 | 0.000962 | 0.0002411 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2584-1_0_4_load_81 | 61 | 0.0021824 | 0.00054696 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2584-1_0_4_load_107 | 62 | 0.00095645 | 0.00023971 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2584-1_0_4_load_41 | 63 | 0.0036191 | 0.00090704 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2584-1_0_4_load_39 | 64 | 0.0039334 | 0.00098581 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2584-1_0_4_load_33 | 65 | 0.0076675 | 0.0019217 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2584-1_0_4_load_34 | 66 | 0.0093292 | 0.0023381 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2584-1_0_4_load_35 | 67 | 0.0020247 | 0.00050745 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2584-1_0_4_load_37 | 68 | 0.0016114 | 0.00040386 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2584-1_0_4_load_100 | 69 | 0.0016032 | 0.00040179 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2584-1_0_4_load_74 | 70 | 0.0016198 | 0.00040595 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2584-1_0_4_load_38 | 71 | 0.0042652 | 0.001069 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2584-1_0_4_load_40 | 72 | 0.0033115 | 0.00082994 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2584-1_0_4_load_42 | 73 | 0.0016173 | 0.00040532 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2584-1_0_4_load_48 | 74 | 0.017318 | 0.0043404 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2584-1_0_4_load_49 | 75 | 0.0044626 | 0.0011184 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2584-1_0_4_load_43 | 76 | 0.0015927 | 0.00039916 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2584-1_0_4_load_44 | 77 | 0.0015937 | 0.00039943 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2584-1_0_4_load_45 | 78 | 0.0016152 | 0.0004048 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2584-1_0_4_load_46 | 79 | 0.001585 | 0.00039724 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2584-1_0_4_load_99 | 81 | 0.0015964 | 0.0004001 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2584-1_0_4_load_84 | 82 | 0.0016665 | 0.00041766 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2584-1_0_4_load_83 | 83 | 0.0015938 | 0.00039944 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2584-1_0_4_load_88 | 84 | 0.0015973 | 0.00040032 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2584-1_0_4_load_75 | 85 | 0.0064429 | 0.0016147 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2584-1_0_4_load_51 | 86 | 0.0033498 | 0.00083953 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2584-1_0_4_load_53 | 88 | 0.0042494 | 0.001065 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2584-1_0_4_load_54 | 89 | 0.008949 | 0.0022428 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2584-1_0_4_load_102 | 91 | 0.0033905 | 0.00084974 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2584-1_0_4_load_55 | 92 | 0.0017131 | 0.00042936 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2584-1_0_4_load_111 | 94 | 0.0033859 | 0.00084859 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2584-1_0_4_load_117 | 97 | 0.0014308 | 0.00035858 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2584-1_0_4_load_108 | 98 | 0.0027296 | 0.0006841 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2584-1_0_4_load_93 | 99 | 0.001711 | 0.00042882 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2584-1_0_4_load_124 | 100 | 0.0011216 | 0.0002811 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2584-1_0_4_load_71 | 101 | 0.012334 | 0.0030913 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2584-1_0_4_load_72 | 102 | 0.0015917 | 0.00039891 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2584-1_0_4_load_76 | 104 | 0.00051936 | 0.00013016 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2584-1_0_4_load_116 | 105 | 0.0032396 | 0.00081192 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2584-1_0_4_load_85 | 106 | 0.0015873 | 0.00039782 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2584-1_0_4_load_86 | 107 | 0.0016184 | 0.00040562 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2584-1_0_4_load_87 | 108 | 0.0015892 | 0.00039828 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2584-1_0_4_load_89 | 109 | 0.0015902 | 0.00039853 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2584-1_0_4_load_115 | 110 | 0.001593 | 0.00039924 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2584-1_0_4_load_114 | 111 | 0.0016172 | 0.0004053 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2584-1_0_4_load_92 | 112 | 0.0016153 | 0.00040483 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2584-1_0_4_load_94 | 113 | 0.00087859 | 0.0002202 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2584-1_0_4_load_103 | 114 | 0.0013851 | 0.00034713 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2584-1_0_4_load_126 | 115 | 0.0033653 | 0.00084343 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2584-1_0_4_load_125 | 116 | 0.0035219 | 0.00088266 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2584-1_0_4_load_109 | 118 | 0.0024699 | 0.00061901 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2584-1_0_4_load_118 | 119 | 0.0016264 | 0.00040762 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2584-1_0_4_load_119 | 120 | 0.0033659 | 0.00084356 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2584-1_0_4_line_0 |  | 0 | 1 | 0.0023645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2584-1_0_4_line_1 |  | 0 | 2 | 0.012016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2584-1_0_4_line_2 |  | 1 | 3 | 0.013667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2584-1_0_4_line_3 |  | 2 | 4 | 0.0033538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2584-1_0_4_line_4 |  | 3 | 5 | 0.00036461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2584-1_0_4_line_5 |  | 4 | 6 | 0.023828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2584-1_0_4_line_6 |  | 5 | 7 | 0.014708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2584-1_0_4_line_7 |  | 6 | 8 | 0.02342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2584-1_0_4_line_8 |  | 7 | 33 | 6.0013e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2584-1_0_4_line_9 |  | 8 | 46 | 0.014966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2584-1_0_4_line_10 |  | 8 | 40 | 0.044541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2584-1_0_4_line_11 |  | 9 | 10 | 0.0049858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2584-1_0_4_line_12 |  | 9 | 11 | 0.014864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2584-1_0_4_line_13 |  | 10 | 12 | 0.015339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2584-1_0_4_line_14 |  | 11 | 13 | 0.015591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2584-1_0_4_line_15 |  | 11 | 14 | 0.034231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2584-1_0_4_line_16 |  | 11 | 15 | 0.042624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2584-1_0_4_line_17 |  | 12 | 16 | 0.021552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2584-1_0_4_line_18 |  | 13 | 17 | 0.0067342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2584-1_0_4_line_19 |  | 14 | 18 | 0.0027872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2584-1_0_4_line_20 |  | 16 | 19 | 0.0012844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2584-1_0_4_line_21 |  | 17 | 20 | 0.013888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2584-1_0_4_line_22 |  | 18 | 21 | 0.01431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2584-1_0_4_line_23 |  | 19 | 92 | 0.015002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2584-1_0_4_line_24 |  | 20 | 35 | 0.015631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2584-1_0_4_line_25 |  | 20 | 36 | 0.01332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2584-1_0_4_line_26 |  | 21 | 100 | 0.014225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2584-1_0_4_line_27 |  | 22 | 23 | 0.0054173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2584-1_0_4_line_28 |  | 22 | 24 | 0.014027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2584-1_0_4_line_29 |  | 23 | 25 | 0.007799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2584-1_0_4_line_30 |  | 24 | 26 | 0.0052864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2584-1_0_4_line_31 |  | 25 | 27 | 0.0062204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2584-1_0_4_line_32 |  | 26 | 28 | 0.0038741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2584-1_0_4_line_33 |  | 27 | 31 | 0.0053606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2584-1_0_4_line_34 |  | 28 | 32 | 0.012106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2584-1_0_4_line_35 |  | 28 | 30 | 0.12704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2584-1_0_4_line_36 |  | 29 | 30 | 0.009764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2584-1_0_4_line_37 |  | 31 | 112 | 0.0053504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2584-1_0_4_line_38 |  | 32 | 82 | 0.0076567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2584-1_0_4_line_39 |  | 33 | 34 | 0.025502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2584-1_0_4_line_40 |  | 34 | 114 | 0.021685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2584-1_0_4_line_41 |  | 35 | 37 | 0.0096188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2584-1_0_4_line_42 |  | 36 | 38 | 0.0022781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2584-1_0_4_line_43 |  | 37 | 117 | 0.035943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2584-1_0_4_line_44 |  | 39 | 40 | 0.026956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2584-1_0_4_line_45 |  | 39 | 41 | 0.010372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2584-1_0_4_line_46 |  | 40 | 42 | 0.019879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2584-1_0_4_line_47 |  | 41 | 43 | 0.0038594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2584-1_0_4_line_48 |  | 41 | 44 | 0.018556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2584-1_0_4_line_49 |  | 42 | 45 | 0.0033187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2584-1_0_4_line_50 |  | 43 | 47 | 0.025619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2584-1_0_4_line_51 |  | 44 | 48 | 0.022796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2584-1_0_4_line_52 |  | 45 | 49 | 0.020078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2584-1_0_4_line_53 |  | 46 | 50 | 0.0095393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2584-1_0_4_line_54 |  | 46 | 51 | 0.017307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2584-1_0_4_line_55 |  | 47 | 52 | 0.0014095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2584-1_0_4_line_56 |  | 48 | 53 | 0.0056489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2584-1_0_4_line_57 |  | 49 | 116 | 0.018304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2584-1_0_4_line_58 |  | 50 | 66 | 0.016979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2584-1_0_4_line_59 |  | 51 | 75 | 0.001971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2584-1_0_4_line_60 |  | 52 | 93 | 0.03782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2584-1_0_4_line_61 |  | 52 | 92 | 0.013732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2584-1_0_4_line_62 |  | 53 | 113 | 0.029852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2584-1_0_4_line_63 |  | 54 | 55 | 0.012373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2584-1_0_4_line_64 |  | 54 | 56 | 0.0064995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2584-1_0_4_line_65 |  | 55 | 57 | 0.012677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2584-1_0_4_line_66 |  | 56 | 58 | 0.0070197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2584-1_0_4_line_67 |  | 57 | 59 | 0.010318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2584-1_0_4_line_68 |  | 58 | 60 | 0.012147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2584-1_0_4_line_69 |  | 59 | 61 | 0.0012012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2584-1_0_4_line_70 |  | 60 | 62 | 0.0060497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2584-1_0_4_line_71 |  | 62 | 99 | 0.0039937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2584-1_0_4_line_72 |  | 63 | 64 | 0.0031393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2584-1_0_4_line_73 |  | 64 | 71 | 0.029665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2584-1_0_4_line_74 |  | 65 | 66 | 0.0067505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2584-1_0_4_line_75 |  | 65 | 67 | 0.018984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2584-1_0_4_line_76 |  | 67 | 68 | 0.017956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2584-1_0_4_line_77 |  | 68 | 69 | 0.0018903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2584-1_0_4_line_78 |  | 69 | 70 | 0.022992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2584-1_0_4_line_79 |  | 70 | 102 | 0.0016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2584-1_0_4_line_80 |  | 71 | 72 | 0.0049636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2584-1_0_4_line_81 |  | 72 | 73 | 0.0022145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2584-1_0_4_line_82 |  | 73 | 74 | 0.0075078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2584-1_0_4_line_83 |  | 74 | 75 | 0.016538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2584-1_0_4_line_84 |  | 76 | 77 | 0.0011426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2584-1_0_4_line_85 |  | 76 | 78 | 2.1936e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2584-1_0_4_line_86 |  | 77 | 79 | 0.027213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2584-1_0_4_line_87 |  | 78 | 80 | 0.01554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2584-1_0_4_line_88 |  | 79 | 81 | 6.9426e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2584-1_0_4_line_89 |  | 80 | 82 | 0.020636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2584-1_0_4_line_90 |  | 80 | 83 | 0.020921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2584-1_0_4_line_91 |  | 81 | 84 | 0.0011351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2584-1_0_4_line_92 |  | 83 | 85 | 0.0081946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2584-1_0_4_line_93 |  | 84 | 107 | 4.631e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2584-1_0_4_line_94 |  | 85 | 103 | 0.02055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2584-1_0_4_line_95 |  | 86 | 87 | 0.00381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2584-1_0_4_line_96 |  | 87 | 88 | 0.032535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2584-1_0_4_line_97 |  | 87 | 89 | 0.018699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2584-1_0_4_line_98 |  | 88 | 90 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2584-1_0_4_line_99 |  | 90 | 91 | 0.022309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2584-1_0_4_line_100 |  | 91 | 93 | 0.016399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2584-1_0_4_line_101 |  | 93 | 94 | 0.028391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2584-1_0_4_line_102 |  | 94 | 95 | 0.042191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2584-1_0_4_line_103 |  | 95 | 98 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2584-1_0_4_line_104 |  | 95 | 96 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2584-1_0_4_line_105 |  | 96 | 97 | 0.012969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2584-1_0_4_line_106 |  | 98 | 118 | 0.019181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2584-1_0_4_line_107 |  | 99 | 112 | 0.010957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2584-1_0_4_line_108 |  | 101 | 102 | 0.0032841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2584-1_0_4_line_109 |  | 101 | 103 | 0.01935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2584-1_0_4_line_110 |  | 103 | 104 | 0.006057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2584-1_0_4_line_111 |  | 104 | 105 | 0.017761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2584-1_0_4_line_112 |  | 106 | 107 | 0.026605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2584-1_0_4_line_113 |  | 106 | 108 | 0.0011291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2584-1_0_4_line_114 |  | 108 | 109 | 6.6262e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2584-1_0_4_line_115 |  | 109 | 110 | 0.0011337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2584-1_0_4_line_116 |  | 110 | 111 | 3.8479e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2584-1_0_4_line_117 |  | 115 | 116 | 0.019251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2584-1_0_4_line_118 |  | 117 | 121 | 0.072576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2584-1_0_4_line_119 |  | 119 | 120 | 0.0098357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2584-1_0_4_line_120 |  | 119 | 121 | 0.014779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2584-1_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 122 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2636834.9657 | 1244637.9146 | 2636835.2437 | 1244635.5665
1 | 2636834.9657 | 1244637.9146 | 2636833.5529 | 1244649.8472
2 | 2636835.2437 | 1244635.5665 | 2636836.8506 | 1244621.9944
3 | 2636833.1586 | 1244653.1778 | 2636833.5529 | 1244649.8472
4 | 2636836.8935 | 1244621.6323 | 2636836.8506 | 1244621.9944
5 | 2636830.3571 | 1244676.8404 | 2636833.1586 | 1244653.1778
6 | 2636836.8935 | 1244621.6323 | 2636838.6228 | 1244607.026
7 | 2636827.6034 | 1244700.0982 | 2636830.3571 | 1244676.8404
8 | 2636838.6299 | 1244606.9664 | 2636838.6228 | 1244607.026
9 | 2636812.5993 | 1244699.805 | 2636820.0569 | 1244699.8068 | 2636827.6034 | 1244700.0982
10 | 2636827.6034 | 1244700.0982 | 2636841.9031 | 1244701.8992 | 2636854.652 | 1244705.2027 | 2636871.2731 | 1244701.837
11 | 2637011.232 | 1244702.1801 | 2637006.2532 | 1244701.9143
12 | 2637026.079 | 1244702.8785 | 2637017.0068 | 1244702.4884 | 2637011.232 | 1244702.1801
13 | 2637006.2532 | 1244701.9143 | 2636990.9361 | 1244701.0967
14 | 2637026.079 | 1244702.8785 | 2637038.4519 | 1244703.4449 | 2637041.6563 | 1244703.5247
15 | 2637026.079 | 1244702.8785 | 2637026.6534 | 1244693.1647 | 2637027.9992 | 1244679.6976 | 2637029.729 | 1244668.8686
16 | 2637026.079 | 1244702.8785 | 2637025.6207 | 1244713.3602 | 2637024.3176 | 1244735.7111 | 2637023.7885 | 1244745.4404
17 | 2636969.4106 | 1244700.0972 | 2636972.2002 | 1244700.0966 | 2636990.9361 | 1244701.0967
18 | 2637041.6563 | 1244703.5247 | 2637048.3885 | 1244703.6925
19 | 2637029.729 | 1244668.8686 | 2637030.1687 | 1244666.1163
20 | 2636969.4106 | 1244700.0972 | 2636968.1262 | 1244700.0975
21 | 2637062.2719 | 1244704.0383 | 2637048.3885 | 1244703.6925
22 | 2637032.4261 | 1244651.985 | 2637030.1687 | 1244666.1163
23 | 2636953.1243 | 1244700.1007 | 2636968.1262 | 1244700.0975
24 | 2637062.2719 | 1244704.0383 | 2637077.7625 | 1244701.945
25 | 2637062.2719 | 1244704.0383 | 2637065.6017 | 1244714.099 | 2637065.983 | 1244716.7949
26 | 2637032.4261 | 1244651.985 | 2637018.5859 | 1244648.6983
27 | 2636742.0343 | 1244808.0325 | 2636747.4379 | 1244808.4186
28 | 2636728.0433 | 1244807.0328 | 2636742.0343 | 1244808.0325
29 | 2636755.2171 | 1244808.9744 | 2636747.4379 | 1244808.4186
30 | 2636728.0433 | 1244807.0328 | 2636723.8966 | 1244806.7366 | 2636722.77 | 1244806.661
31 | 2636761.4216 | 1244809.4177 | 2636755.2171 | 1244808.9744
32 | 2636722.77 | 1244806.661 | 2636718.9046 | 1244806.4016
33 | 2636766.7686 | 1244809.7998 | 2636761.4216 | 1244809.4177
34 | 2636709.3608 | 1244800.387 | 2636709.3608 | 1244800.387 | 2636711.0662 | 1244803.1883 | 2636713.1692 | 1244805.2359 | 2636716.412 | 1244806.2344 | 2636718.9046 | 1244806.4016
35 | 2636718.9046 | 1244806.4016 | 2636709.5978 | 1244933.0971
36 | 2636719.2458 | 1244934.5981 | 2636709.5978 | 1244933.0971
37 | 2636766.7686 | 1244809.7998 | 2636772.1054 | 1244810.1811
38 | 2636707.6669 | 1244792.92 | 2636709.3608 | 1244800.387
39 | 2636842.972 | 1244582.0279 | 2636841.1192 | 1244585.9412 | 2636838.6299 | 1244606.9664
40 | 2636842.972 | 1244582.0279 | 2636821.5204 | 1244585.1989
41 | 2637077.7625 | 1244701.945 | 2637079.0223 | 1244701.7747 | 2637087.3658 | 1244702.0344
42 | 2637066.3021 | 1244719.0505 | 2637065.983 | 1244716.7949
43 | 2637123.2911 | 1244703.1522 | 2637087.3658 | 1244702.0344
44 | 2636871.2731 | 1244701.837 | 2636876.1971 | 1244702.2345 | 2636883.3609 | 1244702.1011 | 2636895.4038 | 1244701.0752 | 2636898.1604 | 1244700.8701
45 | 2636908.5042 | 1244700.1004 | 2636898.1604 | 1244700.8701
46 | 2636871.2731 | 1244701.837 | 2636868.1062 | 1244699.5714 | 2636866.0614 | 1244695.4672 | 2636867.2145 | 1244684.1264
47 | 2636908.5042 | 1244700.1004 | 2636912.3636 | 1244700.1008
48 | 2636908.5042 | 1244700.1004 | 2636910.2099 | 1244681.623
49 | 2636867.2145 | 1244684.1264 | 2636867.5502 | 1244680.8247
50 | 2636912.3636 | 1244700.1008 | 2636937.9831 | 1244700.1034
51 | 2636910.2099 | 1244681.623 | 2636912.3053 | 1244658.9239
52 | 2636870.6048 | 1244660.9983 | 2636868.8197 | 1244669.8565 | 2636867.6306 | 1244680.0335 | 2636867.5502 | 1244680.8247
53 | 2636812.5993 | 1244699.805 | 2636803.1022 | 1244700.7021
54 | 2636812.5993 | 1244699.805 | 2636811.4609 | 1244717.0743
55 | 2636939.3926 | 1244700.1036 | 2636937.9831 | 1244700.1034
56 | 2636912.8245 | 1244653.2989 | 2636912.3053 | 1244658.9239
57 | 2636870.6048 | 1244660.9983 | 2636872.4449 | 1244651.8673 | 2636873.8353 | 1244642.9862
58 | 2636803.1022 | 1244700.7021 | 2636786.1987 | 1244702.2986
59 | 2636811.3313 | 1244719.041 | 2636811.4609 | 1244717.0743
60 | 2636922.3266 | 1244733.6637 | 2636927.5384 | 1244723.0226 | 2636934.5863 | 1244706.2888 | 2636939.3926 | 1244700.1036
61 | 2636939.3926 | 1244700.1036 | 2636953.1243 | 1244700.1007
62 | 2636915.5685 | 1244623.5735 | 2636912.8245 | 1244653.2989
63 | 2636818.5029 | 1244814.7671 | 2636830.7078 | 1244816.8022
64 | 2636812.0919 | 1244813.698 | 2636818.5029 | 1244814.7671
65 | 2636843.3349 | 1244817.4303 | 2636842.4927 | 1244817.5003 | 2636834.0462 | 1244817.3589 | 2636830.7078 | 1244816.8022
66 | 2636805.1679 | 1244812.5434 | 2636812.0919 | 1244813.698
67 | 2636843.3349 | 1244817.4303 | 2636853.6178 | 1244816.5756
68 | 2636805.1679 | 1244812.5434 | 2636793.0522 | 1244811.6778
69 | 2636854.8148 | 1244816.4761 | 2636853.6178 | 1244816.5756
70 | 2636787.018 | 1244811.2466 | 2636793.0522 | 1244811.6778
71 | 2636787.018 | 1244811.2466 | 2636783.0344 | 1244810.962
72 | 2636807.1199 | 1244782.9305 | 2636807.3264 | 1244779.798
73 | 2636807.3264 | 1244779.798 | 2636809.2776 | 1244750.1973
74 | 2636779.6359 | 1244703.8794 | 2636786.1987 | 1244702.2986 | 2636786.1987 | 1244702.2986
75 | 2636761.1801 | 1244708.325 | 2636779.6359 | 1244703.8794
76 | 2636743.7231 | 1244712.53 | 2636761.1801 | 1244708.325
77 | 2636743.7231 | 1244712.53 | 2636742.9978 | 1244712.7047 | 2636741.8883 | 1244712.9845
78 | 2636741.8883 | 1244712.9845 | 2636719.5946 | 1244718.6074
79 | 2636719.5946 | 1244718.6074 | 2636717.9487 | 1244719.0225
80 | 2636809.604 | 1244745.2444 | 2636809.2776 | 1244750.1973
81 | 2636809.7497 | 1244743.0347 | 2636809.604 | 1244745.2444
82 | 2636810.2435 | 1244735.5431 | 2636809.7497 | 1244743.0347
83 | 2636810.2435 | 1244735.5431 | 2636811.3313 | 1244719.041
84 | 2636720.4378 | 1244773.8287 | 2636719.2981 | 1244773.7486
85 | 2636719.2981 | 1244773.7486 | 2636719.2762 | 1244773.747
86 | 2636720.4378 | 1244773.8287 | 2636747.5833 | 1244775.7381
87 | 2636703.7749 | 1244772.6567 | 2636719.2762 | 1244773.747
88 | 2636747.6525 | 1244775.743 | 2636747.5833 | 1244775.7381
89 | 2636703.7749 | 1244772.6567 | 2636706.8527 | 1244789.331 | 2636707.6669 | 1244792.92
90 | 2636703.7749 | 1244772.6567 | 2636699.6887 | 1244752.1388
91 | 2636747.6525 | 1244775.743 | 2636748.7848 | 1244775.8226
92 | 2636699.6887 | 1244752.1388 | 2636698.0882 | 1244744.102
93 | 2636748.831 | 1244775.8259 | 2636748.7848 | 1244775.8226
94 | 2636695.819 | 1244723.709 | 2636696.9156 | 1244738.2141 | 2636698.0882 | 1244744.102
95 | 2636954.7059 | 1244793.9377 | 2636954.3697 | 1244797.7329
96 | 2636954.7059 | 1244793.9377 | 2636956.5324 | 1244761.4537
97 | 2636954.7059 | 1244793.9377 | 2636962.0538 | 1244795.7735 | 2636972.4241 | 1244799.8014
98 | 2636958.4015 | 1244747.6972 | 2636956.7451 | 1244757.6712 | 2636956.5324 | 1244761.4537
99 | 2636958.4015 | 1244747.6972 | 2636937.6099 | 1244739.6091
100 | 2636922.3266 | 1244733.6637 | 2636937.6099 | 1244739.6091
101 | 2636922.3266 | 1244733.6637 | 2636916.6771 | 1244746.6704 | 2636912.4647 | 1244758.2184 | 2636911.1736 | 1244759.6371
102 | 2636894.9631 | 1244797.4908 | 2636896.8395 | 1244786.1395 | 2636900.0285 | 1244775.1299 | 2636904.4156 | 1244767.063 | 2636911.1736 | 1244759.6371
103 | 2636894.9631 | 1244797.4908 | 2636908.0547 | 1244799.2415
104 | 2636891.3878 | 1244818.3822 | 2636894.9631 | 1244797.4908
105 | 2636891.3878 | 1244818.3822 | 2636904.1327 | 1244820.7829
106 | 2636908.0547 | 1244799.2415 | 2636927.0664 | 1244801.7838
107 | 2636772.1054 | 1244810.1811 | 2636783.0344 | 1244810.962
108 | 2636714.7643 | 1244719.8257 | 2636717.9487 | 1244719.0225
109 | 2636695.819 | 1244723.709 | 2636708.1033 | 1244721.5057 | 2636714.7643 | 1244719.8257
110 | 2636695.819 | 1244723.709 | 2636689.8309 | 1244724.6203
111 | 2636672.1647 | 1244726.347 | 2636684.6561 | 1244725.4078 | 2636689.8309 | 1244724.6203
112 | 2636775.3706 | 1244777.6927 | 2636748.831 | 1244775.8259
113 | 2636775.3706 | 1244777.6927 | 2636776.4969 | 1244777.7719
114 | 2636776.563 | 1244777.7765 | 2636776.4969 | 1244777.7719
115 | 2636777.694 | 1244777.8561 | 2636776.563 | 1244777.7765
116 | 2636777.7323 | 1244777.8588 | 2636777.694 | 1244777.8561
117 | 2636873.8353 | 1244642.9862 | 2636874.8447 | 1244636.5389 | 2636875.8739 | 1244626.5499 | 2636875.9869 | 1244623.8691
118 | 2637123.2911 | 1244703.1522 | 2637186.5452 | 1244667.5692
119 | 2637199.6955 | 1244661.1105 | 2637201.3413 | 1244660.0792 | 2637204.5233 | 1244659.9212 | 2637208.0932 | 1244662.99
120 | 2637186.5452 | 1244667.5692 | 2637191.9426 | 1244665.9686 | 2637199.6955 | 1244661.1105

## bus_geodata
| x | y | coords
0 | 2636834.9657 | 1244637.9146
1 | 2636835.2437 | 1244635.5665
2 | 2636833.5529 | 1244649.8472
3 | 2636836.8506 | 1244621.9944
4 | 2636833.1586 | 1244653.1778
5 | 2636836.8935 | 1244621.6323
6 | 2636830.3571 | 1244676.8404
7 | 2636838.6228 | 1244607.026
8 | 2636827.6034 | 1244700.0982
9 | 2637011.232 | 1244702.1801
10 | 2637006.2532 | 1244701.9143
11 | 2637026.079 | 1244702.8785
12 | 2636990.9361 | 1244701.0967
13 | 2637041.6563 | 1244703.5247
14 | 2637029.729 | 1244668.8686
15 | 2637023.7885 | 1244745.4404
16 | 2636969.4106 | 1244700.0972
17 | 2637048.3885 | 1244703.6925
18 | 2637030.1687 | 1244666.1163
19 | 2636968.1262 | 1244700.0975
20 | 2637062.2719 | 1244704.0383
21 | 2637032.4261 | 1244651.985
22 | 2636742.0343 | 1244808.0325
23 | 2636747.4379 | 1244808.4186
24 | 2636728.0433 | 1244807.0328
25 | 2636755.2171 | 1244808.9744
26 | 2636722.77 | 1244806.661
27 | 2636761.4216 | 1244809.4177
28 | 2636718.9046 | 1244806.4016
29 | 2636719.2458 | 1244934.5981
30 | 2636709.5978 | 1244933.0971
31 | 2636766.7686 | 1244809.7998
32 | 2636709.3608 | 1244800.387
33 | 2636838.6299 | 1244606.9664
34 | 2636842.972 | 1244582.0279
35 | 2637077.7625 | 1244701.945
36 | 2637065.983 | 1244716.7949
37 | 2637087.3658 | 1244702.0344
38 | 2637066.3021 | 1244719.0505
39 | 2636898.1604 | 1244700.8701
40 | 2636871.2731 | 1244701.837
41 | 2636908.5042 | 1244700.1004
42 | 2636867.2145 | 1244684.1264
43 | 2636912.3636 | 1244700.1008
44 | 2636910.2099 | 1244681.623
45 | 2636867.5502 | 1244680.8247
46 | 2636812.5993 | 1244699.805
47 | 2636937.9831 | 1244700.1034
48 | 2636912.3053 | 1244658.9239
49 | 2636870.6048 | 1244660.9983
50 | 2636803.1022 | 1244700.7021
51 | 2636811.4609 | 1244717.0743
52 | 2636939.3926 | 1244700.1036
53 | 2636912.8245 | 1244653.2989
54 | 2636818.5029 | 1244814.7671
55 | 2636830.7078 | 1244816.8022
56 | 2636812.0919 | 1244813.698
57 | 2636843.3349 | 1244817.4303
58 | 2636805.1679 | 1244812.5434
59 | 2636853.6178 | 1244816.5756
60 | 2636793.0522 | 1244811.6778
61 | 2636854.8148 | 1244816.4761
62 | 2636787.018 | 1244811.2466
63 | 2636807.1199 | 1244782.9305
64 | 2636807.3264 | 1244779.798
65 | 2636779.6359 | 1244703.8794
66 | 2636786.1987 | 1244702.2986
67 | 2636761.1801 | 1244708.325
68 | 2636743.7231 | 1244712.53
69 | 2636741.8883 | 1244712.9845
70 | 2636719.5946 | 1244718.6074
71 | 2636809.2776 | 1244750.1973
72 | 2636809.604 | 1244745.2444
73 | 2636809.7497 | 1244743.0347
74 | 2636810.2435 | 1244735.5431
75 | 2636811.3313 | 1244719.041
76 | 2636719.2981 | 1244773.7486
77 | 2636720.4378 | 1244773.8287
78 | 2636719.2762 | 1244773.747
79 | 2636747.5833 | 1244775.7381
80 | 2636703.7748 | 1244772.6567
81 | 2636747.6525 | 1244775.743
82 | 2636707.6669 | 1244792.92
83 | 2636699.6887 | 1244752.1388
84 | 2636748.7848 | 1244775.8226
85 | 2636698.0882 | 1244744.102
86 | 2636954.3697 | 1244797.7329
87 | 2636954.7059 | 1244793.9377
88 | 2636956.5324 | 1244761.4537
89 | 2636972.4241 | 1244799.8014
90 | 2636958.4015 | 1244747.6972
91 | 2636937.6099 | 1244739.6091
92 | 2636953.1243 | 1244700.1007
93 | 2636922.3266 | 1244733.6637
94 | 2636911.1736 | 1244759.6371
95 | 2636894.9631 | 1244797.4908
96 | 2636891.3878 | 1244818.3822
97 | 2636904.1327 | 1244820.7829
98 | 2636908.0547 | 1244799.2415
99 | 2636783.0344 | 1244810.962
100 | 2637018.5859 | 1244648.6983
101 | 2636714.7643 | 1244719.8257
102 | 2636717.9487 | 1244719.0225
103 | 2636695.819 | 1244723.709
104 | 2636689.8309 | 1244724.6203
105 | 2636672.1647 | 1244726.347
106 | 2636775.3706 | 1244777.6927
107 | 2636748.831 | 1244775.8259
108 | 2636776.4969 | 1244777.7719
109 | 2636776.563 | 1244777.7765
110 | 2636777.694 | 1244777.8561
111 | 2636777.7323 | 1244777.8588
112 | 2636772.1054 | 1244810.1811
113 | 2636915.5685 | 1244623.5734
114 | 2636821.5204 | 1244585.1989
115 | 2636875.9869 | 1244623.8691
116 | 2636873.8353 | 1244642.9862
117 | 2637123.2911 | 1244703.1522
118 | 2636927.0664 | 1244801.7838
119 | 2637199.6955 | 1244661.1105
120 | 2637208.0932 | 1244662.99
121 | 2637186.5452 | 1244667.5692
122 | 2636854.652 | 1244705.2027

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99401 | -0.1147 | 0.0039078 | 0.00097939
1 | 0.99396 | -0.11553 | 0.002674 | 0.00067017
2 | 0.99427 | -0.10967 | 0.0061718 | 0.0015468
3 | 0.99375 | -0.11968 | 0.0049134 | 0.0012314
4 | 0.99436 | -0.1079 | 0.0047291 | 0.0011852
5 | 0.99375 | -0.11975 | 0.0031654 | 0.00079333
6 | 0.99511 | -0.093349 | 0.0059227 | 0.0014844
7 | 0.99362 | -0.12212 | 0.0038206 | 0.00095753
8 | 0.99598 | -0.076633 | 0 | 0
9 | 0.99236 | -0.14685 | 0.0012186 | 0.00030541
10 | 0.99249 | -0.14444 | 0.0039946 | 0.0010011
11 | 0.99201 | -0.15374 | 0 | 0
12 | 0.99293 | -0.13593 | 0.0063545 | 0.0015926
13 | 0.99172 | -0.15939 | 0.0011073 | 0.00027752
14 | 0.99188 | -0.1562 | 0.0015793 | 0.00039582
15 | 0.99194 | -0.15496 | 0.0016259 | 0.00040748
16 | 0.99367 | -0.12157 | 0.00079441 | 0.0001991
17 | 0.9916 | -0.16169 | 0.0060652 | 0.0015201
18 | 0.99187 | -0.15632 | 0.0013617 | 0.00034126
19 | 0.99372 | -0.1207 | 0.0021808 | 0.00054657
20 | 0.99143 | -0.16496 | 0 | 0
21 | 0.99186 | -0.15661 | 0 | 0
22 | 0.97996 | -0.38628 | 0.0016195 | 0.00040588
23 | 0.97983 | -0.38892 | 0.0016165 | 0.00040513
24 | 0.98033 | -0.37905 | 0.0016128 | 0.00040419
25 | 0.97964 | -0.39248 | 0.00125 | 0.00031327
26 | 0.98048 | -0.37617 | 0.0015832 | 0.00039679
27 | 0.97951 | -0.39519 | 0.0016244 | 0.0004071
28 | 0.98059 | -0.37395 | 0.001753 | 0.00043933
29 | 0.9802 | -0.38162 | 0.0016595 | 0.00041591
30 | 0.98021 | -0.38132 | 0.0015394 | 0.0003858
31 | 0.9794 | -0.39736 | 0.0015943 | 0.00039957
32 | 0.981 | -0.36593 | 0.0013611 | 0.00034113
33 | 0.99362 | -0.12212 | 0.0038939 | 0.00097591
34 | 0.99359 | -0.12275 | 0 | 0
35 | 0.99131 | -0.16719 | 0.0015099 | 0.00037841
36 | 0.99136 | -0.16621 | 0.0030194 | 0.00075674
37 | 0.99126 | -0.1683 | 0.0015077 | 0.00037786
38 | 0.99136 | -0.1663 | 0.0022461 | 0.00056291
39 | 0.9978 | -0.042148 | 0.0029494 | 0.00073918
40 | 1 | 0 | -0.3311 | -0.083612
41 | 0.99698 | -0.05788 | 0 | 0
42 | 0.99927 | -0.014084 | 0.011658 | 0.0029217
43 | 0.99669 | -0.063473 | 0.0062303 | 0.0015615
44 | 0.99691 | -0.059162 | 0.0018741 | 0.0004697
45 | 0.99918 | -0.015761 | 0.018546 | 0.0046481
46 | 0.99491 | -0.097171 | 0 | 0
47 | 0.9949 | -0.097873 | 0.0040206 | 0.0010077
48 | 0.99687 | -0.059988 | 0.00058822 | 0.00014742
49 | 0.99899 | -0.019413 | 0.0035256 | 0.00088361
50 | 0.99392 | -0.11603 | 0.0038076 | 0.00095427
51 | 0.99421 | -0.11055 | 0.0053384 | 0.0013379
52 | 0.99481 | -0.099669 | 0 | 0
53 | 0.99686 | -0.060135 | 0.00059793 | 0.00014986
54 | 0.97859 | -0.41321 | 0.0020459 | 0.00051275
55 | 0.97846 | -0.41573 | 0.0020887 | 0.00052347
56 | 0.97867 | -0.41164 | 0.002219 | 0.00055613
57 | 0.97835 | -0.41783 | 0.005131 | 0.0012859
58 | 0.97877 | -0.40966 | 0 | 0
59 | 0.97831 | -0.41858 | 0.0017999 | 0.00045111
60 | 0.97894 | -0.40625 | 0.000962 | 0.0002411
61 | 0.97831 | -0.41863 | 0.0021824 | 0.00054696
62 | 0.97903 | -0.40444 | 0.00095645 | 0.00023971
63 | 0.99322 | -0.12984 | 0.0036191 | 0.00090704
64 | 0.99323 | -0.12963 | 0.0039334 | 0.00098581
65 | 0.9916 | -0.16039 | 0.0076675 | 0.0019217
66 | 0.99222 | -0.14855 | 0.0093292 | 0.0023381
67 | 0.99 | -0.19118 | 0.0020247 | 0.00050745
68 | 0.98852 | -0.21976 | 0.0016114 | 0.00040386
69 | 0.98837 | -0.22271 | 0.0016032 | 0.00040179
70 | 0.98654 | -0.25811 | 0.0016198 | 0.00040595
71 | 0.99343 | -0.12568 | 0.0042652 | 0.001069
72 | 0.99348 | -0.12464 | 0.0033115 | 0.00082994
73 | 0.99351 | -0.12405 | 0.0016173 | 0.00040532
74 | 0.99363 | -0.12183 | 0.017318 | 0.0043404
75 | 0.99414 | -0.11189 | 0.0044626 | 0.0011184
76 | 0.98175 | -0.35128 | 0.0015927 | 0.00039916
77 | 0.98173 | -0.35161 | 0.0015937 | 0.00039943
78 | 0.98175 | -0.35127 | 0.0016152 | 0.0004048
79 | 0.98137 | -0.35869 | 0.001585 | 0.00039724
80 | 0.98203 | -0.34589 | 0 | 0
81 | 0.98137 | -0.3587 | 0.0015964 | 0.0004001
82 | 0.98127 | -0.36067 | 0.0016665 | 0.00041766
83 | 0.98316 | -0.32369 | 0.0015938 | 0.00039944
84 | 0.98136 | -0.35893 | 0.0015973 | 0.00040032
85 | 0.98362 | -0.31477 | 0.0064429 | 0.0016147
86 | 0.99255 | -0.14331 | 0.0033498 | 0.00083953
87 | 0.99256 | -0.14309 | 0 | 0
88 | 0.99292 | -0.13601 | 0.0042494 | 0.001065
89 | 0.99241 | -0.14605 | 0.008949 | 0.0022428
90 | 0.99313 | -0.13194 | 0 | 0
91 | 0.99347 | -0.12542 | 0.0033905 | 0.00084974
92 | 0.99427 | -0.10993 | 0.0017131 | 0.00042936
93 | 0.99377 | -0.11965 | 0 | 0
94 | 0.99351 | -0.12467 | 0.0033859 | 0.00084859
95 | 0.99326 | -0.12961 | 0 | 0
96 | 0.99323 | -0.13015 | 0 | 0
97 | 0.99321 | -0.13048 | 0.0014308 | 0.00035858
98 | 0.99319 | -0.13083 | 0.0027296 | 0.0006841
99 | 0.9791 | -0.40318 | 0.001711 | 0.00042882
100 | 0.99184 | -0.15689 | 0.0011216 | 0.0002811
101 | 0.98615 | -0.26556 | 0.012334 | 0.0030913
102 | 0.9864 | -0.26068 | 0.0015917 | 0.00039891
103 | 0.98489 | -0.29007 | 0 | 0
104 | 0.98487 | -0.29047 | 0.00051936 | 0.00013016
105 | 0.98482 | -0.29151 | 0.0032396 | 0.00081192
106 | 0.98116 | -0.36278 | 0.0015873 | 0.00039782
107 | 0.98136 | -0.35894 | 0.0016184 | 0.00040562
108 | 0.98116 | -0.36291 | 0.0015892 | 0.00039828
109 | 0.98116 | -0.36292 | 0.0015902 | 0.00039853
110 | 0.98115 | -0.36299 | 0.001593 | 0.00039924
111 | 0.98115 | -0.36299 | 0.0016172 | 0.0004053
112 | 0.97929 | -0.39937 | 0.0016153 | 0.00040483
113 | 0.99684 | -0.060595 | 0.00087859 | 0.0002202
114 | 0.99356 | -0.12328 | 0.0013851 | 0.00034713
115 | 0.99882 | -0.022747 | 0.0033653 | 0.00084343
116 | 0.99888 | -0.021615 | 0.0035219 | 0.00088266
117 | 0.99109 | -0.17148 | 0 | 0
118 | 0.99315 | -0.13166 | 0.0024699 | 0.00061901
119 | 0.99069 | -0.17923 | 0.0016264 | 0.00040762
120 | 0.99066 | -0.17981 | 0.0033659 | 0.00084356
121 | 0.99076 | -0.17792 | 0 | 0
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.019858 | 0.0049779 | -0.019857 | -0.0049774 | 7.8357e-07 | 4.7084e-07 | 0.029727 | 0.029727 | 0.029727 | 0.99401 | -0.1147 | 0.99396 | -0.11553 | 8.1668
1 | -0.023766 | -0.0059573 | 0.023771 | 0.0059608 | 5.7034e-06 | 3.4944e-06 | 0.035577 | 0.035577 | 0.035577 | 0.99401 | -0.1147 | 0.99427 | -0.10967 | 9.7739
2 | 0.017183 | 0.0043072 | -0.01718 | -0.0043052 | 3.3914e-06 | 1.9934e-06 | 0.025724 | 0.025724 | 0.025724 | 0.99396 | -0.11553 | 0.99375 | -0.11968 | 7.0671
3 | -0.029943 | -0.0075076 | 0.029946 | 0.0075091 | 2.5257e-06 | 1.573e-06 | 0.044814 | 0.044814 | 0.044814 | 0.99427 | -0.10967 | 0.99436 | -0.1079 | 12.3115
4 | 0.012266 | 0.0030738 | -0.012266 | -0.0030738 | 4.6125e-08 | 2.4796e-08 | 0.018367 | 0.018367 | 0.018367 | 0.99375 | -0.11968 | 0.99375 | -0.11975 | 5.0459
5 | -0.034675 | -0.0086944 | 0.034699 | 0.0087095 | 2.406e-05 | 1.5089e-05 | 0.051891 | 0.051891 | 0.051891 | 0.99436 | -0.1079 | 0.99511 | -0.093349 | 14.2557
6 | 0.0091007 | 0.0022805 | -0.0090997 | -0.00228 | 1.0242e-06 | 4.6498e-07 | 0.013627 | 0.013627 | 0.013627 | 0.99375 | -0.11975 | 0.99362 | -0.12212 | 3.7437
7 | -0.040621 | -0.010194 | 0.040654 | 0.010214 | 3.2409e-05 | 2.0438e-05 | 0.060747 | 0.060747 | 0.060747 | 0.99511 | -0.093349 | 0.99598 | -0.076633 | 16.6887
8 | 0.0052791 | 0.0013225 | -0.0052791 | -0.0013225 | 1.4067e-09 | 1.248e-10 | 0.0079056 | 0.0079056 | 0.0079056 | 0.99362 | -0.12212 | 0.99362 | -0.12212 | 2.1719
9 | 0.15737 | 0.039955 | -0.15721 | -0.039856 | 0.00015535 | 9.9035e-05 | 0.23529 | 0.23529 | 0.23529 | 0.99598 | -0.076633 | 0.99491 | -0.097171 | 32.3201
10 | -0.19802 | -0.050169 | 0.19875 | 0.050637 | 0.0007319 | 0.00046725 | 0.29604 | 0.29604 | 0.29604 | 0.99598 | -0.076633 | 1 | 0 | 40.6644
11 | -0.027378 | -0.0068663 | 0.027381 | 0.0068682 | 3.1513e-06 | 1.9524e-06 | 0.041054 | 0.041054 | 0.041054 | 0.99236 | -0.14685 | 0.99249 | -0.14444 | 11.2786
12 | 0.026159 | 0.0065609 | -0.026151 | -0.0065556 | 8.5768e-06 | 5.2972e-06 | 0.039227 | 0.039227 | 0.039227 | 0.99236 | -0.14685 | 0.99201 | -0.15374 | 10.7766
13 | -0.031376 | -0.0078694 | 0.031389 | 0.0078773 | 1.273e-05 | 7.9487e-06 | 0.047043 | 0.047043 | 0.047043 | 0.99249 | -0.14444 | 0.99293 | -0.13593 | 12.9239
14 | 0.020462 | 0.0051309 | -0.020456 | -0.0051276 | 5.5082e-06 | 3.324e-06 | 0.030694 | 0.030694 | 0.030694 | 0.99201 | -0.15374 | 0.99172 | -0.15939 | 8.4323
15 | 0.0040631 | 0.0010177 | -0.0040627 | -0.0010178 | 4.7681e-07 | -1.3673e-07 | 0.0060945 | 0.0060947 | 0.0060947 | 0.99201 | -0.15374 | 0.99188 | -0.1562 | 1.6744
16 | 0.001626 | 0.000407 | -0.0016259 | -0.00040748 | 9.5076e-08 | -4.8941e-07 | 0.0024388 | 0.002439 | 0.002439 | 0.99201 | -0.15374 | 0.99194 | -0.15496 | 0.67005
17 | -0.037743 | -0.0094699 | 0.037769 | 0.0094862 | 2.586e-05 | 1.6272e-05 | 0.056566 | 0.056566 | 0.056566 | 0.99293 | -0.13593 | 0.99367 | -0.12157 | 15.5401
18 | 0.019349 | 0.0048501 | -0.019347 | -0.0048488 | 2.1285e-06 | 1.2754e-06 | 0.029032 | 0.029032 | 0.029032 | 0.99172 | -0.15939 | 0.9916 | -0.16169 | 7.9759
19 | 0.0024833 | 0.00062199 | -0.0024833 | -0.00062202 | 1.4506e-08 | -2.6691e-08 | 0.0037253 | 0.0037254 | 0.0037254 | 0.99188 | -0.1562 | 0.99187 | -0.15632 | 1.0235
20 | -0.038563 | -0.0096853 | 0.038565 | 0.0096863 | 1.6067e-06 | 1.0116e-06 | 0.057756 | 0.057756 | 0.057756 | 0.99367 | -0.12157 | 0.99372 | -0.1207 | 15.8669
21 | 0.013282 | 0.0033287 | -0.01328 | -0.0033276 | 2.0688e-06 | 1.1449e-06 | 0.019931 | 0.019931 | 0.019931 | 0.9916 | -0.16169 | 0.99143 | -0.16496 | 5.4755
22 | 0.0011217 | 0.00028076 | -0.0011216 | -0.00028093 | 1.5193e-08 | -1.7498e-07 | 0.0016826 | 0.0016826 | 0.0016826 | 0.99187 | -0.15632 | 0.99186 | -0.15661 | 0.46227
23 | -0.040746 | -0.010233 | 0.040767 | 0.010246 | 2.0948e-05 | 1.3212e-05 | 0.061021 | 0.061021 | 0.061021 | 0.99372 | -0.1207 | 0.99427 | -0.10993 | 16.7641
24 | 0.0080137 | 0.0020079 | -0.0080129 | -0.0020076 | 8.4797e-07 | 3.4115e-07 | 0.012027 | 0.012028 | 0.012028 | 0.99143 | -0.16496 | 0.99131 | -0.16719 | 3.3043
25 | 0.0052658 | 0.0013197 | -0.0052655 | -0.0013196 | 3.12e-07 | 2.7926e-08 | 0.0079033 | 0.0079034 | 0.0079034 | 0.99143 | -0.16496 | 0.99136 | -0.16621 | 2.1713
26 | 0.0011216 | 0.00028093 | -0.0011216 | -0.0002811 | 1.5104e-08 | -1.7393e-07 | 0.0016826 | 0.0016827 | 0.0016827 | 0.99186 | -0.15661 | 0.99184 | -0.15689 | 0.46228
27 | 0.026825 | 0.0067326 | -0.026822 | -0.0067305 | 3.3711e-06 | 2.0892e-06 | 0.040736 | 0.040736 | 0.040736 | 0.97996 | -0.38628 | 0.97983 | -0.38892 | 11.1912
28 | -0.028445 | -0.0071385 | 0.028454 | 0.0071446 | 9.8141e-06 | 6.1042e-06 | 0.043195 | 0.043195 | 0.043195 | 0.97996 | -0.38628 | 0.98033 | -0.37905 | 11.8667
29 | 0.025205 | 0.0063254 | -0.025201 | -0.0063227 | 4.2858e-06 | 2.6447e-06 | 0.038281 | 0.038281 | 0.038281 | 0.97983 | -0.38892 | 0.97964 | -0.39248 | 10.5167
30 | -0.030067 | -0.0075488 | 0.030071 | 0.0075514 | 4.1299e-06 | 2.5765e-06 | 0.045643 | 0.045643 | 0.045643 | 0.98033 | -0.37905 | 0.98048 | -0.37617 | 12.5392
31 | 0.023951 | 0.0060095 | -0.023948 | -0.0060076 | 3.0877e-06 | 1.8978e-06 | 0.036382 | 0.036382 | 0.036382 | 0.97964 | -0.39248 | 0.97951 | -0.39519 | 9.9952
32 | -0.031654 | -0.0079481 | 0.031658 | 0.0079502 | 3.3536e-06 | 2.0974e-06 | 0.048046 | 0.048046 | 0.048046 | 0.98048 | -0.37617 | 0.98059 | -0.37395 | 13.1993
33 | 0.022323 | 0.0056005 | -0.022321 | -0.0055991 | 2.3122e-06 | 1.4123e-06 | 0.033915 | 0.033915 | 0.033915 | 0.97951 | -0.39519 | 0.9794 | -0.39736 | 9.3172
34 | -0.036611 | -0.0091903 | 0.036625 | 0.0091991 | 1.4014e-05 | 8.8163e-06 | 0.055561 | 0.055561 | 0.055561 | 0.98059 | -0.37395 | 0.981 | -0.36593 | 15.264
35 | 0.0032 | 0.00080072 | -0.0031989 | -0.0008016 | 1.1232e-06 | -8.8307e-07 | 0.0048555 | 0.004856 | 0.004856 | 0.98059 | -0.37395 | 0.98021 | -0.38132 | 1.3341
36 | -0.0016595 | -0.00041591 | 0.0016595 | 0.0004158 | 2.3238e-08 | -1.082e-07 | 0.0025192 | 0.0025192 | 0.0025192 | 0.9802 | -0.38162 | 0.98021 | -0.38132 | 0.6921
37 | 0.020727 | 0.0051995 | -0.020725 | -0.0051983 | 1.9899e-06 | 1.2062e-06 | 0.031493 | 0.031493 | 0.031493 | 0.9794 | -0.39736 | 0.97929 | -0.39937 | 8.6518
38 | -0.037986 | -0.0095402 | 0.037995 | 0.0095463 | 9.5346e-06 | 6.0055e-06 | 0.057626 | 0.057626 | 0.057626 | 0.981 | -0.36593 | 0.98127 | -0.36067 | 15.8312
39 | 0.0013851 | 0.00034657 | -0.0013851 | -0.00034687 | 4.1143e-08 | -3.0397e-07 | 0.0020741 | 0.0020742 | 0.0020742 | 0.99362 | -0.12212 | 0.99359 | -0.12275 | 0.56985
40 | 0.0013851 | 0.00034687 | -0.0013851 | -0.00034713 | 3.4988e-08 | -2.5845e-07 | 0.0020742 | 0.0020743 | 0.0020743 | 0.99359 | -0.12275 | 0.99356 | -0.12328 | 0.56987
41 | 0.006503 | 0.0016292 | -0.0065027 | -0.0016291 | 3.4368e-07 | 9.5954e-08 | 0.0097612 | 0.0097612 | 0.0097612 | 0.99131 | -0.16719 | 0.99126 | -0.1683 | 2.6816
42 | 0.0022461 | 0.00056289 | -0.0022461 | -0.00056291 | 9.7093e-09 | -2.3159e-08 | 0.0033713 | 0.0033713 | 0.0033713 | 0.99136 | -0.16621 | 0.99136 | -0.1663 | 0.92618
43 | 0.004995 | 0.0012512 | -0.0049942 | -0.0012512 | 7.5777e-07 | 2.1714e-08 | 0.0074979 | 0.0074981 | 0.0074981 | 0.99126 | -0.1683 | 0.99109 | -0.17148 | 2.0599
44 | -0.089867 | -0.022661 | 0.090049 | 0.022776 | 0.00018169 | 0.00011593 | 0.13407 | 0.13407 | 0.13407 | 0.9978 | -0.042148 | 1 | 0 | 36.8317
45 | 0.086918 | 0.021921 | -0.086852 | -0.02188 | 6.54e-05 | 4.1721e-05 | 0.12967 | 0.12967 | 0.12967 | 0.9978 | -0.042148 | 0.99698 | -0.05788 | 35.6233
46 | 0.040649 | 0.010199 | -0.040622 | -0.010182 | 2.7276e-05 | 1.7196e-05 | 0.06049 | 0.06049 | 0.06049 | 1 | 0 | 0.99927 | -0.014084 | 16.6182
47 | 0.082913 | 0.020893 | -0.082891 | -0.020879 | 2.2178e-05 | 1.4144e-05 | 0.12379 | 0.12379 | 0.12379 | 0.99698 | -0.05788 | 0.99669 | -0.063473 | 34.0082
48 | 0.0039392 | 0.00098639 | -0.003939 | -0.00098648 | 2.4051e-07 | -8.8027e-08 | 0.0058791 | 0.0058792 | 0.0058792 | 0.99698 | -0.05788 | 0.99691 | -0.059162 | 1.6152
49 | 0.028964 | 0.0072602 | -0.028962 | -0.0072588 | 2.3151e-06 | 1.4382e-06 | 0.043131 | 0.043131 | 0.043131 | 0.99927 | -0.014084 | 0.99918 | -0.015761 | 11.8491
50 | 0.07666 | 0.019318 | -0.076535 | -0.019237 | 0.00012593 | 8.0261e-05 | 0.11449 | 0.11449 | 0.11449 | 0.99669 | -0.063473 | 0.9949 | -0.097873 | 31.4529
51 | 0.0020649 | 0.00051678 | -0.0020648 | -0.00051703 | 8.1191e-08 | -2.4524e-07 | 0.0030818 | 0.0030819 | 0.0030819 | 0.99691 | -0.059162 | 0.99687 | -0.059988 | 0.84668
52 | 0.010416 | 0.0026107 | -0.010414 | -0.0026098 | 1.8115e-06 | 8.9646e-07 | 0.015511 | 0.015511 | 0.015511 | 0.99918 | -0.015761 | 0.99899 | -0.019413 | 4.2614
53 | 0.11329 | 0.028831 | -0.11319 | -0.028765 | 0.0001029 | 6.573e-05 | 0.1696 | 0.1696 | 0.1696 | 0.99491 | -0.097171 | 0.99392 | -0.11603 | 46.5934
54 | 0.043917 | 0.011025 | -0.043889 | -0.011008 | 2.8006e-05 | 1.7699e-05 | 0.06569 | 0.06569 | 0.06569 | 0.99491 | -0.097171 | 0.99421 | -0.11055 | 18.0468
55 | 0.072514 | 0.01823 | -0.072508 | -0.018226 | 6.2195e-06 | 3.9621e-06 | 0.10848 | 0.10848 | 0.10848 | 0.9949 | -0.097873 | 0.99481 | -0.099669 | 29.8008
56 | 0.0014766 | 0.00036961 | -0.0014765 | -0.00036967 | 1.0289e-08 | -6.7061e-08 | 0.0022039 | 0.0022039 | 0.0022039 | 0.99687 | -0.059988 | 0.99686 | -0.060135 | 0.60547
57 | 0.0068881 | 0.0017262 | -0.0068874 | -0.001726 | 7.2254e-07 | 2.228e-07 | 0.01026 | 0.01026 | 0.01026 | 0.99899 | -0.019413 | 0.99888 | -0.021615 | 2.8187
58 | 0.10938 | 0.027811 | -0.10921 | -0.027701 | 0.00017104 | 0.00010924 | 0.1639 | 0.1639 | 0.1639 | 0.99392 | -0.11603 | 0.99222 | -0.14855 | 45.0274
59 | 0.03855 | 0.0096697 | -0.038548 | -0.0096681 | 2.4607e-06 | 1.5493e-06 | 0.0577 | 0.0577 | 0.0577 | 0.99421 | -0.11055 | 0.99414 | -0.11189 | 15.8518
60 | 0.030007 | 0.0075372 | -0.029978 | -0.0075194 | 2.858e-05 | 1.78e-05 | 0.04489 | 0.04489 | 0.04489 | 0.99481 | -0.099669 | 0.99377 | -0.11965 | 12.3325
61 | 0.042501 | 0.010689 | -0.04248 | -0.010675 | 2.0819e-05 | 1.3146e-05 | 0.063585 | 0.063585 | 0.063585 | 0.99481 | -0.099669 | 0.99427 | -0.10993 | 17.4684
62 | 0.00087861 | 0.00021982 | -0.00087859 | -0.0002202 | 1.9253e-08 | -3.7685e-07 | 0.0013114 | 0.0013115 | 0.0013115 | 0.99686 | -0.060135 | 0.99684 | -0.060595 | 0.3603
63 | 0.011204 | 0.0028086 | -0.011203 | -0.0028079 | 1.3469e-06 | 7.0656e-07 | 0.017037 | 0.017037 | 0.017037 | 0.97859 | -0.41321 | 0.97846 | -0.41573 | 4.6806
64 | -0.01325 | -0.0033213 | 0.013251 | 0.0033219 | 9.8942e-07 | 5.5157e-07 | 0.020148 | 0.020148 | 0.020148 | 0.97859 | -0.41321 | 0.97867 | -0.41164 | 5.5352
65 | 0.0091144 | 0.0022844 | -0.0091135 | -0.002284 | 9.1336e-07 | 4.2534e-07 | 0.013861 | 0.013861 | 0.013861 | 0.97846 | -0.41573 | 0.97835 | -0.41783 | 3.808
66 | -0.01547 | -0.003878 | 0.015472 | 0.0038788 | 1.4565e-06 | 8.4391e-07 | 0.023522 | 0.023522 | 0.023522 | 0.97867 | -0.41164 | 0.97877 | -0.40966 | 6.4621
67 | 0.0039825 | 0.00099801 | -0.0039823 | -0.00099805 | 1.4196e-07 | -3.8711e-08 | 0.0060571 | 0.0060571 | 0.0060571 | 0.97835 | -0.41783 | 0.97831 | -0.41858 | 1.664
68 | -0.015472 | -0.0038788 | 0.015474 | 0.0038803 | 2.5202e-06 | 1.4602e-06 | 0.023522 | 0.023522 | 0.023522 | 0.97877 | -0.40966 | 0.97894 | -0.40625 | 6.4621
69 | 0.0021824 | 0.00054695 | -0.0021824 | -0.00054696 | 4.9633e-09 | -1.1906e-08 | 0.0033194 | 0.0033194 | 0.0033194 | 0.97831 | -0.41858 | 0.97831 | -0.41863 | 0.91193
70 | -0.016436 | -0.0041214 | 0.016438 | 0.0041222 | 1.4161e-06 | 8.3023e-07 | 0.024984 | 0.024984 | 0.024984 | 0.97894 | -0.40625 | 0.97903 | -0.40444 | 6.8638
71 | -0.017394 | -0.0043619 | 0.017395 | 0.0043626 | 1.0468e-06 | 6.1972e-07 | 0.026438 | 0.026438 | 0.026438 | 0.97903 | -0.40444 | 0.9791 | -0.40318 | 7.2631
72 | -0.0036191 | -0.00090704 | 0.0036192 | 0.00090702 | 3.461e-08 | -1.8478e-08 | 0.0054221 | 0.0054221 | 0.0054221 | 0.99322 | -0.12984 | 0.99323 | -0.12963 | 1.4896
73 | -0.0075526 | -0.0018928 | 0.007554 | 0.0018934 | 1.4242e-06 | 5.275e-07 | 0.011315 | 0.011315 | 0.011315 | 0.99323 | -0.12963 | 0.99343 | -0.12568 | 3.1085
74 | -0.099825 | -0.025327 | 0.099882 | 0.025363 | 5.6888e-05 | 3.6321e-05 | 0.14991 | 0.14991 | 0.14991 | 0.9916 | -0.16039 | 0.99222 | -0.14855 | 41.1838
75 | 0.092158 | 0.023405 | -0.092021 | -0.023318 | 0.00013637 | 8.7029e-05 | 0.1384 | 0.1384 | 0.1384 | 0.9916 | -0.16039 | 0.99 | -0.19118 | 38.0228
76 | 0.089997 | 0.022811 | -0.089873 | -0.022732 | 0.00012338 | 7.873e-05 | 0.13536 | 0.13536 | 0.13536 | 0.99 | -0.19118 | 0.98852 | -0.21976 | 37.1868
77 | 0.088262 | 0.022328 | -0.088249 | -0.02232 | 1.2527e-05 | 7.9928e-06 | 0.13293 | 0.13293 | 0.13293 | 0.98852 | -0.21976 | 0.98837 | -0.22271 | 36.5204
78 | 0.086646 | 0.021918 | -0.086499 | -0.021825 | 0.00014688 | 9.371e-05 | 0.13052 | 0.13052 | 0.13052 | 0.98837 | -0.22271 | 0.98654 | -0.25811 | 35.8574
79 | 0.084879 | 0.021419 | -0.084869 | -0.021412 | 1.0442e-05 | 6.6609e-06 | 0.12808 | 0.12808 | 0.12808 | 0.98654 | -0.25811 | 0.9864 | -0.26068 | 35.1862
80 | -0.011819 | -0.0029623 | 0.01182 | 0.0029626 | 5.8338e-07 | 3.0909e-07 | 0.017704 | 0.017703 | 0.017704 | 0.99343 | -0.12568 | 0.99348 | -0.12464 | 4.8636
81 | -0.015131 | -0.0037926 | 0.015132 | 0.0037928 | 4.2654e-07 | 2.4431e-07 | 0.022663 | 0.022663 | 0.022663 | 0.99348 | -0.12464 | 0.99351 | -0.12405 | 6.2262
82 | -0.016749 | -0.0041981 | 0.016751 | 0.0041992 | 1.7717e-06 | 1.0367e-06 | 0.025086 | 0.025086 | 0.025086 | 0.99351 | -0.12405 | 0.99363 | -0.12183 | 6.8916
83 | -0.034069 | -0.0085396 | 0.034085 | 0.0085497 | 1.6144e-05 | 1.0118e-05 | 0.051021 | 0.051021 | 0.051021 | 0.99363 | -0.12183 | 0.99414 | -0.11189 | 14.0167
84 | 0.015974 | 0.0040055 | -0.015974 | -0.0040053 | 2.5119e-07 | 1.4632e-07 | 0.024213 | 0.024213 | 0.024213 | 0.98175 | -0.35128 | 0.98173 | -0.35161 | 6.6519
85 | -0.017567 | -0.0044046 | 0.017567 | 0.0044046 | 5.8303e-09 | 3.4539e-09 | 0.026627 | 0.026627 | 0.026627 | 0.98175 | -0.35128 | 0.98175 | -0.35127 | 7.3151
86 | 0.01438 | 0.0036059 | -0.014376 | -0.0036031 | 4.8485e-06 | 2.7591e-06 | 0.021797 | 0.021797 | 0.021797 | 0.98173 | -0.35161 | 0.98137 | -0.35869 | 5.9883
87 | -0.019182 | -0.0048094 | 0.019187 | 0.0048124 | 4.9261e-06 | 2.9562e-06 | 0.029075 | 0.029075 | 0.029075 | 0.98175 | -0.35127 | 0.98203 | -0.34589 | 7.9876
88 | 0.012791 | 0.0032059 | -0.012791 | -0.0032059 | 9.7923e-09 | 5.3906e-09 | 0.019394 | 0.019394 | 0.019394 | 0.98137 | -0.35869 | 0.98137 | -0.3587 | 5.328
89 | 0.03969 | 0.0099816 | -0.039662 | -0.0099639 | 2.8001e-05 | 1.766e-05 | 0.060153 | 0.060153 | 0.060153 | 0.98203 | -0.34589 | 0.98127 | -0.36067 | 16.5255
90 | -0.058877 | -0.014794 | 0.05894 | 0.014834 | 6.246e-05 | 3.971e-05 | 0.089227 | 0.089227 | 0.089227 | 0.98203 | -0.34589 | 0.98316 | -0.32369 | 24.513
91 | 0.011194 | 0.0028058 | -0.011194 | -0.0028057 | 1.2263e-07 | 6.4141e-08 | 0.016973 | 0.016973 | 0.016973 | 0.98137 | -0.3587 | 0.98136 | -0.35893 | 4.663
92 | -0.060533 | -0.015233 | 0.060559 | 0.01525 | 2.5806e-05 | 1.6412e-05 | 0.091639 | 0.091639 | 0.091639 | 0.98316 | -0.32369 | 0.98362 | -0.31477 | 25.1757
93 | 0.0095967 | 0.0024054 | -0.0095967 | -0.0024054 | 3.6771e-09 | 1.7679e-09 | 0.014551 | 0.014551 | 0.014551 | 0.98136 | -0.35893 | 0.98136 | -0.35894 | 3.9977
94 | -0.067002 | -0.016864 | 0.067081 | 0.016915 | 7.9214e-05 | 5.0436e-05 | 0.10139 | 0.10139 | 0.10139 | 0.98362 | -0.31477 | 0.98489 | -0.29007 | 27.8533
95 | -0.0033498 | -0.00083953 | 0.0033498 | 0.00083951 | 3.6033e-08 | -2.6182e-08 | 0.005022 | 0.0050219 | 0.005022 | 0.99255 | -0.14331 | 0.99256 | -0.14309 | 1.3797
96 | -0.0123 | -0.0030829 | 0.012304 | 0.0030851 | 4.1486e-06 | 2.2345e-06 | 0.01844 | 0.01844 | 0.01844 | 0.99256 | -0.14309 | 0.99292 | -0.13601 | 5.0659
97 | 0.0089503 | 0.0022434 | -0.008949 | -0.0022428 | 1.2625e-06 | 5.6635e-07 | 0.013418 | 0.013418 | 0.013418 | 0.99256 | -0.14309 | 0.99241 | -0.14605 | 3.6863
98 | -0.016554 | -0.0041501 | 0.016557 | 0.004152 | 3.2077e-06 | 1.8731e-06 | 0.024808 | 0.024808 | 0.024808 | 0.99292 | -0.13601 | 0.99313 | -0.13194 | 6.8154
99 | -0.016557 | -0.004152 | 0.016562 | 0.004155 | 5.1487e-06 | 3.0064e-06 | 0.024808 | 0.024808 | 0.024808 | 0.99313 | -0.13194 | 0.99347 | -0.12542 | 6.8154
100 | -0.019952 | -0.0050048 | 0.019958 | 0.0050081 | 5.4927e-06 | 3.3029e-06 | 0.029886 | 0.029886 | 0.029886 | 0.99347 | -0.12542 | 0.99377 | -0.11965 | 8.2105
101 | 0.010021 | 0.0025113 | -0.010018 | -0.0025102 | 2.3969e-06 | 1.1662e-06 | 0.015004 | 0.015004 | 0.015004 | 0.99377 | -0.11965 | 0.99351 | -0.12467 | 4.1221
102 | 0.0066322 | 0.0016616 | -0.0066307 | -0.0016611 | 1.5611e-06 | 4.5288e-07 | 0.0099331 | 0.0099333 | 0.0099333 | 0.99351 | -0.12467 | 0.99326 | -0.12961 | 2.7289
103 | 0.0051999 | 0.0013029 | -0.0051996 | -0.0013029 | 3.0057e-07 | 2.1421e-08 | 0.0077899 | 0.00779 | 0.00779 | 0.99326 | -0.12961 | 0.99319 | -0.13083 | 2.1401
104 | 0.0014308 | 0.00035818 | -0.0014308 | -0.00035843 | 3.6518e-08 | -2.5096e-07 | 0.0021434 | 0.0021435 | 0.0021435 | 0.99326 | -0.12961 | 0.99323 | -0.13015 | 0.58887
105 | 0.0014308 | 0.00035843 | -0.0014308 | -0.00035858 | 2.2346e-08 | -1.5354e-07 | 0.0021435 | 0.0021435 | 0.0021435 | 0.99323 | -0.13015 | 0.99321 | -0.13048 | 0.58889
106 | 0.00247 | 0.00061882 | -0.0024699 | -0.00061901 | 9.8497e-08 | -1.8518e-07 | 0.0037005 | 0.0037006 | 0.0037006 | 0.99319 | -0.13083 | 0.99315 | -0.13166 | 1.0166
107 | -0.019106 | -0.0047914 | 0.01911 | 0.0047935 | 3.4646e-06 | 2.0795e-06 | 0.029038 | 0.029038 | 0.029038 | 0.9791 | -0.40318 | 0.97929 | -0.39937 | 7.9775
108 | -0.083258 | -0.021001 | 0.083277 | 0.021013 | 1.9452e-05 | 1.2407e-05 | 0.12568 | 0.12568 | 0.12568 | 0.98615 | -0.26556 | 0.9864 | -0.26068 | 34.5265
109 | 0.070924 | 0.01791 | -0.07084 | -0.017857 | 8.3178e-05 | 5.2988e-05 | 0.10707 | 0.10707 | 0.10707 | 0.98615 | -0.26556 | 0.98489 | -0.29007 | 29.4136
110 | 0.0037592 | 0.00094193 | -0.0037591 | -0.00094196 | 7.3267e-08 | -3.0188e-08 | 0.0056795 | 0.0056795 | 0.0056795 | 0.98489 | -0.29007 | 0.98487 | -0.29047 | 1.5603
111 | 0.0032397 | 0.00081179 | -0.0032396 | -0.00081192 | 1.5958e-07 | -1.2387e-07 | 0.0048948 | 0.0048949 | 0.0048949 | 0.98487 | -0.29047 | 0.98482 | -0.29151 | 1.3447
112 | -0.0079768 | -0.0019992 | 0.0079783 | 0.0019998 | 1.4601e-06 | 5.984e-07 | 0.012098 | 0.012097 | 0.012098 | 0.98116 | -0.36278 | 0.98136 | -0.35894 | 3.3235
113 | 0.0063895 | 0.0016014 | -0.0063895 | -0.0016013 | 3.976e-08 | 1.1186e-08 | 0.0096903 | 0.0096903 | 0.0096903 | 0.98116 | -0.36278 | 0.98116 | -0.36291 | 2.6622
114 | 0.0048003 | 0.0012031 | -0.0048003 | -0.0012031 | 1.317e-09 | 7.6014e-12 | 0.0072802 | 0.0072802 | 0.0072802 | 0.98116 | -0.36291 | 0.98116 | -0.36292 | 2
115 | 0.0032102 | 0.00080454 | -0.0032102 | -0.00080454 | 1.0077e-08 | -7.8688e-09 | 0.0048685 | 0.0048685 | 0.0048685 | 0.98116 | -0.36292 | 0.98115 | -0.36299 | 1.3375
116 | 0.0016172 | 0.0004053 | -0.0016172 | -0.0004053 | 8.7292e-11 | -4.299e-10 | 0.0024526 | 0.0024526 | 0.0024526 | 0.98115 | -0.36299 | 0.98115 | -0.36299 | 0.67379
117 | -0.0033653 | -0.00084343 | 0.0033655 | 0.00084329 | 1.8145e-07 | -1.3584e-07 | 0.0050136 | 0.0050135 | 0.0050136 | 0.99882 | -0.022747 | 0.99888 | -0.021615 | 1.3774
118 | 0.0049942 | 0.0012512 | -0.0049927 | -0.0012511 | 1.5302e-06 | 4.4377e-08 | 0.0074981 | 0.0074984 | 0.0074984 | 0.99109 | -0.17148 | 0.99076 | -0.17792 | 2.06
119 | 0.003366 | 0.0008435 | -0.0033659 | -0.00084356 | 9.4274e-08 | -6.6308e-08 | 0.0050556 | 0.0050557 | 0.0050557 | 0.99069 | -0.17923 | 0.99066 | -0.17981 | 1.3889
120 | -0.0049924 | -0.0012511 | 0.0049927 | 0.0012511 | 3.1162e-07 | 9.124e-09 | 0.0074985 | 0.0074984 | 0.0074985 | 0.99069 | -0.17923 | 0.99076 | -0.17792 | 2.06

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3311 | 0.083612

## res_load
| p_mw | q_mvar
0 | 0.0039078 | 0.00097939
1 | 0.002674 | 0.00067017
2 | 0.0061718 | 0.0015468
3 | 0.0049134 | 0.0012314
4 | 0.0047291 | 0.0011852
5 | 0.0031654 | 0.00079333
6 | 0.0059227 | 0.0014844
7 | 0.0038206 | 0.00095753
8 | 0.0012186 | 0.00030541
9 | 0.0039946 | 0.0010011
10 | 0.0063545 | 0.0015926
11 | 0.0011073 | 0.00027752
12 | 0.0015793 | 0.00039582
13 | 0.0016259 | 0.00040748
14 | 0.00079441 | 0.0001991
15 | 0.0060652 | 0.0015201
16 | 0.0013617 | 0.00034126
17 | 0.0021808 | 0.00054657
18 | 0.0016195 | 0.00040588
19 | 0.0016165 | 0.00040513
20 | 0.0016128 | 0.00040419
21 | 0.00125 | 0.00031327
22 | 0.0015832 | 0.00039679
23 | 0.0016244 | 0.0004071
24 | 0.001753 | 0.00043933
25 | 0.0016595 | 0.00041591
26 | 0.0015394 | 0.0003858
27 | 0.0015943 | 0.00039957
28 | 0.0013611 | 0.00034113
29 | 0.0038939 | 0.00097591
30 | 0.0015099 | 0.00037841
31 | 0.0030194 | 0.00075674
32 | 0.0015077 | 0.00037786
33 | 0.0022461 | 0.00056291
34 | 0.0029494 | 0.00073918
35 | 0.011658 | 0.0029217
36 | 0.0062303 | 0.0015615
37 | 0.0018741 | 0.0004697
38 | 0.018546 | 0.0046481
39 | 0.0040206 | 0.0010077
40 | 0.00058822 | 0.00014742
41 | 0.0035256 | 0.00088361
42 | 0.0038076 | 0.00095427
43 | 0.0053384 | 0.0013379
44 | 0.00059793 | 0.00014986
45 | 0.0020459 | 0.00051275
46 | 0.0020887 | 0.00052347
47 | 0.002219 | 0.00055613
48 | 0.005131 | 0.0012859
49 | 0.0017999 | 0.00045111
50 | 0.000962 | 0.0002411
51 | 0.0021824 | 0.00054696
52 | 0.00095645 | 0.00023971
53 | 0.0036191 | 0.00090704
54 | 0.0039334 | 0.00098581
55 | 0.0076675 | 0.0019217
56 | 0.0093292 | 0.0023381
57 | 0.0020247 | 0.00050745
58 | 0.0016114 | 0.00040386
59 | 0.0016032 | 0.00040179
60 | 0.0016198 | 0.00040595
61 | 0.0042652 | 0.001069
62 | 0.0033115 | 0.00082994
63 | 0.0016173 | 0.00040532
64 | 0.017318 | 0.0043404
65 | 0.0044626 | 0.0011184
66 | 0.0015927 | 0.00039916
67 | 0.0015937 | 0.00039943
68 | 0.0016152 | 0.0004048
69 | 0.001585 | 0.00039724
70 | 0.0015964 | 0.0004001
71 | 0.0016665 | 0.00041766
72 | 0.0015938 | 0.00039944
73 | 0.0015973 | 0.00040032
74 | 0.0064429 | 0.0016147
75 | 0.0033498 | 0.00083953
76 | 0.0042494 | 0.001065
77 | 0.008949 | 0.0022428
78 | 0.0033905 | 0.00084974
79 | 0.0017131 | 0.00042936
80 | 0.0033859 | 0.00084859
81 | 0.0014308 | 0.00035858
82 | 0.0027296 | 0.0006841
83 | 0.001711 | 0.00042882
84 | 0.0011216 | 0.0002811
85 | 0.012334 | 0.0030913
86 | 0.0015917 | 0.00039891
87 | 0.00051936 | 0.00013016
88 | 0.0032396 | 0.00081192
89 | 0.0015873 | 0.00039782
90 | 0.0016184 | 0.00040562
91 | 0.0015892 | 0.00039828
92 | 0.0015902 | 0.00039853
93 | 0.001593 | 0.00039924
94 | 0.0016172 | 0.0004053
95 | 0.0016153 | 0.00040483
96 | 0.00087859 | 0.0002202
97 | 0.0013851 | 0.00034713
98 | 0.0033653 | 0.00084343
99 | 0.0035219 | 0.00088266
100 | 0.0024699 | 0.00061901
101 | 0.0016264 | 0.00040762
102 | 0.0033659 | 0.00084356

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1