## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2586-4_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2586-4_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2586-4_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2586-4_0_6_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2586-4_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2586-4_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2586-4_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2586-4_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2586-4_0_6_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_2586-4_0_6_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2586-4_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2586-4_0_6_node_124 | 0.4 | n |  | TRUE
12 | bus_LV_2586-4_0_6_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_2586-4_0_6_node_57 | 0.4 | n |  | TRUE
14 | bus_LV_2586-4_0_6_node_147 | 0.4 | n |  | TRUE
15 | bus_LV_2586-4_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2586-4_0_6_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_2586-4_0_6_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_2586-4_0_6_node_59 | 0.4 | n |  | TRUE
19 | bus_LV_2586-4_0_6_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_2586-4_0_6_node_142 | 0.4 | n |  | TRUE
21 | bus_LV_2586-4_0_6_node_143 | 0.4 | n |  | TRUE
22 | bus_LV_2586-4_0_6_node_144 | 0.4 | n |  | TRUE
23 | bus_LV_2586-4_0_6_node_145 | 0.4 | n |  | TRUE
24 | bus_LV_2586-4_0_6_node_146 | 0.4 | n |  | TRUE
25 | bus_LV_2586-4_0_6_node_148 | 0.4 | n |  | TRUE
26 | bus_LV_2586-4_0_6_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2586-4_0_6_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2586-4_0_6_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2586-4_0_6_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2586-4_0_6_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2586-4_0_6_node_76 | 0.4 | n |  | TRUE
32 | bus_LV_2586-4_0_6_node_82 | 0.4 | n |  | TRUE
33 | bus_LV_2586-4_0_6_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_2586-4_0_6_node_81 | 0.4 | n |  | TRUE
35 | bus_LV_2586-4_0_6_node_129 | 0.4 | n |  | TRUE
36 | bus_LV_2586-4_0_6_node_130 | 0.4 | n |  | TRUE
37 | bus_LV_2586-4_0_6_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2586-4_0_6_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_2586-4_0_6_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2586-4_0_6_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2586-4_0_6_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_2586-4_0_6_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_2586-4_0_6_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_2586-4_0_6_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_2586-4_0_6_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_2586-4_0_6_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_2586-4_0_6_node_133 | 0.4 | n |  | TRUE
48 | bus_LV_2586-4_0_6_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_2586-4_0_6_node_107 | 0.4 | n |  | TRUE
50 | bus_LV_2586-4_0_6_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_2586-4_0_6_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_2586-4_0_6_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_2586-4_0_6_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_2586-4_0_6_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_2586-4_0_6_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_2586-4_0_6_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_2586-4_0_6_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_2586-4_0_6_node_125 | 0.4 | n |  | TRUE
59 | bus_LV_2586-4_0_6_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2586-4_0_6_node_66 | 0.4 | n |  | TRUE
61 | bus_LV_2586-4_0_6_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_2586-4_0_6_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_2586-4_0_6_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_2586-4_0_6_node_32 | 0.4 | n |  | TRUE
65 | bus_LV_2586-4_0_6_node_33 | 0.4 | n |  | TRUE
66 | bus_LV_2586-4_0_6_node_34 | 0.4 | n |  | TRUE
67 | bus_LV_2586-4_0_6_node_35 | 0.4 | n |  | TRUE
68 | bus_LV_2586-4_0_6_node_36 | 0.4 | n |  | TRUE
69 | bus_LV_2586-4_0_6_node_37 | 0.4 | n |  | TRUE
70 | bus_LV_2586-4_0_6_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_2586-4_0_6_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2586-4_0_6_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2586-4_0_6_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2586-4_0_6_node_110 | 0.4 | n |  | TRUE
75 | bus_LV_2586-4_0_6_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_2586-4_0_6_node_109 | 0.4 | n |  | TRUE
77 | bus_LV_2586-4_0_6_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_2586-4_0_6_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_2586-4_0_6_node_94 | 0.4 | n |  | TRUE
80 | bus_LV_2586-4_0_6_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_2586-4_0_6_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_2586-4_0_6_node_47 | 0.4 | n |  | TRUE
83 | bus_LV_2586-4_0_6_node_48 | 0.4 | n |  | TRUE
84 | bus_LV_2586-4_0_6_node_92 | 0.4 | n |  | TRUE
85 | bus_LV_2586-4_0_6_node_90 | 0.4 | n |  | TRUE
86 | bus_LV_2586-4_0_6_node_93 | 0.4 | n |  | TRUE
87 | bus_LV_2586-4_0_6_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_2586-4_0_6_node_49 | 0.4 | n |  | TRUE
89 | bus_LV_2586-4_0_6_node_50 | 0.4 | n |  | TRUE
90 | bus_LV_2586-4_0_6_node_51 | 0.4 | n |  | TRUE
91 | bus_LV_2586-4_0_6_node_52 | 0.4 | n |  | TRUE
92 | bus_LV_2586-4_0_6_node_53 | 0.4 | n |  | TRUE
93 | bus_LV_2586-4_0_6_node_54 | 0.4 | n |  | TRUE
94 | bus_LV_2586-4_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_2586-4_0_6_node_95 | 0.4 | n |  | TRUE
96 | bus_LV_2586-4_0_6_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_2586-4_0_6_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_2586-4_0_6_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_2586-4_0_6_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_2586-4_0_6_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_2586-4_0_6_node_128 | 0.4 | n |  | TRUE
102 | bus_LV_2586-4_0_6_node_127 | 0.4 | n |  | TRUE
103 | bus_LV_2586-4_0_6_node_78 | 0.4 | n |  | TRUE
104 | bus_LV_2586-4_0_6_node_56 | 0.4 | n |  | TRUE
105 | bus_LV_2586-4_0_6_node_58 | 0.4 | n |  | TRUE
106 | bus_LV_2586-4_0_6_node_60 | 0.4 | n |  | TRUE
107 | bus_LV_2586-4_0_6_node_61 | 0.4 | n |  | TRUE
108 | bus_LV_2586-4_0_6_node_62 | 0.4 | n |  | TRUE
109 | bus_LV_2586-4_0_6_node_140 | 0.4 | n |  | TRUE
110 | bus_LV_2586-4_0_6_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_2586-4_0_6_node_112 | 0.4 | n |  | TRUE
112 | bus_LV_2586-4_0_6_node_77 | 0.4 | n |  | TRUE
113 | bus_LV_2586-4_0_6_node_68 | 0.4 | n |  | TRUE
114 | bus_LV_2586-4_0_6_node_69 | 0.4 | n |  | TRUE
115 | bus_LV_2586-4_0_6_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_2586-4_0_6_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_2586-4_0_6_node_70 | 0.4 | n |  | TRUE
118 | bus_LV_2586-4_0_6_node_71 | 0.4 | n |  | TRUE
119 | bus_LV_2586-4_0_6_node_72 | 0.4 | n |  | TRUE
120 | bus_LV_2586-4_0_6_node_74 | 0.4 | n |  | TRUE
121 | bus_LV_2586-4_0_6_node_138 | 0.4 | n |  | TRUE
122 | bus_LV_2586-4_0_6_node_137 | 0.4 | n |  | TRUE
123 | bus_LV_2586-4_0_6_node_75 | 0.4 | n |  | TRUE
124 | bus_LV_2586-4_0_6_node_98 | 0.4 | n |  | TRUE
125 | bus_LV_2586-4_0_6_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_2586-4_0_6_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_2586-4_0_6_node_83 | 0.4 | n |  | TRUE
128 | bus_LV_2586-4_0_6_node_85 | 0.4 | n |  | TRUE
129 | bus_LV_2586-4_0_6_node_86 | 0.4 | n |  | TRUE
130 | bus_LV_2586-4_0_6_node_87 | 0.4 | n |  | TRUE
131 | bus_LV_2586-4_0_6_node_88 | 0.4 | n |  | TRUE
132 | bus_LV_2586-4_0_6_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_2586-4_0_6_node_131 | 0.4 | n |  | TRUE
134 | bus_LV_2586-4_0_6_node_116 | 0.4 | n |  | TRUE
135 | bus_LV_2586-4_0_6_node_135 | 0.4 | n |  | TRUE
136 | bus_LV_2586-4_0_6_node_134 | 0.4 | n |  | TRUE
137 | bus_LV_2586-4_0_6_node_117 | 0.4 | n |  | TRUE
138 | bus_LV_2586-4_0_6_node_118 | 0.4 | n |  | TRUE
139 | bus_LV_2586-4_0_6_node_119 | 0.4 | n |  | TRUE
140 | bus_LV_2586-4_0_6_node_121 | 0.4 | n |  | TRUE
141 | bus_LV_2586-4_0_6_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_2586-4_0_6_node_136 | 0.4 | n |  | TRUE
143 | bus_LV_2586-4_0_6_node_132 | 0.4 | n |  | TRUE
144 | bus_MV_480_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2586-4_0_6_load_0 | 0 | 0.0019985 | 0.00050086 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2586-4_0_6_load_4 | 4 | 0.025515 | 0.0063946 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2586-4_0_6_load_5 | 5 | 0.054919 | 0.013764 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2586-4_0_6_load_6 | 6 | 0.0031012 | 0.00077722 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2586-4_0_6_load_7 | 7 | 0.0028469 | 0.00071349 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2586-4_0_6_load_10 | 8 | 0.062096 | 0.015563 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2586-4_0_6_load_11 | 9 | 0.004724 | 0.001184 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2586-4_0_6_load_8 | 10 | 0.0011509 | 0.00028843 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2586-4_0_6_load_124 | 11 | 0.0093371 | 0.0023401 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2586-4_0_6_load_9 | 15 | 0.0011704 | 0.00029333 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2586-4_0_6_load_46 | 16 | 0.0013451 | 0.00033712 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2586-4_0_6_load_42 | 17 | 0.0015981 | 0.00040052 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2586-4_0_6_load_55 | 19 | 0.0096721 | 0.0024241 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2586-4_0_6_load_142 | 20 | 0.0039779 | 0.00099696 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2586-4_0_6_load_146 | 24 | 0.00017465 | 4.377e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2586-4_0_6_load_148 | 25 | 0.00057755 | 0.00014475 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2586-4_0_6_load_12 | 26 | 0.005732 | 0.0014366 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2586-4_0_6_load_13 | 27 | 0.00080723 | 0.00020231 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2586-4_0_6_load_14 | 28 | 0.0048755 | 0.0012219 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2586-4_0_6_load_15 | 29 | 0.00061908 | 0.00015515 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2586-4_0_6_load_76 | 31 | 0.0054397 | 0.0013633 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2586-4_0_6_load_81 | 34 | 0.0011982 | 0.0003003 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2586-4_0_6_load_129 | 35 | 0.012608 | 0.0031598 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2586-4_0_6_load_130 | 36 | 0.0030822 | 0.00077248 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2586-4_0_6_load_17 | 37 | 0.002693 | 0.00067492 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2586-4_0_6_load_18 | 38 | 0.00147 | 0.00036842 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2586-4_0_6_load_20 | 40 | 0.0014714 | 0.00036876 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2586-4_0_6_load_21 | 41 | 0.0048166 | 0.0012072 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2586-4_0_6_load_22 | 42 | 0.0032713 | 0.00081987 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2586-4_0_6_load_23 | 43 | 0.0012278 | 0.00030771 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2586-4_0_6_load_104 | 44 | 0.0046757 | 0.0011718 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2586-4_0_6_load_102 | 45 | 0.0014265 | 0.00035751 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2586-4_0_6_load_101 | 46 | 0.0014709 | 0.00036865 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2586-4_0_6_load_133 | 47 | 0.0013246 | 0.00033196 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2586-4_0_6_load_103 | 48 | 0.012196 | 0.0030565 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2586-4_0_6_load_107 | 49 | 0.0033189 | 0.00083181 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2586-4_0_6_load_24 | 50 | 0.00038251 | 9.5866e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2586-4_0_6_load_25 | 51 | 0.0032254 | 0.00080837 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2586-4_0_6_load_26 | 52 | 0.0012809 | 0.00032103 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2586-4_0_6_load_27 | 53 | 0.0045784 | 0.0011475 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2586-4_0_6_load_28 | 54 | 0.0017873 | 0.00044794 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2586-4_0_6_load_29 | 55 | 0.001466 | 0.00036742 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2586-4_0_6_load_125 | 58 | 0.00030392 | 7.617e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2586-4_0_6_load_84 | 59 | 0.00056654 | 0.00014199 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2586-4_0_6_load_66 | 60 | 0.0021492 | 0.00053864 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2586-4_0_6_load_67 | 61 | 0.0024408 | 0.00061171 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2586-4_0_6_load_126 | 62 | 0.0010979 | 0.00027515 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2586-4_0_6_load_31 | 63 | 0.0019799 | 0.00049622 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2586-4_0_6_load_35 | 67 | 0.0023119 | 0.00057941 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2586-4_0_6_load_36 | 68 | 0.0013051 | 0.00032709 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2586-4_0_6_load_37 | 69 | 0.0015108 | 0.00037865 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2586-4_0_6_load_38 | 70 | 0.0015977 | 0.00040042 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2586-4_0_6_load_39 | 71 | 0.0015427 | 0.00038663 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2586-4_0_6_load_40 | 72 | 0.0014165 | 0.000355 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2586-4_0_6_load_110 | 74 | 0.0014259 | 0.00035736 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2586-4_0_6_load_63 | 75 | 0.0019559 | 0.00049019 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2586-4_0_6_load_109 | 76 | 0.0015184 | 0.00038054 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2586-4_0_6_load_105 | 77 | 0.0037823 | 0.00094794 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2586-4_0_6_load_64 | 78 | 0.0015359 | 0.00038492 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2586-4_0_6_load_94 | 79 | 0.0015466 | 0.00038762 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2586-4_0_6_load_43 | 80 | 0.0036599 | 0.00091725 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2586-4_0_6_load_45 | 81 | 0.0017343 | 0.00043465 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2586-4_0_6_load_47 | 82 | 0.0017827 | 0.00044679 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2586-4_0_6_load_48 | 83 | 0.0018152 | 0.00045494 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2586-4_0_6_load_92 | 84 | 0.001896 | 0.00047517 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2586-4_0_6_load_93 | 86 | 0.0015277 | 0.00038287 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2586-4_0_6_load_91 | 87 | 0.0030992 | 0.00077674 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2586-4_0_6_load_49 | 88 | 0.0014235 | 0.00035676 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2586-4_0_6_load_50 | 89 | 0.0019488 | 0.00048842 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2586-4_0_6_load_51 | 90 | 0.018962 | 0.0047523 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2586-4_0_6_load_53 | 92 | 0.021154 | 0.0053017 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2586-4_0_6_load_79 | 94 | 0.0014259 | 0.00035736 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2586-4_0_6_load_95 | 95 | 0.024107 | 0.0060417 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2586-4_0_6_load_100 | 99 | 0.019343 | 0.0048477 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2586-4_0_6_load_128 | 101 | 0.0071187 | 0.0017841 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2586-4_0_6_load_127 | 102 | 0.0046043 | 0.001154 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2586-4_0_6_load_78 | 103 | 0.0024167 | 0.00060569 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2586-4_0_6_load_56 | 104 | 0.017732 | 0.0044441 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2586-4_0_6_load_61 | 107 | 0.0018087 | 0.00045329 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2586-4_0_6_load_62 | 108 | 0.00091758 | 0.00022997 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2586-4_0_6_load_140 | 109 | 0.0051123 | 0.0012813 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2586-4_0_6_load_114 | 110 | 0.0055091 | 0.0013807 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2586-4_0_6_load_77 | 112 | 0.0020429 | 0.000512 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2586-4_0_6_load_68 | 113 | 0.0016343 | 0.00040961 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2586-4_0_6_load_69 | 114 | 0.0022248 | 0.00055758 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2586-4_0_6_load_113 | 116 | 0.0013292 | 0.00033314 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2586-4_0_6_load_70 | 117 | 0.0085879 | 0.0021523 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2586-4_0_6_load_71 | 118 | 0.0045509 | 0.0011406 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2586-4_0_6_load_74 | 120 | 0.00048473 | 0.00012148 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2586-4_0_6_load_138 | 121 | 0.0027438 | 0.00068767 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2586-4_0_6_load_137 | 122 | 0.00059511 | 0.00014915 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2586-4_0_6_load_108 | 125 | 0.0094599 | 0.0023709 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2586-4_0_6_load_115 | 126 | 0.0027254 | 0.00068306 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2586-4_0_6_load_86 | 129 | 0.0011991 | 0.00030052 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2586-4_0_6_load_87 | 130 | 0.00032937 | 8.2547e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2586-4_0_6_load_88 | 131 | 0.0015005 | 0.00037607 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2586-4_0_6_load_139 | 132 | 0.0012903 | 0.00032339 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2586-4_0_6_load_131 | 133 | 0.001387 | 0.00034762 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2586-4_0_6_load_116 | 134 | 0.0008814 | 0.0002209 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2586-4_0_6_load_135 | 135 | 0.0010139 | 0.00025411 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2586-4_0_6_load_117 | 137 | 0.0012391 | 0.00031056 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2586-4_0_6_load_118 | 138 | 0.0013867 | 0.00034753 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2586-4_0_6_load_119 | 139 | 0.0014309 | 0.00035862 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2586-4_0_6_load_121 | 140 | 0.0012889 | 0.00032302 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2586-4_0_6_load_123 | 141 | 0.0010702 | 0.00026821 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2586-4_0_6_load_136 | 142 | 0.0015101 | 0.00037846 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2586-4_0_6_load_132 | 143 | 0.0091709 | 0.0022984 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2586-4_0_6_line_0 |  | 0 | 1 | 0.015923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2586-4_0_6_line_1 |  | 1 | 2 | 0.020086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2586-4_0_6_line_2 |  | 2 | 6 | 0.022622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2586-4_0_6_line_3 |  | 2 | 7 | 0.0062666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2586-4_0_6_line_4 |  | 3 | 4 | 0.018846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2586-4_0_6_line_5 |  | 3 | 5 | 0.075952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2586-4_0_6_line_6 |  | 4 | 8 | 0.022224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2586-4_0_6_line_7 |  | 5 | 9 | 0.071762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2586-4_0_6_line_8 |  | 5 | 10 | 0.06626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2586-4_0_6_line_9 |  | 6 | 11 | 0.029125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2586-4_0_6_line_10 |  | 7 | 12 | 0.026506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2586-4_0_6_line_11 |  | 8 | 13 | 0.032603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2586-4_0_6_line_12 |  | 9 | 14 | 0.052333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2586-4_0_6_line_13 |  | 10 | 15 | 0.0091284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2586-4_0_6_line_14 |  | 12 | 16 | 0.0048124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2586-4_0_6_line_15 |  | 12 | 17 | 0.014053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2586-4_0_6_line_16 |  | 13 | 18 | 0.024028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2586-4_0_6_line_17 |  | 13 | 19 | 0.032309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2586-4_0_6_line_18 |  | 14 | 24 | 0.012154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2586-4_0_6_line_19 |  | 16 | 83 | 0.013585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2586-4_0_6_line_20 |  | 17 | 80 | 0.021795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2586-4_0_6_line_21 |  | 18 | 107 | 0.018451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2586-4_0_6_line_22 |  | 18 | 108 | 0.0378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2586-4_0_6_line_23 |  | 19 | 104 | 0.01916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2586-4_0_6_line_24 |  | 20 | 21 | 0.045619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2586-4_0_6_line_25 |  | 20 | 22 | 0.015062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2586-4_0_6_line_26 |  | 21 | 23 | 0.016847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2586-4_0_6_line_27 |  | 22 | 24 | 0.018722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2586-4_0_6_line_28 |  | 23 | 25 | 0.024457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2586-4_0_6_line_29 |  | 26 | 27 | 0.010074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2586-4_0_6_line_30 |  | 26 | 28 | 0.0037534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2586-4_0_6_line_31 |  | 27 | 29 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2586-4_0_6_line_32 |  | 29 | 30 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2586-4_0_6_line_33 |  | 30 | 31 | 0.029682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2586-4_0_6_line_34 |  | 30 | 32 | 0.023624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2586-4_0_6_line_35 |  | 31 | 33 | 0.020761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2586-4_0_6_line_36 |  | 32 | 34 | 0.020376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2586-4_0_6_line_37 |  | 33 | 123 | 0.042399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2586-4_0_6_line_38 |  | 33 | 118 | 0.034507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2586-4_0_6_line_39 |  | 34 | 127 | 0.012018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2586-4_0_6_line_40 |  | 35 | 36 | 0.12319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2586-4_0_6_line_41 |  | 36 | 122 | 0.069279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2586-4_0_6_line_42 |  | 37 | 38 | 8.2248e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2586-4_0_6_line_43 |  | 37 | 39 | 0.0058084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2586-4_0_6_line_44 |  | 38 | 40 | 0.0006263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2586-4_0_6_line_45 |  | 39 | 41 | 0.013906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2586-4_0_6_line_46 |  | 39 | 42 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2586-4_0_6_line_47 |  | 40 | 43 | 0.00029558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2586-4_0_6_line_48 |  | 41 | 44 | 0.014965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2586-4_0_6_line_49 |  | 42 | 45 | 0.014674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2586-4_0_6_line_50 |  | 43 | 46 | 0.00030485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2586-4_0_6_line_51 |  | 44 | 47 | 0.014787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2586-4_0_6_line_52 |  | 45 | 48 | 0.01539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2586-4_0_6_line_53 |  | 46 | 49 | 0.021788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2586-4_0_6_line_54 |  | 47 | 133 | 0.0013003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2586-4_0_6_line_55 |  | 49 | 73 | 0.035841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2586-4_0_6_line_56 |  | 50 | 51 | 0.0082795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2586-4_0_6_line_57 |  | 50 | 52 | 0.010344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2586-4_0_6_line_58 |  | 51 | 53 | 0.0010034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2586-4_0_6_line_59 |  | 52 | 54 | 0.020805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2586-4_0_6_line_60 |  | 53 | 55 | 0.02907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2586-4_0_6_line_61 |  | 54 | 56 | 0.00232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2586-4_0_6_line_62 |  | 55 | 57 | 0.017134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2586-4_0_6_line_63 |  | 56 | 58 | 0.012918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2586-4_0_6_line_64 |  | 56 | 59 | 0.021529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2586-4_0_6_line_65 |  | 57 | 60 | 0.024656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2586-4_0_6_line_66 |  | 57 | 61 | 0.00092031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2586-4_0_6_line_67 |  | 58 | 62 | 0.0053825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2586-4_0_6_line_68 |  | 60 | 113 | 0.022247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2586-4_0_6_line_69 |  | 61 | 114 | 0.012845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2586-4_0_6_line_70 |  | 62 | 132 | 0.015456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2586-4_0_6_line_71 |  | 63 | 64 | 0.01911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2586-4_0_6_line_72 |  | 63 | 65 | 0.024757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2586-4_0_6_line_73 |  | 64 | 66 | 0.022582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2586-4_0_6_line_74 |  | 64 | 67 | 0.019182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2586-4_0_6_line_75 |  | 65 | 68 | 0.0087039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2586-4_0_6_line_76 |  | 65 | 69 | 0.00541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2586-4_0_6_line_77 |  | 66 | 70 | 0.016313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2586-4_0_6_line_78 |  | 67 | 71 | 0.018788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2586-4_0_6_line_79 |  | 68 | 72 | 0.016244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2586-4_0_6_line_80 |  | 69 | 73 | 0.023032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2586-4_0_6_line_81 |  | 70 | 74 | 0.0097543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2586-4_0_6_line_82 |  | 71 | 75 | 0.030378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2586-4_0_6_line_83 |  | 72 | 76 | 0.017605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2586-4_0_6_line_84 |  | 73 | 77 | 0.016059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2586-4_0_6_line_85 |  | 75 | 78 | 0.018819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2586-4_0_6_line_86 |  | 76 | 79 | 0.0025039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2586-4_0_6_line_87 |  | 78 | 112 | 0.024481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2586-4_0_6_line_88 |  | 79 | 86 | 0.019311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2586-4_0_6_line_89 |  | 80 | 81 | 0.0027838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2586-4_0_6_line_90 |  | 81 | 82 | 0.009978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2586-4_0_6_line_91 |  | 82 | 84 | 0.023314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2586-4_0_6_line_92 |  | 83 | 85 | 0.0049379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2586-4_0_6_line_93 |  | 84 | 86 | 0.0016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2586-4_0_6_line_94 |  | 85 | 87 | 0.043748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2586-4_0_6_line_95 |  | 88 | 89 | 0.0080229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2586-4_0_6_line_96 |  | 88 | 90 | 0.055186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2586-4_0_6_line_97 |  | 89 | 91 | 0.017437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2586-4_0_6_line_98 |  | 90 | 92 | 0.020824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2586-4_0_6_line_99 |  | 91 | 93 | 0.009786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2586-4_0_6_line_100 |  | 93 | 94 | 0.01544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2586-4_0_6_line_101 |  | 94 | 103 | 0.026769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2586-4_0_6_line_102 |  | 95 | 96 | 0.073216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2586-4_0_6_line_103 |  | 96 | 97 | 0.050453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2586-4_0_6_line_104 |  | 96 | 98 | 0.048977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2586-4_0_6_line_105 |  | 97 | 99 | 0.02258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2586-4_0_6_line_106 |  | 98 | 124 | 0.013441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2586-4_0_6_line_107 |  | 100 | 101 | 0.021486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2586-4_0_6_line_108 |  | 100 | 102 | 0.032307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2586-4_0_6_line_109 |  | 101 | 126 | 0.0088153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2586-4_0_6_line_110 |  | 102 | 125 | 0.045986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2586-4_0_6_line_111 |  | 103 | 107 | 0.0026952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2586-4_0_6_line_112 |  | 104 | 105 | 0.016233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2586-4_0_6_line_113 |  | 105 | 106 | 0.023891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2586-4_0_6_line_114 |  | 106 | 109 | 0.0069327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2586-4_0_6_line_115 |  | 108 | 110 | 0.017835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2586-4_0_6_line_116 |  | 110 | 111 | 0.02329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2586-4_0_6_line_117 |  | 111 | 126 | 0.025977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2586-4_0_6_line_118 |  | 111 | 115 | 0.005021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_2586-4_0_6_line_119 |  | 113 | 115 | 0.030954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_2586-4_0_6_line_120 |  | 115 | 116 | 0.013501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_2586-4_0_6_line_121 |  | 116 | 134 | 0.028167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
122 | LV_2586-4_0_6_line_122 |  | 117 | 118 | 0.050539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_2586-4_0_6_line_123 |  | 117 | 119 | 0.032522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_2586-4_0_6_line_124 |  | 119 | 120 | 0.019574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2586-4_0_6_line_125 |  | 120 | 124 | 0.102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_2586-4_0_6_line_126 |  | 121 | 122 | 0.057631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2586-4_0_6_line_127 |  | 122 | 123 | 0.11035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2586-4_0_6_line_128 |  | 127 | 128 | 0.010318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2586-4_0_6_line_129 |  | 127 | 129 | 0.016012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_2586-4_0_6_line_130 |  | 128 | 130 | 0.015359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2586-4_0_6_line_131 |  | 129 | 131 | 0.034944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_2586-4_0_6_line_132 |  | 131 | 132 | 0.012514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_2586-4_0_6_line_133 |  | 133 | 143 | 0.017804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2586-4_0_6_line_134 |  | 134 | 135 | 0.0012871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
135 | LV_2586-4_0_6_line_135 |  | 135 | 136 | 0.0090614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
136 | LV_2586-4_0_6_line_136 |  | 136 | 142 | 0.026234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2586-4_0_6_line_137 |  | 136 | 143 | 0.010697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2586-4_0_6_line_138 |  | 137 | 138 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2586-4_0_6_line_139 |  | 137 | 139 | 0.0060271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2586-4_0_6_line_140 |  | 139 | 140 | 0.012389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2586-4_0_6_line_141 |  | 140 | 141 | 0.0039508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2586-4_0_6_line_142 |  | 141 | 142 | 0.013549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2586-4_0_6_trafo_57 | 0.63 MVA 20/0.4 kV | 144 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2632147.3037 | 1243692.5978 | 2632151.1497 | 1243681.5449 | 2632152.6587 | 1243677.6041
1 | 2632147.3037 | 1243692.5978 | 2632141.4035 | 1243711.8005
2 | 2632141.4035 | 1243711.8005 | 2632162.5967 | 1243719.7116
3 | 2632141.4035 | 1243711.8005 | 2632139.3182 | 1243717.71
4 | 2632177.6555 | 1243639.15 | 2632187.5969 | 1243630.098 | 2632190.9977 | 1243625.9026 | 2632190.9977 | 1243625.9026
5 | 2632177.6555 | 1243639.15 | 2632169.3583 | 1243636.2588 | 2632105.0424 | 1243616.9008
6 | 2632190.9977 | 1243625.9026 | 2632199.704 | 1243606.3039 | 2632200.0116 | 1243605.5887
7 | 2632105.0424 | 1243616.9008 | 2632036.3258 | 1243596.2182
8 | 2632105.0424 | 1243616.9008 | 2632061.9912 | 1243667.2698
9 | 2632189.8822 | 1243729.8968 | 2632162.5967 | 1243719.7116
10 | 2632130.4977 | 1243742.7058 | 2632139.3182 | 1243717.71
11 | 2632210.0931 | 1243574.6398 | 2632205.5843 | 1243590.8258 | 2632203.5156 | 1243597.441 | 2632200.0116 | 1243605.5887
12 | 2632036.3258 | 1243596.2182 | 2632010.2871 | 1243550.8226
13 | 2632053.2402 | 1243664.6717 | 2632061.9912 | 1243667.2698
14 | 2632130.4977 | 1243742.7058 | 2632128.8897 | 1243747.2417
15 | 2632130.4977 | 1243742.7058 | 2632143.7831 | 1243747.2863
16 | 2632233.3041 | 1243581.1032 | 2632210.0931 | 1243574.6398
17 | 2632210.0931 | 1243574.6398 | 2632188.6607 | 1243569.0756 | 2632178.8664 | 1243566.3532
18 | 2632010.2871 | 1243550.8226 | 2631999.0285 | 1243546.2454
19 | 2632128.8897 | 1243747.2417 | 2632124.3507 | 1243760.0459
20 | 2632143.7831 | 1243747.2863 | 2632153.1039 | 1243750.4998 | 2632164.3668 | 1243754.4498
21 | 2632233.3041 | 1243581.1032 | 2632237.5316 | 1243563.1426
22 | 2632233.3041 | 1243581.1032 | 2632267.2006 | 1243590.4042 | 2632269.7731 | 1243591.044
23 | 2632160.4067 | 1243561.2221 | 2632178.8664 | 1243566.3532
24 | 2631925.4759 | 1243516.333 | 2631967.7332 | 1243533.5199
25 | 2631981.685 | 1243539.1944 | 2631967.7332 | 1243533.5199
26 | 2631909.7827 | 1243510.0892 | 2631925.4759 | 1243516.333
27 | 2631981.685 | 1243539.1944 | 2631999.0285 | 1243546.2454
28 | 2631909.7827 | 1243510.0892 | 2631900.6116 | 1243532.7616
29 | 2632405.7724 | 1243498.5495 | 2632409.7783 | 1243489.3058
30 | 2632404.2799 | 1243501.9934 | 2632405.7724 | 1243498.5495
31 | 2632416.4714 | 1243473.8616 | 2632409.7783 | 1243489.3058
32 | 2632424.12 | 1243461.4644 | 2632418.6383 | 1243468.8615 | 2632416.4714 | 1243473.8616
33 | 2632424.12 | 1243461.4644 | 2632415.3975 | 1243453.4005 | 2632406.1029 | 1243446.3008 | 2632400.8908 | 1243443.1178
34 | 2632424.12 | 1243461.4644 | 2632441.5659 | 1243477.4477
35 | 2632381.3982 | 1243436.5043 | 2632390.1021 | 1243438.2973 | 2632397.1017 | 1243440.8038 | 2632400.8908 | 1243443.1178
36 | 2632441.5659 | 1243477.4477 | 2632457.0901 | 1243490.645
37 | 2632381.3982 | 1243436.5043 | 2632388.7607 | 1243420.9789 | 2632392.266 | 1243422.6102 | 2632387.0664 | 1243433.7001 | 2632378.7743 | 1243429.8413
38 | 2632381.3982 | 1243436.5043 | 2632371.2994 | 1243435.5042 | 2632352.3022 | 1243435.1005 | 2632346.9512 | 1243434.8451
39 | 2632466.2469 | 1243498.4293 | 2632457.0901 | 1243490.645
40 | 2632416.7103 | 1243272.2299 | 2632515.2246 | 1243346.1896
41 | 2632366.6874 | 1243320.1593 | 2632416.7103 | 1243272.2299
42 | 2632262.1651 | 1243717.0785 | 2632262.1976 | 1243717.0029
43 | 2632265.6012 | 1243712.2962 | 2632262.1976 | 1243717.0029 | 2632262.1976 | 1243717.0029
44 | 2632261.9175 | 1243717.6537 | 2632262.1651 | 1243717.0785
45 | 2632265.6012 | 1243712.2962 | 2632274.4108 | 1243701.5371 | 2632274.4108 | 1243701.5371
46 | 2632265.6012 | 1243712.2962 | 2632266.6019 | 1243713.1021 | 2632268.598 | 1243714.3026 | 2632283.6822 | 1243719.8412
47 | 2632261.8006 | 1243717.9252 | 2632261.9175 | 1243717.6537
48 | 2632274.4108 | 1243701.5371 | 2632276.6014 | 1243701.7046 | 2632278.7039 | 1243701.4048 | 2632279.9023 | 1243700.5996 | 2632284.1917 | 1243692.4606
49 | 2632283.6822 | 1243719.8412 | 2632297.4572 | 1243724.8991
50 | 2632261.6801 | 1243718.2052 | 2632261.8006 | 1243717.9252
51 | 2632284.1917 | 1243692.4606 | 2632287.416 | 1243686.3424 | 2632289.382 | 1243680.5716 | 2632289.8398 | 1243678.8568
52 | 2632311.9042 | 1243730.2037 | 2632297.4572 | 1243724.8991
53 | 2632260.4114 | 1243739.1029 | 2632258.6025 | 1243734.7059 | 2632258.3021 | 1243730.2014 | 2632260.001 | 1243722.1054 | 2632261.6801 | 1243718.2052
54 | 2632290.1752 | 1243677.6006 | 2632289.8398 | 1243678.8568
55 | 2632279.7032 | 1243769.1982 | 2632274.5982 | 1243761.599 | 2632262.302 | 1243743.6984 | 2632260.4114 | 1243739.1029
56 | 2632403.7041 | 1243576.6832 | 2632401.2695 | 1243584.5966
57 | 2632403.7041 | 1243576.6832 | 2632406.7457 | 1243566.7968
58 | 2632401.2695 | 1243584.5966 | 2632400.9744 | 1243585.5556
59 | 2632406.7457 | 1243566.7968 | 2632408.0992 | 1243562.3975 | 2632413.6296 | 1243547.1681
60 | 2632400.9744 | 1243585.5556 | 2632392.4263 | 1243613.3403
61 | 2632414.4214 | 1243544.9874 | 2632413.6296 | 1243547.1681
62 | 2632387.3879 | 1243629.7167 | 2632392.4263 | 1243613.3403
63 | 2632414.4214 | 1243544.9874 | 2632426.6701 | 1243549.0921
64 | 2632414.4214 | 1243544.9874 | 2632421.4153 | 1243524.6265
65 | 2632387.3879 | 1243629.7167 | 2632364.4829 | 1243620.5911
66 | 2632388.2454 | 1243630.0508 | 2632387.3879 | 1243629.7167
67 | 2632431.7736 | 1243550.8024 | 2632426.6701 | 1243549.0921
68 | 2632343.8162 | 1243612.3573 | 2632364.4829 | 1243620.5911
69 | 2632388.2454 | 1243630.0508 | 2632399.5442 | 1243634.4527 | 2632400.2059 | 1243634.7343
70 | 2632431.7736 | 1243550.8024 | 2632446.4284 | 1243555.7135
71 | 2632232.9022 | 1243823.6014 | 2632233.8981 | 1243821.1052 | 2632237.4031 | 1243815.7986 | 2632244.2806 | 1243808.4522
72 | 2632260.2017 | 1243789.5054 | 2632247.6037 | 1243804.9025 | 2632244.2806 | 1243808.4522
73 | 2632232.9022 | 1243823.6014 | 2632231.6001 | 1243826.7964 | 2632229.3997 | 1243835.4011 | 2632227.5616 | 1243845.4865
74 | 2632232.9022 | 1243823.6014 | 2632220.2007 | 1243819.0963 | 2632214.6685 | 1243817.7025
75 | 2632260.2017 | 1243789.5054 | 2632257.0985 | 1243787.5984 | 2632253.2996 | 1243785.7989 | 2632252.4907 | 1243785.5125
76 | 2632260.2017 | 1243789.5054 | 2632263.6424 | 1243785.3306
77 | 2632227.5616 | 1243845.4865 | 2632212.4027 | 1243839.4607
78 | 2632196.158 | 1243814.6872 | 2632197.4021 | 1243814.8033 | 2632208.6997 | 1243816.1987 | 2632214.6685 | 1243817.7025
79 | 2632237.1781 | 1243780.0914 | 2632252.4907 | 1243785.5125
80 | 2632279.7032 | 1243769.1982 | 2632278.4007 | 1243769.7026 | 2632273.8032 | 1243773.002 | 2632263.6424 | 1243785.3306
81 | 2632212.4027 | 1243839.4607 | 2632203.3384 | 1243835.8575
82 | 2632196.158 | 1243814.6872 | 2632188.7991 | 1243814.0006 | 2632179.2034 | 1243813.704 | 2632165.8197 | 1243813.4343
83 | 2632237.1781 | 1243780.0914 | 2632220.5825 | 1243774.2161
84 | 2632279.7032 | 1243769.1982 | 2632282.2014 | 1243768.4002 | 2632288.1018 | 1243767.2982 | 2632295.5326 | 1243767.0927
85 | 2632147.0041 | 1243813.0551 | 2632165.8197 | 1243813.4343
86 | 2632220.5825 | 1243774.2161 | 2632218.2221 | 1243773.3805
87 | 2632122.5283 | 1243813.3986 | 2632126.9035 | 1243813.3986 | 2632144.4982 | 1243813.0046 | 2632147.0041 | 1243813.0551
88 | 2632200.0124 | 1243766.9512 | 2632205.2992 | 1243768.8054 | 2632218.2221 | 1243773.3805
89 | 2632164.3668 | 1243754.4498 | 2632166.9937 | 1243755.3711
90 | 2632176.4095 | 1243758.6734 | 2632166.9937 | 1243755.3711
91 | 2632176.4095 | 1243758.6734 | 2632198.4092 | 1243766.389
92 | 2632122.7008 | 1243764.7001 | 2632124.3507 | 1243760.0459
93 | 2632200.0124 | 1243766.9512 | 2632198.4092 | 1243766.389
94 | 2632081.1989 | 1243750.5 | 2632122.7008 | 1243764.7001
95 | 2632217.0288 | 1243515.9997 | 2632224.797 | 1243518.0054
96 | 2632163.5946 | 1243502.2036 | 2632217.0288 | 1243515.9997
97 | 2632241.1261 | 1243512.8462 | 2632235.3001 | 1243515.5052 | 2632231.2002 | 1243517.6065 | 2632227.7973 | 1243517.9994 | 2632224.797 | 1243518.0054
98 | 2632143.4316 | 1243496.9977 | 2632163.5946 | 1243502.2036
99 | 2632241.1261 | 1243512.8462 | 2632243.3395 | 1243515.7934 | 2632248.1862 | 1243519.5221
100 | 2632248.1862 | 1243519.5221 | 2632244.3743 | 1243534.4845
101 | 2632238.1491 | 1243560.5191 | 2632243.0975 | 1243539.4962 | 2632244.3743 | 1243534.4845
102 | 2632098.8063 | 1243342.3328 | 2632078.1643 | 1243387.5504 | 2632099.5725 | 1243397.2656
103 | 2632052.7425 | 1243321.4485 | 2632098.8063 | 1243342.3328
104 | 2632098.8063 | 1243342.3328 | 2632143.5356 | 1243362.5765
105 | 2632052.7425 | 1243321.4485 | 2632043.4794 | 1243342.0406
106 | 2632155.8091 | 1243368.1353 | 2632143.5356 | 1243362.5765
107 | 2632329.1786 | 1243548.5364 | 2632321.6678 | 1243568.6673
108 | 2632329.1786 | 1243548.5364 | 2632340.3842 | 1243518.2351
109 | 2632318.5863 | 1243576.9265 | 2632321.6678 | 1243568.6673
110 | 2632358.0192 | 1243475.795 | 2632347.3111 | 1243499.5036 | 2632340.3842 | 1243518.2351
111 | 2632238.1491 | 1243560.5191 | 2632237.5316 | 1243563.1426
112 | 2632144.7662 | 1243556.8746 | 2632160.4067 | 1243561.2221
113 | 2632144.7662 | 1243556.8746 | 2632140.0069 | 1243580.2862
114 | 2632140.0069 | 1243580.2862 | 2632143.8288 | 1243584.8542 | 2632143.5703 | 1243585.7961
115 | 2632287.0808 | 1243595.3486 | 2632269.7731 | 1243591.044
116 | 2632309.5978 | 1243601.2972 | 2632291.7888 | 1243596.5195 | 2632287.0808 | 1243595.3486
117 | 2632309.5978 | 1243601.2972 | 2632315.4753 | 1243585.0187 | 2632317.997 | 1243578.506 | 2632318.5863 | 1243576.9265
118 | 2632314.4575 | 1243602.6133 | 2632309.5978 | 1243601.2972
119 | 2632314.4575 | 1243602.6133 | 2632335.9219 | 1243609.2121 | 2632343.8162 | 1243612.3573
120 | 2632314.4575 | 1243602.6133 | 2632310.5862 | 1243615.5471
121 | 2632302.511 | 1243642.5322 | 2632308.1382 | 1243623.7259 | 2632310.5862 | 1243615.5471
122 | 2632296.8004 | 1243429.5672 | 2632299.6683 | 1243430.2888 | 2632318.8995 | 1243433.5066 | 2632346.9512 | 1243434.8451
123 | 2632265.6769 | 1243420.1977 | 2632285.8043 | 1243426.8001 | 2632296.8004 | 1243429.5672
124 | 2632265.6769 | 1243420.1977 | 2632247.9878 | 1243411.8162
125 | 2632247.9878 | 1243411.8162 | 2632155.8091 | 1243368.1353
126 | 2632327.5113 | 1243277.893 | 2632339.3278 | 1243290.4591 | 2632366.6874 | 1243320.1593
127 | 2632378.7743 | 1243429.8413 | 2632366.6874 | 1243320.1593
128 | 2632466.2469 | 1243498.4293 | 2632474.4043 | 1243504.778
129 | 2632466.2469 | 1243498.4293 | 2632460.9152 | 1243513.5273
130 | 2632474.4043 | 1243504.778 | 2632482.5176 | 1243495.7165 | 2632484.8371 | 1243493.5168
131 | 2632460.9152 | 1243513.5273 | 2632453.942 | 1243533.2734 | 2632455.5815 | 1243547.1802
132 | 2632455.5815 | 1243547.1802 | 2632446.4284 | 1243555.7135 | 2632446.4284 | 1243555.7135
133 | 2632290.1752 | 1243677.6006 | 2632294.7674 | 1243660.399
134 | 2632302.511 | 1243642.5322 | 2632302.142 | 1243643.7653
135 | 2632300.4013 | 1243652.6024 | 2632300.397 | 1243650.6011 | 2632301.2031 | 1243646.9031 | 2632302.142 | 1243643.7653
136 | 2632300.4013 | 1243652.6024 | 2632300.7969 | 1243653.5051 | 2632302.0989 | 1243654.5017 | 2632324.1878 | 1243662.8366
137 | 2632300.4013 | 1243652.6024 | 2632298.397 | 1243652.9028 | 2632297.0016 | 1243653.7958 | 2632296.1011 | 1243655.403 | 2632294.7674 | 1243660.399
138 | 2632357.8289 | 1243675.4134 | 2632373.7836 | 1243681.1432
139 | 2632357.8289 | 1243675.4134 | 2632352.1565 | 1243673.3763
140 | 2632340.5605 | 1243669.0146 | 2632351.3985 | 1243673.1041 | 2632352.1565 | 1243673.3763
141 | 2632340.5605 | 1243669.0146 | 2632336.8641 | 1243667.6198
142 | 2632324.1878 | 1243662.8366 | 2632336.8641 | 1243667.6198

## bus_geodata
| x | y | coords
0 | 2632152.6587 | 1243677.6041
1 | 2632147.3037 | 1243692.5978
2 | 2632141.4035 | 1243711.8005
3 | 2632177.6555 | 1243639.15
4 | 2632190.9977 | 1243625.9026
5 | 2632105.0424 | 1243616.9008
6 | 2632162.5967 | 1243719.7116
7 | 2632139.3182 | 1243717.71
8 | 2632200.0116 | 1243605.5887
9 | 2632036.3258 | 1243596.2182
10 | 2632061.9912 | 1243667.2698
11 | 2632189.8822 | 1243729.8968
12 | 2632130.4977 | 1243742.7058
13 | 2632210.0931 | 1243574.6398
14 | 2632010.2871 | 1243550.8226
15 | 2632053.2402 | 1243664.6717
16 | 2632128.8897 | 1243747.2417
17 | 2632143.7831 | 1243747.2863
18 | 2632233.3041 | 1243581.1032
19 | 2632178.8664 | 1243566.3532
20 | 2631967.7332 | 1243533.5199
21 | 2631925.4759 | 1243516.333
22 | 2631981.685 | 1243539.1944
23 | 2631909.7827 | 1243510.0892
24 | 2631999.0285 | 1243546.2454
25 | 2631900.6116 | 1243532.7616
26 | 2632405.7724 | 1243498.5494
27 | 2632409.7783 | 1243489.3058
28 | 2632404.2799 | 1243501.9934
29 | 2632416.4714 | 1243473.8616
30 | 2632424.12 | 1243461.4644
31 | 2632400.8908 | 1243443.1178
32 | 2632441.5659 | 1243477.4477
33 | 2632381.3982 | 1243436.5043
34 | 2632457.0901 | 1243490.645
35 | 2632515.2246 | 1243346.1896
36 | 2632416.7103 | 1243272.2299
37 | 2632262.1976 | 1243717.0029
38 | 2632262.1651 | 1243717.0785
39 | 2632265.6012 | 1243712.2962
40 | 2632261.9175 | 1243717.6537
41 | 2632274.4108 | 1243701.5371
42 | 2632283.6822 | 1243719.8412
43 | 2632261.8006 | 1243717.9252
44 | 2632284.1917 | 1243692.4606
45 | 2632297.4572 | 1243724.8991
46 | 2632261.68 | 1243718.2052
47 | 2632289.8398 | 1243678.8568
48 | 2632311.9042 | 1243730.2037
49 | 2632260.4114 | 1243739.1029
50 | 2632403.7041 | 1243576.6832
51 | 2632401.2695 | 1243584.5966
52 | 2632406.7457 | 1243566.7968
53 | 2632400.9744 | 1243585.5556
54 | 2632413.6296 | 1243547.1681
55 | 2632392.4263 | 1243613.3403
56 | 2632414.4214 | 1243544.9874
57 | 2632387.3879 | 1243629.7167
58 | 2632426.6701 | 1243549.0921
59 | 2632421.4153 | 1243524.6265
60 | 2632364.4829 | 1243620.5911
61 | 2632388.2454 | 1243630.0508
62 | 2632431.7736 | 1243550.8024
63 | 2632244.2806 | 1243808.4522
64 | 2632232.9022 | 1243823.6014
65 | 2632260.2016 | 1243789.5054
66 | 2632227.5616 | 1243845.4865
67 | 2632214.6685 | 1243817.7025
68 | 2632252.4907 | 1243785.5125
69 | 2632263.6424 | 1243785.3306
70 | 2632212.4027 | 1243839.4607
71 | 2632196.158 | 1243814.6872
72 | 2632237.1781 | 1243780.0914
73 | 2632279.7032 | 1243769.1982
74 | 2632203.3384 | 1243835.8575
75 | 2632165.8197 | 1243813.4343
76 | 2632220.5825 | 1243774.2161
77 | 2632295.5326 | 1243767.0927
78 | 2632147.0041 | 1243813.0551
79 | 2632218.2221 | 1243773.3805
80 | 2632164.3668 | 1243754.4498
81 | 2632166.9937 | 1243755.3711
82 | 2632176.4095 | 1243758.6734
83 | 2632124.3507 | 1243760.0459
84 | 2632198.4092 | 1243766.389
85 | 2632122.7008 | 1243764.7001
86 | 2632200.0124 | 1243766.9512
87 | 2632081.1989 | 1243750.5
88 | 2632217.0288 | 1243515.9997
89 | 2632224.797 | 1243518.0054
90 | 2632163.5946 | 1243502.2036
91 | 2632241.1261 | 1243512.8462
92 | 2632143.4316 | 1243496.9977
93 | 2632248.1862 | 1243519.5221
94 | 2632244.3743 | 1243534.4845
95 | 2632099.5725 | 1243397.2656
96 | 2632098.8063 | 1243342.3328
97 | 2632052.7425 | 1243321.4485
98 | 2632143.5356 | 1243362.5765
99 | 2632043.4794 | 1243342.0406
100 | 2632329.1786 | 1243548.5364
101 | 2632321.6678 | 1243568.6673
102 | 2632340.3842 | 1243518.2351
103 | 2632238.1491 | 1243560.5191
104 | 2632160.4067 | 1243561.2221
105 | 2632144.7662 | 1243556.8746
106 | 2632140.0069 | 1243580.2862
107 | 2632237.5316 | 1243563.1426
108 | 2632269.7731 | 1243591.044
109 | 2632143.5703 | 1243585.7961
110 | 2632287.0808 | 1243595.3486
111 | 2632309.5978 | 1243601.2972
112 | 2632122.5283 | 1243813.3986
113 | 2632343.8162 | 1243612.3573
114 | 2632400.2059 | 1243634.7343
115 | 2632314.4575 | 1243602.6133
116 | 2632310.5862 | 1243615.5471
117 | 2632296.8004 | 1243429.5672
118 | 2632346.9512 | 1243434.8451
119 | 2632265.6769 | 1243420.1977
120 | 2632247.9878 | 1243411.8162
121 | 2632327.5113 | 1243277.893
122 | 2632366.6874 | 1243320.1593
123 | 2632378.7743 | 1243429.8413
124 | 2632155.8091 | 1243368.1353
125 | 2632358.0192 | 1243475.795
126 | 2632318.5863 | 1243576.9265
127 | 2632466.2469 | 1243498.4293
128 | 2632474.4043 | 1243504.778
129 | 2632460.9152 | 1243513.5273
130 | 2632484.8371 | 1243493.5168
131 | 2632455.5815 | 1243547.1802
132 | 2632446.4284 | 1243555.7135
133 | 2632290.1752 | 1243677.6006
134 | 2632302.511 | 1243642.5322
135 | 2632302.142 | 1243643.7653
136 | 2632300.4013 | 1243652.6024
137 | 2632357.8289 | 1243675.4134
138 | 2632373.7836 | 1243681.1432
139 | 2632352.1565 | 1243673.3763
140 | 2632340.5605 | 1243669.0146
141 | 2632336.8641 | 1243667.6198
142 | 2632324.1878 | 1243662.8366
143 | 2632294.7674 | 1243660.399
144 | 2632233.3041 | 1243581.1032

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97096 | -0.56077 | 0.0019985 | 0.00050086
1 | 0.97099 | -0.56018 | 0 | 0
2 | 0.97103 | -0.55944 | 0 | 0
3 | 0.99468 | -0.10202 | 0 | 0
4 | 0.99583 | -0.079902 | 0.025515 | 0.0063946
5 | 0.99004 | -0.19169 | 0.054919 | 0.013764
6 | 0.97077 | -0.56464 | 0.0031012 | 0.00077722
7 | 0.97111 | -0.55776 | 0.0028469 | 0.00071349
8 | 0.9977 | -0.043947 | 0.062096 | 0.015563
9 | 0.98942 | -0.20378 | 0.004724 | 0.001184
10 | 0.9899 | -0.19443 | 0.0011509 | 0.00028843
11 | 0.97051 | -0.56967 | 0.0093371 | 0.0023401
12 | 0.97154 | -0.5493 | 0 | 0
13 | 1 | 0 | -0.51913 | -0.13223
14 | 0.98919 | -0.20819 | 0 | 0
15 | 0.98989 | -0.19462 | 0.0011704 | 0.00029333
16 | 0.97151 | -0.54985 | 0.0013451 | 0.00033712
17 | 0.97185 | -0.54319 | 0.0015981 | 0.00040052
18 | 0.9976 | -0.045355 | 0 | 0
19 | 0.99905 | -0.01833 | 0.0096721 | 0.0024241
20 | 0.989 | -0.21196 | 0.0039779 | 0.00099696
21 | 0.98897 | -0.21243 | 0 | 0
22 | 0.98906 | -0.21073 | 0 | 0
23 | 0.98896 | -0.2126 | 0 | 0
24 | 0.98914 | -0.20921 | 0.00017465 | 4.377e-05
25 | 0.98895 | -0.21285 | 0.00057755 | 0.00014475
26 | 0.97965 | -0.38999 | 0.005732 | 0.0014366
27 | 0.97975 | -0.38805 | 0.00080723 | 0.00020231
28 | 0.97963 | -0.39032 | 0.0048755 | 0.0012219
29 | 0.97992 | -0.38456 | 0.00061908 | 0.00015515
30 | 0.98009 | -0.38136 | 0 | 0
31 | 0.97934 | -0.39602 | 0.0054397 | 0.0013633
32 | 0.98077 | -0.36799 | 0 | 0
33 | 0.97884 | -0.4056 | 0 | 0
34 | 0.98137 | -0.35648 | 0.0011982 | 0.0003003
35 | 0.97368 | -0.50707 | 0.012608 | 0.0031598
36 | 0.97513 | -0.47856 | 0.0030822 | 0.00077248
37 | 0.98075 | -0.36869 | 0.002693 | 0.00067492
38 | 0.98074 | -0.36879 | 0.00147 | 0.00036842
39 | 0.98114 | -0.36102 | 0 | 0
40 | 0.9807 | -0.36957 | 0.0014714 | 0.00036876
41 | 0.9823 | -0.33844 | 0.0048166 | 0.0012072
42 | 0.98083 | -0.36704 | 0.0032713 | 0.00081987
43 | 0.98068 | -0.36993 | 0.0012278 | 0.00030771
44 | 0.98362 | -0.31291 | 0.0046757 | 0.0011718
45 | 0.98065 | -0.37067 | 0.0014265 | 0.00035751
46 | 0.98067 | -0.3703 | 0.0014709 | 0.00036865
47 | 0.98498 | -0.2865 | 0.0013246 | 0.00033196
48 | 0.98048 | -0.37407 | 0.012196 | 0.0030565
49 | 0.97935 | -0.39582 | 0.0033189 | 0.00083181
50 | 0.98573 | -0.27192 | 0.00038251 | 9.5866e-05
51 | 0.986 | -0.26675 | 0.0032254 | 0.00080837
52 | 0.9854 | -0.27837 | 0.0012809 | 0.00032103
53 | 0.98604 | -0.2661 | 0.0045784 | 0.0011475
54 | 0.98474 | -0.29119 | 0.0017873 | 0.00044794
55 | 0.98705 | -0.2466 | 0.001466 | 0.00036742
56 | 0.98466 | -0.29259 | 0 | 0
57 | 0.98765 | -0.23497 | 0 | 0
58 | 0.98426 | -0.30038 | 0.00030392 | 7.617e-05
59 | 0.98465 | -0.29281 | 0.00056654 | 0.00014199
60 | 0.98856 | -0.21758 | 0.0021492 | 0.00053864
61 | 0.98765 | -0.23505 | 0.0024408 | 0.00061171
62 | 0.98409 | -0.30362 | 0.0010979 | 0.00027515
63 | 0.97546 | -0.47203 | 0.0019799 | 0.00049622
64 | 0.97524 | -0.47638 | 0 | 0
65 | 0.97579 | -0.4655 | 0 | 0
66 | 0.97518 | -0.47763 | 0 | 0
67 | 0.97508 | -0.47968 | 0.0023119 | 0.00057941
68 | 0.97546 | -0.47212 | 0.0013051 | 0.00032709
69 | 0.97608 | -0.45996 | 0.0015108 | 0.00037865
70 | 0.97513 | -0.47853 | 0.0015977 | 0.00040042
71 | 0.97495 | -0.48212 | 0.0015427 | 0.00038663
72 | 0.97485 | -0.4841 | 0.0014165 | 0.000355
73 | 0.97731 | -0.43579 | 0 | 0
74 | 0.97512 | -0.47879 | 0.0014259 | 0.00035736
75 | 0.9748 | -0.4852 | 0.0019559 | 0.00049019
76 | 0.97421 | -0.49664 | 0.0015184 | 0.00038054
77 | 0.97725 | -0.4369 | 0.0037823 | 0.00094794
78 | 0.97473 | -0.48644 | 0.0015359 | 0.00038492
79 | 0.97412 | -0.49836 | 0.0015466 | 0.00038762
80 | 0.97236 | -0.53308 | 0.0036599 | 0.00091725
81 | 0.97244 | -0.5316 | 0.0017343 | 0.00043465
82 | 0.97272 | -0.52599 | 0.0017827 | 0.00044679
83 | 0.97145 | -0.55109 | 0.0018152 | 0.00045494
84 | 0.97342 | -0.51211 | 0.001896 | 0.00047517
85 | 0.97144 | -0.55137 | 0 | 0
86 | 0.97348 | -0.51104 | 0.0015277 | 0.00038287
87 | 0.97131 | -0.55388 | 0.0030992 | 0.00077674
88 | 0.99355 | -0.12318 | 0.0014235 | 0.00035676
89 | 0.99385 | -0.1173 | 0.0019488 | 0.00048842
90 | 0.99152 | -0.16235 | 0.018962 | 0.0047523
91 | 0.99455 | -0.10392 | 0 | 0
92 | 0.99112 | -0.17016 | 0.021154 | 0.0053017
93 | 0.99494 | -0.096427 | 0 | 0
94 | 0.99555 | -0.08461 | 0.0014259 | 0.00035736
95 | 0.97044 | -0.57072 | 0.024107 | 0.0060417
96 | 0.97209 | -0.53811 | 0 | 0
97 | 0.97118 | -0.55613 | 0 | 0
98 | 0.97408 | -0.49893 | 0 | 0
99 | 0.97077 | -0.5642 | 0.019343 | 0.0048477
100 | 0.98992 | -0.19165 | 0 | 0
101 | 0.9902 | -0.18627 | 0.0071187 | 0.0017841
102 | 0.98951 | -0.19974 | 0.0046043 | 0.001154
103 | 0.99665 | -0.063488 | 0.0024167 | 0.00060569
104 | 0.99865 | -0.025977 | 0.017732 | 0.0044441
105 | 0.99857 | -0.027427 | 0 | 0
106 | 0.99846 | -0.029563 | 0 | 0
107 | 0.99677 | -0.06125 | 0.0018087 | 0.00045329
108 | 0.99438 | -0.10623 | 0.00091758 | 0.00022997
109 | 0.99843 | -0.030182 | 0.0051123 | 0.0012813
110 | 0.99287 | -0.13499 | 0.0055091 | 0.0013807
111 | 0.99094 | -0.17192 | 0 | 0
112 | 0.97469 | -0.48735 | 0.0020429 | 0.000512
113 | 0.98939 | -0.20164 | 0.0016343 | 0.00040961
114 | 0.98762 | -0.23556 | 0.0022248 | 0.00055758
115 | 0.99056 | -0.17919 | 0 | 0
116 | 0.99005 | -0.18898 | 0.0013292 | 0.00033314
117 | 0.97741 | -0.43369 | 0.0085879 | 0.0021523
118 | 0.97823 | -0.41755 | 0.0045509 | 0.0011406
119 | 0.97696 | -0.44239 | 0 | 0
120 | 0.97669 | -0.44762 | 0.00048473 | 0.00012148
121 | 0.97599 | -0.46154 | 0.0027438 | 0.00068767
122 | 0.97614 | -0.45865 | 0.00059511 | 0.00014915
123 | 0.97809 | -0.4203 | 0 | 0
124 | 0.97462 | -0.48821 | 0 | 0
125 | 0.98911 | -0.20748 | 0.0094599 | 0.0023709
126 | 0.99037 | -0.18296 | 0.0027254 | 0.00068306
127 | 0.98172 | -0.34961 | 0 | 0
128 | 0.98172 | -0.34967 | 0 | 0
129 | 0.98219 | -0.34043 | 0.0011991 | 0.00030052
130 | 0.98171 | -0.34976 | 0.00032937 | 8.2547e-05
131 | 0.98324 | -0.32017 | 0.0015005 | 0.00037607
132 | 0.98362 | -0.31281 | 0.0012903 | 0.00032339
133 | 0.9851 | -0.28415 | 0.001387 | 0.00034762
134 | 0.98847 | -0.21932 | 0.0008814 | 0.0002209
135 | 0.9884 | -0.2207 | 0.0010139 | 0.00025411
136 | 0.9879 | -0.23033 | 0 | 0
137 | 0.98755 | -0.23716 | 0.0012391 | 0.00031056
138 | 0.98752 | -0.23758 | 0.0013867 | 0.00034753
139 | 0.98756 | -0.23688 | 0.0014309 | 0.00035862
140 | 0.98761 | -0.23598 | 0.0012889 | 0.00032302
141 | 0.98763 | -0.2356 | 0.0010702 | 0.00026821
142 | 0.98771 | -0.23405 | 0.0015101 | 0.00037846
143 | 0.98679 | -0.25159 | 0.0091709 | 0.0022984
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019985 | -0.00050086 | 0.0019985 | 0.0005007 | 5.6007e-08 | -1.611e-07 | 0.0030627 | 0.0030626 | 0.0030627 | 0.97096 | -0.56077 | 0.97099 | -0.56018 | 0.8414
1 | -0.0019985 | -0.0005007 | 0.0019986 | 0.0005005 | 7.0647e-08 | -2.0324e-07 | 0.0030626 | 0.0030625 | 0.0030626 | 0.97099 | -0.56018 | 0.97103 | -0.55944 | 0.84138
2 | 0.012444 | 0.0031201 | -0.01244 | -0.0031184 | 3.0847e-06 | 1.6945e-06 | 0.019069 | 0.019069 | 0.019069 | 0.97103 | -0.55944 | 0.97077 | -0.56464 | 5.2388
3 | -0.014442 | -0.0036206 | 0.014443 | 0.0036212 | 1.151e-06 | 6.5914e-07 | 0.022132 | 0.022132 | 0.022132 | 0.97103 | -0.55944 | 0.97111 | -0.55776 | 6.0801
4 | -0.066988 | -0.016898 | 0.067059 | 0.016943 | 7.1027e-05 | 4.5212e-05 | 0.10025 | 0.10025 | 0.10025 | 0.99468 | -0.10202 | 0.99583 | -0.079902 | 27.5415
5 | 0.066988 | 0.016898 | -0.066702 | -0.016716 | 0.00028625 | 0.00018222 | 0.10025 | 0.10025 | 0.10025 | 0.99468 | -0.10202 | 0.99004 | -0.19169 | 27.5416
6 | -0.092574 | -0.023338 | 0.092733 | 0.02344 | 0.00015958 | 0.00010184 | 0.13838 | 0.13838 | 0.13838 | 0.99583 | -0.079902 | 0.9977 | -0.043947 | 38.0155
7 | 0.0094615 | 0.0023708 | -0.009456 | -0.0023682 | 5.4419e-06 | 2.5606e-06 | 0.01422 | 0.014221 | 0.014221 | 0.99004 | -0.19169 | 0.98942 | -0.20378 | 3.9068
8 | 0.0023216 | 0.000581 | -0.0023213 | -0.00058166 | 3.0251e-07 | -6.5833e-07 | 0.003489 | 0.0034893 | 0.0034893 | 0.99004 | -0.19169 | 0.9899 | -0.19443 | 0.95861
9 | 0.0093393 | 0.0023412 | -0.0093371 | -0.0023401 | 2.2383e-06 | 1.0725e-06 | 0.014316 | 0.014316 | 0.014316 | 0.97077 | -0.56464 | 0.97051 | -0.56967 | 3.9329
10 | -0.01729 | -0.0043347 | 0.017297 | 0.0043389 | 6.977e-06 | 4.1372e-06 | 0.026494 | 0.026494 | 0.026494 | 0.97111 | -0.55776 | 0.97154 | -0.5493 | 7.2785
11 | -0.15483 | -0.039002 | 0.15516 | 0.03921 | 0.00032616 | 0.00020789 | 0.23099 | 0.23099 | 0.23099 | 0.9977 | -0.043947 | 1 | 0 | 31.7292
12 | 0.004732 | 0.0011843 | -0.004731 | -0.0011843 | 9.9379e-07 | -3.5942e-08 | 0.007116 | 0.0071162 | 0.0071162 | 0.98942 | -0.20378 | 0.98919 | -0.20819 | 1.955
13 | 0.0011704 | 0.00029322 | -0.0011704 | -0.00029333 | 1.0596e-08 | -1.1057e-07 | 0.0017594 | 0.0017594 | 0.0017594 | 0.9899 | -0.19443 | 0.98989 | -0.19462 | 0.48335
14 | 0.0062604 | 0.0015685 | -0.0062603 | -0.0015685 | 1.6591e-07 | 4.6593e-08 | 0.0095883 | 0.0095883 | 0.0095883 | 0.97154 | -0.5493 | 0.97151 | -0.54985 | 2.6342
15 | -0.023558 | -0.0059074 | 0.023564 | 0.0059116 | 6.8608e-06 | 4.2169e-06 | 0.036082 | 0.036082 | 0.036082 | 0.97154 | -0.5493 | 0.97185 | -0.54319 | 9.9126
16 | 0.32977 | 0.084849 | -0.32905 | -0.084385 | 0.00072552 | 0.00046339 | 0.49149 | 0.49149 | 0.49149 | 1 | 0 | 0.9976 | -0.045355 | 45.008
17 | 0.032554 | 0.0081723 | -0.032526 | -0.0081545 | 2.8436e-05 | 1.7776e-05 | 0.048446 | 0.048446 | 0.048446 | 1 | 0 | 0.99905 | -0.01833 | 13.3094
18 | 0.004731 | 0.0011843 | -0.0047307 | -0.0011843 | 2.308e-07 | -8.2967e-09 | 0.0071162 | 0.0071163 | 0.0071163 | 0.98919 | -0.20819 | 0.98914 | -0.20921 | 1.955
19 | 0.0049152 | 0.0012314 | -0.0049149 | -0.0012313 | 2.8871e-07 | 1.6571e-08 | 0.0075281 | 0.0075282 | 0.0075282 | 0.97151 | -0.54985 | 0.97145 | -0.55109 | 2.0682
20 | -0.025162 | -0.0063121 | 0.025175 | 0.0063196 | 1.2133e-05 | 7.4946e-06 | 0.038529 | 0.038529 | 0.038529 | 0.97185 | -0.54319 | 0.97236 | -0.53308 | 10.5848
21 | 0.049391 | 0.012474 | -0.049353 | -0.01245 | 3.7589e-05 | 2.3816e-05 | 0.073705 | 0.073705 | 0.073705 | 0.9976 | -0.045355 | 0.99677 | -0.06125 | 20.2487
22 | 0.27966 | 0.071911 | -0.27883 | -0.071385 | 0.00082472 | 0.00052635 | 0.41778 | 0.41778 | 0.41778 | 0.9976 | -0.045355 | 0.99438 | -0.10623 | 38.2585
23 | 0.022854 | 0.0057305 | -0.022845 | -0.0057254 | 8.3253e-06 | 5.0774e-06 | 0.03404 | 0.03404 | 0.03404 | 0.99905 | -0.01833 | 0.99865 | -0.025977 | 9.3517
24 | 0.00057757 | 0.00014365 | -0.00057756 | -0.00014422 | 1.291e-08 | -5.7711e-07 | 0.0008686 | 0.00086881 | 0.00086881 | 0.989 | -0.21196 | 0.98897 | -0.21243 | 0.23868
25 | -0.0045555 | -0.0011406 | 0.0045558 | 0.0011406 | 2.6531e-07 | -2.3489e-08 | 0.0068537 | 0.0068536 | 0.0068537 | 0.989 | -0.21196 | 0.98906 | -0.21073 | 1.8829
26 | 0.00057756 | 0.00014422 | -0.00057755 | -0.00014444 | 4.7692e-09 | -2.1312e-07 | 0.00086881 | 0.00086889 | 0.00086889 | 0.98897 | -0.21243 | 0.98896 | -0.2126 | 0.23871
27 | -0.0045558 | -0.0011406 | 0.0045561 | 0.0011406 | 3.2978e-07 | -2.9236e-08 | 0.0068536 | 0.0068535 | 0.0068536 | 0.98906 | -0.21073 | 0.98914 | -0.20921 | 1.8829
28 | 0.00057755 | 0.00014444 | -0.00057755 | -0.00014475 | 6.925e-09 | -3.0938e-07 | 0.00086889 | 0.000869 | 0.000869 | 0.98896 | -0.2126 | 0.98895 | -0.21285 | 0.23874
29 | -0.010608 | -0.0026585 | 0.010609 | 0.002659 | 9.8074e-07 | 5.0082e-07 | 0.016112 | 0.016112 | 0.016112 | 0.97965 | -0.38999 | 0.97975 | -0.38805 | 4.4264
30 | 0.0048756 | 0.0012219 | -0.0048755 | -0.0012219 | 7.7196e-08 | 2.148e-09 | 0.0074057 | 0.0074057 | 0.0074057 | 0.97965 | -0.38999 | 0.97963 | -0.39032 | 2.0345
31 | -0.011416 | -0.0028613 | 0.011418 | 0.0028623 | 1.8975e-06 | 1.0024e-06 | 0.017338 | 0.017338 | 0.017338 | 0.97975 | -0.38805 | 0.97992 | -0.38456 | 4.7632
32 | -0.012037 | -0.0030175 | 0.012039 | 0.0030185 | 1.8362e-06 | 9.9049e-07 | 0.018278 | 0.018278 | 0.018278 | 0.97992 | -0.38456 | 0.98009 | -0.38136 | 5.0215
33 | 0.082069 | 0.020756 | -0.082011 | -0.020721 | 5.7665e-05 | 3.5785e-05 | 0.12467 | 0.12467 | 0.12467 | 0.98009 | -0.38136 | 0.97934 | -0.39602 | 11.4165
34 | -0.094107 | -0.023775 | 0.094167 | 0.023813 | 6.034e-05 | 3.7724e-05 | 0.14295 | 0.14295 | 0.14295 | 0.98009 | -0.38136 | 0.98077 | -0.36799 | 13.0903
35 | 0.076571 | 0.019357 | -0.076536 | -0.019336 | 3.5164e-05 | 2.1722e-05 | 0.1164 | 0.1164 | 0.1164 | 0.97934 | -0.39602 | 0.97884 | -0.4056 | 10.6597
36 | -0.094167 | -0.023813 | 0.09422 | 0.023845 | 5.2043e-05 | 3.2536e-05 | 0.14295 | 0.14295 | 0.14295 | 0.98077 | -0.36799 | 0.98137 | -0.35648 | 13.0903
37 | 0.01911 | 0.0048158 | -0.019096 | -0.0048077 | 1.3427e-05 | 8.0605e-06 | 0.029059 | 0.02906 | 0.02906 | 0.97884 | -0.4056 | 0.97809 | -0.4203 | 7.9834
38 | 0.057426 | 0.01452 | -0.057393 | -0.0145 | 3.2907e-05 | 1.976e-05 | 0.087344 | 0.087345 | 0.087345 | 0.97884 | -0.4056 | 0.97823 | -0.41755 | 7.9986
39 | -0.095418 | -0.024145 | 0.095449 | 0.024165 | 3.1482e-05 | 1.9693e-05 | 0.14476 | 0.14476 | 0.14476 | 0.98137 | -0.35648 | 0.98172 | -0.34961 | 13.2566
40 | -0.012608 | -0.0031598 | 0.012625 | 0.0031692 | 1.7149e-05 | 9.4407e-06 | 0.019267 | 0.019267 | 0.019267 | 0.97368 | -0.50707 | 0.97513 | -0.47856 | 5.2933
41 | -0.015707 | -0.0039417 | 0.015722 | 0.0039504 | 1.4927e-05 | 8.6881e-06 | 0.02397 | 0.02397 | 0.02397 | 0.97513 | -0.47856 | 0.97614 | -0.45865 | 6.5852
42 | 0.070619 | 0.017865 | -0.070619 | -0.017865 | 3.5448e-07 | 2.2583e-07 | 0.10721 | 0.10721 | 0.10721 | 0.98075 | -0.36869 | 0.98074 | -0.36879 | 29.452
43 | -0.073312 | -0.01854 | 0.073339 | 0.018557 | 2.6978e-05 | 1.7193e-05 | 0.11129 | 0.11129 | 0.11129 | 0.98075 | -0.36869 | 0.98114 | -0.36102 | 30.5744
44 | 0.069149 | 0.017496 | -0.069146 | -0.017494 | 2.5881e-06 | 1.6485e-06 | 0.10497 | 0.10497 | 0.10497 | 0.98074 | -0.36879 | 0.9807 | -0.36957 | 28.8392
45 | -0.090242 | -0.022796 | 0.09034 | 0.022858 | 9.7768e-05 | 6.2396e-05 | 0.13693 | 0.13693 | 0.13693 | 0.98114 | -0.36102 | 0.9823 | -0.33844 | 37.6172
46 | 0.016903 | 0.0042391 | -0.016898 | -0.0042363 | 4.8508e-06 | 2.856e-06 | 0.025636 | 0.025636 | 0.025636 | 0.98114 | -0.36102 | 0.98083 | -0.36704 | 7.0428
47 | 0.067675 | 0.017126 | -0.067674 | -0.017125 | 1.1701e-06 | 7.4511e-07 | 0.10274 | 0.10274 | 0.10274 | 0.9807 | -0.36957 | 0.98068 | -0.36993 | 28.2259
48 | -0.095156 | -0.024066 | 0.095273 | 0.02414 | 0.00011673 | 7.4515e-05 | 0.14422 | 0.14422 | 0.14422 | 0.9823 | -0.33844 | 0.98362 | -0.31291 | 39.6217
49 | 0.013626 | 0.0034164 | -0.013624 | -0.0034151 | 2.3518e-06 | 1.32e-06 | 0.020673 | 0.020673 | 0.020673 | 0.98083 | -0.36704 | 0.98065 | -0.37067 | 5.6794
50 | 0.066446 | 0.016817 | -0.066445 | -0.016817 | 1.1634e-06 | 7.4073e-07 | 0.10088 | 0.10088 | 0.10088 | 0.98068 | -0.36993 | 0.98067 | -0.3703 | 27.7141
51 | -0.099949 | -0.025312 | 0.10008 | 0.025393 | 0.00012693 | 8.1049e-05 | 0.1513 | 0.1513 | 0.1513 | 0.98362 | -0.31291 | 0.98498 | -0.2865 | 41.5649
52 | 0.012198 | 0.0030576 | -0.012196 | -0.0030565 | 1.977e-06 | 1.0712e-06 | 0.018508 | 0.018509 | 0.018509 | 0.98065 | -0.37067 | 0.98048 | -0.37407 | 5.0848
53 | 0.064974 | 0.016448 | -0.064894 | -0.016397 | 7.9508e-05 | 5.0611e-05 | 0.098647 | 0.098648 | 0.098648 | 0.98067 | -0.3703 | 0.97935 | -0.39582 | 27.101
54 | -0.1014 | -0.025725 | 0.10141 | 0.025732 | 1.1458e-05 | 7.3169e-06 | 0.1533 | 0.1533 | 0.1533 | 0.98498 | -0.2865 | 0.9851 | -0.28415 | 42.1146
55 | 0.061576 | 0.015565 | -0.061458 | -0.015491 | 0.00011776 | 7.4918e-05 | 0.093605 | 0.093605 | 0.093605 | 0.97935 | -0.39582 | 0.97731 | -0.43579 | 25.7156
56 | -0.10556 | -0.026839 | 0.10559 | 0.026856 | 2.6325e-05 | 1.6531e-05 | 0.15949 | 0.15949 | 0.15949 | 0.98573 | -0.27192 | 0.986 | -0.26675 | 14.605
57 | 0.10518 | 0.026743 | -0.10515 | -0.026723 | 3.265e-05 | 2.0501e-05 | 0.15891 | 0.15891 | 0.15891 | 0.98573 | -0.27192 | 0.9854 | -0.27837 | 14.5522
58 | -0.10881 | -0.027664 | 0.10882 | 0.027666 | 3.3879e-06 | 2.1299e-06 | 0.16435 | 0.16435 | 0.16435 | 0.986 | -0.26675 | 0.98604 | -0.2661 | 15.0508
59 | 0.10386 | 0.026402 | -0.1038 | -0.026361 | 6.4084e-05 | 4.0219e-05 | 0.15698 | 0.15698 | 0.15698 | 0.9854 | -0.27837 | 0.98474 | -0.29119 | 14.3751
60 | -0.11339 | -0.028814 | 0.1135 | 0.028881 | 0.00010658 | 6.7099e-05 | 0.17126 | 0.17126 | 0.17126 | 0.98604 | -0.2661 | 0.98705 | -0.2466 | 15.6835
61 | 0.10201 | 0.025914 | -0.10201 | -0.025909 | 6.9022e-06 | 4.3289e-06 | 0.15427 | 0.15427 | 0.15427 | 0.98474 | -0.29119 | 0.98466 | -0.29259 | 14.1277
62 | -0.11497 | -0.029248 | 0.11503 | 0.029289 | 6.4452e-05 | 4.0592e-05 | 0.17347 | 0.17347 | 0.17347 | 0.98705 | -0.2466 | 0.98765 | -0.23497 | 15.8858
63 | 0.10144 | 0.025767 | -0.1014 | -0.025744 | 3.8007e-05 | 2.3832e-05 | 0.15342 | 0.15342 | 0.15342 | 0.98466 | -0.29259 | 0.98426 | -0.30038 | 14.0494
64 | 0.00056655 | 0.00014172 | -0.00056654 | -0.00014199 | 5.9171e-09 | -2.7005e-07 | 0.00085607 | 0.00085616 | 0.00085616 | 0.98466 | -0.29259 | 0.98465 | -0.29281 | 0.23521
65 | -0.1197 | -0.030458 | 0.1198 | 0.030521 | 0.00010041 | 6.3318e-05 | 0.1805 | 0.1805 | 0.1805 | 0.98765 | -0.23497 | 0.98856 | -0.21758 | 16.5295
66 | 0.0046656 | 0.0011692 | -0.0046656 | -0.0011692 | 1.7052e-08 | -8.6387e-10 | 0.0070293 | 0.0070293 | 0.0070293 | 0.98765 | -0.23497 | 0.98765 | -0.23505 | 1.9311
67 | 0.1011 | 0.025667 | -0.10108 | -0.025658 | 1.5742e-05 | 9.8695e-06 | 0.15296 | 0.15296 | 0.15296 | 0.98426 | -0.30038 | 0.98409 | -0.30362 | 14.0073
68 | -0.12195 | -0.03106 | 0.12204 | 0.031119 | 9.3879e-05 | 5.9226e-05 | 0.18374 | 0.18374 | 0.18374 | 0.98856 | -0.21758 | 0.98939 | -0.20164 | 16.8257
69 | 0.0022248 | 0.00055745 | -0.0022248 | -0.00055758 | 5.4121e-08 | -1.2974e-07 | 0.0033519 | 0.003352 | 0.003352 | 0.98765 | -0.23505 | 0.98762 | -0.23556 | 0.92088
70 | 0.099984 | 0.025382 | -0.09994 | -0.025355 | 4.4226e-05 | 2.7716e-05 | 0.1513 | 0.1513 | 0.1513 | 0.98409 | -0.30362 | 0.98362 | -0.31281 | 13.8553
71 | 0.012419 | 0.0031127 | -0.012417 | -0.0031113 | 2.5721e-06 | 1.4076e-06 | 0.018945 | 0.018945 | 0.018945 | 0.97546 | -0.47203 | 0.97524 | -0.47638 | 5.2046
72 | -0.014399 | -0.003609 | 0.014404 | 0.0036115 | 4.479e-06 | 2.5574e-06 | 0.021965 | 0.021965 | 0.021965 | 0.97546 | -0.47203 | 0.97579 | -0.4655 | 6.0343
73 | 0.0030239 | 0.00075738 | -0.0030237 | -0.00075755 | 1.8026e-07 | -1.6639e-07 | 0.0046137 | 0.0046138 | 0.0046138 | 0.97524 | -0.47638 | 0.97518 | -0.47763 | 1.2675
74 | 0.0093926 | 0.0023539 | -0.0093911 | -0.0023532 | 1.4774e-06 | 7.062e-07 | 0.014331 | 0.014331 | 0.014331 | 0.97524 | -0.47638 | 0.97508 | -0.47968 | 3.9371
75 | 0.041679 | 0.010501 | -0.041666 | -0.010492 | 1.3193e-05 | 8.3351e-06 | 0.063578 | 0.063578 | 0.063578 | 0.97579 | -0.4655 | 0.97546 | -0.47212 | 17.4665
76 | -0.056083 | -0.014112 | 0.056098 | 0.014122 | 1.4845e-05 | 9.4335e-06 | 0.085543 | 0.085543 | 0.085543 | 0.97579 | -0.4655 | 0.97608 | -0.45996 | 23.5008
77 | 0.0030237 | 0.00075755 | -0.0030236 | -0.00075767 | 1.3022e-07 | -1.2017e-07 | 0.0046138 | 0.0046138 | 0.0046138 | 0.97518 | -0.47763 | 0.97513 | -0.47853 | 1.2675
78 | 0.0070793 | 0.0017738 | -0.0070784 | -0.0017735 | 8.2229e-07 | 2.9194e-07 | 0.010803 | 0.010803 | 0.010803 | 0.97508 | -0.47968 | 0.97495 | -0.48212 | 2.9679
79 | 0.040361 | 0.010165 | -0.040338 | -0.010151 | 2.3105e-05 | 1.4584e-05 | 0.061587 | 0.061587 | 0.061587 | 0.97546 | -0.47212 | 0.97485 | -0.4841 | 16.9195
80 | -0.057609 | -0.0145 | 0.057675 | 0.014543 | 6.665e-05 | 4.2368e-05 | 0.087846 | 0.087846 | 0.087846 | 0.97608 | -0.45996 | 0.97731 | -0.43579 | 24.1335
81 | 0.0014259 | 0.00035725 | -0.0014259 | -0.00035736 | 1.7317e-08 | -1.106e-07 | 0.0021758 | 0.0021759 | 0.0021759 | 0.97513 | -0.47853 | 0.97512 | -0.47879 | 0.59777
82 | 0.0055358 | 0.0013869 | -0.005535 | -0.0013868 | 8.1317e-07 | 1.4167e-07 | 0.0084488 | 0.0084489 | 0.0084489 | 0.97495 | -0.48212 | 0.9748 | -0.4852 | 2.3211
83 | 0.038922 | 0.0097957 | -0.038898 | -0.009781 | 2.3313e-05 | 1.4701e-05 | 0.059425 | 0.059425 | 0.059425 | 0.97485 | -0.4841 | 0.97421 | -0.49664 | 16.3256
84 | 0.0037825 | 0.00094786 | -0.0037823 | -0.00094794 | 1.9973e-07 | -7.3385e-08 | 0.0057591 | 0.0057591 | 0.0057591 | 0.97731 | -0.43579 | 0.97725 | -0.4369 | 1.5822
85 | 0.0035791 | 0.00089657 | -0.0035789 | -0.00089667 | 2.1064e-07 | -9.9781e-08 | 0.0054633 | 0.0054633 | 0.0054633 | 0.9748 | -0.4852 | 0.97473 | -0.48644 | 1.5009
86 | 0.03738 | 0.0094005 | -0.037377 | -0.0093985 | 3.062e-06 | 1.9285e-06 | 0.057106 | 0.057106 | 0.057106 | 0.97421 | -0.49664 | 0.97412 | -0.49836 | 15.6885
87 | 0.002043 | 0.00051175 | -0.0020429 | -0.000512 | 8.9293e-08 | -2.4798e-07 | 0.0031187 | 0.0031188 | 0.0031188 | 0.97473 | -0.48644 | 0.97469 | -0.48735 | 0.85682
88 | 0.03583 | 0.0090109 | -0.035809 | -0.0089973 | 2.1703e-05 | 1.3649e-05 | 0.054743 | 0.054744 | 0.054744 | 0.97412 | -0.49836 | 0.97348 | -0.51104 | 15.0394
89 | -0.028834 | -0.0072369 | 0.028837 | 0.0072381 | 2.0329e-06 | 1.2665e-06 | 0.044129 | 0.044129 | 0.044129 | 0.97236 | -0.53308 | 0.97244 | -0.5316 | 12.1235
90 | -0.030571 | -0.0076728 | 0.030579 | 0.0076779 | 8.1895e-06 | 5.1174e-06 | 0.046783 | 0.046783 | 0.046783 | 0.97244 | -0.5316 | 0.97272 | -0.52599 | 12.8525
91 | -0.032362 | -0.0081247 | 0.032383 | 0.0081381 | 2.143e-05 | 1.3426e-05 | 0.04951 | 0.04951 | 0.04951 | 0.97272 | -0.52599 | 0.97342 | -0.51211 | 13.6017
92 | 0.0030996 | 0.0007764 | -0.0030996 | -0.00077643 | 4.1739e-08 | -3.4422e-08 | 0.0047477 | 0.0047477 | 0.0047477 | 0.97145 | -0.55109 | 0.97144 | -0.55137 | 1.3043
93 | -0.034279 | -0.0086133 | 0.034281 | 0.0086144 | 1.7499e-06 | 1.0988e-06 | 0.052408 | 0.052408 | 0.052408 | 0.97342 | -0.51211 | 0.97348 | -0.51104 | 14.3979
94 | 0.0030996 | 0.00077643 | -0.0030992 | -0.00077674 | 3.6981e-07 | -3.0488e-07 | 0.0047477 | 0.0047479 | 0.0047479 | 0.97144 | -0.55137 | 0.97131 | -0.55388 | 1.3044
95 | -0.041623 | -0.010463 | 0.041634 | 0.01047 | 1.1695e-05 | 7.3811e-06 | 0.062348 | 0.062348 | 0.062348 | 0.99355 | -0.12318 | 0.99385 | -0.1173 | 17.1287
96 | 0.040199 | 0.010106 | -0.040124 | -0.010059 | 7.504e-05 | 4.7313e-05 | 0.060216 | 0.060217 | 0.060217 | 0.99355 | -0.12318 | 0.99152 | -0.16235 | 16.543
97 | -0.043583 | -0.010959 | 0.043611 | 0.010976 | 2.7853e-05 | 1.76e-05 | 0.065266 | 0.065266 | 0.065266 | 0.99385 | -0.1173 | 0.99455 | -0.10392 | 17.9302
98 | 0.021162 | 0.0053065 | -0.021154 | -0.0053017 | 7.8768e-06 | 4.7727e-06 | 0.03176 | 0.03176 | 0.03176 | 0.99152 | -0.16235 | 0.99112 | -0.17016 | 8.7252
99 | -0.043611 | -0.010976 | 0.043627 | 0.010986 | 1.5632e-05 | 9.8773e-06 | 0.065266 | 0.065266 | 0.065266 | 0.99455 | -0.10392 | 0.99494 | -0.096427 | 17.9302
100 | -0.043627 | -0.010986 | 0.043651 | 0.011002 | 2.4664e-05 | 1.5584e-05 | 0.065266 | 0.065266 | 0.065266 | 0.99494 | -0.096427 | 0.99555 | -0.08461 | 17.9302
101 | -0.045077 | -0.011359 | 0.045123 | 0.011388 | 4.5598e-05 | 2.8834e-05 | 0.067397 | 0.067397 | 0.067397 | 0.99555 | -0.08461 | 0.99665 | -0.063488 | 18.5157
102 | -0.024107 | -0.0060417 | 0.024144 | 0.0060648 | 3.7513e-05 | 2.3102e-05 | 0.036964 | 0.036963 | 0.036964 | 0.97044 | -0.57072 | 0.97209 | -0.53811 | 10.1549
103 | 0.019367 | 0.0048622 | -0.01935 | -0.0048522 | 1.6631e-05 | 1.0019e-05 | 0.029648 | 0.029649 | 0.029649 | 0.97209 | -0.53811 | 0.97118 | -0.55613 | 8.1452
104 | -0.043511 | -0.010927 | 0.043592 | 0.010979 | 8.1494e-05 | 5.1548e-05 | 0.066612 | 0.066612 | 0.066612 | 0.97209 | -0.53811 | 0.97408 | -0.49893 | 18.3
105 | 0.01935 | 0.0048522 | -0.019343 | -0.0048477 | 7.4432e-06 | 4.4843e-06 | 0.029649 | 0.029649 | 0.029649 | 0.97118 | -0.55613 | 0.97077 | -0.5642 | 8.1452
106 | -0.043592 | -0.010979 | 0.043615 | 0.010993 | 2.2365e-05 | 1.4146e-05 | 0.066612 | 0.066612 | 0.066612 | 0.97408 | -0.49893 | 0.97462 | -0.48821 | 18.2999
107 | -0.014073 | -0.0035295 | 0.014077 | 0.0035316 | 3.606e-06 | 2.0315e-06 | 0.021155 | 0.021155 | 0.021155 | 0.98992 | -0.19165 | 0.9902 | -0.18627 | 5.8118
108 | 0.014073 | 0.0035295 | -0.014068 | -0.0035265 | 5.422e-06 | 3.0549e-06 | 0.021155 | 0.021155 | 0.021155 | 0.98992 | -0.19165 | 0.98951 | -0.19974 | 5.8119
109 | -0.021195 | -0.0053157 | 0.021199 | 0.0053177 | 3.354e-06 | 2.0331e-06 | 0.031853 | 0.031852 | 0.031853 | 0.9902 | -0.18627 | 0.99037 | -0.18296 | 8.7507
110 | 0.0094634 | 0.0023725 | -0.0094599 | -0.0023709 | 3.4926e-06 | 1.6448e-06 | 0.014231 | 0.014231 | 0.014231 | 0.98951 | -0.19974 | 0.98911 | -0.20748 | 3.9097
111 | -0.047539 | -0.011994 | 0.047545 | 0.011997 | 5.0958e-06 | 3.2262e-06 | 0.071005 | 0.071005 | 0.071005 | 0.99665 | -0.063488 | 0.99677 | -0.06125 | 19.5069
112 | 0.0051133 | 0.0012813 | -0.0051129 | -0.0012813 | 3.5337e-07 | 1.3776e-08 | 0.0076189 | 0.007619 | 0.007619 | 0.99865 | -0.025977 | 0.99857 | -0.027427 | 2.0931
113 | 0.0051129 | 0.0012813 | -0.0051124 | -0.0012813 | 5.2007e-07 | 2.034e-08 | 0.007619 | 0.0076191 | 0.0076191 | 0.99857 | -0.027427 | 0.99846 | -0.029563 | 2.0931
114 | 0.0051124 | 0.0012813 | -0.0051123 | -0.0012813 | 1.5092e-07 | 5.9172e-09 | 0.0076191 | 0.0076191 | 0.0076191 | 0.99846 | -0.029563 | 0.99843 | -0.030182 | 2.0932
115 | 0.27791 | 0.071155 | -0.27753 | -0.070908 | 0.00038657 | 0.00024671 | 0.41641 | 0.41641 | 0.41641 | 0.99438 | -0.10623 | 0.99287 | -0.13499 | 38.1328
116 | 0.27202 | 0.069527 | -0.27153 | -0.069218 | 0.00048499 | 0.00030949 | 0.40815 | 0.40815 | 0.40815 | 0.99287 | -0.13499 | 0.99094 | -0.17192 | 37.3768
117 | 0.023937 | 0.0060085 | -0.023924 | -0.0060008 | 1.2588e-05 | 7.7217e-06 | 0.035947 | 0.035947 | 0.035947 | 0.99094 | -0.17192 | 0.99037 | -0.18296 | 9.8757
118 | 0.2476 | 0.063209 | -0.24751 | -0.063154 | 8.695e-05 | 5.5454e-05 | 0.37221 | 0.37221 | 0.37221 | 0.99094 | -0.17192 | 0.99056 | -0.17919 | 34.0849
119 | -0.12368 | -0.031529 | 0.12381 | 0.031613 | 0.00013414 | 8.4655e-05 | 0.18619 | 0.18619 | 0.18619 | 0.98939 | -0.20164 | 0.99056 | -0.17919 | 17.0508
120 | 0.1237 | 0.031541 | -0.12364 | -0.031504 | 5.8392e-05 | 3.685e-05 | 0.18601 | 0.18601 | 0.18601 | 0.99056 | -0.17919 | 0.99005 | -0.18898 | 17.0342
121 | 0.12231 | 0.031171 | -0.12213 | -0.031057 | 0.00017884 | 0.00011373 | 0.18402 | 0.18402 | 0.18402 | 0.99005 | -0.18898 | 0.98847 | -0.21932 | 25.2769
122 | -0.052802 | -0.013335 | 0.052843 | 0.013359 | 4.086e-05 | 2.4248e-05 | 0.080423 | 0.080422 | 0.080423 | 0.97741 | -0.43369 | 0.97823 | -0.41755 | 7.3647
123 | 0.044214 | 0.011183 | -0.044195 | -0.011172 | 1.8439e-05 | 1.0579e-05 | 0.067348 | 0.067349 | 0.067349 | 0.97741 | -0.43369 | 0.97696 | -0.44239 | 6.1675
124 | 0.044195 | 0.011172 | -0.044184 | -0.011166 | 1.1098e-05 | 6.3678e-06 | 0.067349 | 0.067349 | 0.067349 | 0.97696 | -0.44239 | 0.97669 | -0.44762 | 6.1675
125 | 0.0437 | 0.011044 | -0.043615 | -0.010993 | 8.4862e-05 | 5.1764e-05 | 0.066611 | 0.066612 | 0.066612 | 0.97669 | -0.44762 | 0.97462 | -0.48821 | 9.1499
126 | -0.0027438 | -0.00068767 | 0.0027442 | 0.00068719 | 3.7817e-07 | -4.7828e-07 | 0.0041833 | 0.004183 | 0.0041833 | 0.97599 | -0.46154 | 0.97614 | -0.45865 | 1.1493
127 | -0.019061 | -0.0047867 | 0.019096 | 0.0048077 | 3.4944e-05 | 2.0982e-05 | 0.02906 | 0.02906 | 0.02906 | 0.97614 | -0.45865 | 0.97809 | -0.4203 | 7.9836
128 | 0.00032937 | 8.2224e-05 | -0.00032937 | -8.2353e-05 | 9.6398e-10 | -1.2984e-07 | 0.00049912 | 0.00049916 | 0.00049916 | 0.98172 | -0.34961 | 0.98172 | -0.34967 | 0.13713
129 | -0.095779 | -0.024247 | 0.095821 | 0.024274 | 4.2233e-05 | 2.6421e-05 | 0.14526 | 0.14526 | 0.14526 | 0.98172 | -0.34961 | 0.98219 | -0.34043 | 13.3023
130 | 0.00032937 | 8.2353e-05 | -0.00032937 | -8.2547e-05 | 1.4353e-09 | -1.9328e-07 | 0.00049916 | 0.00049923 | 0.00049923 | 0.98172 | -0.34967 | 0.98171 | -0.34976 | 0.13715
131 | -0.09702 | -0.024574 | 0.097114 | 0.024633 | 9.4488e-05 | 5.9144e-05 | 0.14708 | 0.14708 | 0.14708 | 0.98219 | -0.34043 | 0.98324 | -0.32017 | 13.4686
132 | -0.098615 | -0.025009 | 0.09865 | 0.025031 | 3.489e-05 | 2.1853e-05 | 0.14935 | 0.14935 | 0.14935 | 0.98324 | -0.32017 | 0.98362 | -0.31281 | 13.6766
133 | -0.1028 | -0.02608 | 0.10296 | 0.026183 | 0.00016122 | 0.00010295 | 0.15539 | 0.15539 | 0.15539 | 0.9851 | -0.28415 | 0.98679 | -0.25159 | 42.6902
134 | 0.12125 | 0.030836 | -0.12124 | -0.030831 | 8.0545e-06 | 5.1219e-06 | 0.18269 | 0.18269 | 0.18269 | 0.98847 | -0.21932 | 0.9884 | -0.2207 | 25.0946
135 | 0.12023 | 0.030577 | -0.12017 | -0.030541 | 5.5761e-05 | 3.5455e-05 | 0.18116 | 0.18116 | 0.18116 | 0.9884 | -0.2207 | 0.9879 | -0.23033 | 24.885
136 | 0.007928 | 0.0019868 | -0.0079266 | -0.0019862 | 1.4029e-06 | 5.6201e-07 | 0.011941 | 0.011942 | 0.011942 | 0.9879 | -0.23033 | 0.98771 | -0.23405 | 3.2807
137 | 0.11225 | 0.028555 | -0.11213 | -0.028481 | 0.00011486 | 7.3376e-05 | 0.16922 | 0.16922 | 0.16922 | 0.9879 | -0.23033 | 0.98679 | -0.25159 | 46.4893
138 | 0.0013867 | 0.00034733 | -0.0013867 | -0.00034753 | 2.7753e-08 | -1.9913e-07 | 0.0020894 | 0.0020894 | 0.0020894 | 0.98755 | -0.23716 | 0.98752 | -0.23758 | 0.57402
139 | -0.0026258 | -0.00065789 | 0.0026259 | 0.00065783 | 3.5379e-08 | -5.4472e-08 | 0.0039565 | 0.0039564 | 0.0039565 | 0.98755 | -0.23716 | 0.98756 | -0.23688 | 1.0869
140 | -0.0040568 | -0.0010165 | 0.0040569 | 0.0010164 | 1.7358e-07 | -4.7433e-08 | 0.0061125 | 0.0061124 | 0.0061125 | 0.98756 | -0.23688 | 0.98761 | -0.23598 | 1.6793
141 | -0.0053458 | -0.0013394 | 0.0053459 | 0.0013394 | 9.6113e-08 | 1.0956e-08 | 0.0080543 | 0.0080543 | 0.0080543 | 0.98761 | -0.23598 | 0.98763 | -0.2356 | 2.2127
142 | -0.0064161 | -0.0016076 | 0.0064165 | 0.0016078 | 4.7477e-07 | 1.3046e-07 | 0.0096667 | 0.0096666 | 0.0096667 | 0.98763 | -0.2356 | 0.98771 | -0.23405 | 2.6557

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51913 | 0.13223

## res_load
| p_mw | q_mvar
0 | 0.0019985 | 0.00050086
1 | 0.025515 | 0.0063946
2 | 0.054919 | 0.013764
3 | 0.0031012 | 0.00077722
4 | 0.0028469 | 0.00071349
5 | 0.062096 | 0.015563
6 | 0.004724 | 0.001184
7 | 0.0011509 | 0.00028843
8 | 0.0093371 | 0.0023401
9 | 0.0011704 | 0.00029333
10 | 0.0013451 | 0.00033712
11 | 0.0015981 | 0.00040052
12 | 0.0096721 | 0.0024241
13 | 0.0039779 | 0.00099696
14 | 0.00017465 | 4.377e-05
15 | 0.00057755 | 0.00014475
16 | 0.005732 | 0.0014366
17 | 0.00080723 | 0.00020231
18 | 0.0048755 | 0.0012219
19 | 0.00061908 | 0.00015515
20 | 0.0054397 | 0.0013633
21 | 0.0011982 | 0.0003003
22 | 0.012608 | 0.0031598
23 | 0.0030822 | 0.00077248
24 | 0.002693 | 0.00067492
25 | 0.00147 | 0.00036842
26 | 0.0014714 | 0.00036876
27 | 0.0048166 | 0.0012072
28 | 0.0032713 | 0.00081987
29 | 0.0012278 | 0.00030771
30 | 0.0046757 | 0.0011718
31 | 0.0014265 | 0.00035751
32 | 0.0014709 | 0.00036865
33 | 0.0013246 | 0.00033196
34 | 0.012196 | 0.0030565
35 | 0.0033189 | 0.00083181
36 | 0.00038251 | 9.5866e-05
37 | 0.0032254 | 0.00080837
38 | 0.0012809 | 0.00032103
39 | 0.0045784 | 0.0011475
40 | 0.0017873 | 0.00044794
41 | 0.001466 | 0.00036742
42 | 0.00030392 | 7.617e-05
43 | 0.00056654 | 0.00014199
44 | 0.0021492 | 0.00053864
45 | 0.0024408 | 0.00061171
46 | 0.0010979 | 0.00027515
47 | 0.0019799 | 0.00049622
48 | 0.0023119 | 0.00057941
49 | 0.0013051 | 0.00032709
50 | 0.0015108 | 0.00037865
51 | 0.0015977 | 0.00040042
52 | 0.0015427 | 0.00038663
53 | 0.0014165 | 0.000355
54 | 0.0014259 | 0.00035736
55 | 0.0019559 | 0.00049019
56 | 0.0015184 | 0.00038054
57 | 0.0037823 | 0.00094794
58 | 0.0015359 | 0.00038492
59 | 0.0015466 | 0.00038762
60 | 0.0036599 | 0.00091725
61 | 0.0017343 | 0.00043465
62 | 0.0017827 | 0.00044679
63 | 0.0018152 | 0.00045494
64 | 0.001896 | 0.00047517
65 | 0.0015277 | 0.00038287
66 | 0.0030992 | 0.00077674
67 | 0.0014235 | 0.00035676
68 | 0.0019488 | 0.00048842
69 | 0.018962 | 0.0047523
70 | 0.021154 | 0.0053017
71 | 0.0014259 | 0.00035736
72 | 0.024107 | 0.0060417
73 | 0.019343 | 0.0048477
74 | 0.0071187 | 0.0017841
75 | 0.0046043 | 0.001154
76 | 0.0024167 | 0.00060569
77 | 0.017732 | 0.0044441
78 | 0.0018087 | 0.00045329
79 | 0.00091758 | 0.00022997
80 | 0.0051123 | 0.0012813
81 | 0.0055091 | 0.0013807
82 | 0.0020429 | 0.000512
83 | 0.0016343 | 0.00040961
84 | 0.0022248 | 0.00055758
85 | 0.0013292 | 0.00033314
86 | 0.0085879 | 0.0021523
87 | 0.0045509 | 0.0011406
88 | 0.00048473 | 0.00012148
89 | 0.0027438 | 0.00068767
90 | 0.00059511 | 0.00014915
91 | 0.0094599 | 0.0023709
92 | 0.0027254 | 0.00068306
93 | 0.0011991 | 0.00030052
94 | 0.00032937 | 8.2547e-05
95 | 0.0015005 | 0.00037607
96 | 0.0012903 | 0.00032339
97 | 0.001387 | 0.00034762
98 | 0.0008814 | 0.0002209
99 | 0.0010139 | 0.00025411
100 | 0.0012391 | 0.00031056
101 | 0.0013867 | 0.00034753
102 | 0.0014309 | 0.00035862
103 | 0.0012889 | 0.00032302
104 | 0.0010702 | 0.00026821
105 | 0.0015101 | 0.00037846
106 | 0.0091709 | 0.0022984

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1