## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2601-23_1_3_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_2601-23_1_3_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_2601-23_1_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2601-23_1_3_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_2601-23_1_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_2601-23_1_3_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_2601-23_1_3_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_2601-23_1_3_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_2601-23_1_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2601-23_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2601-23_1_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2601-23_1_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_2601-23_1_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_2601-23_1_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_2601-23_1_3_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_2601-23_1_3_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_2601-23_1_3_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_2601-23_1_3_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_2601-23_1_3_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_2601-23_1_3_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_2601-23_1_3_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_2601-23_1_3_node_109 | 0.4 | n |  | TRUE
22 | bus_LV_2601-23_1_3_node_74 | 0.4 | n |  | TRUE
23 | bus_LV_2601-23_1_3_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_2601-23_1_3_node_111 | 0.4 | n |  | TRUE
25 | bus_LV_2601-23_1_3_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_2601-23_1_3_node_60 | 0.4 | n |  | TRUE
27 | bus_LV_2601-23_1_3_node_85 | 0.4 | n |  | TRUE
28 | bus_LV_2601-23_1_3_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_2601-23_1_3_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_2601-23_1_3_node_112 | 0.4 | n |  | TRUE
31 | bus_MV_395_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2601-23_1_3_load_6 | 0 | 0.0043497 | 0.0010901 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2601-23_1_3_load_7 | 1 | 0.0060841 | 0.0015248 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2601-23_1_3_load_9 | 3 | 0.0064071 | 0.0016058 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2601-23_1_3_load_10 | 4 | 0.0061514 | 0.0015417 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2601-23_1_3_load_11 | 5 | 0.034828 | 0.0087287 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2601-23_1_3_load_31 | 6 | 0.0025466 | 0.00063823 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2601-23_1_3_load_29 | 7 | 0.0029627 | 0.00074253 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2601-23_1_3_load_12 | 9 | 0.034025 | 0.0085275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2601-23_1_3_load_13 | 10 | 0.014821 | 0.0037145 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2601-23_1_3_load_17 | 13 | 0.031521 | 0.0079 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2601-23_1_3_load_62 | 14 | 0.048001 | 0.01203 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2601-23_1_3_load_30 | 15 | 0.0011551 | 0.00028951 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2601-23_1_3_load_57 | 16 | 0.0053255 | 0.0013347 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2601-23_1_3_load_37 | 18 | 0.0064705 | 0.0016217 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2601-23_1_3_load_109 | 21 | 0.0034447 | 0.00086332 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2601-23_1_3_load_111 | 24 | 0.0024703 | 0.00061912 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2601-23_1_3_load_59 | 25 | 0.044821 | 0.011233 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2601-23_1_3_load_86 | 28 | 0.0048766 | 0.0012222 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2601-23_1_3_load_108 | 29 | 0.0016968 | 0.00042525 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2601-23_1_3_load_112 | 30 | 0.0093161 | 0.0023348 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2601-23_1_3_line_0 |  | 0 | 1 | 0.0019753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2601-23_1_3_line_1 |  | 0 | 2 | 0.0196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2601-23_1_3_line_2 |  | 1 | 3 | 0.052427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2601-23_1_3_line_3 |  | 2 | 4 | 0.0032901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2601-23_1_3_line_4 |  | 2 | 5 | 0.047375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2601-23_1_3_line_5 |  | 3 | 6 | 0.0070979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2601-23_1_3_line_6 |  | 4 | 7 | 0.025786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2601-23_1_3_line_7 |  | 5 | 8 | 0.0273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2601-23_1_3_line_8 |  | 6 | 17 | 0.026831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2601-23_1_3_line_9 |  | 7 | 15 | 0.01863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2601-23_1_3_line_10 |  | 8 | 10 | 0.016608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2601-23_1_3_line_11 |  | 9 | 10 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2601-23_1_3_line_12 |  | 9 | 11 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2601-23_1_3_line_13 |  | 11 | 12 | 0.008247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2601-23_1_3_line_14 |  | 11 | 13 | 0.0085286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2601-23_1_3_line_15 |  | 12 | 14 | 0.021934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2601-23_1_3_line_16 |  | 14 | 26 | 0.022162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2601-23_1_3_line_17 |  | 15 | 16 | 0.0061876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2601-23_1_3_line_18 |  | 16 | 22 | 0.02326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2601-23_1_3_line_19 |  | 17 | 18 | 0.051582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2601-23_1_3_line_20 |  | 18 | 19 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2601-23_1_3_line_21 |  | 19 | 23 | 0.026366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2601-23_1_3_line_22 |  | 20 | 21 | 0.076462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2601-23_1_3_line_23 |  | 20 | 22 | 0.026184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2601-23_1_3_line_24 |  | 22 | 27 | 0.066364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2601-23_1_3_line_25 |  | 22 | 28 | 0.053217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2601-23_1_3_line_26 |  | 23 | 24 | 0.020711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2601-23_1_3_line_27 |  | 25 | 26 | 0.0083346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2601-23_1_3_line_28 |  | 27 | 29 | 0.010448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2601-23_1_3_line_29 |  | 28 | 30 | 0.016252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2601-23_1_3_trafo_62 | 0.63 MVA 20/0.4 kV | 31 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2607015.2295 | 1228908.2359 | 2607015.7711 | 1228906.3363
1 | 2607009.8554 | 1228927.0848 | 2607015.2295 | 1228908.2359
2 | 2607015.7711 | 1228906.3363 | 2607027.0015 | 1228866.947 | 2607024.8961 | 1228855.6739
3 | 2607009.8554 | 1228927.0848 | 2607013.0109 | 1228928.0163
4 | 2607009.8554 | 1228927.0848 | 2606964.1183 | 1228914.7367
5 | 2607024.8961 | 1228855.6739 | 2607023.5931 | 1228848.6966
6 | 2607037.7416 | 1228935.317 | 2607013.0109 | 1228928.0163
7 | 2606939.1847 | 1228904.7562 | 2606942.6738 | 1228907.6286 | 2606945.7092 | 1228909.7667 | 2606964.1183 | 1228914.7367
8 | 2607018.6673 | 1228822.3219 | 2607023.5931 | 1228848.6966
9 | 2607037.7416 | 1228935.317 | 2607055.6095 | 1228940.5917
10 | 2606939.1847 | 1228904.7562 | 2606939.9784 | 1228899.7652 | 2606940.2049 | 1228893.862 | 2606938.6481 | 1228888.4343
11 | 2606932.9592 | 1228868.6152 | 2606933.9498 | 1228872.0529 | 2606938.6481 | 1228888.4343
12 | 2606928.185 | 1228852.0455 | 2606932.9592 | 1228868.6152
13 | 2606928.185 | 1228852.0455 | 2606936.044 | 1228849.4753
14 | 2606928.185 | 1228852.0455 | 2606925.8213 | 1228843.8511
15 | 2606936.044 | 1228849.4753 | 2606956.893 | 1228842.6621
16 | 2606951.3724 | 1228821.1985 | 2606956.893 | 1228842.6621
17 | 2607055.6095 | 1228940.5917 | 2607061.5439 | 1228942.3436
18 | 2607083.8519 | 1228948.929 | 2607061.5439 | 1228942.3436
19 | 2607018.6673 | 1228822.3219 | 2607070.2102 | 1228820.3233
20 | 2607093.2473 | 1228819.43 | 2607070.2102 | 1228820.3233
21 | 2607119.6731 | 1228818.4496 | 2607093.2473 | 1228819.43
22 | 2607107.7935 | 1228959.6859 | 2607092.354 | 1229011.2093 | 2607094.4494 | 1229020.2394 | 2607099.4596 | 1229024.2811 | 2607106.0856 | 1229026.5458
23 | 2607083.8519 | 1228948.929 | 2607107.7935 | 1228959.6859
24 | 2607083.8519 | 1228948.929 | 2607079.0758 | 1228951.9029 | 2607045.9026 | 1229002.8497
25 | 2607083.8519 | 1228948.929 | 2607109.797 | 1228902.4652
26 | 2607120.5046 | 1228839.1406 | 2607119.6731 | 1228818.4496
27 | 2606951.3724 | 1228821.1985 | 2606943.1542 | 1228819.8104
28 | 2607045.9026 | 1229002.8497 | 2607043.3171 | 1229004.77 | 2607042.194 | 1229006.3585 | 2607039.1209 | 1229010.6686
29 | 2607109.797 | 1228902.4652 | 2607118.5799 | 1228916.1396

## bus_geodata
| x | y | coords
0 | 2607015.2295 | 1228908.2359
1 | 2607015.7711 | 1228906.3363
2 | 2607009.8554 | 1228927.0848
3 | 2607024.8961 | 1228855.6739
4 | 2607013.0109 | 1228928.0163
5 | 2606964.1183 | 1228914.7367
6 | 2607023.5931 | 1228848.6966
7 | 2607037.7416 | 1228935.317
8 | 2606939.1847 | 1228904.7562
9 | 2606932.9592 | 1228868.6152
10 | 2606938.6481 | 1228888.4343
11 | 2606928.185 | 1228852.0455
12 | 2606936.044 | 1228849.4753
13 | 2606925.8213 | 1228843.8511
14 | 2606956.893 | 1228842.6621
15 | 2607055.6095 | 1228940.5917
16 | 2607061.5439 | 1228942.3436
17 | 2607018.6673 | 1228822.3219
18 | 2607070.2102 | 1228820.3233
19 | 2607093.2473 | 1228819.43
20 | 2607107.7935 | 1228959.6859
21 | 2607106.0856 | 1229026.5458
22 | 2607083.8519 | 1228948.929
23 | 2607119.6731 | 1228818.4496
24 | 2607120.5046 | 1228839.1406
25 | 2606943.1542 | 1228819.8104
26 | 2606951.3724 | 1228821.1985
27 | 2607045.9026 | 1229002.8497
28 | 2607109.797 | 1228902.4652
29 | 2607039.1209 | 1229010.6686
30 | 2607118.5799 | 1228916.1396
31 | 2606936.044 | 1228849.4753

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98702 | -0.24986 | 0.0043497 | 0.0010901
1 | 0.98697 | -0.25071 | 0.0060841 | 0.0015248
2 | 0.98753 | -0.23993 | 0 | 0
3 | 0.98611 | -0.26751 | 0.0064071 | 0.0016058
4 | 0.98742 | -0.24198 | 0.0061514 | 0.0015417
5 | 0.99028 | -0.1865 | 0.034828 | 0.0087287
6 | 0.98603 | -0.26898 | 0.0025466 | 0.00063823
7 | 0.98674 | -0.25526 | 0.0029627 | 0.00074253
8 | 0.99274 | -0.13902 | 0 | 0
9 | 0.99638 | -0.069277 | 0.034025 | 0.0085275
10 | 0.99424 | -0.11025 | 0.014821 | 0.0037145
11 | 0.99754 | -0.047059 | 0 | 0
12 | 0.99821 | -0.034177 | 0 | 0
13 | 0.99729 | -0.051769 | 0.031521 | 0.0079
14 | 1 | 0 | -0.22638 | -0.05688
15 | 0.9863 | -0.26388 | 0.0011551 | 0.00028951
16 | 0.98616 | -0.26661 | 0.0053255 | 0.0013347
17 | 0.98581 | -0.27328 | 0 | 0
18 | 0.98539 | -0.28156 | 0.0064705 | 0.0016217
19 | 0.98534 | -0.28258 | 0 | 0
20 | 0.98566 | -0.2763 | 0 | 0
21 | 0.98542 | -0.28103 | 0.0034447 | 0.00086332
22 | 0.98574 | -0.27468 | 0 | 0
23 | 0.98528 | -0.28375 | 0 | 0
24 | 0.98523 | -0.28467 | 0.0024703 | 0.00061912
25 | 0.99876 | -0.023854 | 0.044821 | 0.011233
26 | 0.9991 | -0.017329 | 0 | 0
27 | 0.98564 | -0.2767 | 0 | 0
28 | 0.98505 | -0.28824 | 0.0048766 | 0.0012222
29 | 0.98562 | -0.27702 | 0.0016968 | 0.00042525
30 | 0.98491 | -0.29096 | 0.0093161 | 0.0023348
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024001 | 0.0060209 | -0.024 | -0.0060203 | 9.6988e-07 | 5.9548e-07 | 0.036185 | 0.036185 | 0.036185 | 0.98702 | -0.24986 | 0.98697 | -0.25071 | 9.941
1 | -0.02835 | -0.0071111 | 0.028364 | 0.0071194 | 1.3428e-05 | 8.3433e-06 | 0.042743 | 0.042743 | 0.042743 | 0.98702 | -0.24986 | 0.98753 | -0.23993 | 11.7425
2 | 0.017915 | 0.0044955 | -0.017901 | -0.004487 | 1.4345e-05 | 8.5117e-06 | 0.027012 | 0.027013 | 0.027013 | 0.98697 | -0.25071 | 0.98611 | -0.26751 | 7.421
3 | 0.034983 | 0.0087848 | -0.03498 | -0.0087826 | 3.4291e-06 | 2.1525e-06 | 0.05272 | 0.05272 | 0.05272 | 0.98753 | -0.23993 | 0.98742 | -0.24198 | 14.4834
4 | -0.063347 | -0.015904 | 0.063509 | 0.016007 | 0.0001619 | 0.00010301 | 0.095462 | 0.095462 | 0.095462 | 0.98753 | -0.23993 | 0.99028 | -0.1865 | 26.2259
5 | 0.011494 | 0.0028812 | -0.011493 | -0.0028808 | 8.0071e-07 | 4.2191e-07 | 0.017344 | 0.017344 | 0.017344 | 0.98611 | -0.26751 | 0.98603 | -0.26898 | 4.7649
6 | 0.028829 | 0.0072409 | -0.02881 | -0.0072296 | 1.8255e-05 | 1.1354e-05 | 0.04345 | 0.04345 | 0.04345 | 0.98742 | -0.24198 | 0.98674 | -0.25526 | 11.9367
7 | -0.098337 | -0.024736 | 0.09856 | 0.024879 | 0.00022362 | 0.00014277 | 0.14779 | 0.14779 | 0.14779 | 0.99028 | -0.1865 | 0.99274 | -0.13902 | 40.6029
8 | 0.0089466 | 0.0022426 | -0.0089448 | -0.0022417 | 1.8341e-06 | 8.3166e-07 | 0.013501 | 0.013501 | 0.013501 | 0.98603 | -0.26898 | 0.98581 | -0.27328 | 3.7092
9 | 0.025848 | 0.006487 | -0.025837 | -0.0064805 | 1.0616e-05 | 6.5566e-06 | 0.038982 | 0.038982 | 0.038982 | 0.98674 | -0.25526 | 0.9863 | -0.26388 | 10.7093
10 | -0.09856 | -0.024879 | 0.098696 | 0.024965 | 0.00013604 | 8.6849e-05 | 0.14779 | 0.14779 | 0.14779 | 0.99274 | -0.13902 | 0.99424 | -0.11025 | 40.6029
11 | 0.11374 | 0.028823 | -0.11352 | -0.02868 | 0.0002234 | 0.00014271 | 0.16998 | 0.16998 | 0.16998 | 0.99638 | -0.069277 | 0.99424 | -0.11025 | 46.6968
12 | -0.14777 | -0.03735 | 0.14792 | 0.037451 | 0.00015761 | 0.00010042 | 0.22079 | 0.22079 | 0.22079 | 0.99638 | -0.069277 | 0.99754 | -0.047059 | 30.3284
13 | -0.17945 | -0.045355 | 0.17956 | 0.045426 | 0.00011091 | 7.077e-05 | 0.26782 | 0.26782 | 0.26782 | 0.99754 | -0.047059 | 0.99821 | -0.034177 | 36.7887
14 | 0.031528 | 0.0079044 | -0.031521 | -0.0079 | 7.0744e-06 | 4.4163e-06 | 0.047032 | 0.047032 | 0.047032 | 0.99754 | -0.047059 | 0.99729 | -0.051769 | 12.9208
15 | -0.17956 | -0.045426 | 0.17986 | 0.045614 | 0.00029499 | 0.00018822 | 0.26782 | 0.26782 | 0.26782 | 0.99821 | -0.034177 | 1 | 0 | 36.7887
16 | 0.044872 | 0.011266 | -0.044835 | -0.011242 | 3.706e-05 | 2.3428e-05 | 0.066778 | 0.066778 | 0.066778 | 1 | 0 | 0.9991 | -0.017329 | 18.3455
17 | 0.024682 | 0.006191 | -0.024679 | -0.006189 | 3.2177e-06 | 1.9804e-06 | 0.037239 | 0.037239 | 0.037239 | 0.9863 | -0.26388 | 0.98616 | -0.26661 | 10.2305
18 | 0.019353 | 0.0048543 | -0.019346 | -0.0048498 | 7.4389e-06 | 4.4643e-06 | 0.029204 | 0.029204 | 0.029204 | 0.98616 | -0.26661 | 0.98574 | -0.27468 | 8.023
19 | 0.0089448 | 0.0022417 | -0.0089412 | -0.0022401 | 3.5261e-06 | 1.5993e-06 | 0.013501 | 0.013502 | 0.013502 | 0.98581 | -0.27328 | 0.98539 | -0.28156 | 3.7093
20 | 0.0024707 | 0.00061846 | -0.0024706 | -0.00061868 | 1.2033e-07 | -2.1666e-07 | 0.0037307 | 0.0037308 | 0.0037308 | 0.98539 | -0.28156 | 0.98534 | -0.28258 | 1.0249
21 | 0.0024706 | 0.00061868 | -0.0024704 | -0.00061893 | 1.3762e-07 | -2.4774e-07 | 0.0037308 | 0.0037309 | 0.0037309 | 0.98534 | -0.28258 | 0.98528 | -0.28375 | 1.025
22 | 0.0034454 | 0.00086284 | -0.0034447 | -0.00086332 | 7.7575e-07 | -4.7784e-07 | 0.0052012 | 0.0052016 | 0.0052016 | 0.98566 | -0.2763 | 0.98542 | -0.28103 | 1.429
23 | -0.0034454 | -0.00086284 | 0.0034457 | 0.00086267 | 2.6563e-07 | -1.6376e-07 | 0.0052012 | 0.0052011 | 0.0052012 | 0.98566 | -0.2763 | 0.98574 | -0.27468 | 1.4289
24 | 0.001697 | 0.0004244 | -0.0016968 | -0.00042514 | 1.6328e-07 | -7.4141e-07 | 0.0025613 | 0.0025616 | 0.0025616 | 0.98574 | -0.27468 | 0.98564 | -0.2767 | 0.70374
25 | 0.014203 | 0.0035628 | -0.014194 | -0.0035576 | 9.1745e-06 | 5.1938e-06 | 0.021441 | 0.021441 | 0.021441 | 0.98574 | -0.27468 | 0.98505 | -0.28824 | 5.8905
26 | 0.0024704 | 0.00061893 | -0.0024703 | -0.00061912 | 1.0811e-07 | -1.9457e-07 | 0.0037309 | 0.003731 | 0.003731 | 0.98528 | -0.28375 | 0.98523 | -0.28467 | 1.025
27 | -0.044821 | -0.011233 | 0.044835 | 0.011242 | 1.3937e-05 | 8.8108e-06 | 0.066778 | 0.066778 | 0.066778 | 0.99876 | -0.023854 | 0.9991 | -0.017329 | 18.3455
28 | 0.0016968 | 0.00042514 | -0.0016968 | -0.00042525 | 2.571e-08 | -1.167e-07 | 0.0025616 | 0.0025617 | 0.0025617 | 0.98564 | -0.2767 | 0.98562 | -0.27702 | 0.70376
29 | 0.0093173 | 0.0023354 | -0.0093161 | -0.0023348 | 1.2073e-06 | 5.6584e-07 | 0.014075 | 0.014075 | 0.014075 | 0.98505 | -0.28824 | 0.98491 | -0.29096 | 3.8667

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27438 | 0.06891

## res_load
| p_mw | q_mvar
0 | 0.0043497 | 0.0010901
1 | 0.0060841 | 0.0015248
2 | 0.0064071 | 0.0016058
3 | 0.0061514 | 0.0015417
4 | 0.034828 | 0.0087287
5 | 0.0025466 | 0.00063823
6 | 0.0029627 | 0.00074253
7 | 0.034025 | 0.0085275
8 | 0.014821 | 0.0037145
9 | 0.031521 | 0.0079
10 | 0.048001 | 0.01203
11 | 0.0011551 | 0.00028951
12 | 0.0053255 | 0.0013347
13 | 0.0064705 | 0.0016217
14 | 0.0034447 | 0.00086332
15 | 0.0024703 | 0.00061912
16 | 0.044821 | 0.011233
17 | 0.0048766 | 0.0012222
18 | 0.0016968 | 0.00042525
19 | 0.0093161 | 0.0023348

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1