## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2601-26_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2601-26_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2601-26_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2601-26_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2601-26_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2601-26_0_4_node_124 | 0.4 | n |  | TRUE
6 | bus_LV_2601-26_0_4_node_94 | 0.4 | n |  | TRUE
7 | bus_LV_2601-26_0_4_node_91 | 0.4 | n |  | TRUE
8 | bus_LV_2601-26_0_4_node_125 | 0.4 | n |  | TRUE
9 | bus_LV_2601-26_0_4_node_139 | 0.4 | n |  | TRUE
10 | bus_LV_2601-26_0_4_node_71 | 0.4 | n |  | TRUE
11 | bus_LV_2601-26_0_4_node_70 | 0.4 | n |  | TRUE
12 | bus_LV_2601-26_0_4_node_92 | 0.4 | n |  | TRUE
13 | bus_LV_2601-26_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_2601-26_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2601-26_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2601-26_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2601-26_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2601-26_0_4_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_2601-26_0_4_node_68 | 0.4 | n |  | TRUE
20 | bus_LV_2601-26_0_4_node_66 | 0.4 | n |  | TRUE
21 | bus_LV_2601-26_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2601-26_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2601-26_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2601-26_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2601-26_0_4_node_74 | 0.4 | n |  | TRUE
26 | bus_LV_2601-26_0_4_node_152 | 0.4 | n |  | TRUE
27 | bus_LV_2601-26_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2601-26_0_4_node_158 | 0.4 | n |  | TRUE
29 | bus_LV_2601-26_0_4_node_96 | 0.4 | n |  | TRUE
30 | bus_LV_2601-26_0_4_node_75 | 0.4 | n |  | TRUE
31 | bus_LV_2601-26_0_4_node_103 | 0.4 | n |  | TRUE
32 | bus_LV_2601-26_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_2601-26_0_4_node_95 | 0.4 | n |  | TRUE
34 | bus_LV_2601-26_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2601-26_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2601-26_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2601-26_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2601-26_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2601-26_0_4_node_126 | 0.4 | n |  | TRUE
40 | bus_LV_2601-26_0_4_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_2601-26_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_2601-26_0_4_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_2601-26_0_4_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_2601-26_0_4_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_2601-26_0_4_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_2601-26_0_4_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_2601-26_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_2601-26_0_4_node_104 | 0.4 | n |  | TRUE
49 | bus_LV_2601-26_0_4_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_2601-26_0_4_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_2601-26_0_4_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_2601-26_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_2601-26_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_2601-26_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2601-26_0_4_node_69 | 0.4 | n |  | TRUE
56 | bus_LV_2601-26_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_2601-26_0_4_node_129 | 0.4 | n |  | TRUE
58 | bus_LV_2601-26_0_4_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_2601-26_0_4_node_30 | 0.4 | n |  | TRUE
60 | bus_LV_2601-26_0_4_node_31 | 0.4 | n |  | TRUE
61 | bus_LV_2601-26_0_4_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_2601-26_0_4_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_2601-26_0_4_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_2601-26_0_4_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_2601-26_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_2601-26_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2601-26_0_4_node_155 | 0.4 | n |  | TRUE
68 | bus_LV_2601-26_0_4_node_130 | 0.4 | n |  | TRUE
69 | bus_LV_2601-26_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_2601-26_0_4_node_35 | 0.4 | n |  | TRUE
71 | bus_LV_2601-26_0_4_node_36 | 0.4 | n |  | TRUE
72 | bus_LV_2601-26_0_4_node_37 | 0.4 | n |  | TRUE
73 | bus_LV_2601-26_0_4_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_2601-26_0_4_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_2601-26_0_4_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_2601-26_0_4_node_131 | 0.4 | n |  | TRUE
77 | bus_LV_2601-26_0_4_node_138 | 0.4 | n |  | TRUE
78 | bus_LV_2601-26_0_4_node_153 | 0.4 | n |  | TRUE
79 | bus_LV_2601-26_0_4_node_42 | 0.4 | n |  | TRUE
80 | bus_LV_2601-26_0_4_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_2601-26_0_4_node_157 | 0.4 | n |  | TRUE
82 | bus_LV_2601-26_0_4_node_44 | 0.4 | n |  | TRUE
83 | bus_LV_2601-26_0_4_node_45 | 0.4 | n |  | TRUE
84 | bus_LV_2601-26_0_4_node_49 | 0.4 | n |  | TRUE
85 | bus_LV_2601-26_0_4_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_2601-26_0_4_node_145 | 0.4 | n |  | TRUE
87 | bus_LV_2601-26_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_2601-26_0_4_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_2601-26_0_4_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_2601-26_0_4_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_2601-26_0_4_node_63 | 0.4 | n |  | TRUE
92 | bus_LV_2601-26_0_4_node_64 | 0.4 | n |  | TRUE
93 | bus_LV_2601-26_0_4_node_136 | 0.4 | n |  | TRUE
94 | bus_LV_2601-26_0_4_node_134 | 0.4 | n |  | TRUE
95 | bus_LV_2601-26_0_4_node_149 | 0.4 | n |  | TRUE
96 | bus_LV_2601-26_0_4_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_2601-26_0_4_node_67 | 0.4 | n |  | TRUE
98 | bus_LV_2601-26_0_4_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_2601-26_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_2601-26_0_4_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_2601-26_0_4_node_107 | 0.4 | n |  | TRUE
102 | bus_LV_2601-26_0_4_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_2601-26_0_4_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_2601-26_0_4_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_2601-26_0_4_node_128 | 0.4 | n |  | TRUE
106 | bus_LV_2601-26_0_4_node_72 | 0.4 | n |  | TRUE
107 | bus_LV_2601-26_0_4_node_73 | 0.4 | n |  | TRUE
108 | bus_LV_2601-26_0_4_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_2601-26_0_4_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_2601-26_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_2601-26_0_4_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_2601-26_0_4_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2601-26_0_4_node_146 | 0.4 | n |  | TRUE
114 | bus_LV_2601-26_0_4_node_120 | 0.4 | n |  | TRUE
115 | bus_LV_2601-26_0_4_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_2601-26_0_4_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_2601-26_0_4_node_127 | 0.4 | n |  | TRUE
118 | bus_LV_2601-26_0_4_node_87 | 0.4 | n |  | TRUE
119 | bus_LV_2601-26_0_4_node_89 | 0.4 | n |  | TRUE
120 | bus_LV_2601-26_0_4_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_2601-26_0_4_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_2601-26_0_4_node_119 | 0.4 | n |  | TRUE
123 | bus_LV_2601-26_0_4_node_137 | 0.4 | n |  | TRUE
124 | bus_LV_2601-26_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_2601-26_0_4_node_93 | 0.4 | n |  | TRUE
126 | bus_LV_2601-26_0_4_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_2601-26_0_4_node_111 | 0.4 | n |  | TRUE
128 | bus_LV_2601-26_0_4_node_99 | 0.4 | n |  | TRUE
129 | bus_LV_2601-26_0_4_node_100 | 0.4 | n |  | TRUE
130 | bus_LV_2601-26_0_4_node_101 | 0.4 | n |  | TRUE
131 | bus_LV_2601-26_0_4_node_102 | 0.4 | n |  | TRUE
132 | bus_LV_2601-26_0_4_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_2601-26_0_4_node_115 | 0.4 | n |  | TRUE
134 | bus_LV_2601-26_0_4_node_114 | 0.4 | n |  | TRUE
135 | bus_LV_2601-26_0_4_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_2601-26_0_4_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_2601-26_0_4_node_121 | 0.4 | n |  | TRUE
138 | bus_LV_2601-26_0_4_node_122 | 0.4 | n |  | TRUE
139 | bus_LV_2601-26_0_4_node_147 | 0.4 | n |  | TRUE
140 | bus_LV_2601-26_0_4_node_148 | 0.4 | n |  | TRUE
141 | bus_LV_2601-26_0_4_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_2601-26_0_4_node_140 | 0.4 | n |  | TRUE
143 | bus_LV_2601-26_0_4_node_150 | 0.4 | n |  | TRUE
144 | bus_LV_2601-26_0_4_node_143 | 0.4 | n |  | TRUE
145 | bus_LV_2601-26_0_4_node_141 | 0.4 | n |  | TRUE
146 | bus_LV_2601-26_0_4_node_154 | 0.4 | n |  | TRUE
147 | bus_LV_2601-26_0_4_node_132 | 0.4 | n |  | TRUE
148 | bus_LV_2601-26_0_4_node_133 | 0.4 | n |  | TRUE
149 | bus_LV_2601-26_0_4_node_151 | 0.4 | n |  | TRUE
150 | bus_LV_2601-26_0_4_node_142 | 0.4 | n |  | TRUE
151 | bus_LV_2601-26_0_4_node_144 | 0.4 | n |  | TRUE
152 | bus_MV_395_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2601-26_0_4_load_0 | 0 | 0.0042154 | 0.0010565 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2601-26_0_4_load_1 | 1 | 0.0033615 | 0.00084247 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2601-26_0_4_load_2 | 2 | 0.0042724 | 0.0010708 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2601-26_0_4_load_3 | 3 | 0.0045739 | 0.0011463 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2601-26_0_4_load_124 | 5 | 0.0032634 | 0.00081787 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2601-26_0_4_load_94 | 6 | 0.0026209 | 0.00065686 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2601-26_0_4_load_91 | 7 | 0.001675 | 0.0004198 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2601-26_0_4_load_125 | 8 | 0.0030669 | 0.00076863 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2601-26_0_4_load_139 | 9 | 0.0026282 | 0.0006587 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2601-26_0_4_load_71 | 10 | 0.0013672 | 0.00034265 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2601-26_0_4_load_70 | 11 | 0.0016782 | 0.00042059 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2601-26_0_4_load_92 | 12 | 0.001522 | 0.00038144 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2601-26_0_4_load_5 | 13 | 0.0015197 | 0.00038088 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2601-26_0_4_load_6 | 14 | 0.0031518 | 0.00078992 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2601-26_0_4_load_7 | 15 | 0.0016871 | 0.00042284 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2601-26_0_4_load_8 | 16 | 0.0016268 | 0.00040772 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2601-26_0_4_load_9 | 17 | 0.0014193 | 0.0003557 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2601-26_0_4_load_81 | 18 | 0.0014749 | 0.00036965 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2601-26_0_4_load_10 | 21 | 0.0018572 | 0.00046545 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2601-26_0_4_load_14 | 24 | 0.0021721 | 0.00054437 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2601-26_0_4_load_74 | 25 | 0.01993 | 0.0049948 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2601-26_0_4_load_152 | 26 | 0.0033521 | 0.00084011 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2601-26_0_4_load_158 | 28 | 0.0080728 | 0.0020232 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2601-26_0_4_load_75 | 30 | 0.00097793 | 0.00024509 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2601-26_0_4_load_95 | 33 | 0.0016328 | 0.00040921 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2601-26_0_4_load_16 | 34 | 0.0018848 | 0.00047237 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2601-26_0_4_load_17 | 35 | 0.0019619 | 0.00049169 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2601-26_0_4_load_18 | 36 | 0.004474 | 0.0011213 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2601-26_0_4_load_20 | 38 | 0.0016761 | 0.00042006 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2601-26_0_4_load_126 | 39 | 0.0021131 | 0.0005296 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2601-26_0_4_load_21 | 41 | 0.002746 | 0.00068821 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2601-26_0_4_load_78 | 42 | 0.0038662 | 0.00096896 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2601-26_0_4_load_58 | 43 | 0.0019749 | 0.00049495 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2601-26_0_4_load_23 | 45 | 0.0038548 | 0.0009661 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2601-26_0_4_load_24 | 46 | 0.0052079 | 0.0013052 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2601-26_0_4_load_40 | 47 | 0.0019636 | 0.00049212 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2601-26_0_4_load_104 | 48 | 0.0022417 | 0.00056183 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2601-26_0_4_load_25 | 50 | 0.0022316 | 0.0005593 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2601-26_0_4_load_26 | 51 | 0.0056494 | 0.0014159 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2601-26_0_4_load_27 | 52 | 0.0020154 | 0.00050511 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2601-26_0_4_load_28 | 53 | 0.0011529 | 0.00028894 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2601-26_0_4_load_29 | 54 | 0.0062933 | 0.0015773 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2601-26_0_4_load_48 | 56 | 0.0022287 | 0.00055857 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2601-26_0_4_load_46 | 58 | 0.0015909 | 0.00039873 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2601-26_0_4_load_30 | 59 | 0.0037162 | 0.00093138 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2601-26_0_4_load_56 | 62 | 0.0044149 | 0.0011065 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2601-26_0_4_load_54 | 63 | 0.004133 | 0.0010358 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2601-26_0_4_load_55 | 65 | 0.0033242 | 0.00083313 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2601-26_0_4_load_53 | 66 | 0.00098879 | 0.00024781 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2601-26_0_4_load_155 | 67 | 0.0030241 | 0.00075792 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2601-26_0_4_load_130 | 68 | 0.0010677 | 0.00026758 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2601-26_0_4_load_51 | 69 | 0.0066001 | 0.0016542 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2601-26_0_4_load_35 | 70 | 0.0049056 | 0.0012295 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2601-26_0_4_load_36 | 71 | 0.0024096 | 0.00060391 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2601-26_0_4_load_37 | 72 | 0.0039918 | 0.0010004 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2601-26_0_4_load_38 | 73 | 0.0024119 | 0.00060447 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2601-26_0_4_load_80 | 75 | 0.0026225 | 0.00065725 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2601-26_0_4_load_131 | 76 | 0.0009299 | 0.00023305 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2601-26_0_4_load_138 | 77 | 0.002604 | 0.00065262 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2601-26_0_4_load_153 | 78 | 0.0010203 | 0.00025571 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2601-26_0_4_load_42 | 79 | 0.0012963 | 0.00032489 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2601-26_0_4_load_157 | 81 | 0.0047369 | 0.0011872 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2601-26_0_4_load_44 | 82 | 0.006912 | 0.0017323 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2601-26_0_4_load_45 | 83 | 0.002272 | 0.00056942 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2601-26_0_4_load_49 | 84 | 0.002639 | 0.00066139 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2601-26_0_4_load_50 | 85 | 0.001676 | 0.00042005 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2601-26_0_4_load_145 | 86 | 0.0038278 | 0.00095934 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2601-26_0_4_load_57 | 87 | 0.0041599 | 0.0010426 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2601-26_0_4_load_76 | 88 | 0.001833 | 0.0004594 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2601-26_0_4_load_61 | 89 | 0.010068 | 0.0025232 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2601-26_0_4_load_62 | 90 | 0.0049859 | 0.0012496 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2601-26_0_4_load_63 | 91 | 0.00065024 | 0.00016297 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2601-26_0_4_load_64 | 92 | 0.018436 | 0.0046204 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2601-26_0_4_load_136 | 93 | 0.0052009 | 0.0013035 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2601-26_0_4_load_149 | 95 | 0.011621 | 0.0029125 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2601-26_0_4_load_65 | 96 | 0.004726 | 0.0011844 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2601-26_0_4_load_67 | 97 | 0.0033697 | 0.00084454 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2601-26_0_4_load_85 | 98 | 0.0089488 | 0.0022428 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2601-26_0_4_load_83 | 99 | 0.0043107 | 0.0010804 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2601-26_0_4_load_82 | 100 | 0.005178 | 0.0012977 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2601-26_0_4_load_109 | 102 | 0.002689 | 0.00067393 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2601-26_0_4_load_110 | 103 | 0.0016793 | 0.00042088 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2601-26_0_4_load_105 | 104 | 0.0024193 | 0.00060633 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2601-26_0_4_load_128 | 105 | 0.0030464 | 0.00076351 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2601-26_0_4_load_72 | 106 | 0.0029574 | 0.00074119 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2601-26_0_4_load_73 | 107 | 0.0025108 | 0.00062926 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2601-26_0_4_load_90 | 109 | 0.0019216 | 0.0004816 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2601-26_0_4_load_86 | 110 | 0.0017696 | 0.0004435 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2601-26_0_4_load_77 | 111 | 0.0013731 | 0.00034413 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2601-26_0_4_load_79 | 112 | 0.0013821 | 0.00034638 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2601-26_0_4_load_146 | 113 | 0.0015199 | 0.00038092 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2601-26_0_4_load_120 | 114 | 0.0017438 | 0.00043703 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2601-26_0_4_load_98 | 116 | 0.008491 | 0.0021281 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2601-26_0_4_load_127 | 117 | 0.007731 | 0.0019376 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2601-26_0_4_load_87 | 118 | 0.0014104 | 0.00035347 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2601-26_0_4_load_89 | 119 | 0.0015329 | 0.00038419 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2601-26_0_4_load_119 | 122 | 0.0016421 | 0.00041156 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2601-26_0_4_load_137 | 123 | 0.0031841 | 0.000798 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2601-26_0_4_load_116 | 124 | 0.0020302 | 0.00050882 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2601-26_0_4_load_93 | 125 | 0.0015247 | 0.00038212 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2601-26_0_4_load_113 | 126 | 0.0073394 | 0.0018394 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2601-26_0_4_load_111 | 127 | 0.0024351 | 0.00061029 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2601-26_0_4_load_99 | 128 | 0.0023633 | 0.0005923 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2601-26_0_4_load_100 | 129 | 0.0018838 | 0.00047212 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2601-26_0_4_load_101 | 130 | 0.0021196 | 0.00053123 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2601-26_0_4_load_102 | 131 | 0.0012495 | 0.00031316 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2601-26_0_4_load_112 | 132 | 0.0082821 | 0.0020757 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2601-26_0_4_load_115 | 133 | 0.001261 | 0.00031604 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2601-26_0_4_load_114 | 134 | 0.0016159 | 0.00040498 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2601-26_0_4_load_106 | 135 | 0.0015758 | 0.00039493 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2601-26_0_4_load_108 | 136 | 0.0017851 | 0.0004474 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2601-26_0_4_load_121 | 137 | 0.0027916 | 0.00069964 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2601-26_0_4_load_122 | 138 | 0.0036638 | 0.00091824 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2601-26_0_4_load_147 | 139 | 0.0026215 | 0.00065701 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2601-26_0_4_load_148 | 140 | 0.0059496 | 0.0014911 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2601-26_0_4_load_123 | 141 | 0.0040285 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2601-26_0_4_load_140 | 142 | 0.0037987 | 0.00095205 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2601-26_0_4_load_150 | 143 | 0.0070142 | 0.0017579 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2601-26_0_4_load_141 | 145 | 0.0033035 | 0.00082793 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2601-26_0_4_load_154 | 146 | 0.0013651 | 0.00034211 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2601-26_0_4_load_132 | 147 | 0.0015968 | 0.00040019 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2601-26_0_4_load_133 | 148 | 0.0017651 | 0.00044236 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2601-26_0_4_load_151 | 149 | 0.003629 | 0.00090952 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2601-26_0_4_load_142 | 150 | 0.0036501 | 0.00091481 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2601-26_0_4_line_0 |  | 0 | 1 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2601-26_0_4_line_1 |  | 0 | 2 | 0.013437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2601-26_0_4_line_2 |  | 1 | 3 | 0.0078836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2601-26_0_4_line_3 |  | 2 | 4 | 0.024541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2601-26_0_4_line_4 |  | 3 | 5 | 0.012784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2601-26_0_4_line_5 |  | 4 | 6 | 0.015569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2601-26_0_4_line_6 |  | 4 | 7 | 0.01658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2601-26_0_4_line_7 |  | 5 | 8 | 0.020851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2601-26_0_4_line_8 |  | 6 | 9 | 0.008243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2601-26_0_4_line_9 |  | 7 | 12 | 0.0094794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2601-26_0_4_line_10 |  | 9 | 77 | 0.0070522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2601-26_0_4_line_11 |  | 10 | 11 | 0.0099915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2601-26_0_4_line_12 |  | 11 | 106 | 0.018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2601-26_0_4_line_13 |  | 12 | 125 | 0.0089983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2601-26_0_4_line_14 |  | 13 | 14 | 0.0087863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2601-26_0_4_line_15 |  | 13 | 15 | 0.023426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2601-26_0_4_line_16 |  | 14 | 16 | 0.011703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2601-26_0_4_line_17 |  | 15 | 17 | 0.0024139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2601-26_0_4_line_18 |  | 16 | 18 | 0.00061216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2601-26_0_4_line_19 |  | 17 | 19 | 0.010882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2601-26_0_4_line_20 |  | 19 | 20 | 0.032734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2601-26_0_4_line_21 |  | 20 | 55 | 0.013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2601-26_0_4_line_22 |  | 20 | 96 | 0.040223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2601-26_0_4_line_23 |  | 21 | 22 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2601-26_0_4_line_24 |  | 22 | 23 | 0.037757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2601-26_0_4_line_25 |  | 22 | 24 | 0.012611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2601-26_0_4_line_26 |  | 23 | 25 | 0.051367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2601-26_0_4_line_27 |  | 24 | 26 | 0.021035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2601-26_0_4_line_28 |  | 25 | 30 | 0.017238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2601-26_0_4_line_29 |  | 26 | 31 | 0.021144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2601-26_0_4_line_30 |  | 27 | 28 | 0.023699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2601-26_0_4_line_31 |  | 27 | 29 | 0.03048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2601-26_0_4_line_32 |  | 29 | 32 | 0.030999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2601-26_0_4_line_33 |  | 29 | 33 | 0.0021148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2601-26_0_4_line_34 |  | 31 | 132 | 0.023893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2601-26_0_4_line_35 |  | 31 | 133 | 0.012451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2601-26_0_4_line_36 |  | 31 | 130 | 0.018681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2601-26_0_4_line_37 |  | 32 | 83 | 0.019307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2601-26_0_4_line_38 |  | 33 | 115 | 0.01778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2601-26_0_4_line_39 |  | 34 | 35 | 0.00086888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2601-26_0_4_line_40 |  | 34 | 36 | 0.0071286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2601-26_0_4_line_41 |  | 35 | 37 | 0.034914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2601-26_0_4_line_42 |  | 36 | 38 | 0.0095389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2601-26_0_4_line_43 |  | 37 | 39 | 0.0024242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2601-26_0_4_line_44 |  | 37 | 40 | 0.02926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2601-26_0_4_line_45 |  | 38 | 41 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2601-26_0_4_line_46 |  | 40 | 42 | 0.013273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2601-26_0_4_line_47 |  | 40 | 43 | 0.0088726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2601-26_0_4_line_48 |  | 41 | 44 | 0.01288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2601-26_0_4_line_49 |  | 42 | 88 | 0.022413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2601-26_0_4_line_50 |  | 43 | 87 | 0.049315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2601-26_0_4_line_51 |  | 44 | 45 | 0.015084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2601-26_0_4_line_52 |  | 44 | 46 | 0.017286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2601-26_0_4_line_53 |  | 45 | 47 | 0.032858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2601-26_0_4_line_54 |  | 46 | 48 | 0.023943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2601-26_0_4_line_55 |  | 47 | 49 | 0.022114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2601-26_0_4_line_56 |  | 49 | 79 | 0.049513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2601-26_0_4_line_57 |  | 49 | 80 | 0.082223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2601-26_0_4_line_58 |  | 50 | 51 | 0.0076569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2601-26_0_4_line_59 |  | 50 | 52 | 0.015717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2601-26_0_4_line_60 |  | 51 | 53 | 0.0041505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2601-26_0_4_line_61 |  | 52 | 54 | 0.0075047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2601-26_0_4_line_62 |  | 53 | 55 | 0.011679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2601-26_0_4_line_63 |  | 54 | 56 | 0.0057093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2601-26_0_4_line_64 |  | 55 | 57 | 0.004593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2601-26_0_4_line_65 |  | 56 | 58 | 0.014421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2601-26_0_4_line_66 |  | 57 | 105 | 0.015357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2601-26_0_4_line_67 |  | 58 | 82 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2601-26_0_4_line_68 |  | 59 | 60 | 0.028742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2601-26_0_4_line_69 |  | 60 | 61 | 0.028912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2601-26_0_4_line_70 |  | 61 | 62 | 0.012042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2601-26_0_4_line_71 |  | 61 | 63 | 0.016743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2601-26_0_4_line_72 |  | 62 | 67 | 0.0024062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2601-26_0_4_line_73 |  | 63 | 64 | 0.015236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2601-26_0_4_line_74 |  | 64 | 65 | 0.026412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2601-26_0_4_line_75 |  | 64 | 66 | 0.050739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2601-26_0_4_line_76 |  | 65 | 68 | 0.0025586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2601-26_0_4_line_77 |  | 66 | 69 | 0.021891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2601-26_0_4_line_78 |  | 67 | 86 | 0.021369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2601-26_0_4_line_79 |  | 69 | 84 | 0.021701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2601-26_0_4_line_80 |  | 70 | 71 | 0.0093162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2601-26_0_4_line_81 |  | 70 | 72 | 0.010849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2601-26_0_4_line_82 |  | 71 | 73 | 0.0081835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2601-26_0_4_line_83 |  | 72 | 74 | 0.017929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2601-26_0_4_line_84 |  | 73 | 75 | 0.010312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2601-26_0_4_line_85 |  | 74 | 76 | 0.013077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2601-26_0_4_line_86 |  | 75 | 77 | 0.0081916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2601-26_0_4_line_87 |  | 76 | 78 | 0.018683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2601-26_0_4_line_88 |  | 78 | 146 | 0.0048978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2601-26_0_4_line_89 |  | 80 | 81 | 0.046253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2601-26_0_4_line_90 |  | 82 | 83 | 0.0037613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2601-26_0_4_line_91 |  | 84 | 85 | 0.052766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2601-26_0_4_line_92 |  | 86 | 144 | 0.0054947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2601-26_0_4_line_93 |  | 88 | 111 | 0.026144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2601-26_0_4_line_94 |  | 89 | 90 | 0.00013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2601-26_0_4_line_95 |  | 89 | 91 | 0.0086687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2601-26_0_4_line_96 |  | 90 | 92 | 0.004475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2601-26_0_4_line_97 |  | 91 | 93 | 0.034692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2601-26_0_4_line_98 |  | 92 | 95 | 0.012388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2601-26_0_4_line_99 |  | 93 | 94 | 0.07843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2601-26_0_4_line_100 |  | 94 | 123 | 0.018194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2601-26_0_4_line_101 |  | 94 | 147 | 0.014561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2601-26_0_4_line_102 |  | 96 | 97 | 0.0066664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2601-26_0_4_line_103 |  | 96 | 98 | 0.038039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2601-26_0_4_line_104 |  | 98 | 99 | 0.016037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2601-26_0_4_line_105 |  | 99 | 100 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2601-26_0_4_line_106 |  | 101 | 102 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2601-26_0_4_line_107 |  | 101 | 103 | 0.016914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2601-26_0_4_line_108 |  | 101 | 104 | 0.021657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2601-26_0_4_line_109 |  | 102 | 131 | 0.024327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
110 | LV_2601-26_0_4_line_110 |  | 103 | 125 | 0.0094739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2601-26_0_4_line_111 |  | 104 | 135 | 0.0013608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2601-26_0_4_line_112 |  | 105 | 117 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2601-26_0_4_line_113 |  | 106 | 107 | 0.0095512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2601-26_0_4_line_114 |  | 107 | 108 | 0.0066985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2601-26_0_4_line_115 |  | 108 | 109 | 0.0075614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2601-26_0_4_line_116 |  | 108 | 110 | 0.01477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2601-26_0_4_line_117 |  | 109 | 121 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2601-26_0_4_line_118 |  | 110 | 118 | 0.030618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2601-26_0_4_line_119 |  | 111 | 112 | 0.0053719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2601-26_0_4_line_120 |  | 112 | 113 | 0.010852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2601-26_0_4_line_121 |  | 113 | 114 | 0.001198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2601-26_0_4_line_122 |  | 114 | 120 | 0.020972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2601-26_0_4_line_123 |  | 115 | 116 | 0.0049916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2601-26_0_4_line_124 |  | 116 | 126 | 0.013823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2601-26_0_4_line_125 |  | 118 | 119 | 0.0087826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2601-26_0_4_line_126 |  | 119 | 120 | 0.0052889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2601-26_0_4_line_127 |  | 120 | 122 | 0.021541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2601-26_0_4_line_128 |  | 121 | 123 | 0.021767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2601-26_0_4_line_129 |  | 121 | 124 | 0.033854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_2601-26_0_4_line_130 |  | 122 | 139 | 0.0019505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2601-26_0_4_line_131 |  | 124 | 134 | 0.00043077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_2601-26_0_4_line_132 |  | 126 | 127 | 0.024222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2601-26_0_4_line_133 |  | 127 | 132 | 0.00080227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2601-26_0_4_line_134 |  | 128 | 129 | 0.0036067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2601-26_0_4_line_135 |  | 128 | 130 | 0.027012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_2601-26_0_4_line_136 |  | 129 | 131 | 0.011761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_2601-26_0_4_line_137 |  | 133 | 134 | 0.014228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_2601-26_0_4_line_138 |  | 135 | 136 | 0.027643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2601-26_0_4_line_139 |  | 136 | 137 | 0.022562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2601-26_0_4_line_140 |  | 137 | 138 | 0.0036958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2601-26_0_4_line_141 |  | 138 | 141 | 0.019475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2601-26_0_4_line_142 |  | 139 | 140 | 0.052571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2601-26_0_4_line_143 |  | 141 | 142 | 0.0010337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2601-26_0_4_line_144 |  | 142 | 143 | 0.018514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2601-26_0_4_line_145 |  | 143 | 149 | 0.01333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2601-26_0_4_line_146 |  | 144 | 145 | 0.010918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2601-26_0_4_line_147 |  | 145 | 150 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2601-26_0_4_line_148 |  | 147 | 148 | 0.0382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2601-26_0_4_line_149 |  | 149 | 151 | 0.018733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2601-26_0_4_line_150 |  | 150 | 151 | 0.029512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2601-26_0_4_trafo_71 | 0.63 MVA 20/0.4 kV | 152 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2607976.7938 | 1229460.9478 | 2607971.5268 | 1229476.7652
1 | 2607976.7938 | 1229460.9478 | 2607981.039 | 1229448.199
2 | 2607969.0361 | 1229484.2451 | 2607971.5268 | 1229476.7652
3 | 2607988.7923 | 1229424.9148 | 2607981.039 | 1229448.199
4 | 2607969.0361 | 1229484.2451 | 2607964.9973 | 1229496.3739
5 | 2607988.7923 | 1229424.9148 | 2607973.242 | 1229425.6869
6 | 2607988.7923 | 1229424.9148 | 2608004.4259 | 1229430.4377
7 | 2607958.4097 | 1229516.1574 | 2607964.9973 | 1229496.3739
8 | 2607965.0091 | 1229426.0956 | 2607973.242 | 1229425.6869
9 | 2608013.364 | 1229433.5952 | 2608004.4259 | 1229430.4377
10 | 2607957.9655 | 1229426.4454 | 2607965.0091 | 1229426.0956
11 | 2608004.7752 | 1229381.0144 | 2608001.3571 | 1229390.4031
12 | 2608010.9462 | 1229364.0646 | 2608004.7752 | 1229381.0144
13 | 2608021.8485 | 1229436.5925 | 2608013.364 | 1229433.5952
14 | 2608110.3797 | 1229430.468 | 2608115.1418 | 1229423.0842
15 | 2608110.3797 | 1229430.468 | 2608097.6827 | 1229450.155
16 | 2608115.1418 | 1229423.0842 | 2608121.485 | 1229413.249
17 | 2608097.6827 | 1229450.155 | 2608096.3743 | 1229452.1836
18 | 2608121.8168 | 1229412.7346 | 2608121.485 | 1229413.249
19 | 2608090.4765 | 1229461.3283 | 2608096.3743 | 1229452.1836
20 | 2608090.4765 | 1229461.3283 | 2608116.9326 | 1229480.7089
21 | 2608127.5497 | 1229488.4835 | 2608116.9326 | 1229480.7089
22 | 2608116.9326 | 1229480.7089 | 2608099.7275 | 1229504.7889 | 2608091.0867 | 1229498.6009
23 | 2608113.9739 | 1229304.956 | 2608125.2827 | 1229313.2999
24 | 2608113.9739 | 1229304.956 | 2608139.6613 | 1229277.2188
25 | 2608113.9739 | 1229304.956 | 2608105.8311 | 1229314.5857
26 | 2608139.6613 | 1229277.2188 | 2608115.3606 | 1229254.2834 | 2608103.1002 | 1229267.3966
27 | 2608093.8465 | 1229331.8364 | 2608102.5928 | 1229318.4153 | 2608105.8311 | 1229314.5857
28 | 2608091.3273 | 1229279.9884 | 2608103.1002 | 1229267.3966
29 | 2608082.3023 | 1229349.5509 | 2608093.8465 | 1229331.8364
30 | 2608190.3382 | 1229383.74 | 2608190.9344 | 1229379.8385 | 2608190.6184 | 1229378.2482 | 2608189.5304 | 1229376.1677 | 2608186.5351 | 1229372.895 | 2608177.515 | 1229365.9675
31 | 2608159.657 | 1229390.7023 | 2608177.515 | 1229365.9675
32 | 2608186.2237 | 1229406.8036 | 2608175.0823 | 1229400.0511 | 2608159.657 | 1229390.7023
33 | 2608159.657 | 1229390.7023 | 2608157.8136 | 1229389.6657
34 | 2608082.3023 | 1229349.5509 | 2608103.4727 | 1229360.6275
35 | 2608082.3023 | 1229349.5509 | 2608071.1378 | 1229344.0386
36 | 2608082.3023 | 1229349.5509 | 2608075.8011 | 1229367.0645
37 | 2608186.2237 | 1229406.8036 | 2608174.9599 | 1229422.4843
38 | 2608142.3156 | 1229380.9507 | 2608157.8136 | 1229389.6657
39 | 2607849.8623 | 1229384.9421 | 2607850.6294 | 1229385.3501
40 | 2607843.5684 | 1229381.595 | 2607849.8623 | 1229384.9421
41 | 2607883.438 | 1229390.4327 | 2607875.2313 | 1229392.5565 | 2607867.9886 | 1229393.2919 | 2607861.8477 | 1229391.316 | 2607850.6294 | 1229385.3501
42 | 2607843.5684 | 1229381.595 | 2607835.1463 | 1229377.1161
43 | 2607883.438 | 1229390.4327 | 2607884.1466 | 1229392.751
44 | 2607883.438 | 1229390.4327 | 2607873.7251 | 1229362.8257
45 | 2607835.1463 | 1229377.1161 | 2607824.4064 | 1229371.4046
46 | 2607873.7251 | 1229362.8257 | 2607886.9311 | 1229361.4984
47 | 2607873.7251 | 1229362.8257 | 2607870.4467 | 1229354.5811
48 | 2607813.3256 | 1229364.8813 | 2607817.1249 | 1229367.5323 | 2607824.4064 | 1229371.4046
49 | 2607909.2703 | 1229359.6916 | 2607890.976 | 1229361.0918 | 2607886.9311 | 1229361.4984
50 | 2607852.2252 | 1229308.7564 | 2607870.4467 | 1229354.5811
51 | 2607813.3256 | 1229364.8813 | 2607799.7789 | 1229358.2474
52 | 2607813.3256 | 1229364.8813 | 2607805.3562 | 1229380.2204
53 | 2607770.269 | 1229343.7962 | 2607799.7789 | 1229358.2474
54 | 2607794.3175 | 1229401.4672 | 2607805.3562 | 1229380.2204
55 | 2607750.4083 | 1229334.0703 | 2607770.269 | 1229343.7962
56 | 2607750.4083 | 1229334.0703 | 2607783.8861 | 1229297.5908
57 | 2607750.4083 | 1229334.0703 | 2607731.0956 | 1229354.4352 | 2607710.6838 | 1229375.5104 | 2607701.4293 | 1229385.4822 | 2607693.5106 | 1229393.4212
58 | 2608141.253 | 1229469.4095 | 2608136.7855 | 1229475.6279
59 | 2608150.4221 | 1229456.6442 | 2608146.3562 | 1229462.3046 | 2608144.3146 | 1229465.1479 | 2608141.253 | 1229469.4095
60 | 2608134.3639 | 1229478.9987 | 2608136.7855 | 1229475.6279
61 | 2608150.4221 | 1229456.6442 | 2608154.8004 | 1229450.549
62 | 2608127.5497 | 1229488.4835 | 2608134.3639 | 1229478.9987
63 | 2608158.1313 | 1229445.912 | 2608154.8004 | 1229450.549
64 | 2608127.5497 | 1229488.4835 | 2608131.2047 | 1229491.279
65 | 2608158.1313 | 1229445.912 | 2608166.5448 | 1229434.1993
66 | 2608131.2047 | 1229491.279 | 2608121.9297 | 1229503.5187
67 | 2608172.7656 | 1229425.5391 | 2608166.5448 | 1229434.1993
68 | 2607892.9169 | 1229526.6817 | 2607892.0447 | 1229544.7135 | 2607892.6917 | 1229555.3833
69 | 2607917.6378 | 1229517.9869 | 2607910.8448 | 1229516.6994 | 2607908.2924 | 1229516.4069 | 2607905.5653 | 1229516.4923 | 2607904.2468 | 1229516.8463 | 2607902.9207 | 1229517.2003 | 2607900.6391 | 1229518.4092 | 2607898.448 | 1229519.8182 | 2607895.907 | 1229522.4498 | 2607892.9169 | 1229526.6817
70 | 2607917.6378 | 1229517.9869 | 2607926.7069 | 1229525.9096
71 | 2607917.6378 | 1229517.9869 | 2607905.1757 | 1229507.5198 | 2607904.8236 | 1229507.2109
72 | 2607928.519 | 1229527.4926 | 2607926.7069 | 1229525.9096
73 | 2607894.3963 | 1229496.1432 | 2607901.3547 | 1229504.1683 | 2607904.8236 | 1229507.2109
74 | 2607894.3963 | 1229496.1432 | 2607894.608 | 1229479.2335 | 2607894.3505 | 1229469.7357
75 | 2607894.3963 | 1229496.1432 | 2607879.4879 | 1229491.054 | 2607856.5375 | 1229483.8307 | 2607845.9304 | 1229481.2124
76 | 2607894.2812 | 1229467.178 | 2607894.3505 | 1229469.7357
77 | 2607824.274 | 1229478.1229 | 2607843.3158 | 1229480.567 | 2607845.9304 | 1229481.2124
78 | 2607928.519 | 1229527.4926 | 2607944.6119 | 1229541.5514
79 | 2607824.274 | 1229478.1229 | 2607802.7491 | 1229475.3601
80 | 2607931.3116 | 1229427.7687 | 2607922.0068 | 1229428.2307
81 | 2607911.1708 | 1229428.7687 | 2607922.0068 | 1229428.2307
82 | 2607931.3116 | 1229427.7687 | 2607939.485 | 1229427.3629
83 | 2607893.2643 | 1229429.6578 | 2607911.1708 | 1229428.7687
84 | 2607949.784 | 1229426.8516 | 2607939.485 | 1229427.3629
85 | 2607893.2643 | 1229429.6578 | 2607880.1894 | 1229429.9074
86 | 2607957.9655 | 1229426.4454 | 2607949.784 | 1229426.8516
87 | 2607880.1894 | 1229429.9074 | 2607880.1894 | 1229429.9074 | 2607861.8649 | 1229426.263
88 | 2607857.0611 | 1229425.3077 | 2607861.8649 | 1229426.263
89 | 2607693.5106 | 1229393.4212 | 2607708.8617 | 1229408.0718 | 2607709.8909 | 1229414.766 | 2607727.7933 | 1229418.7581
90 | 2608172.7656 | 1229425.5391 | 2608174.9599 | 1229422.4843
91 | 2607802.7491 | 1229475.3601 | 2607793.0867 | 1229474.1199 | 2607750.6253 | 1229467.1854
92 | 2607948.75 | 1229545.1664 | 2607944.6119 | 1229541.5514
93 | 2607909.2703 | 1229359.6916 | 2607935.0982 | 1229357.7147 | 2607935.3177 | 1229357.6175
94 | 2607953.5546 | 1229221.4715 | 2607953.435 | 1229221.4032
95 | 2607961.082 | 1229225.7708 | 2607953.5546 | 1229221.4715
96 | 2607949.5491 | 1229219.1838 | 2607953.435 | 1229221.4032
97 | 2607979.3599 | 1229255.257 | 2607961.082 | 1229225.7708
98 | 2607949.5491 | 1229219.1838 | 2607938.7923 | 1229213.0402
99 | 2608049.8099 | 1229289.3158 | 2608004.1886 | 1229263.3171 | 2607979.3599 | 1229255.257
100 | 2608049.8099 | 1229289.3158 | 2608039.7151 | 1229304.4524
101 | 2608049.8099 | 1229289.3158 | 2608058.7228 | 1229277.8016
102 | 2608085.6667 | 1229494.7195 | 2608091.0867 | 1229498.6009
103 | 2608091.0867 | 1229498.6009 | 2608068.1981 | 1229528.983
104 | 2608068.1981 | 1229528.983 | 2608080.4268 | 1229539.3588
105 | 2608093.5756 | 1229550.5153 | 2608080.4268 | 1229539.3588
106 | 2608046.7293 | 1229445.3822 | 2608052.5869 | 1229429.6023
107 | 2608046.7293 | 1229445.3822 | 2608030.7814 | 1229439.7483
108 | 2608046.7293 | 1229445.3822 | 2608039.5721 | 1229465.8219
109 | 2608061.0528 | 1229406.7957 | 2608052.5869 | 1229429.6023
110 | 2608021.8485 | 1229436.5925 | 2608030.7814 | 1229439.7483
111 | 2608039.5721 | 1229465.8219 | 2608039.1224 | 1229467.1063
112 | 2608121.9297 | 1229503.5187 | 2608113.5309 | 1229514.6023 | 2608121.0385 | 1229520.3113
113 | 2608010.9462 | 1229364.0646 | 2608014.2137 | 1229355.0897
114 | 2608016.5053 | 1229348.7954 | 2608014.2137 | 1229355.0897
115 | 2608016.5053 | 1229348.7954 | 2608019.2847 | 1229341.7634
116 | 2608016.5053 | 1229348.7954 | 2608002.5969 | 1229343.8236
117 | 2608027.6381 | 1229322.5614 | 2608023.8174 | 1229330.272 | 2608019.3556 | 1229341.5839 | 2608019.2847 | 1229341.7634
118 | 2607973.7656 | 1229333.5174 | 2608002.5969 | 1229343.8236
119 | 2607940.2296 | 1229355.4424 | 2607940.2296 | 1229355.4424 | 2607935.3177 | 1229357.6175
120 | 2607940.2296 | 1229355.4424 | 2607944.2052 | 1229350.7448 | 2607945.7736 | 1229346.3169
121 | 2607946.1735 | 1229345.1876 | 2607945.7736 | 1229346.3169
122 | 2607960.2082 | 1229330.4318 | 2607954.9547 | 1229333.3487 | 2607950.738 | 1229337.0342 | 2607946.5471 | 1229344.1329 | 2607946.1735 | 1229345.1876
123 | 2608142.3156 | 1229380.9507 | 2608137.8928 | 1229378.6366
124 | 2608137.8928 | 1229378.6366 | 2608125.6449 | 1229372.2284
125 | 2607973.7656 | 1229333.5174 | 2607965.4955 | 1229330.5611 | 2607965.4955 | 1229330.5611
126 | 2607960.2082 | 1229330.4318 | 2607965.4955 | 1229330.5611
127 | 2607960.2082 | 1229330.4318 | 2607947.942 | 1229320.4874 | 2607942.5067 | 1229318.6102
128 | 2608027.6381 | 1229322.5614 | 2608039.7151 | 1229304.4524
129 | 2608027.6381 | 1229322.5614 | 2608057.9936 | 1229337.5489
130 | 2607942.5067 | 1229318.6102 | 2607940.6631 | 1229317.9734
131 | 2608058.3798 | 1229337.7396 | 2608057.9936 | 1229337.5489
132 | 2608125.6449 | 1229372.2284 | 2608104.1835 | 1229360.9995
133 | 2608104.1835 | 1229360.9995 | 2608103.4727 | 1229360.6275
134 | 2608066.4008 | 1229392.3884 | 2608065.1457 | 1229395.7697
135 | 2608066.4008 | 1229392.3884 | 2608075.8011 | 1229367.0645
136 | 2608061.0528 | 1229406.7957 | 2608065.1457 | 1229395.7697
137 | 2608071.1378 | 1229344.0386 | 2608058.3798 | 1229337.7396
138 | 2608029.9866 | 1229493.1964 | 2608039.1224 | 1229467.1063
139 | 2608022.5302 | 1229514.4908 | 2608029.9866 | 1229493.1964
140 | 2608022.5302 | 1229514.4908 | 2608021.3088 | 1229517.9789
141 | 2608014.8727 | 1229536.3592 | 2608021.3088 | 1229517.9789
142 | 2607890.972 | 1229300.8116 | 2607940.6631 | 1229317.9734
143 | 2608014.8727 | 1229536.3592 | 2608014.5311 | 1229537.3349
144 | 2608014.5311 | 1229537.3349 | 2608010.8761 | 1229547.7728 | 2608007.7578 | 1229554.544
145 | 2608002.0062 | 1229566.5656 | 2608003.9173 | 1229562.8836 | 2608007.7578 | 1229554.544
146 | 2607948.75 | 1229545.1664 | 2607957.0604 | 1229552.2477
147 | 2607957.0604 | 1229552.2477 | 2607970.9135 | 1229564.0521
148 | 2608058.7228 | 1229277.8016 | 2608082.1054 | 1229247.5946
149 | 2607993.3762 | 1229583.1928 | 2608002.0062 | 1229566.5656
150 | 2607993.3762 | 1229583.1928 | 2607970.9135 | 1229564.0521

## bus_geodata
| x | y | coords
0 | 2607976.7938 | 1229460.9478
1 | 2607971.5268 | 1229476.7652
2 | 2607981.039 | 1229448.199
3 | 2607969.0361 | 1229484.2451
4 | 2607988.7923 | 1229424.9148
5 | 2607964.9973 | 1229496.3739
6 | 2607973.242 | 1229425.6869
7 | 2608004.4259 | 1229430.4377
8 | 2607958.4097 | 1229516.1574
9 | 2607965.0091 | 1229426.0956
10 | 2608001.3571 | 1229390.4031
11 | 2608004.7752 | 1229381.0144
12 | 2608013.364 | 1229433.5952
13 | 2608110.3797 | 1229430.468
14 | 2608115.1418 | 1229423.0842
15 | 2608097.6827 | 1229450.155
16 | 2608121.485 | 1229413.249
17 | 2608096.3743 | 1229452.1836
18 | 2608121.8168 | 1229412.7346
19 | 2608090.4765 | 1229461.3283
20 | 2608116.9326 | 1229480.7089
21 | 2608125.2827 | 1229313.2999
22 | 2608113.9739 | 1229304.956
23 | 2608139.6613 | 1229277.2188
24 | 2608105.8311 | 1229314.5857
25 | 2608103.1002 | 1229267.3966
26 | 2608093.8465 | 1229331.8364
27 | 2608177.515 | 1229365.9675
28 | 2608190.3382 | 1229383.74
29 | 2608159.657 | 1229390.7023
30 | 2608091.3273 | 1229279.9884
31 | 2608082.3023 | 1229349.5509
32 | 2608186.2237 | 1229406.8036
33 | 2608157.8136 | 1229389.6657
34 | 2607849.8623 | 1229384.9421
35 | 2607850.6294 | 1229385.35
36 | 2607843.5684 | 1229381.595
37 | 2607883.438 | 1229390.4327
38 | 2607835.1463 | 1229377.1161
39 | 2607884.1466 | 1229392.751
40 | 2607873.7251 | 1229362.8257
41 | 2607824.4064 | 1229371.4046
42 | 2607886.9311 | 1229361.4984
43 | 2607870.4467 | 1229354.5811
44 | 2607813.3256 | 1229364.8813
45 | 2607799.7789 | 1229358.2474
46 | 2607805.3562 | 1229380.2204
47 | 2607770.269 | 1229343.7962
48 | 2607794.3175 | 1229401.4672
49 | 2607750.4083 | 1229334.0703
50 | 2608141.253 | 1229469.4095
51 | 2608136.7855 | 1229475.6279
52 | 2608150.4221 | 1229456.6442
53 | 2608134.3639 | 1229478.9987
54 | 2608154.8004 | 1229450.549
55 | 2608127.5497 | 1229488.4835
56 | 2608158.1313 | 1229445.912
57 | 2608131.2047 | 1229491.279
58 | 2608166.5448 | 1229434.1993
59 | 2607892.6917 | 1229555.3833
60 | 2607892.9169 | 1229526.6817
61 | 2607917.6378 | 1229517.9869
62 | 2607926.7069 | 1229525.9096
63 | 2607904.8236 | 1229507.2109
64 | 2607894.3963 | 1229496.1432
65 | 2607894.3505 | 1229469.7357
66 | 2607845.9304 | 1229481.2124
67 | 2607928.519 | 1229527.4926
68 | 2607894.2812 | 1229467.178
69 | 2607824.274 | 1229478.1229
70 | 2607922.0068 | 1229428.2307
71 | 2607931.3116 | 1229427.7687
72 | 2607911.1708 | 1229428.7687
73 | 2607939.485 | 1229427.3629
74 | 2607893.2643 | 1229429.6578
75 | 2607949.784 | 1229426.8516
76 | 2607880.1894 | 1229429.9074
77 | 2607957.9656 | 1229426.4454
78 | 2607861.8649 | 1229426.263
79 | 2607783.8861 | 1229297.5908
80 | 2607693.5106 | 1229393.4212
81 | 2607727.7933 | 1229418.7581
82 | 2608172.7656 | 1229425.5391
83 | 2608174.9599 | 1229422.4843
84 | 2607802.7491 | 1229475.3601
85 | 2607750.6253 | 1229467.1854
86 | 2607944.6119 | 1229541.5514
87 | 2607852.2252 | 1229308.7564
88 | 2607909.2703 | 1229359.6916
89 | 2607953.5546 | 1229221.4715
90 | 2607953.435 | 1229221.4032
91 | 2607961.082 | 1229225.7708
92 | 2607949.5491 | 1229219.1838
93 | 2607979.3599 | 1229255.257
94 | 2608049.8099 | 1229289.3158
95 | 2607938.7923 | 1229213.0402
96 | 2608091.0867 | 1229498.6009
97 | 2608085.6667 | 1229494.7195
98 | 2608068.1981 | 1229528.983
99 | 2608080.4268 | 1229539.3588
100 | 2608093.5756 | 1229550.5153
101 | 2608046.7293 | 1229445.3822
102 | 2608052.5869 | 1229429.6023
103 | 2608030.7814 | 1229439.7483
104 | 2608039.5721 | 1229465.8219
105 | 2608121.9297 | 1229503.5187
106 | 2608010.9462 | 1229364.0646
107 | 2608014.2137 | 1229355.0897
108 | 2608016.5053 | 1229348.7954
109 | 2608019.2847 | 1229341.7634
110 | 2608002.5969 | 1229343.8236
111 | 2607935.3177 | 1229357.6175
112 | 2607940.2296 | 1229355.4424
113 | 2607945.7736 | 1229346.3169
114 | 2607946.1735 | 1229345.1876
115 | 2608142.3156 | 1229380.9507
116 | 2608137.8928 | 1229378.6366
117 | 2608121.0385 | 1229520.3113
118 | 2607973.7656 | 1229333.5174
119 | 2607965.4955 | 1229330.5611
120 | 2607960.2082 | 1229330.4318
121 | 2608027.6381 | 1229322.5614
122 | 2607942.5067 | 1229318.6102
123 | 2608039.7151 | 1229304.4524
124 | 2608057.9936 | 1229337.5489
125 | 2608021.8485 | 1229436.5925
126 | 2608125.6449 | 1229372.2284
127 | 2608104.1835 | 1229360.9995
128 | 2608066.4008 | 1229392.3884
129 | 2608065.1457 | 1229395.7697
130 | 2608075.8011 | 1229367.0645
131 | 2608061.0528 | 1229406.7957
132 | 2608103.4727 | 1229360.6275
133 | 2608071.1378 | 1229344.0386
134 | 2608058.3798 | 1229337.7396
135 | 2608039.1224 | 1229467.1063
136 | 2608029.9866 | 1229493.1964
137 | 2608022.5302 | 1229514.4908
138 | 2608021.3088 | 1229517.9789
139 | 2607940.6631 | 1229317.9734
140 | 2607890.972 | 1229300.8116
141 | 2608014.8727 | 1229536.3592
142 | 2608014.5311 | 1229537.3349
143 | 2608007.7578 | 1229554.544
144 | 2607948.75 | 1229545.1664
145 | 2607957.0604 | 1229552.2477
146 | 2607857.0611 | 1229425.3077
147 | 2608058.7228 | 1229277.8016
148 | 2608082.1054 | 1229247.5946
149 | 2608002.0062 | 1229566.5656
150 | 2607970.9135 | 1229564.0521
151 | 2607993.3762 | 1229583.1928
152 | 2607988.7923 | 1229424.9148

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98012 | -0.38157 | 0.0042154 | 0.0010565
1 | 0.97989 | -0.38588 | 0.0033615 | 0.00084247
2 | 0.98034 | -0.37706 | 0.0042724 | 0.0010708
3 | 0.97982 | -0.38744 | 0.0045739 | 0.0011463
4 | 0.98086 | -0.36694 | 0 | 0
5 | 0.97974 | -0.38891 | 0.0032634 | 0.00081787
6 | 0.98047 | -0.3747 | 0.0026209 | 0.00065686
7 | 0.98163 | -0.35185 | 0.001675 | 0.0004198
8 | 0.97968 | -0.39008 | 0.0030669 | 0.00076863
9 | 0.98028 | -0.37842 | 0.0026282 | 0.0006587
10 | 1 | 0 | -0.43051 | -0.11029
11 | 0.99903 | -0.018375 | 0.0016782 | 0.00042059
12 | 0.98209 | -0.34295 | 0.001522 | 0.00038144
13 | 0.97175 | -0.54488 | 0.0015197 | 0.00038088
14 | 0.9717 | -0.5459 | 0.0031518 | 0.00078992
15 | 0.97192 | -0.54152 | 0.0016871 | 0.00042284
16 | 0.97167 | -0.54657 | 0.0016268 | 0.00040772
17 | 0.97195 | -0.5411 | 0.0014193 | 0.0003557
18 | 0.97167 | -0.54659 | 0.0014749 | 0.00036965
19 | 0.97206 | -0.53892 | 0 | 0
20 | 0.97239 | -0.53235 | 0 | 0
21 | 0.98806 | -0.22761 | 0.0018572 | 0.00046545
22 | 0.98808 | -0.22715 | 0 | 0
23 | 0.98735 | -0.24125 | 0 | 0
24 | 0.98834 | -0.22202 | 0.0021721 | 0.00054437
25 | 0.98637 | -0.26047 | 0.01993 | 0.0049948
26 | 0.98883 | -0.21267 | 0.0033521 | 0.00084011
27 | 0.98088 | -0.36591 | 0 | 0
28 | 0.98071 | -0.36938 | 0.0080728 | 0.0020232
29 | 0.98111 | -0.36146 | 0 | 0
30 | 0.98635 | -0.26078 | 0.00097793 | 0.00024509
31 | 0.98938 | -0.20201 | 0 | 0
32 | 0.97884 | -0.40565 | 0 | 0
33 | 0.98128 | -0.35814 | 0.0016328 | 0.00040921
34 | 0.98589 | -0.27083 | 0.0018848 | 0.00047237
35 | 0.98591 | -0.27036 | 0.0019619 | 0.00049169
36 | 0.98571 | -0.27444 | 0.004474 | 0.0011213
37 | 0.98694 | -0.25031 | 0 | 0
38 | 0.9855 | -0.2785 | 0.0016761 | 0.00042006
39 | 0.98694 | -0.25041 | 0.0021131 | 0.0005296
40 | 0.98786 | -0.23244 | 0 | 0
41 | 0.98525 | -0.28331 | 0.002746 | 0.00068821
42 | 0.98836 | -0.22289 | 0.0038662 | 0.00096896
43 | 0.98781 | -0.23341 | 0.0019749 | 0.00049495
44 | 0.98502 | -0.28778 | 0 | 0
45 | 0.98486 | -0.291 | 0.0038548 | 0.0009661
46 | 0.9849 | -0.2901 | 0.0052079 | 0.0013052
47 | 0.98462 | -0.29572 | 0.0019636 | 0.00049212
48 | 0.98485 | -0.29106 | 0.0022417 | 0.00056183
49 | 0.98449 | -0.29812 | 0 | 0
50 | 0.97396 | -0.50142 | 0.0022316 | 0.0005593
51 | 0.97356 | -0.50916 | 0.0056494 | 0.0014159
52 | 0.9748 | -0.48491 | 0.0020154 | 0.00050511
53 | 0.97337 | -0.51293 | 0.0011529 | 0.00028894
54 | 0.97521 | -0.47676 | 0.0062933 | 0.0015773
55 | 0.97285 | -0.52329 | 0 | 0
56 | 0.97556 | -0.4699 | 0.0022287 | 0.00055857
57 | 0.9728 | -0.5242 | 0 | 0
58 | 0.97647 | -0.45202 | 0.0015909 | 0.00039873
59 | 0.97201 | -0.54021 | 0.0037162 | 0.00093138
60 | 0.97211 | -0.53824 | 0 | 0
61 | 0.97221 | -0.53625 | 0 | 0
62 | 0.97248 | -0.53089 | 0.0044149 | 0.0011065
63 | 0.97189 | -0.54257 | 0.004133 | 0.0010358
64 | 0.97166 | -0.54715 | 0 | 0
65 | 0.97155 | -0.54929 | 0.0033242 | 0.00083313
66 | 0.97109 | -0.55831 | 0.00098879 | 0.00024781
67 | 0.97254 | -0.52962 | 0.0030241 | 0.00075792
68 | 0.97155 | -0.54934 | 0.0010677 | 0.00026758
69 | 0.97087 | -0.56273 | 0.0066001 | 0.0016542
70 | 0.9796 | -0.39162 | 0.0049056 | 0.0012295
71 | 0.97971 | -0.38956 | 0.0024096 | 0.00060391
72 | 0.97953 | -0.39306 | 0.0039918 | 0.0010004
73 | 0.97982 | -0.38738 | 0.0024119 | 0.00060447
74 | 0.97947 | -0.39414 | 0 | 0
75 | 0.97998 | -0.3842 | 0.0026225 | 0.00065725
76 | 0.97943 | -0.39493 | 0.0009299 | 0.00023305
77 | 0.98013 | -0.38127 | 0.002604 | 0.00065262
78 | 0.97939 | -0.39574 | 0.0010203 | 0.00025571
79 | 0.98443 | -0.29928 | 0.0012963 | 0.00032489
80 | 0.98413 | -0.30513 | 0 | 0
81 | 0.98393 | -0.30908 | 0.0047369 | 0.0011872
82 | 0.97716 | -0.43851 | 0.006912 | 0.0017323
83 | 0.97743 | -0.43327 | 0.002272 | 0.00056942
84 | 0.97078 | -0.56446 | 0.002639 | 0.00066139
85 | 0.9707 | -0.5661 | 0.001676 | 0.00042005
86 | 0.97317 | -0.51719 | 0.0038278 | 0.00095934
87 | 0.98763 | -0.23708 | 0.0041599 | 0.0010426
88 | 0.98927 | -0.20524 | 0.001833 | 0.0004594
89 | 0.98587 | -0.27087 | 0.010068 | 0.0025232
90 | 0.98586 | -0.27095 | 0.0049859 | 0.0012496
91 | 0.98623 | -0.26386 | 0.00065024 | 0.00016297
92 | 0.98574 | -0.27337 | 0.018436 | 0.0046204
93 | 0.98769 | -0.23545 | 0.0052009 | 0.0013035
94 | 0.99136 | -0.1643 | 0 | 0
95 | 0.98561 | -0.27595 | 0.011621 | 0.0029125
96 | 0.97139 | -0.55204 | 0.004726 | 0.0011844
97 | 0.97137 | -0.55246 | 0.0033697 | 0.00084454
98 | 0.97074 | -0.56501 | 0.0089488 | 0.0022428
99 | 0.97059 | -0.56782 | 0.0043107 | 0.0010804
100 | 0.97051 | -0.56948 | 0.005178 | 0.0012977
101 | 0.9839 | -0.30758 | 0 | 0
102 | 0.98593 | -0.26834 | 0.002689 | 0.00067393
103 | 0.98302 | -0.32486 | 0.0016793 | 0.00042088
104 | 0.98243 | -0.33612 | 0.0024193 | 0.00060633
105 | 0.97265 | -0.52725 | 0.0030464 | 0.00076351
106 | 0.99727 | -0.051506 | 0.0029574 | 0.00074119
107 | 0.99635 | -0.068972 | 0.0025108 | 0.00062926
108 | 0.99571 | -0.081167 | 0 | 0
109 | 0.9951 | -0.092723 | 0.0019216 | 0.0004816
110 | 0.9948 | -0.098569 | 0.0017696 | 0.0004435
111 | 0.99037 | -0.18384 | 0.0013731 | 0.00034413
112 | 0.99061 | -0.17932 | 0.0013821 | 0.00034638
113 | 0.99109 | -0.16993 | 0.0015199 | 0.00038092
114 | 0.99115 | -0.16886 | 0.0017438 | 0.00043703
115 | 0.98274 | -0.32978 | 0 | 0
116 | 0.98316 | -0.32183 | 0.008491 | 0.0021281
117 | 0.97248 | -0.53058 | 0.007731 | 0.0019376
118 | 0.99297 | -0.13379 | 0.0014104 | 0.00035347
119 | 0.99245 | -0.14369 | 0.0015329 | 0.00038419
120 | 0.99215 | -0.14952 | 0 | 0
121 | 0.99342 | -0.12465 | 0 | 0
122 | 0.99195 | -0.15342 | 0.0016421 | 0.00041156
123 | 0.99227 | -0.14679 | 0.0031841 | 0.000798
124 | 0.99116 | -0.16781 | 0.0020302 | 0.00050882
125 | 0.98253 | -0.33426 | 0.0015247 | 0.00038212
126 | 0.9844 | -0.29775 | 0.0073394 | 0.0018394
127 | 0.98675 | -0.25251 | 0.0024351 | 0.00061029
128 | 0.9879 | -0.23029 | 0.0023633 | 0.0005923
129 | 0.98779 | -0.23247 | 0.0018838 | 0.00047212
130 | 0.98877 | -0.21366 | 0.0021196 | 0.00053123
131 | 0.98743 | -0.2395 | 0.0012495 | 0.00031316
132 | 0.98683 | -0.25098 | 0.0082821 | 0.0020757
133 | 0.99019 | -0.18633 | 0.001261 | 0.00031604
134 | 0.99113 | -0.16836 | 0.0016159 | 0.00040498
135 | 0.98234 | -0.33786 | 0.0015758 | 0.00039493
136 | 0.98056 | -0.37242 | 0.0017851 | 0.0004474
137 | 0.97915 | -0.39999 | 0.0027916 | 0.00069964
138 | 0.97893 | -0.40432 | 0.0036638 | 0.00091824
139 | 0.99194 | -0.15371 | 0.0026215 | 0.00065701
140 | 0.99165 | -0.15926 | 0.0059496 | 0.0014911
141 | 0.97782 | -0.4259 | 0.0040285 | 0.0010096
142 | 0.97777 | -0.42697 | 0.0037987 | 0.00095205
143 | 0.97685 | -0.44488 | 0.0070142 | 0.0017579
144 | 0.97336 | -0.51361 | 0 | 0
145 | 0.97372 | -0.5065 | 0.0033035 | 0.00082793
146 | 0.97939 | -0.39586 | 0.0013651 | 0.00034211
147 | 0.99132 | -0.16517 | 0.0015968 | 0.00040019
148 | 0.99126 | -0.16637 | 0.0017651 | 0.00044236
149 | 0.97628 | -0.45609 | 0.003629 | 0.00090952
150 | 0.97437 | -0.49355 | 0.0036501 | 0.00091481
151 | 0.97554 | -0.47062 | 0 | 0
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01427 | 0.0035773 | -0.014267 | -0.0035757 | 2.9344e-06 | 1.668e-06 | 0.021665 | 0.021665 | 0.021665 | 0.98012 | -0.38157 | 0.97989 | -0.38588 | 5.952
1 | -0.018485 | -0.0046338 | 0.018489 | 0.0046362 | 3.9688e-06 | 2.3707e-06 | 0.028065 | 0.028065 | 0.028065 | 0.98012 | -0.38157 | 0.98034 | -0.37706 | 7.7101
2 | 0.010906 | 0.0027332 | -0.010905 | -0.0027328 | 8.1079e-07 | 4.196e-07 | 0.016561 | 0.016561 | 0.016561 | 0.97989 | -0.38588 | 0.97982 | -0.38744 | 4.5496
3 | -0.022762 | -0.005707 | 0.022773 | 0.0057137 | 1.0985e-05 | 6.721e-06 | 0.03455 | 0.03455 | 0.03455 | 0.98034 | -0.37706 | 0.98086 | -0.36694 | 9.4917
4 | 0.0063308 | 0.0015865 | -0.0063304 | -0.0015863 | 4.4313e-07 | 1.226e-07 | 0.0096144 | 0.0096144 | 0.0096144 | 0.97982 | -0.38744 | 0.97974 | -0.38891 | 2.6413
5 | 0.027536 | 0.0069099 | -0.027526 | -0.0069036 | 1.019e-05 | 6.3253e-06 | 0.041777 | 0.041777 | 0.041777 | 0.98086 | -0.36694 | 0.98047 | -0.3747 | 11.4772
6 | -0.050309 | -0.012624 | 0.050345 | 0.012647 | 3.6223e-05 | 2.2973e-05 | 0.076327 | 0.076326 | 0.076327 | 0.98086 | -0.36694 | 0.98163 | -0.35185 | 20.9688
7 | 0.003067 | 0.00076847 | -0.0030669 | -0.00076863 | 1.6966e-07 | -1.5398e-07 | 0.0046581 | 0.0046582 | 0.0046582 | 0.97974 | -0.38891 | 0.97968 | -0.39008 | 1.2797
8 | 0.024905 | 0.0062467 | -0.024901 | -0.006244 | 4.4166e-06 | 2.7227e-06 | 0.037799 | 0.037799 | 0.037799 | 0.98047 | -0.3747 | 0.98028 | -0.37842 | 10.3845
9 | -0.05202 | -0.013066 | 0.052042 | 0.01308 | 2.211e-05 | 1.403e-05 | 0.078866 | 0.078866 | 0.078866 | 0.98163 | -0.35185 | 0.98209 | -0.34295 | 21.6664
10 | 0.022273 | 0.0055853 | -0.02227 | -0.0055835 | 3.0231e-06 | 1.8459e-06 | 0.03381 | 0.03381 | 0.03381 | 0.98028 | -0.37842 | 0.98013 | -0.38127 | 9.2885
11 | 0.42886 | 0.11029 | -0.42848 | -0.11005 | 0.00038265 | 0.00024437 | 0.63915 | 0.63915 | 0.63915 | 1 | 0 | 0.99903 | -0.018375 | 43.8975
12 | 0.4268 | 0.10963 | -0.42611 | -0.10919 | 0.00068543 | 0.00043773 | 0.63665 | 0.63665 | 0.63665 | 0.99903 | -0.018375 | 0.99727 | -0.051506 | 43.7259
13 | -0.053564 | -0.013462 | 0.053586 | 0.013476 | 2.2233e-05 | 1.4115e-05 | 0.081172 | 0.081171 | 0.081172 | 0.98209 | -0.34295 | 0.98253 | -0.33426 | 22.2999
14 | 0.0062539 | 0.0015673 | -0.0062536 | -0.0015672 | 3.0217e-07 | 8.4541e-08 | 0.0095764 | 0.0095764 | 0.0095764 | 0.97175 | -0.54488 | 0.9717 | -0.5459 | 2.6309
15 | -0.0077737 | -0.0019482 | 0.0077749 | 0.0019487 | 1.2447e-06 | 5.0637e-07 | 0.011904 | 0.011903 | 0.011904 | 0.97175 | -0.54488 | 0.97192 | -0.54152 | 3.2702
16 | 0.0031018 | 0.00077727 | -0.0031017 | -0.00077736 | 9.9018e-08 | -8.1596e-08 | 0.0047499 | 0.00475 | 0.00475 | 0.9717 | -0.5459 | 0.97167 | -0.54657 | 1.3049
17 | -0.009462 | -0.0023715 | 0.0094622 | 0.0023716 | 1.8996e-07 | 9.1661e-08 | 0.014486 | 0.014486 | 0.014486 | 0.97192 | -0.54152 | 0.97195 | -0.5411 | 3.9798
18 | 0.0014749 | 0.00036964 | -0.0014749 | -0.00036965 | 1.1712e-09 | -6.833e-09 | 0.0022587 | 0.0022587 | 0.0022587 | 0.97167 | -0.54657 | 0.97167 | -0.54659 | 0.62051
19 | -0.010882 | -0.0027273 | 0.010883 | 0.0027279 | 1.1325e-06 | 5.8992e-07 | 0.016659 | 0.016659 | 0.016659 | 0.97195 | -0.5411 | 0.97206 | -0.53892 | 4.5767
20 | -0.010883 | -0.0027279 | 0.010886 | 0.0027297 | 3.4067e-06 | 1.7744e-06 | 0.016659 | 0.016659 | 0.016659 | 0.97206 | -0.53892 | 0.97239 | -0.53235 | 4.5767
21 | -0.037457 | -0.0094024 | 0.037474 | 0.0094126 | 1.6186e-05 | 1.0196e-05 | 0.057325 | 0.057325 | 0.057325 | 0.97239 | -0.53235 | 0.97285 | -0.52329 | 15.7487
22 | 0.026571 | 0.0066728 | -0.026546 | -0.0066573 | 2.4944e-05 | 1.5466e-05 | 0.040666 | 0.040666 | 0.040666 | 0.97239 | -0.53235 | 0.97139 | -0.55204 | 11.1721
23 | -0.0018572 | -0.00046545 | 0.0018572 | 0.0004653 | 4.1226e-08 | -1.5362e-07 | 0.0027969 | 0.0027968 | 0.0027969 | 0.98806 | -0.22761 | 0.98808 | -0.22715 | 0.76838
24 | 0.020941 | 0.0052599 | -0.020927 | -0.0052513 | 1.4085e-05 | 8.5313e-06 | 0.03154 | 0.031541 | 0.031541 | 0.98808 | -0.22715 | 0.98735 | -0.24125 | 8.665
25 | -0.022798 | -0.0057252 | 0.022804 | 0.0057286 | 5.5758e-06 | 3.4069e-06 | 0.034337 | 0.034337 | 0.034337 | 0.98808 | -0.22715 | 0.98834 | -0.22202 | 9.4333
26 | 0.020927 | 0.0052513 | -0.020908 | -0.0052397 | 1.9163e-05 | 1.1608e-05 | 0.031541 | 0.031541 | 0.031541 | 0.98735 | -0.24125 | 0.98637 | -0.26047 | 8.6651
27 | -0.024976 | -0.0062729 | 0.024987 | 0.0062798 | 1.1156e-05 | 6.8702e-06 | 0.037607 | 0.037607 | 0.037607 | 0.98834 | -0.22202 | 0.98883 | -0.21267 | 10.3317
28 | 0.00097795 | 0.00024488 | -0.00097793 | -0.00024509 | 1.4069e-08 | -2.1102e-07 | 0.0014752 | 0.0014753 | 0.0014753 | 0.98637 | -0.26047 | 0.98635 | -0.26078 | 0.40531
29 | -0.028339 | -0.0071199 | 0.028353 | 0.0071289 | 1.4424e-05 | 8.96e-06 | 0.042652 | 0.042651 | 0.042652 | 0.98883 | -0.21267 | 0.98938 | -0.20201 | 11.7175
30 | 0.0080742 | 0.0020238 | -0.0080728 | -0.0020232 | 1.3334e-06 | 5.5426e-07 | 0.012249 | 0.012249 | 0.012249 | 0.98088 | -0.36591 | 0.98071 | -0.36938 | 3.3651
31 | -0.0080742 | -0.0020238 | 0.0080759 | 0.0020245 | 1.7148e-06 | 7.1267e-07 | 0.012249 | 0.012249 | 0.012249 | 0.98088 | -0.36591 | 0.98111 | -0.36146 | 3.365
32 | 0.079138 | 0.020063 | -0.07897 | -0.019956 | 0.0001677 | 0.00010694 | 0.12011 | 0.12011 | 0.12011 | 0.98111 | -0.36146 | 0.97884 | -0.40565 | 32.9968
33 | -0.087214 | -0.022088 | 0.087228 | 0.022097 | 1.3893e-05 | 8.8647e-06 | 0.13236 | 0.13236 | 0.13236 | 0.98111 | -0.36146 | 0.98128 | -0.35814 | 36.3618
34 | 0.11619 | 0.029657 | -0.11591 | -0.029482 | 0.0002742 | 0.00017518 | 0.17494 | 0.17494 | 0.17494 | 0.98938 | -0.20201 | 0.98683 | -0.25098 | 48.06
35 | -0.28609 | -0.072834 | 0.28631 | 0.072972 | 0.00021652 | 0.00013793 | 0.43068 | 0.43068 | 0.43068 | 0.98938 | -0.20201 | 0.99019 | -0.18633 | 29.5798
36 | 0.14155 | 0.036048 | -0.14147 | -0.035998 | 7.9528e-05 | 4.9939e-05 | 0.21309 | 0.21309 | 0.21309 | 0.98938 | -0.20201 | 0.98877 | -0.21366 | 14.6355
37 | 0.07897 | 0.019956 | -0.078866 | -0.01989 | 0.00010445 | 6.6603e-05 | 0.12011 | 0.12011 | 0.12011 | 0.97884 | -0.40565 | 0.97743 | -0.43327 | 32.9968
38 | -0.088861 | -0.022506 | 0.088982 | 0.022583 | 0.00012122 | 7.7354e-05 | 0.13483 | 0.13483 | 0.13483 | 0.98128 | -0.35814 | 0.98274 | -0.32978 | 37.042
39 | -0.030108 | -0.007552 | 0.030109 | 0.0075524 | 6.7293e-07 | 4.1959e-07 | 0.045445 | 0.045445 | 0.045445 | 0.98589 | -0.27083 | 0.98591 | -0.27036 | 12.4849
40 | 0.028224 | 0.0070796 | -0.028219 | -0.0070766 | 4.8513e-06 | 3.014e-06 | 0.0426 | 0.0426 | 0.0426 | 0.98589 | -0.27083 | 0.98571 | -0.27444 | 11.7034
41 | -0.032071 | -0.0080441 | 0.032102 | 0.0080633 | 3.0678e-05 | 1.9188e-05 | 0.048406 | 0.048406 | 0.048406 | 0.98591 | -0.27036 | 0.98694 | -0.25031 | 13.2984
42 | 0.023745 | 0.0059553 | -0.02374 | -0.0059525 | 4.5965e-06 | 2.8202e-06 | 0.035847 | 0.035847 | 0.035847 | 0.98571 | -0.27444 | 0.9855 | -0.2785 | 9.848
43 | 0.0021131 | 0.00052957 | -0.0021131 | -0.0005296 | 9.2276e-09 | -2.5074e-08 | 0.003186 | 0.003186 | 0.003186 | 0.98694 | -0.25031 | 0.98694 | -0.25041 | 0.87526
44 | -0.034215 | -0.0085928 | 0.034244 | 0.0086111 | 2.9206e-05 | 1.8317e-05 | 0.051592 | 0.051592 | 0.051592 | 0.98694 | -0.25031 | 0.98786 | -0.23244 | 14.1736
45 | 0.022064 | 0.0055324 | -0.022059 | -0.0055293 | 5.0631e-06 | 3.0854e-06 | 0.033316 | 0.033316 | 0.033316 | 0.9855 | -0.2785 | 0.98525 | -0.28331 | 9.1527
46 | -0.04038 | -0.010149 | 0.040398 | 0.01016 | 1.842e-05 | 1.1619e-05 | 0.060834 | 0.060834 | 0.060834 | 0.98786 | -0.23244 | 0.98836 | -0.22289 | 16.7127
47 | 0.0061358 | 0.0015374 | -0.0061355 | -0.0015374 | 2.8421e-07 | 6.8305e-08 | 0.0092422 | 0.0092423 | 0.0092423 | 0.98786 | -0.23244 | 0.98781 | -0.23341 | 2.5391
48 | 0.019313 | 0.0048411 | -0.019309 | -0.0048386 | 4.1094e-06 | 2.466e-06 | 0.029169 | 0.029169 | 0.029169 | 0.98525 | -0.28331 | 0.98502 | -0.28778 | 8.0134
49 | -0.044264 | -0.011129 | 0.044302 | 0.011153 | 3.7342e-05 | 2.3611e-05 | 0.066655 | 0.066655 | 0.066655 | 0.98836 | -0.22289 | 0.98927 | -0.20524 | 18.3117
50 | 0.0041607 | 0.0010424 | -0.0041599 | -0.0010426 | 7.2643e-07 | -1.6627e-07 | 0.0062674 | 0.0062676 | 0.0062676 | 0.98781 | -0.23341 | 0.98763 | -0.23708 | 1.7219
51 | 0.011858 | 0.0029715 | -0.011857 | -0.0029706 | 1.8152e-06 | 9.6973e-07 | 0.017914 | 0.017914 | 0.017914 | 0.98502 | -0.28778 | 0.98486 | -0.291 | 4.9214
52 | 0.0074505 | 0.0018671 | -0.0074497 | -0.0018668 | 8.2114e-07 | 3.0552e-07 | 0.011255 | 0.011255 | 0.011255 | 0.98502 | -0.28778 | 0.9849 | -0.2901 | 3.0921
53 | 0.0080019 | 0.0020045 | -0.0080001 | -0.0020037 | 1.801e-06 | 7.346e-07 | 0.01209 | 0.01209 | 0.01209 | 0.98486 | -0.291 | 0.98462 | -0.29572 | 3.3214
54 | 0.0022418 | 0.00056159 | -0.0022417 | -0.00056183 | 1.03e-07 | -2.3877e-07 | 0.0033869 | 0.003387 | 0.003387 | 0.9849 | -0.2901 | 0.98485 | -0.29106 | 0.9305
55 | 0.0060365 | 0.0015116 | -0.0060358 | -0.0015114 | 6.901e-07 | 1.6043e-07 | 0.0091222 | 0.0091223 | 0.0091223 | 0.98462 | -0.29572 | 0.98449 | -0.29812 | 2.5061
56 | 0.0012964 | 0.00032431 | -0.0012963 | -0.00032489 | 7.1281e-08 | -5.8392e-07 | 0.0019592 | 0.0019595 | 0.0019595 | 0.98449 | -0.29812 | 0.98443 | -0.29928 | 0.53831
57 | 0.0047394 | 0.0011871 | -0.0047378 | -0.0011872 | 1.5822e-06 | -3.2548e-08 | 0.0071631 | 0.0071635 | 0.0071635 | 0.98449 | -0.29812 | 0.98413 | -0.30513 | 1.968
58 | 0.05511 | 0.013854 | -0.055089 | -0.013841 | 2.0362e-05 | 1.2937e-05 | 0.084212 | 0.084212 | 0.084212 | 0.97396 | -0.50142 | 0.97356 | -0.50916 | 23.1352
59 | -0.057341 | -0.014413 | 0.057387 | 0.014442 | 4.525e-05 | 2.8764e-05 | 0.087621 | 0.087621 | 0.087621 | 0.97396 | -0.50142 | 0.9748 | -0.48491 | 24.0718
60 | 0.04944 | 0.012425 | -0.049431 | -0.012419 | 8.8902e-06 | 5.6381e-06 | 0.075577 | 0.075577 | 0.075577 | 0.97356 | -0.50916 | 0.97337 | -0.51293 | 20.763
61 | -0.059402 | -0.014947 | 0.059425 | 0.014962 | 2.3151e-05 | 1.4723e-05 | 0.090698 | 0.090698 | 0.090698 | 0.9748 | -0.48491 | 0.97521 | -0.47676 | 24.917
62 | 0.048278 | 0.01213 | -0.048254 | -0.012115 | 2.3863e-05 | 1.5127e-05 | 0.073815 | 0.073815 | 0.073815 | 0.97337 | -0.51293 | 0.97285 | -0.52329 | 20.2788
63 | -0.065718 | -0.016539 | 0.06574 | 0.016553 | 2.1539e-05 | 1.3714e-05 | 0.1003 | 0.1003 | 0.1003 | 0.97521 | -0.47676 | 0.97556 | -0.4699 | 27.5551
64 | 0.010781 | 0.0027026 | -0.01078 | -0.0027024 | 4.6834e-07 | 2.4271e-07 | 0.01649 | 0.01649 | 0.01649 | 0.97285 | -0.52329 | 0.9728 | -0.5242 | 4.5302
65 | -0.067969 | -0.017111 | 0.068027 | 0.017148 | 5.8156e-05 | 3.7039e-05 | 0.1037 | 0.1037 | 0.1037 | 0.97556 | -0.4699 | 0.97647 | -0.45202 | 28.489
66 | 0.01078 | 0.0027024 | -0.010779 | -0.0027016 | 1.5659e-06 | 8.1156e-07 | 0.01649 | 0.01649 | 0.01649 | 0.9728 | -0.5242 | 0.97265 | -0.52725 | 4.5302
67 | -0.069618 | -0.017547 | 0.069663 | 0.017576 | 4.5034e-05 | 2.8688e-05 | 0.10612 | 0.10612 | 0.10612 | 0.97647 | -0.45202 | 0.97716 | -0.43851 | 29.155
68 | -0.0037162 | -0.00093138 | 0.0037166 | 0.00093124 | 3.4884e-07 | -1.3305e-07 | 0.0056891 | 0.0056889 | 0.0056891 | 0.97201 | -0.54021 | 0.97211 | -0.53824 | 1.5629
69 | -0.0037166 | -0.00093124 | 0.0037169 | 0.00093111 | 3.5088e-07 | -1.3391e-07 | 0.0056889 | 0.0056888 | 0.0056889 | 0.97211 | -0.53824 | 0.97221 | -0.53625 | 1.5629
70 | -0.024165 | -0.0060608 | 0.024171 | 0.0060646 | 6.178e-06 | 3.8046e-06 | 0.036987 | 0.036987 | 0.036987 | 0.97221 | -0.53625 | 0.97248 | -0.53089 | 10.1614
71 | 0.020448 | 0.0051297 | -0.020442 | -0.005126 | 6.1506e-06 | 3.7288e-06 | 0.031299 | 0.031299 | 0.031299 | 0.97221 | -0.53625 | 0.97189 | -0.54257 | 8.5986
72 | -0.028586 | -0.0071711 | 0.028588 | 0.0071722 | 1.7266e-06 | 1.0751e-06 | 0.043743 | 0.043743 | 0.043743 | 0.97248 | -0.53089 | 0.97254 | -0.52962 | 12.0172
73 | 0.016309 | 0.0040902 | -0.016305 | -0.0040881 | 3.5626e-06 | 2.0913e-06 | 0.024971 | 0.024971 | 0.024971 | 0.97189 | -0.54257 | 0.97166 | -0.54715 | 6.8602
74 | 0.0043924 | 0.0011006 | -0.0043919 | -0.0011007 | 4.4815e-07 | -4.0298e-08 | 0.0067265 | 0.0067266 | 0.0067266 | 0.97166 | -0.54715 | 0.97155 | -0.54929 | 1.848
75 | 0.011913 | 0.0029874 | -0.011907 | -0.002984 | 6.3335e-06 | 3.4253e-06 | 0.018245 | 0.018245 | 0.018245 | 0.97166 | -0.54715 | 0.97109 | -0.55831 | 5.0123
76 | 0.0010677 | 0.00026755 | -0.0010677 | -0.00026758 | 2.5656e-09 | -3.0042e-08 | 0.0016352 | 0.0016352 | 0.0016352 | 0.97155 | -0.54929 | 0.97155 | -0.54934 | 0.44924
77 | 0.010918 | 0.0027362 | -0.010916 | -0.002735 | 2.2976e-06 | 1.1997e-06 | 0.01673 | 0.01673 | 0.01673 | 0.97109 | -0.55831 | 0.97087 | -0.56273 | 4.5961
78 | -0.031612 | -0.0079301 | 0.031631 | 0.0079418 | 1.8748e-05 | 1.1734e-05 | 0.04837 | 0.04837 | 0.04837 | 0.97254 | -0.52962 | 0.97317 | -0.51719 | 13.2884
79 | 0.0043155 | 0.0010808 | -0.0043151 | -0.0010809 | 3.56e-07 | -4.0502e-08 | 0.0066139 | 0.006614 | 0.006614 | 0.97087 | -0.56273 | 0.97078 | -0.56446 | 1.817
80 | -0.012214 | -0.0030605 | 0.012215 | 0.0030612 | 1.2024e-06 | 6.5226e-07 | 0.018552 | 0.018552 | 0.018552 | 0.9796 | -0.39162 | 0.97971 | -0.38956 | 5.0968
81 | 0.0073079 | 0.0018311 | -0.0073074 | -0.0018309 | 5.0134e-07 | 1.8428e-07 | 0.011101 | 0.011101 | 0.011101 | 0.9796 | -0.39162 | 0.97953 | -0.39306 | 3.0496
82 | -0.014624 | -0.0036651 | 0.014626 | 0.003666 | 1.5141e-06 | 8.6594e-07 | 0.022212 | 0.022212 | 0.022212 | 0.97971 | -0.38956 | 0.97982 | -0.38738 | 6.1022
83 | 0.0033156 | 0.00083045 | -0.0033155 | -0.00083056 | 1.7056e-07 | -1.1651e-07 | 0.0050367 | 0.0050367 | 0.0050367 | 0.97953 | -0.39306 | 0.97947 | -0.39414 | 1.3837
84 | -0.017038 | -0.0042704 | 0.01704 | 0.004272 | 2.5889e-06 | 1.527e-06 | 0.025875 | 0.025875 | 0.025875 | 0.97982 | -0.38738 | 0.97998 | -0.3842 | 7.1085
85 | 0.0033155 | 0.00083056 | -0.0033154 | -0.00083065 | 1.2441e-07 | -8.4965e-08 | 0.0050367 | 0.0050368 | 0.0050368 | 0.97947 | -0.39414 | 0.97943 | -0.39493 | 1.3837
86 | -0.019663 | -0.0049292 | 0.019666 | 0.0049309 | 2.7383e-06 | 1.6493e-06 | 0.029857 | 0.029857 | 0.029857 | 0.97998 | -0.3842 | 0.98013 | -0.38127 | 8.2024
87 | 0.0023855 | 0.00059759 | -0.0023854 | -0.00059777 | 9.202e-08 | -1.7623e-07 | 0.003624 | 0.0036241 | 0.0036241 | 0.97943 | -0.39493 | 0.97939 | -0.39574 | 0.99564
88 | 0.0013651 | 0.00034206 | -0.0013651 | -0.00034211 | 7.9001e-09 | -5.6579e-08 | 0.0020739 | 0.002074 | 0.002074 | 0.97939 | -0.39574 | 0.97939 | -0.39586 | 0.56977
89 | 0.0047378 | 0.0011872 | -0.0047369 | -0.0011872 | 8.9009e-07 | -1.7928e-08 | 0.0071635 | 0.0071637 | 0.0071637 | 0.98413 | -0.30513 | 0.98393 | -0.30908 | 1.968
90 | -0.076575 | -0.019308 | 0.076594 | 0.01932 | 1.9192e-05 | 1.2236e-05 | 0.11665 | 0.11665 | 0.11665 | 0.97716 | -0.43851 | 0.97743 | -0.43327 | 32.0466
91 | 0.0016762 | 0.00041948 | -0.001676 | -0.00042005 | 1.306e-07 | -5.6875e-07 | 0.002569 | 0.0025692 | 0.0025692 | 0.97078 | -0.56446 | 0.9707 | -0.5661 | 0.70583
92 | -0.035459 | -0.0089012 | 0.035465 | 0.008905 | 6.0581e-06 | 3.8089e-06 | 0.054222 | 0.054222 | 0.054222 | 0.97317 | -0.51719 | 0.97336 | -0.51361 | 14.8963
93 | -0.046135 | -0.011612 | 0.046182 | 0.011642 | 4.7235e-05 | 2.9894e-05 | 0.069412 | 0.069412 | 0.069412 | 0.98927 | -0.20524 | 0.99037 | -0.18384 | 19.0692
94 | 0.035048 | 0.0087855 | -0.035047 | -0.0087854 | 1.4451e-07 | 9.0731e-08 | 0.0529 | 0.0529 | 0.0529 | 0.98587 | -0.27087 | 0.98586 | -0.27095 | 14.5328
95 | -0.045115 | -0.011309 | 0.04513 | 0.011318 | 1.5074e-05 | 9.5366e-06 | 0.068095 | 0.068095 | 0.068095 | 0.98587 | -0.27087 | 0.98623 | -0.26386 | 18.7075
96 | 0.030061 | 0.0075358 | -0.030058 | -0.0075337 | 3.455e-06 | 2.1541e-06 | 0.045374 | 0.045374 | 0.045374 | 0.98586 | -0.27095 | 0.98574 | -0.27337 | 12.4654
97 | -0.045781 | -0.011481 | 0.045843 | 0.011521 | 6.2075e-05 | 3.9285e-05 | 0.069077 | 0.069076 | 0.069077 | 0.98623 | -0.26386 | 0.98769 | -0.23545 | 18.9771
98 | 0.011622 | 0.0029132 | -0.011621 | -0.0029125 | 1.4299e-06 | 7.5724e-07 | 0.017545 | 0.017545 | 0.017545 | 0.98574 | -0.27337 | 0.98561 | -0.27595 | 4.8199
99 | -0.051044 | -0.012824 | 0.051218 | 0.012934 | 0.00017398 | 0.00011034 | 0.076912 | 0.076911 | 0.076912 | 0.98769 | -0.23545 | 0.99136 | -0.1643 | 21.1296
100 | -0.05458 | -0.013776 | 0.054626 | 0.013805 | 4.5829e-05 | 2.9096e-05 | 0.081958 | 0.081958 | 0.081958 | 0.99136 | -0.1643 | 0.99227 | -0.14679 | 22.5158
101 | 0.0033621 | 0.00084202 | -0.0033619 | -0.00084212 | 1.3904e-07 | -9.8746e-08 | 0.0050462 | 0.0050462 | 0.0050462 | 0.99136 | -0.1643 | 0.99132 | -0.16517 | 1.3863
102 | 0.0033698 | 0.0008445 | -0.0033697 | -0.00084454 | 6.6614e-08 | -3.9892e-08 | 0.005162 | 0.005162 | 0.005162 | 0.97139 | -0.55204 | 0.97137 | -0.55246 | 1.4181
103 | 0.018451 | 0.0046284 | -0.018439 | -0.0046215 | 1.1396e-05 | 6.8229e-06 | 0.028265 | 0.028265 | 0.028265 | 0.97139 | -0.55204 | 0.97074 | -0.56501 | 7.7651
104 | 0.0094904 | 0.0023788 | -0.0094891 | -0.0023781 | 1.2728e-06 | 6.1634e-07 | 0.014548 | 0.014548 | 0.014548 | 0.97074 | -0.56501 | 0.97059 | -0.56782 | 3.9966
105 | 0.0051784 | 0.0012978 | -0.005178 | -0.0012977 | 4.0757e-07 | 4.7745e-08 | 0.007939 | 0.0079391 | 0.0079391 | 0.97059 | -0.56782 | 0.97051 | -0.56948 | 2.1811
106 | -0.13056 | -0.033032 | 0.13081 | 0.03319 | 0.00024637 | 0.00015746 | 0.19757 | 0.19757 | 0.19757 | 0.9839 | -0.30758 | 0.98593 | -0.26834 | 54.2763
107 | 0.056862 | 0.014325 | -0.056815 | -0.014295 | 4.6935e-05 | 2.9824e-05 | 0.086023 | 0.086023 | 0.086023 | 0.9839 | -0.30758 | 0.98302 | -0.32486 | 23.6326
108 | 0.073698 | 0.018708 | -0.073597 | -0.018644 | 0.00010104 | 6.4393e-05 | 0.11154 | 0.11154 | 0.11154 | 0.9839 | -0.30758 | 0.98243 | -0.33612 | 30.6438
109 | -0.1335 | -0.033864 | 0.13368 | 0.033982 | 0.00018543 | 0.00011805 | 0.20162 | 0.20162 | 0.20162 | 0.98593 | -0.26834 | 0.98743 | -0.2395 | 27.6956
110 | 0.055136 | 0.013874 | -0.055111 | -0.013858 | 2.4759e-05 | 1.5726e-05 | 0.083481 | 0.083481 | 0.083481 | 0.98302 | -0.32486 | 0.98253 | -0.33426 | 22.9342
111 | 0.071178 | 0.018037 | -0.071172 | -0.018033 | 5.9389e-06 | 3.7837e-06 | 0.10788 | 0.10788 | 0.10788 | 0.98243 | -0.33612 | 0.98234 | -0.33786 | 29.6371
112 | 0.0077322 | 0.0019381 | -0.007731 | -0.0019376 | 1.2247e-06 | 4.9417e-07 | 0.011829 | 0.011829 | 0.011829 | 0.97265 | -0.52725 | 0.97248 | -0.53058 | 3.2498
113 | 0.42316 | 0.10845 | -0.4228 | -0.10822 | 0.00035792 | 0.00022857 | 0.63224 | 0.63224 | 0.63224 | 0.99727 | -0.051506 | 0.99635 | -0.068972 | 43.4228
114 | 0.42029 | 0.10759 | -0.42004 | -0.10743 | 0.00024805 | 0.0001584 | 0.62849 | 0.62849 | 0.62849 | 0.99635 | -0.068972 | 0.99571 | -0.081167 | 43.1653
115 | 0.35261 | 0.090349 | -0.35241 | -0.090223 | 0.00019737 | 0.00012592 | 0.52765 | 0.52766 | 0.52766 | 0.99571 | -0.081167 | 0.9951 | -0.092723 | 36.24
116 | 0.067429 | 0.017082 | -0.067372 | -0.017046 | 5.6314e-05 | 3.5849e-05 | 0.10083 | 0.10083 | 0.10083 | 0.99571 | -0.081167 | 0.9948 | -0.098569 | 27.7011
117 | 0.35049 | 0.089742 | -0.34995 | -0.089396 | 0.00054111 | 0.00034522 | 0.52478 | 0.52478 | 0.52478 | 0.9951 | -0.092723 | 0.99342 | -0.12465 | 36.0427
118 | 0.065603 | 0.016603 | -0.065492 | -0.016532 | 0.00011069 | 7.0444e-05 | 0.098185 | 0.098185 | 0.098185 | 0.9948 | -0.098569 | 0.99297 | -0.13379 | 26.974
119 | -0.047555 | -0.011986 | 0.047565 | 0.011993 | 1.0291e-05 | 6.5172e-06 | 0.071475 | 0.071475 | 0.071475 | 0.99037 | -0.18384 | 0.99061 | -0.17932 | 19.6359
120 | -0.048948 | -0.012339 | 0.04897 | 0.012353 | 2.2014e-05 | 1.3949e-05 | 0.073551 | 0.073551 | 0.073551 | 0.99061 | -0.17932 | 0.99109 | -0.16993 | 20.2063
121 | -0.050489 | -0.012734 | 0.050492 | 0.012736 | 2.5835e-06 | 1.638e-06 | 0.075833 | 0.075833 | 0.075833 | 0.99109 | -0.16993 | 0.99115 | -0.16886 | 20.8332
122 | -0.052236 | -0.013173 | 0.052284 | 0.013203 | 4.8401e-05 | 3.0706e-05 | 0.078451 | 0.07845 | 0.078451 | 0.99115 | -0.16886 | 0.99215 | -0.14952 | 21.5524
123 | -0.088982 | -0.022583 | 0.089016 | 0.022605 | 3.403e-05 | 2.1716e-05 | 0.13483 | 0.13483 | 0.13483 | 0.98274 | -0.32978 | 0.98316 | -0.32183 | 37.0419
124 | -0.097507 | -0.024733 | 0.09762 | 0.024805 | 0.00011306 | 7.2181e-05 | 0.14768 | 0.14768 | 0.14768 | 0.98316 | -0.32183 | 0.9844 | -0.29775 | 40.5725
125 | 0.064082 | 0.016179 | -0.064051 | -0.01616 | 3.0398e-05 | 1.9341e-05 | 0.096072 | 0.096072 | 0.096072 | 0.99297 | -0.13379 | 0.99245 | -0.14369 | 26.3934
126 | 0.062518 | 0.015775 | -0.062501 | -0.015764 | 1.744e-05 | 1.1094e-05 | 0.093774 | 0.093774 | 0.093774 | 0.99245 | -0.14369 | 0.99215 | -0.14952 | 25.762
127 | 0.010217 | 0.002561 | -0.010215 | -0.00256 | 1.8967e-06 | 9.3576e-07 | 0.015323 | 0.015323 | 0.015323 | 0.99215 | -0.14952 | 0.99195 | -0.15342 | 4.2097
128 | 0.057871 | 0.014642 | -0.05781 | -0.014603 | 6.1403e-05 | 3.9016e-05 | 0.086732 | 0.086732 | 0.086732 | 0.99342 | -0.12465 | 0.99227 | -0.14679 | 23.8276
129 | 0.29208 | 0.074754 | -0.29147 | -0.074366 | 0.00060901 | 0.00038802 | 0.43805 | 0.43805 | 0.43805 | 0.99342 | -0.12465 | 0.99116 | -0.16781 | 30.0859
130 | 0.0085728 | 0.0021485 | -0.0085726 | -0.0021484 | 1.2097e-07 | 5.2239e-08 | 0.01286 | 0.01286 | 0.01286 | 0.99195 | -0.15342 | 0.99194 | -0.15371 | 3.5329
131 | 0.28944 | 0.073857 | -0.28943 | -0.073852 | 7.6419e-06 | 4.8686e-06 | 0.435 | 0.435 | 0.435 | 0.99116 | -0.16781 | 0.99113 | -0.16836 | 29.8766
132 | -0.10496 | -0.026644 | 0.10519 | 0.026791 | 0.00022899 | 0.00014624 | 0.15878 | 0.15878 | 0.15878 | 0.9844 | -0.29775 | 0.98675 | -0.25251 | 43.6203
133 | -0.10762 | -0.027401 | 0.10763 | 0.027406 | 7.9394e-06 | 5.071e-06 | 0.16245 | 0.16245 | 0.16245 | 0.98675 | -0.25251 | 0.98683 | -0.25098 | 44.6291
134 | 0.13687 | 0.034805 | -0.13686 | -0.034796 | 1.4397e-05 | 9.0292e-06 | 0.20634 | 0.20634 | 0.20634 | 0.9879 | -0.23029 | 0.98779 | -0.23247 | 14.172
135 | -0.13924 | -0.035397 | 0.13935 | 0.035467 | 0.00011158 | 7.0025e-05 | 0.2099 | 0.2099 | 0.2099 | 0.9879 | -0.23029 | 0.98877 | -0.21366 | 14.4165
136 | 0.13498 | 0.034324 | -0.13493 | -0.034295 | 4.5664e-05 | 2.8623e-05 | 0.20351 | 0.20351 | 0.20351 | 0.98779 | -0.23247 | 0.98743 | -0.2395 | 13.9771
137 | -0.28757 | -0.073288 | 0.28782 | 0.073447 | 0.0002496 | 0.00015901 | 0.43258 | 0.43258 | 0.43258 | 0.99019 | -0.18633 | 0.99113 | -0.16836 | 29.71
138 | 0.069596 | 0.017639 | -0.069481 | -0.017565 | 0.00011536 | 7.3482e-05 | 0.10549 | 0.10549 | 0.10549 | 0.98234 | -0.33786 | 0.98056 | -0.37242 | 28.9814
139 | 0.067695 | 0.017118 | -0.067606 | -0.017061 | 8.9383e-05 | 5.6921e-05 | 0.10278 | 0.10278 | 0.10278 | 0.98056 | -0.37242 | 0.97915 | -0.39999 | 28.2372
140 | 0.064814 | 0.016361 | -0.064801 | -0.016353 | 1.3458e-05 | 8.5664e-06 | 0.098541 | 0.098541 | 0.098541 | 0.97915 | -0.39999 | 0.97893 | -0.40432 | 27.0717
141 | 0.061137 | 0.015434 | -0.061074 | -0.015394 | 6.3125e-05 | 4.0155e-05 | 0.092972 | 0.092972 | 0.092972 | 0.97893 | -0.40432 | 0.97782 | -0.4259 | 25.5417
142 | 0.0059511 | 0.0014914 | -0.0059496 | -0.0014911 | 1.5712e-06 | 3.2716e-07 | 0.0089274 | 0.0089276 | 0.0089276 | 0.99194 | -0.15371 | 0.99165 | -0.15926 | 2.4526
143 | 0.057046 | 0.014384 | -0.057043 | -0.014383 | 2.9235e-06 | 1.8581e-06 | 0.086841 | 0.086841 | 0.086841 | 0.97782 | -0.4259 | 0.97777 | -0.42697 | 23.8575
144 | 0.053244 | 0.013431 | -0.053198 | -0.013402 | 4.562e-05 | 2.8965e-05 | 0.08106 | 0.08106 | 0.08106 | 0.97777 | -0.42697 | 0.97685 | -0.44488 | 22.2694
145 | 0.046184 | 0.011644 | -0.046159 | -0.011628 | 2.4757e-05 | 1.5678e-05 | 0.070376 | 0.070376 | 0.070376 | 0.97685 | -0.44488 | 0.97628 | -0.45609 | 19.3341
146 | -0.035465 | -0.008905 | 0.035477 | 0.0089125 | 1.2038e-05 | 7.5683e-06 | 0.054222 | 0.054222 | 0.054222 | 0.97336 | -0.51361 | 0.97372 | -0.5065 | 14.8963
147 | -0.03878 | -0.0097405 | 0.038804 | 0.0097556 | 2.3977e-05 | 1.5119e-05 | 0.059271 | 0.059271 | 0.059271 | 0.97372 | -0.5065 | 0.97437 | -0.49355 | 16.2832
148 | 0.0017652 | 0.00044194 | -0.0017651 | -0.00044236 | 1.0056e-07 | -4.281e-07 | 0.0026494 | 0.0026496 | 0.0026496 | 0.99132 | -0.16517 | 0.99126 | -0.16637 | 0.72791
149 | 0.04253 | 0.010718 | -0.042501 | -0.0107 | 2.9539e-05 | 1.8671e-05 | 0.064845 | 0.064845 | 0.064845 | 0.97628 | -0.45609 | 0.97554 | -0.47062 | 17.8145
150 | -0.042454 | -0.01067 | 0.042501 | 0.0107 | 4.6535e-05 | 2.9414e-05 | 0.064845 | 0.064845 | 0.064845 | 0.97437 | -0.49355 | 0.97554 | -0.47062 | 17.8145

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43188 | 0.11063

## res_load
| p_mw | q_mvar
0 | 0.0042154 | 0.0010565
1 | 0.0033615 | 0.00084247
2 | 0.0042724 | 0.0010708
3 | 0.0045739 | 0.0011463
4 | 0.0032634 | 0.00081787
5 | 0.0026209 | 0.00065686
6 | 0.001675 | 0.0004198
7 | 0.0030669 | 0.00076863
8 | 0.0026282 | 0.0006587
9 | 0.0013672 | 0.00034265
10 | 0.0016782 | 0.00042059
11 | 0.001522 | 0.00038144
12 | 0.0015197 | 0.00038088
13 | 0.0031518 | 0.00078992
14 | 0.0016871 | 0.00042284
15 | 0.0016268 | 0.00040772
16 | 0.0014193 | 0.0003557
17 | 0.0014749 | 0.00036965
18 | 0.0018572 | 0.00046545
19 | 0.0021721 | 0.00054437
20 | 0.01993 | 0.0049948
21 | 0.0033521 | 0.00084011
22 | 0.0080728 | 0.0020232
23 | 0.00097793 | 0.00024509
24 | 0.0016328 | 0.00040921
25 | 0.0018848 | 0.00047237
26 | 0.0019619 | 0.00049169
27 | 0.004474 | 0.0011213
28 | 0.0016761 | 0.00042006
29 | 0.0021131 | 0.0005296
30 | 0.002746 | 0.00068821
31 | 0.0038662 | 0.00096896
32 | 0.0019749 | 0.00049495
33 | 0.0038548 | 0.0009661
34 | 0.0052079 | 0.0013052
35 | 0.0019636 | 0.00049212
36 | 0.0022417 | 0.00056183
37 | 0.0022316 | 0.0005593
38 | 0.0056494 | 0.0014159
39 | 0.0020154 | 0.00050511
40 | 0.0011529 | 0.00028894
41 | 0.0062933 | 0.0015773
42 | 0.0022287 | 0.00055857
43 | 0.0015909 | 0.00039873
44 | 0.0037162 | 0.00093138
45 | 0.0044149 | 0.0011065
46 | 0.004133 | 0.0010358
47 | 0.0033242 | 0.00083313
48 | 0.00098879 | 0.00024781
49 | 0.0030241 | 0.00075792
50 | 0.0010677 | 0.00026758
51 | 0.0066001 | 0.0016542
52 | 0.0049056 | 0.0012295
53 | 0.0024096 | 0.00060391
54 | 0.0039918 | 0.0010004
55 | 0.0024119 | 0.00060447
56 | 0.0026225 | 0.00065725
57 | 0.0009299 | 0.00023305
58 | 0.002604 | 0.00065262
59 | 0.0010203 | 0.00025571
60 | 0.0012963 | 0.00032489
61 | 0.0047369 | 0.0011872
62 | 0.006912 | 0.0017323
63 | 0.002272 | 0.00056942
64 | 0.002639 | 0.00066139
65 | 0.001676 | 0.00042005
66 | 0.0038278 | 0.00095934
67 | 0.0041599 | 0.0010426
68 | 0.001833 | 0.0004594
69 | 0.010068 | 0.0025232
70 | 0.0049859 | 0.0012496
71 | 0.00065024 | 0.00016297
72 | 0.018436 | 0.0046204
73 | 0.0052009 | 0.0013035
74 | 0.011621 | 0.0029125
75 | 0.004726 | 0.0011844
76 | 0.0033697 | 0.00084454
77 | 0.0089488 | 0.0022428
78 | 0.0043107 | 0.0010804
79 | 0.005178 | 0.0012977
80 | 0.002689 | 0.00067393
81 | 0.0016793 | 0.00042088
82 | 0.0024193 | 0.00060633
83 | 0.0030464 | 0.00076351
84 | 0.0029574 | 0.00074119
85 | 0.0025108 | 0.00062926
86 | 0.0019216 | 0.0004816
87 | 0.0017696 | 0.0004435
88 | 0.0013731 | 0.00034413
89 | 0.0013821 | 0.00034638
90 | 0.0015199 | 0.00038092
91 | 0.0017438 | 0.00043703
92 | 0.008491 | 0.0021281
93 | 0.007731 | 0.0019376
94 | 0.0014104 | 0.00035347
95 | 0.0015329 | 0.00038419
96 | 0.0016421 | 0.00041156
97 | 0.0031841 | 0.000798
98 | 0.0020302 | 0.00050882
99 | 0.0015247 | 0.00038212
100 | 0.0073394 | 0.0018394
101 | 0.0024351 | 0.00061029
102 | 0.0023633 | 0.0005923
103 | 0.0018838 | 0.00047212
104 | 0.0021196 | 0.00053123
105 | 0.0012495 | 0.00031316
106 | 0.0082821 | 0.0020757
107 | 0.001261 | 0.00031604
108 | 0.0016159 | 0.00040498
109 | 0.0015758 | 0.00039493
110 | 0.0017851 | 0.0004474
111 | 0.0027916 | 0.00069964
112 | 0.0036638 | 0.00091824
113 | 0.0026215 | 0.00065701
114 | 0.0059496 | 0.0014911
115 | 0.0040285 | 0.0010096
116 | 0.0037987 | 0.00095205
117 | 0.0070142 | 0.0017579
118 | 0.0033035 | 0.00082793
119 | 0.0013651 | 0.00034211
120 | 0.0015968 | 0.00040019
121 | 0.0017651 | 0.00044236
122 | 0.003629 | 0.00090952
123 | 0.0036501 | 0.00091481

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1