## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2601-40_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2601-40_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2601-40_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2601-40_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2601-40_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2601-40_0_4_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_2601-40_0_4_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_2601-40_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2601-40_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2601-40_0_4_node_40 | 0.4 | n |  | TRUE
10 | bus_LV_2601-40_0_4_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_2601-40_0_4_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2601-40_0_4_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_2601-40_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2601-40_0_4_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_2601-40_0_4_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_2601-40_0_4_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_2601-40_0_4_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_2601-40_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2601-40_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2601-40_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2601-40_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2601-40_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2601-40_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2601-40_0_4_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_2601-40_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_2601-40_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2601-40_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2601-40_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2601-40_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2601-40_0_4_node_50 | 0.4 | n |  | TRUE
31 | bus_LV_2601-40_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_2601-40_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_2601-40_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2601-40_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_2601-40_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2601-40_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2601-40_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2601-40_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2601-40_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_2601-40_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2601-40_0_4_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_2601-40_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2601-40_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_2601-40_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_2601-40_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_2601-40_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_2601-40_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_MV_393_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2601-40_0_4_load_0 | 0 | 0.012393 | 0.0031059 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2601-40_0_4_load_1 | 1 | 0.023857 | 0.0059791 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2601-40_0_4_load_4 | 4 | 0.0023623 | 0.00059205 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2601-40_0_4_load_19 | 6 | 0.023644 | 0.0059258 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2601-40_0_4_load_16 | 7 | 0.0013858 | 0.00034731 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2601-40_0_4_load_49 | 10 | 0.024325 | 0.0060964 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2601-40_0_4_load_33 | 11 | 0.023824 | 0.0059709 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2601-40_0_4_load_15 | 13 | 0.0042356 | 0.0010615 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2601-40_0_4_load_39 | 15 | 0.011121 | 0.0027871 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2601-40_0_4_load_6 | 17 | 0.00085792 | 0.00021501 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2601-40_0_4_load_7 | 18 | 0.0038798 | 0.00097237 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2601-40_0_4_load_8 | 19 | 0.00088751 | 0.00022243 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2601-40_0_4_load_9 | 20 | 0.008408 | 0.0021072 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2601-40_0_4_load_10 | 21 | 0.01797 | 0.0045038 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2601-40_0_4_load_20 | 22 | 0.0044487 | 0.001115 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2601-40_0_4_load_11 | 25 | 0.0013456 | 0.00033724 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2601-40_0_4_load_12 | 26 | 0.0019091 | 0.00047846 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2601-40_0_4_load_14 | 27 | 0.0016079 | 0.00040298 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2601-40_0_4_load_22 | 28 | 0.010295 | 0.0025801 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2601-40_0_4_load_50 | 30 | 0.0040336 | 0.0010109 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2601-40_0_4_load_38 | 32 | 0.012296 | 0.0030818 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2601-40_0_4_load_24 | 33 | 0.030395 | 0.0076177 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2601-40_0_4_load_41 | 34 | 0.01219 | 0.0030551 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2601-40_0_4_load_25 | 35 | 0.022982 | 0.0057598 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2601-40_0_4_load_31 | 39 | 0.022605 | 0.0056654 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2601-40_0_4_load_34 | 40 | 0.028298 | 0.0070922 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2601-40_0_4_load_48 | 41 | 0.089362 | 0.022396 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2601-40_0_4_load_35 | 43 | 0.0022745 | 0.00057004 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2601-40_0_4_load_47 | 45 | 0.0093092 | 0.0023331 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2601-40_0_4_load_42 | 47 | 0.030323 | 0.0075997 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2601-40_0_4_line_0 |  | 0 | 1 | 0.021395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2601-40_0_4_line_1 |  | 0 | 2 | 0.0072824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2601-40_0_4_line_2 |  | 1 | 3 | 0.015687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2601-40_0_4_line_3 |  | 2 | 4 | 0.0098797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2601-40_0_4_line_4 |  | 3 | 5 | 0.029927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2601-40_0_4_line_5 |  | 3 | 6 | 0.035227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2601-40_0_4_line_6 |  | 4 | 7 | 0.0082837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2601-40_0_4_line_7 |  | 5 | 11 | 0.044219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2601-40_0_4_line_8 |  | 6 | 12 | 0.014467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2601-40_0_4_line_9 |  | 7 | 13 | 0.020151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2601-40_0_4_line_10 |  | 8 | 9 | 0.011428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2601-40_0_4_line_11 |  | 8 | 10 | 0.0067299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2601-40_0_4_line_12 |  | 9 | 14 | 0.024408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2601-40_0_4_line_13 |  | 9 | 15 | 0.019012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2601-40_0_4_line_14 |  | 10 | 16 | 0.011723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2601-40_0_4_line_15 |  | 11 | 31 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_2601-40_0_4_line_16 |  | 12 | 32 | 0.033788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2601-40_0_4_line_17 |  | 14 | 45 | 0.016448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2601-40_0_4_line_18 |  | 16 | 41 | 0.018359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2601-40_0_4_line_19 |  | 17 | 18 | 0.019606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2601-40_0_4_line_20 |  | 17 | 19 | 0.031658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2601-40_0_4_line_21 |  | 18 | 20 | 0.023377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2601-40_0_4_line_22 |  | 19 | 21 | 0.029084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2601-40_0_4_line_23 |  | 20 | 22 | 0.022081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2601-40_0_4_line_24 |  | 21 | 23 | 0.025568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2601-40_0_4_line_25 |  | 23 | 24 | 0.053895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2601-40_0_4_line_26 |  | 24 | 30 | 0.026668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2601-40_0_4_line_27 |  | 25 | 26 | 0.0053901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2601-40_0_4_line_28 |  | 26 | 27 | 0.0061577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2601-40_0_4_line_29 |  | 27 | 28 | 0.010122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2601-40_0_4_line_30 |  | 28 | 29 | 0.013296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2601-40_0_4_line_31 |  | 29 | 33 | 0.0021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2601-40_0_4_line_32 |  | 30 | 44 | 0.018848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2601-40_0_4_line_33 |  | 31 | 40 | 0.024537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2601-40_0_4_line_34 |  | 31 | 36 | 0.006017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2601-40_0_4_line_35 |  | 32 | 34 | 0.019398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2601-40_0_4_line_36 |  | 33 | 34 | 0.026788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2601-40_0_4_line_37 |  | 35 | 36 | 0.040344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2601-40_0_4_line_38 |  | 35 | 37 | 0.031593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2601-40_0_4_line_39 |  | 36 | 38 | 0.033617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2601-40_0_4_line_40 |  | 37 | 39 | 0.01135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2601-40_0_4_line_41 |  | 38 | 41 | 0.015912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2601-40_0_4_line_42 |  | 39 | 42 | 0.02735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2601-40_0_4_line_43 |  | 40 | 44 | 0.0062254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2601-40_0_4_line_44 |  | 42 | 43 | 0.042736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2601-40_0_4_line_45 |  | 44 | 46 | 0.020955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2601-40_0_4_line_46 |  | 46 | 47 | 0.0019377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2601-40_0_4_trafo_48 | 0.63 MVA 20/0.4 kV | 48 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2607896.7314 | 1227866.8891 | 2607912.205 | 1227881.6644
1 | 2607891.4645 | 1227861.8599 | 2607896.7314 | 1227866.8891
2 | 2607923.5508 | 1227892.498 | 2607912.205 | 1227881.6644
3 | 2607891.4645 | 1227861.8599 | 2607884.319 | 1227855.0371
4 | 2607945.1633 | 1227913.2611 | 2607923.5508 | 1227892.498
5 | 2607923.5508 | 1227892.498 | 2607947.1812 | 1227866.3719
6 | 2607884.319 | 1227855.0371 | 2607878.3277 | 1227849.3165
7 | 2607945.1633 | 1227913.2611 | 2607902.0595 | 1227923.1271
8 | 2607956.8856 | 1227855.6426 | 2607947.1812 | 1227866.3719
9 | 2607878.3277 | 1227849.3165 | 2607863.7536 | 1227835.4006
10 | 2607841.9262 | 1227872.9904 | 2607830.7467 | 1227875.5106
11 | 2607841.9262 | 1227872.9904 | 2607842.1521 | 1227874.0691 | 2607843.3092 | 1227879.5767
12 | 2607830.7467 | 1227875.5106 | 2607806.8644 | 1227880.8715
13 | 2607830.7467 | 1227875.5106 | 2607826.3799 | 1227857.0066
14 | 2607845.7138 | 1227891.0504 | 2607844.4488 | 1227885.0008 | 2607843.3092 | 1227879.5767
15 | 2607884.8928 | 1227927.0564 | 2607902.0595 | 1227923.1271
16 | 2607956.8856 | 1227855.6426 | 2607934.756 | 1227830.454 | 2607934.6165 | 1227830.2358
17 | 2607806.8644 | 1227880.8715 | 2607803.3753 | 1227864.798
18 | 2607845.7138 | 1227891.0504 | 2607849.4855 | 1227909.0181
19 | 2607812.0539 | 1228031.8755 | 2607807.9112 | 1228031.3062 | 2607792.7691 | 1228028.3707
20 | 2607812.0539 | 1228031.8755 | 2607817.3048 | 1228032.597 | 2607822.7599 | 1228032.8153 | 2607829.0412 | 1228032.7124 | 2607835.5959 | 1228032.1984 | 2607842.3934 | 1228031.329 | 2607843.5575 | 1228031.0895
21 | 2607792.7691 | 1228028.3707 | 2607769.8189 | 1228023.9215
22 | 2607871.5973 | 1228023.4816 | 2607862.198 | 1228026.5632 | 2607852.4355 | 1228029.2631 | 2607843.5575 | 1228031.0895
23 | 2607748.1413 | 1228019.719 | 2607769.8189 | 1228023.9215
24 | 2607895.8917 | 1228015.512 | 2607877.093 | 1228021.6799 | 2607871.5973 | 1228023.4816
25 | 2607895.8917 | 1228015.512 | 2607929.3638 | 1228000.2694 | 2607926.2281 | 1227993.6947 | 2607917.7257 | 1227988.7583
26 | 2607917.7257 | 1227988.7583 | 2607904.7149 | 1227983.9494 | 2607897.4849 | 1227979.4484 | 2607896.3674 | 1227975.3162
27 | 2607882.6424 | 1227799.2087 | 2607877.6089 | 1227801.1367
28 | 2607882.6424 | 1227799.2087 | 2607888.3927 | 1227797.0063
29 | 2607888.3927 | 1227797.0063 | 2607897.8453 | 1227793.3858
30 | 2607910.2613 | 1227788.6303 | 2607897.8453 | 1227793.3858
31 | 2607910.2613 | 1227788.6303 | 2607911.1224 | 1227790.5807
32 | 2607891.8242 | 1227957.0277 | 2607894.2125 | 1227967.348 | 2607896.3674 | 1227975.3162
33 | 2607884.8928 | 1227927.0564 | 2607890.4214 | 1227950.9623
34 | 2607884.8928 | 1227927.0564 | 2607879.0037 | 1227928.3717
35 | 2607924.1649 | 1227813.8943 | 2607934.6165 | 1227830.2358
36 | 2607924.1649 | 1227813.8943 | 2607915.2851 | 1227800.0103 | 2607911.1224 | 1227790.5807
37 | 2607879.0037 | 1227928.3717 | 2607839.6302 | 1227937.1678
38 | 2607808.7977 | 1227944.0558 | 2607839.6302 | 1227937.1678
39 | 2607852.7544 | 1227924.5906 | 2607876.6362 | 1227919.4855 | 2607879.0037 | 1227928.3717
40 | 2607808.7977 | 1227944.0558 | 2607797.7211 | 1227946.5326
41 | 2607852.7544 | 1227924.5906 | 2607849.4855 | 1227909.0181
42 | 2607771.0307 | 1227952.5007 | 2607797.7211 | 1227946.5326
43 | 2607891.8242 | 1227957.0277 | 2607890.4214 | 1227950.9623
44 | 2607729.8051 | 1227963.7652 | 2607734.6949 | 1227961.6702 | 2607741.7373 | 1227959.0444 | 2607771.0307 | 1227952.5007
45 | 2607912.4012 | 1227952.7634 | 2607908.4904 | 1227953.5698 | 2607901.1918 | 1227955.0833 | 2607891.8242 | 1227957.0277
46 | 2607912.4012 | 1227952.7634 | 2607914.2984 | 1227952.3694

## bus_geodata
| x | y | coords
0 | 2607896.7314 | 1227866.8891
1 | 2607912.205 | 1227881.6644
2 | 2607891.4645 | 1227861.8599
3 | 2607923.5508 | 1227892.498
4 | 2607884.319 | 1227855.0371
5 | 2607945.1633 | 1227913.2611
6 | 2607947.1812 | 1227866.3719
7 | 2607878.3277 | 1227849.3165
8 | 2607841.9262 | 1227872.9904
9 | 2607830.7467 | 1227875.5106
10 | 2607843.3092 | 1227879.5767
11 | 2607902.0595 | 1227923.1271
12 | 2607956.8856 | 1227855.6426
13 | 2607863.7536 | 1227835.4006
14 | 2607806.8644 | 1227880.8715
15 | 2607826.3799 | 1227857.0066
16 | 2607845.7138 | 1227891.0504
17 | 2607812.0539 | 1228031.8755
18 | 2607792.7691 | 1228028.3707
19 | 2607843.5575 | 1228031.0895
20 | 2607769.8189 | 1228023.9215
21 | 2607871.5973 | 1228023.4816
22 | 2607748.1413 | 1228019.719
23 | 2607895.8917 | 1228015.512
24 | 2607917.7257 | 1227988.7583
25 | 2607877.6089 | 1227801.1367
26 | 2607882.6424 | 1227799.2087
27 | 2607888.3927 | 1227797.0063
28 | 2607897.8453 | 1227793.3858
29 | 2607910.2613 | 1227788.6303
30 | 2607896.3674 | 1227975.3162
31 | 2607884.8928 | 1227927.0564
32 | 2607934.6165 | 1227830.2358
33 | 2607911.1224 | 1227790.5807
34 | 2607924.1649 | 1227813.8943
35 | 2607839.6302 | 1227937.1678
36 | 2607879.0037 | 1227928.3717
37 | 2607808.7977 | 1227944.0558
38 | 2607852.7544 | 1227924.5906
39 | 2607797.7211 | 1227946.5326
40 | 2607890.4214 | 1227950.9623
41 | 2607849.4855 | 1227909.0181
42 | 2607771.0307 | 1227952.5007
43 | 2607729.8051 | 1227963.7652
44 | 2607891.8242 | 1227957.0277
45 | 2607803.3753 | 1227864.798
46 | 2607912.4012 | 1227952.7634
47 | 2607914.2984 | 1227952.3694
48 | 2607852.7544 | 1227924.5906

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98299 | -0.32627 | 0.012393 | 0.0031059
1 | 0.98339 | -0.3184 | 0.023857 | 0.0059791
2 | 0.98294 | -0.32731 | 0 | 0
3 | 0.98403 | -0.30591 | 0 | 0
4 | 0.98286 | -0.32874 | 0.0023623 | 0.00059205
5 | 0.98785 | -0.2319 | 0 | 0
6 | 0.98097 | -0.3655 | 0.023644 | 0.0059258
7 | 0.98282 | -0.32958 | 0.0013858 | 0.00034731
8 | 0.99865 | -0.025899 | 0 | 0
9 | 0.99844 | -0.029981 | 0 | 0
10 | 0.99878 | -0.023496 | 0.024325 | 0.0060964
11 | 0.99351 | -0.12359 | 0.023824 | 0.0059709
12 | 0.98003 | -0.38387 | 0 | 0
13 | 0.98274 | -0.33112 | 0.0042356 | 0.0010615
14 | 0.99823 | -0.033954 | 0 | 0
15 | 0.99825 | -0.033678 | 0.011121 | 0.0027871
16 | 0.99925 | -0.014333 | 0 | 0
17 | 0.98693 | -0.25114 | 0.00085792 | 0.00021501
18 | 0.98663 | -0.25701 | 0.0038798 | 0.00097237
19 | 0.98745 | -0.24118 | 0.00088751 | 0.00022243
20 | 0.98636 | -0.2624 | 0.008408 | 0.0021072
21 | 0.98794 | -0.23157 | 0.01797 | 0.0045038
22 | 0.98627 | -0.26416 | 0.0044487 | 0.001115
23 | 0.9888 | -0.21494 | 0 | 0
24 | 0.9906 | -0.17998 | 0 | 0
25 | 0.97537 | -0.47535 | 0.0013456 | 0.00033724
26 | 0.97537 | -0.47522 | 0.0019091 | 0.00047846
27 | 0.97539 | -0.47485 | 0.0016079 | 0.00040298
28 | 0.97544 | -0.47395 | 0.010295 | 0.0025801
29 | 0.97562 | -0.47026 | 0 | 0
30 | 0.99149 | -0.16272 | 0.0040336 | 0.0010109
31 | 0.99483 | -0.09847 | 0 | 0
32 | 0.97783 | -0.42691 | 0.012296 | 0.0030818
33 | 0.97565 | -0.46967 | 0.030395 | 0.0076177
34 | 0.97679 | -0.44735 | 0.01219 | 0.0030551
35 | 0.99354 | -0.1233 | 0.022982 | 0.0057598
36 | 0.99531 | -0.08926 | 0 | 0
37 | 0.99283 | -0.13719 | 0 | 0
38 | 0.99849 | -0.028585 | 0 | 0
39 | 0.99257 | -0.14218 | 0.022605 | 0.0056654
40 | 0.9926 | -0.1414 | 0.028298 | 0.0070922
41 | 1 | 0 | -0.3592 | -0.091184
42 | 0.99251 | -0.14328 | 0 | 0
43 | 0.99242 | -0.145 | 0.0022745 | 0.00057004
44 | 0.99219 | -0.1492 | 0 | 0
45 | 0.9981 | -0.036633 | 0.0093092 | 0.0023331
46 | 0.99161 | -0.16046 | 0 | 0
47 | 0.99156 | -0.1615 | 0.030323 | 0.0075997
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.020378 | -0.0051072 | 0.020385 | 0.0051118 | 7.6344e-06 | 4.6147e-06 | 0.030847 | 0.030847 | 0.030847 | 0.98299 | -0.32627 | 0.98339 | -0.3184 | 8.4745
1 | 0.0079852 | 0.0020013 | -0.0079848 | -0.0020011 | 3.9902e-07 | 1.6306e-07 | 0.012088 | 0.012088 | 0.012088 | 0.98299 | -0.32627 | 0.98294 | -0.32731 | 3.3208
2 | -0.044242 | -0.011091 | 0.044269 | 0.011108 | 2.6365e-05 | 1.6675e-05 | 0.066946 | 0.066946 | 0.066946 | 0.98339 | -0.3184 | 0.98403 | -0.30591 | 18.3918
3 | 0.0079848 | 0.0020011 | -0.0079842 | -0.0020009 | 5.4133e-07 | 2.2123e-07 | 0.012088 | 0.012088 | 0.012088 | 0.98294 | -0.32731 | 0.98286 | -0.32874 | 3.3208
4 | -0.13853 | -0.034958 | 0.13903 | 0.035273 | 0.0004929 | 0.00031508 | 0.20957 | 0.20957 | 0.20957 | 0.98403 | -0.30591 | 0.98785 | -0.2319 | 57.5749
5 | 0.094266 | 0.02385 | -0.093998 | -0.023679 | 0.00026873 | 0.00017154 | 0.14263 | 0.14263 | 0.14263 | 0.98403 | -0.30591 | 0.98097 | -0.3655 | 39.1832
6 | 0.0056219 | 0.0014088 | -0.0056217 | -0.0014088 | 2.2504e-07 | 3.9044e-08 | 0.0085113 | 0.0085114 | 0.0085114 | 0.98286 | -0.32874 | 0.98282 | -0.32958 | 2.3383
7 | -0.13903 | -0.035273 | 0.13976 | 0.035738 | 0.00072829 | 0.00046553 | 0.20957 | 0.20957 | 0.20957 | 0.98785 | -0.2319 | 0.99351 | -0.12359 | 57.5748
8 | 0.070353 | 0.017753 | -0.070291 | -0.017714 | 6.1835e-05 | 3.9392e-05 | 0.10676 | 0.10676 | 0.10676 | 0.98097 | -0.3655 | 0.98003 | -0.38387 | 29.33
9 | 0.0042359 | 0.0010615 | -0.0042356 | -0.0010615 | 3.108e-07 | -5.6424e-08 | 0.0064132 | 0.0064133 | 0.0064133 | 0.98282 | -0.32958 | 0.98274 | -0.33112 | 1.7619
10 | 0.020439 | 0.005125 | -0.020435 | -0.0051226 | 3.9749e-06 | 2.3944e-06 | 0.030455 | 0.030455 | 0.030455 | 0.99865 | -0.025899 | 0.99844 | -0.029981 | 8.3668
11 | -0.020439 | -0.005125 | 0.020441 | 0.0051264 | 2.3408e-06 | 1.4101e-06 | 0.030455 | 0.030455 | 0.030455 | 0.99865 | -0.025899 | 0.99878 | -0.023496 | 8.3668
12 | 0.0093121 | 0.0023344 | -0.0093103 | -0.0023336 | 1.763e-06 | 8.0916e-07 | 0.013878 | 0.013879 | 0.013879 | 0.99844 | -0.029981 | 0.99823 | -0.033954 | 3.8128
13 | 0.011123 | 0.0027881 | -0.011121 | -0.0027871 | 1.9592e-06 | 1.0053e-06 | 0.016577 | 0.016577 | 0.016577 | 0.99844 | -0.029981 | 0.99825 | -0.033678 | 4.5541
14 | -0.044766 | -0.011223 | 0.044786 | 0.011235 | 1.9555e-05 | 1.2362e-05 | 0.066695 | 0.066695 | 0.066695 | 0.99878 | -0.023496 | 0.99925 | -0.014333 | 18.3229
15 | -0.16358 | -0.041709 | 0.16378 | 0.041836 | 0.00019861 | 0.00012666 | 0.24525 | 0.24525 | 0.24525 | 0.99351 | -0.12359 | 0.99483 | -0.09847 | 33.6888
16 | 0.070291 | 0.017714 | -0.070147 | -0.017622 | 0.00014442 | 9.2002e-05 | 0.10676 | 0.10676 | 0.10676 | 0.98003 | -0.38387 | 0.97783 | -0.42691 | 29.33
17 | 0.0093103 | 0.0023336 | -0.0093092 | -0.0023331 | 1.188e-06 | 5.4535e-07 | 0.013879 | 0.013879 | 0.013879 | 0.99823 | -0.033954 | 0.9981 | -0.036633 | 3.8128
18 | -0.044786 | -0.011235 | 0.044816 | 0.011255 | 3.0625e-05 | 1.9359e-05 | 0.066695 | 0.066695 | 0.066695 | 0.99925 | -0.014333 | 1 | 0 | 18.3229
19 | 0.016745 | 0.0041991 | -0.01674 | -0.0041963 | 4.6865e-06 | 2.7489e-06 | 0.025247 | 0.025247 | 0.025247 | 0.98693 | -0.25114 | 0.98663 | -0.25701 | 6.9361
20 | -0.017603 | -0.0044141 | 0.017611 | 0.0044191 | 8.3626e-06 | 4.9473e-06 | 0.026541 | 0.026541 | 0.026541 | 0.98693 | -0.25114 | 0.98745 | -0.24118 | 7.2915
21 | 0.01286 | 0.003224 | -0.012857 | -0.0032222 | 3.2981e-06 | 1.8123e-06 | 0.019396 | 0.019396 | 0.019396 | 0.98663 | -0.25701 | 0.98636 | -0.2624 | 5.3286
22 | -0.018499 | -0.0046415 | 0.018507 | 0.0046465 | 8.4765e-06 | 5.0527e-06 | 0.027878 | 0.027878 | 0.027878 | 0.98745 | -0.24118 | 0.98794 | -0.23157 | 7.6588
23 | 0.0044491 | 0.0011149 | -0.0044487 | -0.001115 | 3.7303e-07 | -4.3073e-08 | 0.0067118 | 0.0067119 | 0.0067119 | 0.98636 | -0.2624 | 0.98627 | -0.26416 | 1.8439
24 | -0.036478 | -0.0091503 | 0.036506 | 0.0091685 | 2.8946e-05 | 1.8198e-05 | 0.054945 | 0.054945 | 0.054945 | 0.98794 | -0.23157 | 0.9888 | -0.21494 | 15.0947
25 | -0.036506 | -0.0091685 | 0.036567 | 0.0092069 | 6.1014e-05 | 3.8356e-05 | 0.054945 | 0.054944 | 0.054945 | 0.9888 | -0.21494 | 0.9906 | -0.17998 | 15.0947
26 | -0.036567 | -0.0092069 | 0.036598 | 0.0092259 | 3.0191e-05 | 1.8978e-05 | 0.054944 | 0.054944 | 0.054944 | 0.9906 | -0.17998 | 0.99149 | -0.16272 | 15.0946
27 | -0.0013456 | -0.00033724 | 0.0013456 | 0.00033717 | 8.5179e-09 | -6.1823e-08 | 0.0020528 | 0.0020528 | 0.0020528 | 0.97537 | -0.47535 | 0.97537 | -0.47522 | 0.56396
28 | -0.0032547 | -0.00081563 | 0.0032547 | 0.00081559 | 5.6928e-08 | -4.0422e-08 | 0.0049652 | 0.0049652 | 0.0049652 | 0.97537 | -0.47522 | 0.97539 | -0.47485 | 1.3641
29 | -0.0048626 | -0.0012186 | 0.0048628 | 0.0012186 | 2.0888e-07 | 7.3371e-09 | 0.0074182 | 0.0074181 | 0.0074182 | 0.97539 | -0.47485 | 0.97544 | -0.47395 | 2.038
30 | -0.015158 | -0.0037987 | 0.01516 | 0.0038002 | 2.6657e-06 | 1.5401e-06 | 0.023123 | 0.023123 | 0.023123 | 0.97544 | -0.47395 | 0.97562 | -0.47026 | 6.3524
31 | -0.01516 | -0.0038002 | 0.015161 | 0.0038005 | 4.2747e-07 | 2.4696e-07 | 0.023123 | 0.023123 | 0.023123 | 0.97562 | -0.47026 | 0.97565 | -0.46967 | 6.3523
32 | -0.040631 | -0.010237 | 0.040658 | 0.010253 | 2.6297e-05 | 1.6587e-05 | 0.060998 | 0.060998 | 0.060998 | 0.99149 | -0.16272 | 0.99219 | -0.1492 | 16.7576
33 | 0.099527 | 0.025104 | -0.099323 | -0.024973 | 0.00020407 | 0.00013029 | 0.14893 | 0.14893 | 0.14893 | 0.99483 | -0.09847 | 0.9926 | -0.1414 | 40.9135
34 | -0.26331 | -0.06694 | 0.26342 | 0.067014 | 0.00011686 | 7.4558e-05 | 0.39418 | 0.39418 | 0.39418 | 0.99483 | -0.09847 | 0.99531 | -0.08926 | 36.097
35 | 0.05785 | 0.01454 | -0.057794 | -0.014504 | 5.6394e-05 | 3.5849e-05 | 0.088049 | 0.088049 | 0.088049 | 0.97783 | -0.42691 | 0.97679 | -0.44735 | 24.1893
36 | -0.045556 | -0.011418 | 0.045604 | 0.011449 | 4.8494e-05 | 3.0701e-05 | 0.069479 | 0.069479 | 0.069479 | 0.97565 | -0.46967 | 0.97679 | -0.44735 | 19.0878
37 | -0.047884 | -0.012008 | 0.047962 | 0.012058 | 7.7816e-05 | 4.9279e-05 | 0.071718 | 0.071718 | 0.071718 | 0.99354 | -0.1233 | 0.99531 | -0.08926 | 19.7028
38 | 0.024902 | 0.0062485 | -0.024886 | -0.0062384 | 1.6482e-05 | 1.014e-05 | 0.037299 | 0.037299 | 0.037299 | 0.99354 | -0.1233 | 0.99283 | -0.13719 | 10.2469
39 | -0.31139 | -0.079072 | 0.3123 | 0.079654 | 0.00091212 | 0.00058244 | 0.4659 | 0.4659 | 0.4659 | 0.99531 | -0.08926 | 0.99849 | -0.028585 | 42.6645
40 | 0.024886 | 0.0062384 | -0.02488 | -0.0062348 | 5.9213e-06 | 3.6429e-06 | 0.037299 | 0.037299 | 0.037299 | 0.99283 | -0.13719 | 0.99257 | -0.14218 | 10.2469
41 | -0.3123 | -0.079654 | 0.31273 | 0.07993 | 0.00043173 | 0.00027568 | 0.4659 | 0.4659 | 0.4659 | 0.99849 | -0.028585 | 1 | 0 | 42.6645
42 | 0.0022748 | 0.00056933 | -0.0022747 | -0.0005696 | 1.1926e-07 | -2.7715e-07 | 0.00341 | 0.0034101 | 0.0034101 | 0.99257 | -0.14218 | 0.99251 | -0.14328 | 0.93684
43 | 0.071025 | 0.017881 | -0.070999 | -0.017864 | 2.6481e-05 | 1.6867e-05 | 0.1065 | 0.1065 | 0.1065 | 0.9926 | -0.1414 | 0.99219 | -0.1492 | 29.2591
44 | 0.0022747 | 0.0005696 | -0.0022745 | -0.00057004 | 1.8637e-07 | -4.3297e-07 | 0.0034101 | 0.0034103 | 0.0034103 | 0.99251 | -0.14328 | 0.99242 | -0.145 | 0.93689
45 | 0.030341 | 0.0076108 | -0.030325 | -0.0076007 | 1.6272e-05 | 1.0144e-05 | 0.045505 | 0.045506 | 0.045506 | 0.99219 | -0.1492 | 0.99161 | -0.16046 | 12.5015
46 | 0.030325 | 0.0076007 | -0.030323 | -0.0075997 | 1.5047e-06 | 9.3799e-07 | 0.045506 | 0.045506 | 0.045506 | 0.99161 | -0.16046 | 0.99156 | -0.1615 | 12.5015

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44856 | 0.11358

## res_load
| p_mw | q_mvar
0 | 0.012393 | 0.0031059
1 | 0.023857 | 0.0059791
2 | 0.0023623 | 0.00059205
3 | 0.023644 | 0.0059258
4 | 0.0013858 | 0.00034731
5 | 0.024325 | 0.0060964
6 | 0.023824 | 0.0059709
7 | 0.0042356 | 0.0010615
8 | 0.011121 | 0.0027871
9 | 0.00085792 | 0.00021501
10 | 0.0038798 | 0.00097237
11 | 0.00088751 | 0.00022243
12 | 0.008408 | 0.0021072
13 | 0.01797 | 0.0045038
14 | 0.0044487 | 0.001115
15 | 0.0013456 | 0.00033724
16 | 0.0019091 | 0.00047846
17 | 0.0016079 | 0.00040298
18 | 0.010295 | 0.0025801
19 | 0.0040336 | 0.0010109
20 | 0.012296 | 0.0030818
21 | 0.030395 | 0.0076177
22 | 0.01219 | 0.0030551
23 | 0.022982 | 0.0057598
24 | 0.022605 | 0.0056654
25 | 0.028298 | 0.0070922
26 | 0.089362 | 0.022396
27 | 0.0022745 | 0.00057004
28 | 0.0093092 | 0.0023331
29 | 0.030323 | 0.0075997

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1