## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2601-59_1_4_node_2 | 0.4 | n |  | TRUE
1 | bus_LV_2601-59_1_4_node_15 | 0.4 | n |  | TRUE
2 | bus_LV_2601-59_1_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2601-59_1_4_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_2601-59_1_4_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_2601-59_1_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2601-59_1_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_2601-59_1_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2601-59_1_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2601-59_1_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2601-59_1_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2601-59_1_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2601-59_1_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2601-59_1_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2601-59_1_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2601-59_1_4_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_2601-59_1_4_node_56 | 0.4 | n |  | TRUE
17 | bus_LV_2601-59_1_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2601-59_1_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2601-59_1_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2601-59_1_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_2601-59_1_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_2601-59_1_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2601-59_1_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_2601-59_1_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_2601-59_1_4_node_24 | 0.4 | n |  | TRUE
26 | bus_MV_395_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2601-59_1_4_load_19 | 3 | 0.022394 | 0.0056125 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2601-59_1_4_load_30 | 4 | 0.0018587 | 0.00046583 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2601-59_1_4_load_29 | 6 | 0.0018372 | 0.00046043 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2601-59_1_4_load_5 | 7 | 0.062283 | 0.01561 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2601-59_1_4_load_6 | 8 | 0.054089 | 0.013556 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2601-59_1_4_load_8 | 10 | 0.0095222 | 0.0023865 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2601-59_1_4_load_9 | 11 | 0.0011519 | 0.00028868 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2601-59_1_4_load_18 | 13 | 0.070988 | 0.017791 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2601-59_1_4_load_22 | 15 | 0.0010812 | 0.00027098 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2601-59_1_4_load_56 | 16 | 0.0055483 | 0.0013905 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2601-59_1_4_load_12 | 17 | 0.010414 | 0.00261 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2601-59_1_4_load_31 | 21 | 0.010165 | 0.0025476 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2601-59_1_4_load_20 | 22 | 0.036495 | 0.0091465 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2601-59_1_4_load_21 | 23 | 0.070189 | 0.017591 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2601-59_1_4_load_23 | 24 | 0.0056177 | 0.0014079 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2601-59_1_4_load_24 | 25 | 0.010288 | 0.0025785 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2601-59_1_4_line_0 |  | 0 | 1 | 0.044387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2601-59_1_4_line_1 |  | 0 | 2 | 0.053365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2601-59_1_4_line_2 |  | 0 | 3 | 0.05239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2601-59_1_4_line_3 |  | 1 | 21 | 0.02565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2601-59_1_4_line_4 |  | 2 | 4 | 0.024986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2601-59_1_4_line_5 |  | 3 | 22 | 0.039251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2601-59_1_4_line_6 |  | 4 | 5 | 0.044564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2601-59_1_4_line_7 |  | 5 | 6 | 0.041071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2601-59_1_4_line_8 |  | 7 | 8 | 0.011249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2601-59_1_4_line_9 |  | 7 | 9 | 0.038612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2601-59_1_4_line_10 |  | 8 | 10 | 0.014594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2601-59_1_4_line_11 |  | 9 | 11 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2601-59_1_4_line_12 |  | 9 | 12 | 0.087969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2601-59_1_4_line_13 |  | 10 | 13 | 0.012386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2601-59_1_4_line_14 |  | 12 | 14 | 0.012898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2601-59_1_4_line_15 |  | 12 | 15 | 0.040675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2601-59_1_4_line_16 |  | 13 | 19 | 0.057826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_2601-59_1_4_line_17 |  | 14 | 16 | 0.028493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2601-59_1_4_line_18 |  | 15 | 24 | 0.004307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2601-59_1_4_line_19 |  | 17 | 18 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2601-59_1_4_line_20 |  | 17 | 19 | 0.016388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2601-59_1_4_line_21 |  | 18 | 20 | 0.025653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2601-59_1_4_line_22 |  | 20 | 21 | 0.021817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2601-59_1_4_line_23 |  | 22 | 23 | 0.0082165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2601-59_1_4_line_24 |  | 24 | 25 | 0.028265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2601-59_1_4_trafo_18 | 0.63 MVA 20/0.4 kV | 26 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2606873.8742 | 1228468.0779 | 2606867.399 | 1228479.166 | 2606895.4525 | 1228493.5956
1 | 2606831.1291 | 1228461.0917 | 2606858.8428 | 1228474.7647 | 2606867.399 | 1228479.166 | 2606873.8742 | 1228468.0779
2 | 2606873.8742 | 1228468.0779 | 2606877.6362 | 1228464.4912 | 2606911.7096 | 1228431.8399
3 | 2606895.4525 | 1228493.5956 | 2606901.7464 | 1228501.9744 | 2606912.8676 | 1228512.2925
4 | 2606831.1291 | 1228461.0917 | 2606823.1025 | 1228477.3478 | 2606822.9009 | 1228481.4055 | 2606820.1652 | 1228481.9694
5 | 2606911.7096 | 1228431.8399 | 2606940.0496 | 1228404.6826
6 | 2606802.9138 | 1228515.6475 | 2606802.0338 | 1228503.2837 | 2606804.4644 | 1228497.7943 | 2606810.2955 | 1228493.4539 | 2606816.7822 | 1228492.1827 | 2606820.0721 | 1228490.6077 | 2606820.1652 | 1228481.9694
7 | 2606802.9138 | 1228515.6475 | 2606812.4311 | 1228514.2575 | 2606818.4983 | 1228515.4762 | 2606826.3822 | 1228518.109 | 2606832.6566 | 1228516.9043 | 2606838.7275 | 1228514.8989 | 2606842.5705 | 1228513.2801
8 | 2607031.902 | 1228427.6777 | 2607024.0962 | 1228435.7779
9 | 2607058.6949 | 1228399.8742 | 2607031.902 | 1228427.6777
10 | 2607013.97 | 1228446.2866 | 2607017.141 | 1228442.9954 | 2607024.0962 | 1228435.7779
11 | 2607058.6949 | 1228399.8742 | 2607049.1492 | 1228389.7949
12 | 2607018.638 | 1228335.5669 | 2607038.3347 | 1228356.747 | 2607068.6776 | 1228389.5131 | 2607058.6949 | 1228399.8742
13 | 2607005.3762 | 1228455.206 | 2607013.97 | 1228446.2866
14 | 2607018.638 | 1228335.5669 | 2607027.9297 | 1228326.5947
15 | 2607018.638 | 1228335.5669 | 2606998.2414 | 1228355.6995 | 2606996.2773 | 1228357.2426 | 2606994.3137 | 1228358.3632 | 2606991.9641 | 1228359.1275 | 2606989.4635 | 1228359.4471 | 2606987.1982 | 1228359.3999
16 | 2606964.8402 | 1228496.444 | 2606998.7158 | 1228462.1186 | 2607005.3762 | 1228455.206
17 | 2607008.1108 | 1228306.0705 | 2607027.9297 | 1228326.5947
18 | 2606983.2679 | 1228357.7722 | 2606985.2137 | 1228358.9418 | 2606987.1982 | 1228359.3999
19 | 2606936.7655 | 1228520.1477 | 2606938.8035 | 1228520.1612 | 2606940.9027 | 1228519.6856 | 2606942.722 | 1228518.7871 | 2606944.3676 | 1228517.4549 | 2606953.4038 | 1228508.1811
20 | 2606964.8402 | 1228496.444 | 2606953.4038 | 1228508.1811
21 | 2606936.7655 | 1228520.1477 | 2606933.0382 | 1228526.5139 | 2606924.5605 | 1228533.0524 | 2606929.0299 | 1228526.9428
22 | 2606929.0299 | 1228526.9428 | 2606923.4745 | 1228522.1336 | 2606912.8676 | 1228512.2925
23 | 2606945.982 | 1228398.9978 | 2606940.0496 | 1228404.6826
24 | 2606963.6749 | 1228337.4033 | 2606981.5348 | 1228356.1248 | 2606983.2679 | 1228357.7722 | 2606983.2679 | 1228357.7722

## bus_geodata
| x | y | coords
0 | 2606873.8742 | 1228468.0779
1 | 2606895.4525 | 1228493.5956
2 | 2606831.1291 | 1228461.0917
3 | 2606911.7096 | 1228431.8399
4 | 2606820.1652 | 1228481.9694
5 | 2606802.9138 | 1228515.6475
6 | 2606842.5705 | 1228513.2801
7 | 2607031.902 | 1228427.6777
8 | 2607024.0962 | 1228435.7779
9 | 2607058.6949 | 1228399.8742
10 | 2607013.97 | 1228446.2866
11 | 2607049.1492 | 1228389.7949
12 | 2607018.638 | 1228335.5669
13 | 2607005.3762 | 1228455.206
14 | 2607027.9297 | 1228326.5947
15 | 2606987.1982 | 1228359.3999
16 | 2607008.1108 | 1228306.0705
17 | 2606953.4038 | 1228508.1811
18 | 2606936.7655 | 1228520.1477
19 | 2606964.8402 | 1228496.444
20 | 2606929.0299 | 1228526.9428
21 | 2606912.8676 | 1228512.2925
22 | 2606940.0496 | 1228404.6826
23 | 2606945.982 | 1228398.9978
24 | 2606983.2679 | 1228357.7722
25 | 2606963.6749 | 1228337.4033
26 | 2606972.4961 | 1228488.6864

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98142 | -0.3535 | 0 | 0
1 | 0.98692 | -0.24744 | 0 | 0
2 | 0.98124 | -0.35708 | 0 | 0
3 | 0.9751 | -0.47667 | 0.022394 | 0.0056125
4 | 0.98115 | -0.35875 | 0.0018587 | 0.00046583
5 | 0.98107 | -0.36023 | 0 | 0
6 | 0.981 | -0.3616 | 0.0018372 | 0.00046043
7 | 0.99642 | -0.068879 | 0.062283 | 0.01561
8 | 0.9973 | -0.051915 | 0.054089 | 0.013556
9 | 0.99558 | -0.084954 | 0 | 0
10 | 0.99916 | -0.01616 | 0.0095222 | 0.0023865
11 | 0.99557 | -0.085235 | 0.0011519 | 0.00028868
12 | 0.99377 | -0.11988 | 0 | 0
13 | 1 | 0 | -0.30874 | -0.078572
14 | 0.99371 | -0.12115 | 0 | 0
15 | 0.99314 | -0.13209 | 0.0010812 | 0.00027098
16 | 0.99356 | -0.12394 | 0.0055483 | 0.0013905
17 | 0.99469 | -0.099722 | 0.010414 | 0.00261
18 | 0.99327 | -0.12656 | 0 | 0
19 | 0.99586 | -0.07761 | 0 | 0
20 | 0.99156 | -0.15901 | 0 | 0
21 | 0.99011 | -0.18669 | 0.010165 | 0.0025476
22 | 0.97119 | -0.55374 | 0.036495 | 0.0091465
23 | 0.97065 | -0.5644 | 0.070189 | 0.017591
24 | 0.99308 | -0.1333 | 0.0056177 | 0.0014079
25 | 0.99281 | -0.13844 | 0.010288 | 0.0025785
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13397 | -0.03404 | 0.13466 | 0.03448 | 0.00068793 | 0.00043971 | 0.20329 | 0.20329 | 0.20329 | 0.98142 | -0.3535 | 0.98692 | -0.24744 | 55.8502
1 | 0.003697 | 0.00092494 | -0.0036964 | -0.00092521 | 6.2867e-07 | -2.7186e-07 | 0.0056048 | 0.005605 | 0.005605 | 0.98142 | -0.3535 | 0.98124 | -0.35708 | 1.5398
2 | 0.13028 | 0.033115 | -0.12951 | -0.032624 | 0.0007678 | 0.00049074 | 0.19769 | 0.19769 | 0.19769 | 0.98142 | -0.3535 | 0.9751 | -0.47667 | 54.3105
3 | -0.13466 | -0.03448 | 0.13506 | 0.034734 | 0.00039753 | 0.00025409 | 0.20329 | 0.20329 | 0.20329 | 0.98692 | -0.24744 | 0.99011 | -0.18669 | 55.8501
4 | 0.0036964 | 0.00092521 | -0.0036961 | -0.00092534 | 2.9436e-07 | -1.2719e-07 | 0.005605 | 0.0056051 | 0.0056051 | 0.98124 | -0.35708 | 0.98115 | -0.35875 | 1.5399
5 | 0.10711 | 0.027012 | -0.10672 | -0.02676 | 0.00039356 | 0.00025139 | 0.16352 | 0.16352 | 0.16352 | 0.9751 | -0.47667 | 0.97119 | -0.55374 | 44.9221
6 | 0.0018374 | 0.00045951 | -0.0018373 | -0.00045999 | 1.2974e-07 | -4.7974e-07 | 0.0027863 | 0.0027865 | 0.0027865 | 0.98115 | -0.35875 | 0.98107 | -0.36023 | 0.76551
7 | 0.0018373 | 0.00045999 | -0.0018372 | -0.00046043 | 1.1959e-07 | -4.4205e-07 | 0.0027865 | 0.0027866 | 0.0027866 | 0.98107 | -0.36023 | 0.981 | -0.3616 | 0.76556
8 | -0.08604 | -0.021588 | 0.08611 | 0.021632 | 6.9655e-05 | 4.4432e-05 | 0.1285 | 0.1285 | 0.1285 | 0.99642 | -0.068879 | 0.9973 | -0.051915 | 35.3018
9 | 0.023758 | 0.0059783 | -0.023739 | -0.0059671 | 1.8235e-05 | 1.1168e-05 | 0.035487 | 0.035487 | 0.035487 | 0.99642 | -0.068879 | 0.99558 | -0.084954 | 9.7493
10 | -0.1402 | -0.035188 | 0.14044 | 0.035341 | 0.00023951 | 0.0001531 | 0.2092 | 0.2092 | 0.2092 | 0.9973 | -0.051915 | 0.99916 | -0.01616 | 57.4732
11 | 0.0011519 | 0.00028851 | -0.0011519 | -0.00028868 | 1.5429e-08 | -1.7064e-07 | 0.0017216 | 0.0017216 | 0.0017216 | 0.99558 | -0.084954 | 0.99557 | -0.085235 | 0.47297
12 | 0.022587 | 0.0056786 | -0.02255 | -0.0056556 | 3.7612e-05 | 2.293e-05 | 0.033766 | 0.033766 | 0.033766 | 0.99558 | -0.084954 | 0.99377 | -0.11988 | 9.2765
13 | -0.14996 | -0.037728 | 0.15008 | 0.037802 | 0.00011589 | 7.3842e-05 | 0.22338 | 0.22338 | 0.22338 | 0.99916 | -0.01616 | 1 | 0 | 30.6846
14 | 0.0055493 | 0.0013907 | -0.005549 | -0.0013906 | 3.3395e-07 | 4.6626e-08 | 0.0083092 | 0.0083093 | 0.0083093 | 0.99377 | -0.11988 | 0.99371 | -0.12115 | 2.2828
15 | 0.017001 | 0.004265 | -0.016991 | -0.0042592 | 9.8851e-06 | 5.7998e-06 | 0.025457 | 0.025457 | 0.025457 | 0.99377 | -0.11988 | 0.99314 | -0.13209 | 6.9938
16 | 0.15702 | 0.04077 | -0.15642 | -0.040391 | 0.00059444 | 0.00037893 | 0.23415 | 0.23415 | 0.23415 | 1 | 0 | 0.99586 | -0.07761 | 32.1633
17 | 0.005549 | 0.0013906 | -0.0055483 | -0.0013905 | 7.3774e-07 | 1.0309e-07 | 0.0083093 | 0.0083094 | 0.0083094 | 0.99371 | -0.12115 | 0.99356 | -0.12394 | 2.2828
18 | 0.015909 | 0.0039882 | -0.015908 | -0.0039877 | 9.1773e-07 | 5.3162e-07 | 0.023837 | 0.023837 | 0.023837 | 0.99314 | -0.13209 | 0.99308 | -0.1333 | 6.5487
19 | 0.14584 | 0.037674 | -0.14565 | -0.037552 | 0.00019066 | 0.00012147 | 0.21857 | 0.21857 | 0.21857 | 0.99469 | -0.099722 | 0.99327 | -0.12656 | 30.0234
20 | -0.15625 | -0.040284 | 0.15642 | 0.040391 | 0.00016846 | 0.00010739 | 0.23415 | 0.23415 | 0.23415 | 0.99469 | -0.099722 | 0.99586 | -0.07761 | 32.1634
21 | 0.14565 | 0.037552 | -0.14542 | -0.037406 | 0.00022979 | 0.0001464 | 0.21857 | 0.21857 | 0.21857 | 0.99327 | -0.12656 | 0.99156 | -0.15901 | 30.0235
22 | 0.14542 | 0.037406 | -0.14522 | -0.037281 | 0.00019542 | 0.00012451 | 0.21857 | 0.21857 | 0.21857 | 0.99156 | -0.15901 | 0.99011 | -0.18669 | 30.0235
23 | 0.070225 | 0.017614 | -0.070189 | -0.017591 | 3.5673e-05 | 2.2729e-05 | 0.1076 | 0.1076 | 0.1076 | 0.97119 | -0.55374 | 0.97065 | -0.5644 | 29.5605
24 | 0.010291 | 0.0025797 | -0.010288 | -0.0025785 | 2.5203e-06 | 1.2474e-06 | 0.01542 | 0.01542 | 0.01542 | 0.99308 | -0.1333 | 0.99281 | -0.13844 | 4.2363

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37973 | 0.096363

## res_load
| p_mw | q_mvar
0 | 0.022394 | 0.0056125
1 | 0.0018587 | 0.00046583
2 | 0.0018372 | 0.00046043
3 | 0.062283 | 0.01561
4 | 0.054089 | 0.013556
5 | 0.0095222 | 0.0023865
6 | 0.0011519 | 0.00028868
7 | 0.070988 | 0.017791
8 | 0.0010812 | 0.00027098
9 | 0.0055483 | 0.0013905
10 | 0.010414 | 0.00261
11 | 0.010165 | 0.0025476
12 | 0.036495 | 0.0091465
13 | 0.070189 | 0.017591
14 | 0.0056177 | 0.0014079
15 | 0.010288 | 0.0025785

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1