## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_261-101_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_261-101_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_261-101_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_261-101_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_261-101_0_5_node_19 | 0.4 | n |  | TRUE
5 | bus_LV_261-101_0_5_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_261-101_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_261-101_0_5_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_261-101_0_5_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_261-101_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_261-101_0_5_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_261-101_0_5_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_261-101_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_261-101_0_5_node_144 | 0.4 | n |  | TRUE
14 | bus_LV_261-101_0_5_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_261-101_0_5_node_142 | 0.4 | n |  | TRUE
16 | bus_LV_261-101_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_261-101_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_261-101_0_5_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_261-101_0_5_node_143 | 0.4 | n |  | TRUE
20 | bus_LV_261-101_0_5_node_125 | 0.4 | n |  | TRUE
21 | bus_LV_261-101_0_5_node_137 | 0.4 | n |  | TRUE
22 | bus_LV_261-101_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_261-101_0_5_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_261-101_0_5_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_261-101_0_5_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_261-101_0_5_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_261-101_0_5_node_74 | 0.4 | n |  | TRUE
28 | bus_LV_261-101_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_261-101_0_5_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_261-101_0_5_node_140 | 0.4 | n |  | TRUE
31 | bus_LV_261-101_0_5_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_261-101_0_5_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_261-101_0_5_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_261-101_0_5_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_261-101_0_5_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_261-101_0_5_node_129 | 0.4 | n |  | TRUE
37 | bus_LV_261-101_0_5_node_141 | 0.4 | n |  | TRUE
38 | bus_LV_261-101_0_5_node_96 | 0.4 | n |  | TRUE
39 | bus_LV_261-101_0_5_node_148 | 0.4 | n |  | TRUE
40 | bus_LV_261-101_0_5_node_120 | 0.4 | n |  | TRUE
41 | bus_LV_261-101_0_5_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_261-101_0_5_node_128 | 0.4 | n |  | TRUE
43 | bus_LV_261-101_0_5_node_138 | 0.4 | n |  | TRUE
44 | bus_LV_261-101_0_5_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_261-101_0_5_node_76 | 0.4 | n |  | TRUE
46 | bus_LV_261-101_0_5_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_261-101_0_5_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_261-101_0_5_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_261-101_0_5_node_98 | 0.4 | n |  | TRUE
50 | bus_LV_261-101_0_5_node_95 | 0.4 | n |  | TRUE
51 | bus_LV_261-101_0_5_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_261-101_0_5_node_70 | 0.4 | n |  | TRUE
53 | bus_LV_261-101_0_5_node_139 | 0.4 | n |  | TRUE
54 | bus_LV_261-101_0_5_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_261-101_0_5_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_261-101_0_5_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_261-101_0_5_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_261-101_0_5_node_29 | 0.4 | n |  | TRUE
59 | bus_LV_261-101_0_5_node_149 | 0.4 | n |  | TRUE
60 | bus_LV_261-101_0_5_node_121 | 0.4 | n |  | TRUE
61 | bus_LV_261-101_0_5_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_261-101_0_5_node_136 | 0.4 | n |  | TRUE
63 | bus_LV_261-101_0_5_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_261-101_0_5_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_261-101_0_5_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_261-101_0_5_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_261-101_0_5_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_261-101_0_5_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_261-101_0_5_node_147 | 0.4 | n |  | TRUE
70 | bus_LV_261-101_0_5_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_261-101_0_5_node_145 | 0.4 | n |  | TRUE
72 | bus_LV_261-101_0_5_node_101 | 0.4 | n |  | TRUE
73 | bus_LV_261-101_0_5_node_117 | 0.4 | n |  | TRUE
74 | bus_LV_261-101_0_5_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_261-101_0_5_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_261-101_0_5_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_261-101_0_5_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_261-101_0_5_node_37 | 0.4 | n |  | TRUE
79 | bus_LV_261-101_0_5_node_146 | 0.4 | n |  | TRUE
80 | bus_LV_261-101_0_5_node_32 | 0.4 | n |  | TRUE
81 | bus_LV_261-101_0_5_node_33 | 0.4 | n |  | TRUE
82 | bus_LV_261-101_0_5_node_35 | 0.4 | n |  | TRUE
83 | bus_LV_261-101_0_5_node_36 | 0.4 | n |  | TRUE
84 | bus_LV_261-101_0_5_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_261-101_0_5_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_261-101_0_5_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_261-101_0_5_node_41 | 0.4 | n |  | TRUE
88 | bus_LV_261-101_0_5_node_55 | 0.4 | n |  | TRUE
89 | bus_LV_261-101_0_5_node_53 | 0.4 | n |  | TRUE
90 | bus_LV_261-101_0_5_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_261-101_0_5_node_45 | 0.4 | n |  | TRUE
92 | bus_LV_261-101_0_5_node_50 | 0.4 | n |  | TRUE
93 | bus_LV_261-101_0_5_node_52 | 0.4 | n |  | TRUE
94 | bus_LV_261-101_0_5_node_54 | 0.4 | n |  | TRUE
95 | bus_LV_261-101_0_5_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_261-101_0_5_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_261-101_0_5_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_261-101_0_5_node_61 | 0.4 | n |  | TRUE
99 | bus_LV_261-101_0_5_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_261-101_0_5_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_261-101_0_5_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_261-101_0_5_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_261-101_0_5_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_261-101_0_5_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_261-101_0_5_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_261-101_0_5_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_261-101_0_5_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_261-101_0_5_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_261-101_0_5_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_261-101_0_5_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_261-101_0_5_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_261-101_0_5_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_261-101_0_5_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_261-101_0_5_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_261-101_0_5_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_261-101_0_5_node_105 | 0.4 | n |  | TRUE
117 | bus_LV_261-101_0_5_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_261-101_0_5_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_261-101_0_5_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_261-101_0_5_node_104 | 0.4 | n |  | TRUE
121 | bus_LV_261-101_0_5_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_261-101_0_5_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_261-101_0_5_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_261-101_0_5_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_261-101_0_5_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_261-101_0_5_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_261-101_0_5_node_111 | 0.4 | n |  | TRUE
128 | bus_LV_261-101_0_5_node_123 | 0.4 | n |  | TRUE
129 | bus_LV_261-101_0_5_node_122 | 0.4 | n |  | TRUE
130 | bus_LV_261-101_0_5_node_114 | 0.4 | n |  | TRUE
131 | bus_LV_261-101_0_5_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_261-101_0_5_node_127 | 0.4 | n |  | TRUE
133 | bus_LV_261-101_0_5_node_118 | 0.4 | n |  | TRUE
134 | bus_LV_261-101_0_5_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_261-101_0_5_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_261-101_0_5_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_261-101_0_5_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_261-101_0_5_node_130 | 0.4 | n |  | TRUE
139 | bus_LV_261-101_0_5_node_131 | 0.4 | n |  | TRUE
140 | bus_LV_261-101_0_5_node_133 | 0.4 | n |  | TRUE
141 | bus_LV_261-101_0_5_node_150 | 0.4 | n |  | TRUE
142 | bus_MV_524_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_261-101_0_5_load_0 | 0 | 0.0025021 | 0.00062709 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_261-101_0_5_load_1 | 1 | 0.0045848 | 0.0011491 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_261-101_0_5_load_3 | 3 | 0.0042219 | 0.0010581 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_261-101_0_5_load_28 | 5 | 0.0046777 | 0.0011723 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_261-101_0_5_load_51 | 7 | 0.0038184 | 0.00095699 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_261-101_0_5_load_144 | 13 | 0.0089098 | 0.002233 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_261-101_0_5_load_142 | 15 | 0.0031168 | 0.00078115 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_261-101_0_5_load_143 | 19 | 0.0043234 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_261-101_0_5_load_125 | 20 | 0.003877 | 0.00097167 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_261-101_0_5_load_137 | 21 | 0.012548 | 0.0031448 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_261-101_0_5_load_65 | 24 | 0.0027706 | 0.00069437 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_261-101_0_5_load_63 | 25 | 0.0057534 | 0.0014419 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_261-101_0_5_load_74 | 27 | 0.0056009 | 0.0014037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_261-101_0_5_load_64 | 29 | 0.0057675 | 0.0014455 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_261-101_0_5_load_140 | 30 | 0.006284 | 0.0015749 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_261-101_0_5_load_67 | 32 | 0.0081954 | 0.002054 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_261-101_0_5_load_39 | 35 | 0.0045979 | 0.0011523 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_261-101_0_5_load_129 | 36 | 0.0080635 | 0.0020209 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_261-101_0_5_load_141 | 37 | 0.007998 | 0.0020045 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_261-101_0_5_load_96 | 38 | 0.0024877 | 0.00062347 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_261-101_0_5_load_148 | 39 | 0.0063936 | 0.0016024 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_261-101_0_5_load_120 | 40 | 0.0051571 | 0.0012925 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_261-101_0_5_load_128 | 42 | 0.0032979 | 0.00082653 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_261-101_0_5_load_138 | 43 | 0.0079368 | 0.0019892 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_261-101_0_5_load_75 | 46 | 0.0053395 | 0.0013382 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_261-101_0_5_load_97 | 48 | 0.0020973 | 0.00052564 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_261-101_0_5_load_98 | 49 | 0.0010356 | 0.00025955 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_261-101_0_5_load_95 | 50 | 0.0059383 | 0.0014883 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_261-101_0_5_load_139 | 53 | 0.0028196 | 0.00070666 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_261-101_0_5_load_48 | 54 | 0.0048346 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_261-101_0_5_load_49 | 55 | 0.0046654 | 0.0011693 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_261-101_0_5_load_29 | 58 | 0.0058706 | 0.0014713 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_261-101_0_5_load_149 | 59 | 0.019935 | 0.0049962 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_261-101_0_5_load_121 | 60 | 0.0058933 | 0.001477 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_261-101_0_5_load_136 | 62 | 0.0044974 | 0.0011272 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_261-101_0_5_load_66 | 63 | 0.0063266 | 0.0015856 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_261-101_0_5_load_68 | 65 | 0.0080413 | 0.0020153 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_261-101_0_5_load_44 | 66 | 0.0048137 | 0.0012064 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_261-101_0_5_load_38 | 67 | 0.0042192 | 0.0010574 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_261-101_0_5_load_147 | 69 | 0.0066316 | 0.001662 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_261-101_0_5_load_78 | 70 | 0.0051596 | 0.0012931 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_261-101_0_5_load_145 | 71 | 0.0065411 | 0.0016394 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_261-101_0_5_load_117 | 73 | 0.0014776 | 0.00037032 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_261-101_0_5_load_47 | 74 | 0.0047475 | 0.0011898 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_261-101_0_5_load_46 | 75 | 0.0031829 | 0.00079771 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_261-101_0_5_load_71 | 76 | 0.0085714 | 0.0021482 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_261-101_0_5_load_69 | 77 | 0.0078082 | 0.0019569 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_261-101_0_5_load_37 | 78 | 0.0049245 | 0.0012342 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_261-101_0_5_load_146 | 79 | 0.0052147 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_261-101_0_5_load_32 | 80 | 0.0045832 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_261-101_0_5_load_33 | 81 | 0.0046544 | 0.0011665 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_261-101_0_5_load_35 | 82 | 0.0042837 | 0.0010736 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_261-101_0_5_load_36 | 83 | 0.004295 | 0.0010764 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_261-101_0_5_load_56 | 85 | 0.004668 | 0.0011699 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_261-101_0_5_load_72 | 86 | 0.005427 | 0.0013601 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_261-101_0_5_load_41 | 87 | 0.0046755 | 0.0011718 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_261-101_0_5_load_55 | 88 | 0.0046307 | 0.0011606 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_261-101_0_5_load_53 | 89 | 0.0042688 | 0.0010699 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_261-101_0_5_load_77 | 90 | 0.0023184 | 0.00058105 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_261-101_0_5_load_45 | 91 | 0.0045204 | 0.0011329 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_261-101_0_5_load_50 | 92 | 0.0055904 | 0.0014011 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_261-101_0_5_load_52 | 93 | 0.0046759 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_261-101_0_5_load_54 | 94 | 0.0043064 | 0.0010793 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_261-101_0_5_load_57 | 95 | 0.0069823 | 0.0017499 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_261-101_0_5_load_58 | 96 | 0.0073865 | 0.0018512 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_261-101_0_5_load_61 | 98 | 0.0075594 | 0.0018946 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_261-101_0_5_load_79 | 99 | 0.0018493 | 0.00046347 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_261-101_0_5_load_80 | 100 | 0.0020621 | 0.00051682 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_261-101_0_5_load_81 | 101 | 0.0018304 | 0.00045874 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_261-101_0_5_load_82 | 102 | 0.002121 | 0.00053157 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_261-101_0_5_load_83 | 103 | 0.0018621 | 0.00046668 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_261-101_0_5_load_86 | 104 | 0.0020609 | 0.00051651 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_261-101_0_5_load_87 | 105 | 0.0019809 | 0.00049645 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_261-101_0_5_load_88 | 108 | 0.0024277 | 0.00060845 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_261-101_0_5_load_89 | 109 | 0.0012647 | 0.00031695 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_261-101_0_5_load_90 | 110 | 0.0034451 | 0.00086342 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_261-101_0_5_load_91 | 111 | 0.0017789 | 0.00044583 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_261-101_0_5_load_99 | 112 | 0.0016208 | 0.00040621 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_261-101_0_5_load_94 | 113 | 0.0019081 | 0.00047822 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_261-101_0_5_load_106 | 114 | 0.0020588 | 0.00051599 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_261-101_0_5_load_100 | 115 | 0.0034091 | 0.0008544 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_261-101_0_5_load_105 | 116 | 0.0021621 | 0.00054188 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_261-101_0_5_load_116 | 118 | 0.0009832 | 0.00024641 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_261-101_0_5_load_112 | 119 | 0.0024589 | 0.00061626 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_261-101_0_5_load_104 | 120 | 0.0021483 | 0.00053841 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_261-101_0_5_load_113 | 121 | 0.0010182 | 0.00025517 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_261-101_0_5_load_103 | 122 | 0.0021064 | 0.0005279 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_261-101_0_5_load_107 | 123 | 0.0032786 | 0.00082168 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_261-101_0_5_load_108 | 124 | 0.0012501 | 0.0003133 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_261-101_0_5_load_109 | 125 | 0.0015582 | 0.00039051 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_261-101_0_5_load_110 | 126 | 0.0020347 | 0.00050993 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_261-101_0_5_load_111 | 127 | 0.00299 | 0.00074938 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_261-101_0_5_load_123 | 128 | 0.0026012 | 0.00065191 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_261-101_0_5_load_122 | 129 | 0.0043589 | 0.0010924 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_261-101_0_5_load_114 | 130 | 0.00097306 | 0.00024387 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_261-101_0_5_load_115 | 131 | 0.0015861 | 0.00039751 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_261-101_0_5_load_127 | 132 | 0.0064223 | 0.0016096 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_261-101_0_5_load_118 | 133 | 0.001073 | 0.00026892 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_261-101_0_5_load_119 | 134 | 0.0034473 | 0.00086399 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_261-101_0_5_load_126 | 135 | 0.010928 | 0.0027389 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_261-101_0_5_load_130 | 138 | 0.0063102 | 0.0015815 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_261-101_0_5_load_131 | 139 | 0.015961 | 0.0040003 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_261-101_0_5_load_133 | 140 | 0.0064762 | 0.0016231 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_261-101_0_5_load_150 | 141 | 0.022841 | 0.0057246 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_261-101_0_5_line_0 |  | 0 | 1 | 0.02467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_261-101_0_5_line_1 |  | 0 | 2 | 0.018372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_261-101_0_5_line_2 |  | 1 | 3 | 0.015721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_261-101_0_5_line_3 |  | 2 | 4 | 0.029806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_261-101_0_5_line_4 |  | 3 | 5 | 0.015831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_261-101_0_5_line_5 |  | 4 | 38 | 0.007336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_261-101_0_5_line_6 |  | 5 | 9 | 0.0089591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_261-101_0_5_line_7 |  | 6 | 7 | 0.034654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_261-101_0_5_line_8 |  | 6 | 8 | 0.0047677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_261-101_0_5_line_9 |  | 7 | 31 | 0.0061839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_261-101_0_5_line_10 |  | 8 | 14 | 0.012199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_261-101_0_5_line_11 |  | 8 | 36 | 0.016139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_261-101_0_5_line_12 |  | 9 | 10 | 0.009216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_261-101_0_5_line_13 |  | 9 | 11 | 0.011823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_261-101_0_5_line_14 |  | 10 | 37 | 0.041647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_261-101_0_5_line_15 |  | 10 | 33 | 0.010594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_261-101_0_5_line_16 |  | 11 | 40 | 0.019091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_261-101_0_5_line_17 |  | 12 | 13 | 0.025118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_261-101_0_5_line_18 |  | 12 | 14 | 0.005505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_261-101_0_5_line_19 |  | 12 | 15 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_261-101_0_5_line_20 |  | 13 | 59 | 0.0019671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_261-101_0_5_line_21 |  | 14 | 43 | 0.043295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_261-101_0_5_line_22 |  | 15 | 17 | 0.022532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_261-101_0_5_line_23 |  | 16 | 17 | 0.011245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_261-101_0_5_line_24 |  | 16 | 18 | 0.013654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_261-101_0_5_line_25 |  | 16 | 19 | 0.0097064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_261-101_0_5_line_26 |  | 17 | 20 | 0.034229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_261-101_0_5_line_27 |  | 17 | 21 | 0.03957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_261-101_0_5_line_28 |  | 18 | 41 | 0.027929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_261-101_0_5_line_29 |  | 18 | 42 | 0.0014952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_261-101_0_5_line_30 |  | 19 | 60 | 0.034347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_261-101_0_5_line_31 |  | 20 | 61 | 0.017879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_261-101_0_5_line_32 |  | 21 | 62 | 0.0023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_261-101_0_5_line_33 |  | 22 | 23 | 0.022706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_261-101_0_5_line_34 |  | 22 | 24 | 0.012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_261-101_0_5_line_35 |  | 22 | 25 | 0.014525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_261-101_0_5_line_36 |  | 23 | 63 | 0.02026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_261-101_0_5_line_37 |  | 24 | 45 | 0.021546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_261-101_0_5_line_38 |  | 25 | 29 | 0.015969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_261-101_0_5_line_39 |  | 26 | 27 | 0.017093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_261-101_0_5_line_40 |  | 26 | 28 | 0.03993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_261-101_0_5_line_41 |  | 26 | 29 | 0.026756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_261-101_0_5_line_42 |  | 26 | 30 | 0.019192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_261-101_0_5_line_43 |  | 27 | 64 | 0.011378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_261-101_0_5_line_44 |  | 28 | 39 | 0.056328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_261-101_0_5_line_45 |  | 30 | 53 | 0.013533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_261-101_0_5_line_46 |  | 31 | 32 | 0.012327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_261-101_0_5_line_47 |  | 32 | 65 | 0.018287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_261-101_0_5_line_48 |  | 33 | 34 | 0.003541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_261-101_0_5_line_49 |  | 33 | 35 | 0.023663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_261-101_0_5_line_50 |  | 34 | 66 | 0.021765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_261-101_0_5_line_51 |  | 34 | 67 | 0.017987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_261-101_0_5_line_52 |  | 35 | 68 | 0.027179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_261-101_0_5_line_53 |  | 38 | 50 | 0.022778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_261-101_0_5_line_54 |  | 39 | 69 | 0.013981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_261-101_0_5_line_55 |  | 41 | 70 | 0.014134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_261-101_0_5_line_56 |  | 44 | 45 | 0.032661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_261-101_0_5_line_57 |  | 44 | 46 | 0.017161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_261-101_0_5_line_58 |  | 45 | 71 | 0.01923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_261-101_0_5_line_59 |  | 47 | 48 | 0.039678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_261-101_0_5_line_60 |  | 47 | 49 | 0.010277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_261-101_0_5_line_61 |  | 47 | 50 | 0.01851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_261-101_0_5_line_62 |  | 48 | 72 | 0.046098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_261-101_0_5_line_63 |  | 48 | 73 | 0.016311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_261-101_0_5_line_64 |  | 51 | 52 | 0.007839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_261-101_0_5_line_65 |  | 51 | 53 | 0.036986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_261-101_0_5_line_66 |  | 52 | 76 | 0.011515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_261-101_0_5_line_67 |  | 52 | 77 | 0.021115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_261-101_0_5_line_68 |  | 54 | 55 | 0.015031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_261-101_0_5_line_69 |  | 55 | 92 | 0.028559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_261-101_0_5_line_70 |  | 56 | 57 | 0.033178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_261-101_0_5_line_71 |  | 56 | 58 | 0.0077574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_261-101_0_5_line_72 |  | 57 | 78 | 0.0022768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_261-101_0_5_line_73 |  | 57 | 79 | 0.029409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_261-101_0_5_line_74 |  | 61 | 135 | 0.025115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_261-101_0_5_line_75 |  | 61 | 129 | 0.01067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_261-101_0_5_line_76 |  | 62 | 140 | 0.021048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_261-101_0_5_line_77 |  | 63 | 98 | 0.0025031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_261-101_0_5_line_78 |  | 64 | 86 | 0.0055412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_261-101_0_5_line_79 |  | 65 | 77 | 0.017784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_261-101_0_5_line_80 |  | 66 | 91 | 0.016397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_261-101_0_5_line_81 |  | 67 | 82 | 0.028099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_261-101_0_5_line_82 |  | 68 | 87 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_261-101_0_5_line_83 |  | 70 | 90 | 0.01107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_261-101_0_5_line_84 |  | 71 | 79 | 0.019009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_261-101_0_5_line_85 |  | 72 | 117 | 0.012369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_261-101_0_5_line_86 |  | 72 | 115 | 0.016225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_261-101_0_5_line_87 |  | 73 | 118 | 0.0068698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_261-101_0_5_line_88 |  | 74 | 75 | 0.0032143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_261-101_0_5_line_89 |  | 75 | 91 | 0.024473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_261-101_0_5_line_90 |  | 76 | 92 | 0.017975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_261-101_0_5_line_91 |  | 80 | 81 | 0.0001019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_261-101_0_5_line_92 |  | 81 | 82 | 0.012912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_261-101_0_5_line_93 |  | 83 | 84 | 0.010231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_261-101_0_5_line_94 |  | 84 | 85 | 0.012351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_261-101_0_5_line_95 |  | 84 | 86 | 0.045495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_261-101_0_5_line_96 |  | 85 | 94 | 0.006983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_261-101_0_5_line_97 |  | 87 | 88 | 0.001298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_261-101_0_5_line_98 |  | 88 | 89 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_261-101_0_5_line_99 |  | 89 | 93 | 0.023254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_261-101_0_5_line_100 |  | 93 | 94 | 0.0021211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_261-101_0_5_line_101 |  | 95 | 96 | 0.010022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_261-101_0_5_line_102 |  | 95 | 97 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_261-101_0_5_line_103 |  | 97 | 98 | 0.018356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_261-101_0_5_line_104 |  | 99 | 100 | 0.00073201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_261-101_0_5_line_105 |  | 99 | 101 | 0.0048412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_261-101_0_5_line_106 |  | 100 | 102 | 0.016029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_261-101_0_5_line_107 |  | 101 | 103 | 0.00085639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_261-101_0_5_line_108 |  | 102 | 104 | 0.0009716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_261-101_0_5_line_109 |  | 104 | 105 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_261-101_0_5_line_110 |  | 105 | 106 | 0.014671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_261-101_0_5_line_111 |  | 106 | 107 | 0.012401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_261-101_0_5_line_112 |  | 107 | 112 | 0.021448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_261-101_0_5_line_113 |  | 107 | 111 | 0.01115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_261-101_0_5_line_114 |  | 108 | 109 | 0.00052609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_261-101_0_5_line_115 |  | 108 | 110 | 0.0075378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_261-101_0_5_line_116 |  | 109 | 111 | 0.017365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_261-101_0_5_line_117 |  | 112 | 115 | 0.00039333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_261-101_0_5_line_118 |  | 113 | 114 | 0.01474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_261-101_0_5_line_119 |  | 114 | 116 | 0.0041958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_261-101_0_5_line_120 |  | 116 | 122 | 0.00022552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_261-101_0_5_line_121 |  | 117 | 119 | 0.01649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_261-101_0_5_line_122 |  | 117 | 120 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_261-101_0_5_line_123 |  | 118 | 133 | 0.024051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_261-101_0_5_line_124 |  | 119 | 121 | 0.0077439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_261-101_0_5_line_125 |  | 120 | 122 | 0.0068708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_261-101_0_5_line_126 |  | 121 | 130 | 0.025181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_261-101_0_5_line_127 |  | 123 | 124 | 0.019451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_261-101_0_5_line_128 |  | 123 | 125 | 0.0032944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_261-101_0_5_line_129 |  | 124 | 126 | 0.0050483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_261-101_0_5_line_130 |  | 125 | 127 | 0.030538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_261-101_0_5_line_131 |  | 127 | 128 | 0.018851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_261-101_0_5_line_132 |  | 128 | 129 | 0.018783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_261-101_0_5_line_133 |  | 130 | 131 | 0.0074626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_261-101_0_5_line_134 |  | 131 | 132 | 2.1782e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_261-101_0_5_line_135 |  | 133 | 134 | 0.0032789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_261-101_0_5_line_136 |  | 135 | 136 | 0.072632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_261-101_0_5_line_137 |  | 136 | 137 | 0.034383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_261-101_0_5_line_138 |  | 137 | 141 | 0.058168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_261-101_0_5_line_139 |  | 138 | 139 | 0.019604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_261-101_0_5_line_140 |  | 139 | 140 | 0.0028097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_261-101_0_5_trafo_121 | 0.63 MVA 20/0.4 kV | 142 | 60 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2680601.5909 | 1252293.1603 | 2680609.5586 | 1252316.5082
1 | 2680601.6784 | 1252275.96 | 2680600.0612 | 1252278.3287 | 2680599.1727 | 1252279.8399 | 2680598.8217 | 1252282.337 | 2680598.9795 | 1252284.6075 | 2680599.5629 | 1252287.2174 | 2680601.5909 | 1252293.1603
2 | 2680609.5586 | 1252316.5082 | 2680614.636 | 1252331.3866
3 | 2680582.0819 | 1252261.2492 | 2680588.4771 | 1252258.8455 | 2680589.2127 | 1252260.8014 | 2680590.3854 | 1252263.3637 | 2680591.9653 | 1252264.8419 | 2680594.3168 | 1252265.6411 | 2680596.3583 | 1252265.9246 | 2680599.3164 | 1252271.5024 | 2680601.6784 | 1252275.96
4 | 2680614.636 | 1252331.3866 | 2680619.749 | 1252346.3694
5 | 2680582.0819 | 1252261.2492 | 2680575.2012 | 1252263.8465
6 | 2680622.6425 | 1252354.8483 | 2680619.749 | 1252346.3694
7 | 2680569.0304 | 1252530.4276 | 2680571.0997 | 1252537.5388 | 2680575.0171 | 1252549.1452 | 2680580.0657 | 1252547.5015 | 2680589.2474 | 1252544.4093
8 | 2680567.8935 | 1252525.7976 | 2680568.3288 | 1252527.6382 | 2680569.0304 | 1252530.4276
9 | 2680595.1079 | 1252542.4356 | 2680589.2474 | 1252544.4093
10 | 2680556.0216 | 1252528.605 | 2680562.1693 | 1252527.1652 | 2680567.8935 | 1252525.7976
11 | 2680567.8935 | 1252525.7976 | 2680564.4204 | 1252510.037
12 | 2680629.9731 | 1252359.1179 | 2680627.5951 | 1252359.1634 | 2680625.7317 | 1252358.5487 | 2680623.8589 | 1252356.9665 | 2680622.6425 | 1252354.8483
13 | 2680611.4001 | 1252358.5092 | 2680617.2449 | 1252356.6095 | 2680622.6425 | 1252354.8483
14 | 2680629.9731 | 1252359.1179 | 2680632.3583 | 1252358.5388 | 2680637.1875 | 1252355.291 | 2680662.1973 | 1252333.1952
15 | 2680629.9731 | 1252359.1179 | 2680633.7402 | 1252363.4724 | 2680636.9055 | 1252367.1293
16 | 2680611.4001 | 1252358.5092 | 2680606.9765 | 1252345.8285 | 2680604.9203 | 1252340.5546
17 | 2680554.5769 | 1252523.2925 | 2680531.7102 | 1252533.6851
18 | 2680556.0216 | 1252528.605 | 2680554.5769 | 1252523.2925
19 | 2680554.5769 | 1252523.2925 | 2680550.2072 | 1252507.1989 | 2680549.5145 | 1252505.0794
20 | 2680529.9194 | 1252534.499 | 2680531.7102 | 1252533.6851
21 | 2680556.0216 | 1252528.605 | 2680556.5168 | 1252531.0357 | 2680551.7448 | 1252534.529 | 2680556.383 | 1252558.6211 | 2680548.5966 | 1252564.0193 | 2680548.6135 | 1252564.9105
22 | 2680545.9249 | 1252483.0227 | 2680545.9873 | 1252490.0843 | 2680546.9105 | 1252497.1132 | 2680549.5145 | 1252505.0794
23 | 2680547.864 | 1252471.963 | 2680546.4585 | 1252478.193 | 2680545.9249 | 1252483.0227
24 | 2680547.864 | 1252471.963 | 2680554.1433 | 1252473.6163 | 2680561.0694 | 1252475.434
25 | 2680547.864 | 1252471.963 | 2680550.3741 | 1252465.5257 | 2680551.945 | 1252463.2115
26 | 2680545.9249 | 1252483.0227 | 2680538.517 | 1252481.6654 | 2680534.2942 | 1252479.184 | 2680529.4972 | 1252475.0824 | 2680519.3785 | 1252467.1723 | 2680517.175 | 1252465.7093
27 | 2680545.9249 | 1252483.0227 | 2680530.5062 | 1252490.7967 | 2680510.6968 | 1252501.0438
28 | 2680561.0694 | 1252475.434 | 2680563.1357 | 1252469.4465 | 2680566.2081 | 1252463.2948 | 2680575.3913 | 1252451.7667
29 | 2680561.0694 | 1252475.434 | 2680560.9245 | 1252476.9222
30 | 2680551.945 | 1252463.2115 | 2680553.732 | 1252460.5788 | 2680557.4849 | 1252455.993 | 2680573.2658 | 1252436.2952
31 | 2680502.2802 | 1252455.8205 | 2680517.175 | 1252465.7093
32 | 2680508.6165 | 1252502.1199 | 2680510.6968 | 1252501.0438
33 | 2680749.6582 | 1252429.311 | 2680762.9005 | 1252447.783
34 | 2680762.9005 | 1252447.783 | 2680771.274 | 1252439.0958
35 | 2680762.9005 | 1252447.783 | 2680752.9131 | 1252458.3294
36 | 2680749.6582 | 1252429.311 | 2680738.8555 | 1252412.1711
37 | 2680786.2267 | 1252423.5829 | 2680771.274 | 1252439.0958
38 | 2680752.9131 | 1252458.3294 | 2680741.9326 | 1252469.9245
39 | 2680722.5589 | 1252488.3635 | 2680711.3943 | 1252475.4208
40 | 2680715.8441 | 1252516.4485 | 2680710.7592 | 1252510.2302 | 2680728.2277 | 1252494.9345 | 2680722.5589 | 1252488.3635
41 | 2680722.5589 | 1252488.3635 | 2680737.7843 | 1252474.3049 | 2680741.9326 | 1252469.9245
42 | 2680722.5589 | 1252488.3635 | 2680707.5643 | 1252500.342
43 | 2680703.9625 | 1252466.8053 | 2680711.3943 | 1252475.4208
44 | 2680715.8441 | 1252516.4485 | 2680734.8871 | 1252537.9017 | 2680739.1468 | 1252538.7715 | 2680757.1083 | 1252523.9386
45 | 2680696.9067 | 1252508.6795 | 2680700.2103 | 1252506.2169 | 2680707.5643 | 1252500.342
46 | 2680595.1079 | 1252542.4356 | 2680606.788 | 1252538.4956
47 | 2680606.788 | 1252538.4956 | 2680624.1159 | 1252532.6505
48 | 2680639.2885 | 1252364.5042 | 2680636.9055 | 1252367.1293
49 | 2680636.9055 | 1252367.1293 | 2680633.0962 | 1252372.5259 | 2680628.7072 | 1252380.0274 | 2680624.8079 | 1252387.4292
50 | 2680639.2885 | 1252364.5042 | 2680642.2075 | 1252361.3082 | 2680655.3274 | 1252349.8241
51 | 2680639.2885 | 1252364.5042 | 2680641.5262 | 1252365.3353 | 2680652.8965 | 1252370.5717 | 2680655.854 | 1252371.4363
52 | 2680609.4281 | 1252409.676 | 2680614.2676 | 1252404.0043 | 2680620.4682 | 1252395.916 | 2680624.5546 | 1252387.9101 | 2680624.8079 | 1252387.4292
53 | 2680575.2012 | 1252263.8465 | 2680578.9578 | 1252273.9718 | 2680583.3101 | 1252285.1316
54 | 2680767.8885 | 1252515.0361 | 2680757.1083 | 1252523.9386
55 | 2680575.3913 | 1252451.7667 | 2680586.3418 | 1252460.7033
56 | 2680786.2267 | 1252423.5829 | 2680808.9179 | 1252400.0303
57 | 2680808.9179 | 1252400.0303 | 2680796.16 | 1252388.553
58 | 2680786.2267 | 1252423.5829 | 2680773.39 | 1252409.2648
59 | 2680550.7016 | 1252308.302 | 2680566.237 | 1252305.8559 | 2680584.4195 | 1252303.5569 | 2680590.0356 | 1252302.3769
60 | 2680590.0356 | 1252302.3769 | 2680593.7688 | 1252311.9521
61 | 2680590.0356 | 1252302.3769 | 2680583.3101 | 1252285.1316
62 | 2680550.7016 | 1252308.302 | 2680540.7918 | 1252311.6476 | 2680529.6694 | 1252319.8025 | 2680513.4533 | 1252334.5709
63 | 2680550.7016 | 1252308.302 | 2680555.5381 | 1252323.8796
64 | 2680660.2211 | 1252525.42 | 2680666.6501 | 1252529.9331
65 | 2680666.6501 | 1252529.9331 | 2680684.1989 | 1252518.1522 | 2680696.9067 | 1252508.6795
66 | 2680660.2211 | 1252525.42 | 2680659.0818 | 1252516.5312 | 2680660.6166 | 1252514.673 | 2680660.5389 | 1252514.5521
67 | 2680660.2211 | 1252525.42 | 2680655.4668 | 1252522.075 | 2680640.9674 | 1252526.966
68 | 2680613.3226 | 1252499.925 | 2680626.3857 | 1252492.4895
69 | 2680650.8203 | 1252499.431 | 2680650.5878 | 1252499.0693 | 2680633.2059 | 1252488.6138 | 2680631.9358 | 1252489.3304 | 2680626.3857 | 1252492.4895
70 | 2680740.0031 | 1252374.6832 | 2680755.9042 | 1252373.0876 | 2680767.5199 | 1252360.3141
71 | 2680767.5199 | 1252360.3141 | 2680761.7874 | 1252355.0877
72 | 2680740.0031 | 1252374.6832 | 2680738.2835 | 1252376.1754
73 | 2680740.0031 | 1252374.6832 | 2680750.1667 | 1252382.0605 | 2680751.9631 | 1252385.3652 | 2680760.7006 | 1252395.111
74 | 2680502.2802 | 1252455.8205 | 2680489.5715 | 1252448.0087 | 2680480.2774 | 1252443.8122
75 | 2680502.2802 | 1252455.8205 | 2680503.4928 | 1252452.1231 | 2680503.9338 | 1252449.1046 | 2680502.7669 | 1252445.5639 | 2680502.7669 | 1252445.5639
76 | 2680508.6165 | 1252502.1199 | 2680489.9215 | 1252511.7905
77 | 2680738.8555 | 1252412.1711 | 2680737.5208 | 1252410.0535 | 2680737.5208 | 1252410.0535
78 | 2680703.9625 | 1252466.8053 | 2680700.3442 | 1252462.6084
79 | 2680640.9674 | 1252526.966 | 2680624.1159 | 1252532.6505
80 | 2680655.3274 | 1252349.8241 | 2680667.6652 | 1252339.0245
81 | 2680655.854 | 1252371.4363 | 2680663.5484 | 1252373.6857 | 2680670.1919 | 1252376.3114 | 2680675.9138 | 1252379.0024 | 2680681.203 | 1252382.9774
82 | 2680609.4281 | 1252409.676 | 2680620.4523 | 1252418.2293
83 | 2680594.918 | 1252467.7023 | 2680586.3418 | 1252460.7033
84 | 2680760.7006 | 1252395.111 | 2680773.39 | 1252409.2648
85 | 2680504.2908 | 1252342.9082 | 2680513.4533 | 1252334.5709
86 | 2680513.4533 | 1252334.5709 | 2680503.1978 | 1252321.9979
87 | 2680557.5751 | 1252330.4405 | 2680555.5381 | 1252323.8796
88 | 2680685.9792 | 1252322.7918 | 2680688.3708 | 1252320.6441
89 | 2680685.9792 | 1252322.7918 | 2680677.0687 | 1252330.7934 | 2680667.6652 | 1252339.0245
90 | 2680650.8203 | 1252499.431 | 2680660.5389 | 1252514.5521
91 | 2680690.2652 | 1252392.3137 | 2680690.1962 | 1252392.2387
92 | 2680690.1962 | 1252392.2387 | 2680687.338 | 1252389.1322 | 2680681.203 | 1252382.9774 | 2680681.203 | 1252382.9774
93 | 2680671.2131 | 1252432.645 | 2680677.2014 | 1252424.6428 | 2680677.3781 | 1252424.4859
94 | 2680671.2131 | 1252432.645 | 2680659.1329 | 1252435.2158 | 2680659.1329 | 1252435.2158
95 | 2680671.2131 | 1252432.645 | 2680680.7336 | 1252436.2662 | 2680702.2671 | 1252461.0668 | 2680700.3442 | 1252462.6084
96 | 2680652.9526 | 1252438.4664 | 2680659.1329 | 1252435.2158
97 | 2680621.4779 | 1252419.025 | 2680620.4523 | 1252418.2293
98 | 2680630.4949 | 1252428.6281 | 2680627.5084 | 1252427.0572 | 2680624.1032 | 1252421.0619 | 2680621.4779 | 1252419.025
99 | 2680651.0752 | 1252439.4538 | 2680630.4949 | 1252428.6281
100 | 2680651.0752 | 1252439.4538 | 2680651.0752 | 1252439.4538 | 2680652.9526 | 1252438.4664
101 | 2680714.7253 | 1252428.2458 | 2680706.619 | 1252434.1394
102 | 2680725.6569 | 1252423.8799 | 2680721.6337 | 1252425.026 | 2680714.9811 | 1252428.0598 | 2680714.7253 | 1252428.2458
103 | 2680725.6569 | 1252423.8799 | 2680726.6894 | 1252421.7702 | 2680731.85 | 1252415.2468 | 2680737.5208 | 1252410.0535
104 | 2680469.856 | 1252261.1525 | 2680470.19 | 1252261.8039
105 | 2680469.856 | 1252261.1525 | 2680467.6475 | 1252256.8444
106 | 2680477.5022 | 1252276.0674 | 2680470.19 | 1252261.8039
107 | 2680467.2568 | 1252256.0824 | 2680467.6475 | 1252256.8444
108 | 2680477.5022 | 1252276.0674 | 2680477.9454 | 1252276.932
109 | 2680483.259 | 1252293.3649 | 2680483.1475 | 1252287.0795 | 2680477.9454 | 1252276.932
110 | 2680483.5193 | 1252308.0335 | 2680483.259 | 1252293.3649
111 | 2680492.5502 | 1252303.8308 | 2680490.067 | 1252302.1736 | 2680484.7094 | 1252305.4366 | 2680484.7877 | 1252306.8943 | 2680483.5193 | 1252308.0335
112 | 2680492.5502 | 1252303.8308 | 2680492.3344 | 1252307.4861 | 2680494.3674 | 1252311.172 | 2680502.9491 | 1252321.6931
113 | 2680492.5502 | 1252303.8308 | 2680494.5769 | 1252301.868 | 2680501.7439 | 1252297.6254
114 | 2680516.6871 | 1252288.7797 | 2680517.1398 | 1252288.5118
115 | 2680523.6263 | 1252284.6721 | 2680517.1398 | 1252288.5118
116 | 2680516.6871 | 1252288.7797 | 2680501.7439 | 1252297.6254
117 | 2680503.1978 | 1252321.9979 | 2680502.9491 | 1252321.6931
118 | 2680478.7623 | 1252353.3163 | 2680469.3959 | 1252349.8728 | 2680470.3845 | 1252347.6512 | 2680471.2939 | 1252345.507
119 | 2680478.7623 | 1252353.3163 | 2680480.9533 | 1252354.1218 | 2680482.7618 | 1252354.5623
120 | 2680482.9809 | 1252354.6156 | 2680482.7618 | 1252354.5623
121 | 2680504.2908 | 1252342.9082 | 2680508.0956 | 1252347.2743 | 2680513.2609 | 1252356.6437
122 | 2680504.2908 | 1252342.9082 | 2680489.6566 | 1252356.2416
123 | 2680557.5751 | 1252330.4405 | 2680558.4815 | 1252333.3598 | 2680559.1828 | 1252336.7385 | 2680560.7382 | 1252354.213
124 | 2680516.9996 | 1252363.4253 | 2680513.2609 | 1252356.6437
125 | 2680482.9809 | 1252354.6156 | 2680489.6566 | 1252356.2416
126 | 2680516.9996 | 1252363.4253 | 2680529.1568 | 1252385.4774
127 | 2680445.206 | 1252403.562 | 2680439.5278 | 1252399.5931 | 2680436.1582 | 1252394.299 | 2680436.243 | 1252388.0517
128 | 2680445.206 | 1252403.562 | 2680447.9062 | 1252405.4493
129 | 2680436.3116 | 1252383.0038 | 2680436.243 | 1252388.0517
130 | 2680473.1049 | 1252422.6895 | 2680456.2782 | 1252411.0179 | 2680453.0746 | 1252409.0619 | 2680447.9062 | 1252405.4493
131 | 2680473.1049 | 1252422.6895 | 2680488.5946 | 1252433.4336
132 | 2680502.7669 | 1252445.5639 | 2680497.3848 | 1252439.5307 | 2680488.5946 | 1252433.4336
133 | 2680529.1568 | 1252385.4774 | 2680532.7596 | 1252392.0126
134 | 2680532.7701 | 1252392.0317 | 2680532.7596 | 1252392.0126
135 | 2680561.0289 | 1252357.479 | 2680560.7382 | 1252354.213
136 | 2680411.6903 | 1252434.8638 | 2680422.9557 | 1252431.1583 | 2680431.741 | 1252428.8981 | 2680440.1468 | 1252428.4675 | 2680448.1784 | 1252429.4772 | 2680457.9034 | 1252433.0453 | 2680477.1047 | 1252442.3796 | 2680480.2774 | 1252443.8122
137 | 2680397.6021 | 1252464.717 | 2680412.049 | 1252444.0199 | 2680411.6903 | 1252434.8638
138 | 2680397.6021 | 1252464.717 | 2680424.7202 | 1252484.055 | 2680439.5436 | 1252463.9857
139 | 2680469.9526 | 1252521.9675 | 2680476.0487 | 1252518.9667 | 2680487.4259 | 1252513.0815
140 | 2680489.9215 | 1252511.7905 | 2680487.4259 | 1252513.0815

## bus_geodata
| x | y | coords
0 | 2680601.5909 | 1252293.1603
1 | 2680609.5586 | 1252316.5082
2 | 2680601.6784 | 1252275.96
3 | 2680614.636 | 1252331.3866
4 | 2680582.0819 | 1252261.2492
5 | 2680619.749 | 1252346.3694
6 | 2680569.0304 | 1252530.4276
7 | 2680589.2474 | 1252544.4093
8 | 2680567.8935 | 1252525.7976
9 | 2680622.6425 | 1252354.8483
10 | 2680629.9731 | 1252359.1179
11 | 2680611.4001 | 1252358.5092
12 | 2680554.5769 | 1252523.2925
13 | 2680531.7102 | 1252533.6851
14 | 2680556.0216 | 1252528.605
15 | 2680549.5145 | 1252505.0794
16 | 2680547.864 | 1252471.963
17 | 2680545.9249 | 1252483.0227
18 | 2680561.0694 | 1252475.434
19 | 2680551.945 | 1252463.2115
20 | 2680517.175 | 1252465.7093
21 | 2680510.6968 | 1252501.0438
22 | 2680762.9005 | 1252447.783
23 | 2680749.6582 | 1252429.311
24 | 2680771.274 | 1252439.0958
25 | 2680752.9131 | 1252458.3294
26 | 2680722.5589 | 1252488.3635
27 | 2680711.3943 | 1252475.4208
28 | 2680715.8441 | 1252516.4485
29 | 2680741.9326 | 1252469.9245
30 | 2680707.5643 | 1252500.342
31 | 2680595.1079 | 1252542.4356
32 | 2680606.788 | 1252538.4956
33 | 2680636.9055 | 1252367.1293
34 | 2680639.2885 | 1252364.5042
35 | 2680624.8079 | 1252387.4292
36 | 2680564.4204 | 1252510.037
37 | 2680662.1973 | 1252333.1952
38 | 2680575.2012 | 1252263.8465
39 | 2680757.1083 | 1252523.9386
40 | 2680604.9203 | 1252340.5546
41 | 2680575.3913 | 1252451.7667
42 | 2680560.9245 | 1252476.9222
43 | 2680548.6135 | 1252564.9105
44 | 2680808.9179 | 1252400.0303
45 | 2680786.2267 | 1252423.5829
46 | 2680796.16 | 1252388.553
47 | 2680590.0356 | 1252302.3769
48 | 2680550.7016 | 1252308.302
49 | 2680593.7688 | 1252311.9521
50 | 2680583.3101 | 1252285.1316
51 | 2680666.6501 | 1252529.9331
52 | 2680660.2211 | 1252525.42
53 | 2680696.9067 | 1252508.6795
54 | 2680613.3226 | 1252499.925
55 | 2680626.3857 | 1252492.4895
56 | 2680767.5199 | 1252360.3141
57 | 2680740.0031 | 1252374.6832
58 | 2680761.7874 | 1252355.0877
59 | 2680529.9193 | 1252534.499
60 | 2680573.2658 | 1252436.2952
61 | 2680502.2802 | 1252455.8205
62 | 2680508.6165 | 1252502.1199
63 | 2680738.8555 | 1252412.1711
64 | 2680703.9625 | 1252466.8053
65 | 2680624.1159 | 1252532.6505
66 | 2680655.3274 | 1252349.8241
67 | 2680655.854 | 1252371.4363
68 | 2680609.4281 | 1252409.676
69 | 2680767.8885 | 1252515.0361
70 | 2680586.3418 | 1252460.7033
71 | 2680773.39 | 1252409.2648
72 | 2680513.4533 | 1252334.5709
73 | 2680555.5381 | 1252323.8796
74 | 2680688.3708 | 1252320.6441
75 | 2680685.9792 | 1252322.7918
76 | 2680660.5389 | 1252514.5521
77 | 2680640.9674 | 1252526.966
78 | 2680738.2835 | 1252376.1754
79 | 2680760.7006 | 1252395.111
80 | 2680690.2652 | 1252392.3137
81 | 2680690.1962 | 1252392.2387
82 | 2680681.203 | 1252382.9774
83 | 2680677.3781 | 1252424.4859
84 | 2680671.2131 | 1252432.645
85 | 2680659.1329 | 1252435.2158
86 | 2680700.3442 | 1252462.6084
87 | 2680620.4523 | 1252418.2293
88 | 2680621.4779 | 1252419.025
89 | 2680630.4949 | 1252428.6281
90 | 2680594.918 | 1252467.7023
91 | 2680667.6652 | 1252339.0245
92 | 2680650.8203 | 1252499.431
93 | 2680651.0752 | 1252439.4538
94 | 2680652.9526 | 1252438.4664
95 | 2680714.7253 | 1252428.2458
96 | 2680706.619 | 1252434.1394
97 | 2680725.6569 | 1252423.8799
98 | 2680737.5208 | 1252410.0535
99 | 2680469.856 | 1252261.1525
100 | 2680470.19 | 1252261.8039
101 | 2680467.6475 | 1252256.8444
102 | 2680477.5022 | 1252276.0674
103 | 2680467.2568 | 1252256.0824
104 | 2680477.9454 | 1252276.932
105 | 2680483.259 | 1252293.3649
106 | 2680483.5193 | 1252308.0335
107 | 2680492.5502 | 1252303.8308
108 | 2680517.1398 | 1252288.5118
109 | 2680516.6871 | 1252288.7797
110 | 2680523.6263 | 1252284.6721
111 | 2680501.7439 | 1252297.6254
112 | 2680502.9491 | 1252321.6931
113 | 2680471.2939 | 1252345.507
114 | 2680478.7623 | 1252353.3163
115 | 2680503.1978 | 1252321.9979
116 | 2680482.7618 | 1252354.5623
117 | 2680504.2908 | 1252342.9082
118 | 2680557.5751 | 1252330.4405
119 | 2680513.2609 | 1252356.6437
120 | 2680489.6566 | 1252356.2416
121 | 2680516.9996 | 1252363.4253
122 | 2680482.9809 | 1252354.6156
123 | 2680445.206 | 1252403.562
124 | 2680436.243 | 1252388.0517
125 | 2680447.9062 | 1252405.4493
126 | 2680436.3116 | 1252383.0038
127 | 2680473.1049 | 1252422.6895
128 | 2680488.5946 | 1252433.4336
129 | 2680502.7669 | 1252445.5639
130 | 2680529.1568 | 1252385.4774
131 | 2680532.7596 | 1252392.0126
132 | 2680532.7701 | 1252392.0317
133 | 2680560.7382 | 1252354.213
134 | 2680561.0289 | 1252357.479
135 | 2680480.2774 | 1252443.8122
136 | 2680411.6903 | 1252434.8638
137 | 2680397.6021 | 1252464.717
138 | 2680469.9526 | 1252521.9675
139 | 2680487.4259 | 1252513.0815
140 | 2680489.9215 | 1252511.7905
141 | 2680439.5436 | 1252463.9857
142 | 2680547.864 | 1252471.963

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97326 | -0.51542 | 0.0025021 | 0.00062709
1 | 0.97359 | -0.50892 | 0.0045848 | 0.0011491
2 | 0.97302 | -0.5201 | 0 | 0
3 | 0.97381 | -0.50452 | 0.0042219 | 0.0010581
4 | 0.97263 | -0.52769 | 0 | 0
5 | 0.97405 | -0.49983 | 0.0046777 | 0.0011723
6 | 0.99079 | -0.17487 | 0 | 0
7 | 0.9887 | -0.2149 | 0.0038184 | 0.00095699
8 | 0.99108 | -0.16938 | 0 | 0
9 | 0.97419 | -0.49703 | 0 | 0
10 | 0.97435 | -0.49398 | 0 | 0
11 | 0.97413 | -0.49815 | 0 | 0
12 | 0.99218 | -0.14834 | 0 | 0
13 | 0.99152 | -0.16118 | 0.0089098 | 0.002233
14 | 0.99183 | -0.15499 | 0 | 0
15 | 0.99348 | -0.12364 | 0.0031168 | 0.00078115
16 | 0.99602 | -0.075283 | 0 | 0
17 | 0.99503 | -0.094035 | 0 | 0
18 | 0.99589 | -0.077869 | 0 | 0
19 | 0.99689 | -0.058759 | 0.0043234 | 0.0010836
20 | 0.99329 | -0.12767 | 0.003877 | 0.00097167
21 | 0.99338 | -0.12599 | 0.012548 | 0.0031448
22 | 0.97695 | -0.44287 | 0 | 0
23 | 0.97636 | -0.4546 | 0 | 0
24 | 0.97661 | -0.44963 | 0.0027706 | 0.00069437
25 | 0.97775 | -0.42726 | 0.0057534 | 0.0014419
26 | 0.98046 | -0.37421 | 0 | 0
27 | 0.97989 | -0.3854 | 0.0056009 | 0.0014037
28 | 0.97998 | -0.38365 | 0 | 0
29 | 0.97871 | -0.40845 | 0.0057675 | 0.0014455
30 | 0.9814 | -0.35586 | 0.006284 | 0.0015749
31 | 0.98833 | -0.22198 | 0 | 0
32 | 0.9876 | -0.2361 | 0.0081954 | 0.002054
33 | 0.97454 | -0.49015 | 0 | 0
34 | 0.97442 | -0.49243 | 0 | 0
35 | 0.97513 | -0.47858 | 0.0045979 | 0.0011523
36 | 0.99096 | -0.17169 | 0.0080635 | 0.0020209
37 | 0.97404 | -0.50009 | 0.007998 | 0.0020045
38 | 0.97254 | -0.52956 | 0.0024877 | 0.00062347
39 | 0.9793 | -0.39697 | 0.0063936 | 0.0016024
40 | 0.97404 | -0.49996 | 0.0051571 | 0.0012925
41 | 0.9957 | -0.08154 | 0 | 0
42 | 0.99588 | -0.077955 | 0.0032979 | 0.00082653
43 | 0.99152 | -0.16108 | 0.0079368 | 0.0019892
44 | 0.97589 | -0.46382 | 0 | 0
45 | 0.97605 | -0.46062 | 0 | 0
46 | 0.9758 | -0.46549 | 0.0053395 | 0.0013382
47 | 0.97205 | -0.5393 | 0 | 0
48 | 0.97161 | -0.54804 | 0.0020973 | 0.00052564
49 | 0.97204 | -0.5395 | 0.0010356 | 0.00025955
50 | 0.97226 | -0.53516 | 0.0059383 | 0.0014883
51 | 0.98396 | -0.30619 | 0 | 0
52 | 0.98436 | -0.29849 | 0 | 0
53 | 0.98208 | -0.34263 | 0.0028196 | 0.00070666
54 | 0.98354 | -0.31447 | 0.0048346 | 0.0012117
55 | 0.98361 | -0.31316 | 0.0046654 | 0.0011693
56 | 0.97489 | -0.48353 | 0 | 0
57 | 0.97507 | -0.47996 | 0 | 0
58 | 0.97485 | -0.48436 | 0.0058706 | 0.0014713
59 | 0.99148 | -0.16187 | 0.019935 | 0.0049962
60 | 1 | 0 | -0.49907 | -0.12785
61 | 0.99244 | -0.14407 | 0 | 0
62 | 0.99331 | -0.12736 | 0.0044974 | 0.0011272
63 | 0.97583 | -0.46507 | 0.0063266 | 0.0015856
64 | 0.97952 | -0.39263 | 0 | 0
65 | 0.98653 | -0.25656 | 0.0080413 | 0.0020153
66 | 0.97407 | -0.49933 | 0.0048137 | 0.0012064
67 | 0.97413 | -0.49829 | 0.0042192 | 0.0010574
68 | 0.97583 | -0.46485 | 0 | 0
69 | 0.97921 | -0.39866 | 0.0066316 | 0.001662
70 | 0.9956 | -0.083399 | 0.0051596 | 0.0012931
71 | 0.97565 | -0.46856 | 0.0065411 | 0.0016394
72 | 0.97117 | -0.55665 | 0 | 0
73 | 0.9715 | -0.55014 | 0.0014776 | 0.00037032
74 | 0.97369 | -0.50693 | 0.0047475 | 0.0011898
75 | 0.9737 | -0.50665 | 0.0031829 | 0.00079771
76 | 0.98411 | -0.30339 | 0.0085714 | 0.0021482
77 | 0.98553 | -0.27598 | 0.0078082 | 0.0019569
78 | 0.97506 | -0.48016 | 0.0049245 | 0.0012342
79 | 0.97537 | -0.47414 | 0.0052147 | 0.0013069
80 | 0.97366 | -0.50747 | 0.0045832 | 0.0011487
81 | 0.97366 | -0.50746 | 0.0046544 | 0.0011665
82 | 0.97377 | -0.50527 | 0.0042837 | 0.0010736
83 | 0.97786 | -0.42501 | 0.004295 | 0.0010764
84 | 0.9779 | -0.42421 | 0 | 0
85 | 0.97752 | -0.43165 | 0.004668 | 0.0011699
86 | 0.97934 | -0.39615 | 0.005427 | 0.0013601
87 | 0.97618 | -0.45781 | 0.0046755 | 0.0011718
88 | 0.97622 | -0.45713 | 0.0046307 | 0.0011606
89 | 0.97659 | -0.44981 | 0.0042688 | 0.0010699
90 | 0.99558 | -0.08385 | 0.0023184 | 0.00058105
91 | 0.97388 | -0.50308 | 0.0045204 | 0.0011329
92 | 0.98386 | -0.30828 | 0.0055904 | 0.0014011
93 | 0.97725 | -0.43695 | 0.0046759 | 0.0011719
94 | 0.97731 | -0.43574 | 0.0043064 | 0.0010793
95 | 0.97537 | -0.47401 | 0.0069823 | 0.0017499
96 | 0.9753 | -0.47537 | 0.0073865 | 0.0018512
97 | 0.97553 | -0.47091 | 0 | 0
98 | 0.97577 | -0.46608 | 0.0075594 | 0.0018946
99 | 0.97055 | -0.56901 | 0.0018493 | 0.00046347
100 | 0.97055 | -0.56893 | 0.0020621 | 0.00051682
101 | 0.97053 | -0.56934 | 0.0018304 | 0.00045874
102 | 0.97066 | -0.56668 | 0.002121 | 0.00053157
103 | 0.97053 | -0.56937 | 0.0018621 | 0.00046668
104 | 0.97067 | -0.5665 | 0.0020609 | 0.00051651
105 | 0.97087 | -0.56265 | 0.0019809 | 0.00049645
106 | 0.97096 | -0.56078 | 0 | 0
107 | 0.97099 | -0.56015 | 0 | 0
108 | 0.97078 | -0.56433 | 0.0024277 | 0.00060845
109 | 0.97078 | -0.56428 | 0.0012647 | 0.00031695
110 | 0.97076 | -0.56481 | 0.0034451 | 0.00086342
111 | 0.9709 | -0.56199 | 0.0017789 | 0.00044583
112 | 0.97108 | -0.55835 | 0.0016208 | 0.00040621
113 | 0.97075 | -0.56496 | 0.0019081 | 0.00047822
114 | 0.97078 | -0.56444 | 0.0020588 | 0.00051599
115 | 0.97109 | -0.55831 | 0.0034091 | 0.0008544
116 | 0.97079 | -0.56413 | 0.0021621 | 0.00054188
117 | 0.97104 | -0.55926 | 0 | 0
118 | 0.97146 | -0.55084 | 0.0009832 | 0.00024641
119 | 0.97085 | -0.56306 | 0.0024589 | 0.00061626
120 | 0.97085 | -0.56306 | 0.0021483 | 0.00053841
121 | 0.97077 | -0.56449 | 0.0010182 | 0.00025517
122 | 0.97079 | -0.56411 | 0.0021064 | 0.0005279
123 | 0.99159 | -0.16053 | 0.0032786 | 0.00082168
124 | 0.99153 | -0.16166 | 0.0012501 | 0.0003133
125 | 0.99161 | -0.16015 | 0.0015582 | 0.00039051
126 | 0.99152 | -0.16185 | 0.0020347 | 0.00050993
127 | 0.99184 | -0.15575 | 0.00299 | 0.00074938
128 | 0.99203 | -0.15204 | 0.0026012 | 0.00065191
129 | 0.99226 | -0.14748 | 0.0043589 | 0.0010924
130 | 0.97056 | -0.56868 | 0.00097306 | 0.00024387
131 | 0.97051 | -0.56978 | 0.0015861 | 0.00039751
132 | 0.97051 | -0.56978 | 0.0064223 | 0.0016096
133 | 0.97136 | -0.55285 | 0.001073 | 0.00026892
134 | 0.97135 | -0.55306 | 0.0034473 | 0.00086399
135 | 0.99166 | -0.15909 | 0.010928 | 0.0027389
136 | 0.99014 | -0.18854 | 0 | 0
137 | 0.98942 | -0.20252 | 0 | 0
138 | 0.99259 | -0.14135 | 0.0063102 | 0.0015815
139 | 0.9927 | -0.13917 | 0.015961 | 0.0040003
140 | 0.99276 | -0.13806 | 0.0064762 | 0.0016231
141 | 0.9882 | -0.2262 | 0.022841 | 0.0057246
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.071742 | -0.018018 | 0.071764 | 0.018031 | 2.2266e-05 | 1.2717e-05 | 0.1097 | 0.1097 | 0.1097 | 0.97326 | -0.51542 | 0.97359 | -0.50892 | 6.0275
1 | 0.06924 | 0.017391 | -0.069224 | -0.017382 | 1.5446e-05 | 8.7441e-06 | 0.10587 | 0.10587 | 0.10587 | 0.97326 | -0.51542 | 0.97302 | -0.5201 | 5.8173
2 | -0.076349 | -0.01918 | 0.076365 | 0.019189 | 1.6059e-05 | 9.3003e-06 | 0.11671 | 0.11671 | 0.11671 | 0.97359 | -0.50892 | 0.97381 | -0.50452 | 6.4125
3 | 0.069224 | 0.017382 | -0.069199 | -0.017368 | 2.5058e-05 | 1.4187e-05 | 0.10587 | 0.10588 | 0.10588 | 0.97302 | -0.5201 | 0.97263 | -0.52769 | 5.8173
4 | -0.080587 | -0.020248 | 0.080605 | 0.020258 | 1.8009e-05 | 1.0541e-05 | 0.12316 | 0.12316 | 0.12316 | 0.97381 | -0.50452 | 0.97405 | -0.49983 | 6.7669
5 | 0.069199 | 0.017368 | -0.069193 | -0.017365 | 6.1676e-06 | 3.492e-06 | 0.10588 | 0.10588 | 0.10588 | 0.97263 | -0.52769 | 0.97254 | -0.52956 | 5.8173
6 | -0.085282 | -0.02143 | 0.085294 | 0.021437 | 1.1409e-05 | 6.7439e-06 | 0.1303 | 0.1303 | 0.1303 | 0.97405 | -0.49983 | 0.97419 | -0.49703 | 7.1595
7 | 0.32883 | 0.084049 | -0.32819 | -0.083645 | 0.00063538 | 0.00040441 | 0.49444 | 0.49444 | 0.49444 | 0.99079 | -0.17487 | 0.9887 | -0.2149 | 27.1669
8 | -0.32883 | -0.084049 | 0.32892 | 0.084105 | 8.7416e-05 | 5.5639e-05 | 0.49444 | 0.49444 | 0.49444 | 0.99079 | -0.17487 | 0.99108 | -0.16938 | 27.1668
9 | 0.32438 | 0.082688 | -0.32426 | -0.082617 | 0.00011076 | 7.0492e-05 | 0.48869 | 0.48869 | 0.48869 | 0.9887 | -0.2149 | 0.98833 | -0.22198 | 26.8511
10 | -0.33698 | -0.086126 | 0.33722 | 0.086275 | 0.00023476 | 0.00014946 | 0.50654 | 0.50654 | 0.50654 | 0.99108 | -0.16938 | 0.99183 | -0.15499 | 27.8321
11 | 0.0080644 | 0.0020213 | -0.0080635 | -0.0020209 | 8.8726e-07 | 3.599e-07 | 0.012108 | 0.012108 | 0.012108 | 0.99108 | -0.16938 | 0.99096 | -0.17169 | 3.3264
12 | -0.090452 | -0.02273 | 0.090465 | 0.022738 | 1.3198e-05 | 7.8728e-06 | 0.13818 | 0.13818 | 0.13818 | 0.97419 | -0.49703 | 0.97435 | -0.49398 | 7.5924
13 | 0.0051578 | 0.0012926 | -0.0051575 | -0.0012925 | 2.7519e-07 | 2.8919e-08 | 0.0078782 | 0.0078783 | 0.0078783 | 0.97419 | -0.49703 | 0.97413 | -0.49815 | 2.1644
14 | 0.0080004 | 0.0020055 | -0.007998 | -0.0020045 | 2.3315e-06 | 9.7363e-07 | 0.012218 | 0.012218 | 0.012218 | 0.97435 | -0.49398 | 0.97404 | -0.50009 | 3.3567
15 | -0.098465 | -0.024743 | 0.098483 | 0.024754 | 1.7973e-05 | 1.0843e-05 | 0.1504 | 0.1504 | 0.1504 | 0.97435 | -0.49398 | 0.97454 | -0.49015 | 8.2637
16 | 0.0051575 | 0.0012925 | -0.0051571 | -0.0012925 | 4.4434e-07 | 4.6735e-08 | 0.0078783 | 0.0078783 | 0.0078783 | 0.97413 | -0.49815 | 0.97404 | -0.49996 | 2.1644
17 | 0.028863 | 0.0072406 | -0.028846 | -0.0072296 | 1.7651e-05 | 1.0973e-05 | 0.04329 | 0.04329 | 0.04329 | 0.99218 | -0.14834 | 0.99152 | -0.16118 | 11.8928
18 | 0.34527 | 0.088336 | -0.34515 | -0.088266 | 0.00011098 | 7.0671e-05 | 0.51845 | 0.51845 | 0.51845 | 0.99218 | -0.14834 | 0.99183 | -0.15499 | 28.4865
19 | -0.37413 | -0.095577 | 0.37458 | 0.095862 | 0.00044744 | 0.00028514 | 0.56174 | 0.56174 | 0.56174 | 0.99218 | -0.14834 | 0.99348 | -0.12364 | 30.865
20 | 0.019936 | 0.0049966 | -0.019935 | -0.0049962 | 6.6029e-07 | 3.9721e-07 | 0.029918 | 0.029918 | 0.029918 | 0.99152 | -0.16118 | 0.99148 | -0.16187 | 8.2194
21 | 0.0079391 | 0.0019901 | -0.0079368 | -0.0019892 | 2.3034e-06 | 9.156e-07 | 0.011911 | 0.011911 | 0.011911 | 0.99183 | -0.15499 | 0.99152 | -0.16108 | 3.2723
22 | -0.37769 | -0.096643 | 0.37824 | 0.096989 | 0.00054216 | 0.00034552 | 0.56641 | 0.56641 | 0.56641 | 0.99348 | -0.12364 | 0.99503 | -0.094035 | 31.1215
23 | 0.48051 | 0.12291 | -0.48007 | -0.12263 | 0.00043568 | 0.00027811 | 0.71875 | 0.71875 | 0.71875 | 0.99602 | -0.075283 | 0.99503 | -0.094035 | 39.4915
24 | 0.010779 | 0.002702 | -0.010778 | -0.0027013 | 1.3279e-06 | 6.7215e-07 | 0.016104 | 0.016104 | 0.016104 | 0.99602 | -0.075283 | 0.99589 | -0.077869 | 4.4242
25 | -0.49129 | -0.12561 | 0.49168 | 0.12586 | 0.00039311 | 0.00025096 | 0.73485 | 0.73485 | 0.73485 | 0.99602 | -0.075283 | 0.99689 | -0.058759 | 40.3763
26 | 0.055956 | 0.014112 | -0.055866 | -0.014055 | 8.9947e-05 | 5.7122e-05 | 0.083711 | 0.083711 | 0.083711 | 0.99503 | -0.094035 | 0.99329 | -0.12767 | 22.9975
27 | 0.045882 | 0.011532 | -0.045812 | -0.011488 | 6.9882e-05 | 4.4212e-05 | 0.068625 | 0.068625 | 0.068625 | 0.99503 | -0.094035 | 0.99338 | -0.12599 | 18.8531
28 | 0.00748 | 0.0018748 | -0.0074787 | -0.0018743 | 1.3083e-06 | 4.7395e-07 | 0.011176 | 0.011176 | 0.011176 | 0.99589 | -0.077869 | 0.9957 | -0.08154 | 3.0705
29 | 0.0032979 | 0.00082652 | -0.0032979 | -0.00082653 | 1.3615e-08 | -1.0742e-08 | 0.0049276 | 0.0049276 | 0.0049276 | 0.99589 | -0.077869 | 0.99588 | -0.077955 | 1.3537
30 | -0.496 | -0.12695 | 0.49742 | 0.12785 | 0.0014156 | 0.00090374 | 0.7413 | 0.7413 | 0.7413 | 0.99689 | -0.058759 | 1 | 0 | 40.7309
31 | 0.051989 | 0.013083 | -0.051949 | -0.013058 | 4.0688e-05 | 2.5809e-05 | 0.077903 | 0.077903 | 0.077903 | 0.99329 | -0.12767 | 0.99244 | -0.14407 | 21.4019
32 | 0.033264 | 0.0083434 | -0.033262 | -0.008342 | 2.1808e-06 | 1.3654e-06 | 0.04983 | 0.04983 | 0.04983 | 0.99338 | -0.12599 | 0.99331 | -0.12736 | 13.6894
33 | 0.028292 | 0.0071039 | -0.028276 | -0.007094 | 1.5814e-05 | 9.8371e-06 | 0.043096 | 0.043097 | 0.043097 | 0.97695 | -0.44287 | 0.97636 | -0.4546 | 11.8397
34 | 0.030704 | 0.0077093 | -0.030694 | -0.0077032 | 9.8976e-06 | 6.1835e-06 | 0.046771 | 0.046771 | 0.046771 | 0.97695 | -0.44287 | 0.97661 | -0.44963 | 12.8491
35 | -0.058996 | -0.014813 | 0.059039 | 0.014841 | 4.3989e-05 | 2.7971e-05 | 0.089867 | 0.089867 | 0.089867 | 0.97695 | -0.44287 | 0.97775 | -0.42726 | 24.6887
36 | 0.028276 | 0.007094 | -0.028262 | -0.0070853 | 1.4111e-05 | 8.7778e-06 | 0.043097 | 0.043097 | 0.043097 | 0.97636 | -0.4546 | 0.97583 | -0.46507 | 11.8397
37 | 0.027923 | 0.0070088 | -0.027909 | -0.0069997 | 1.4628e-05 | 9.0925e-06 | 0.042549 | 0.042549 | 0.042549 | 0.97661 | -0.44963 | 0.97605 | -0.46062 | 11.6894
38 | -0.064793 | -0.016283 | 0.064851 | 0.01632 | 5.8247e-05 | 3.7078e-05 | 0.098623 | 0.098623 | 0.098623 | 0.97775 | -0.42726 | 0.97871 | -0.40845 | 27.0942
39 | 0.18154 | 0.045905 | -0.18144 | -0.045844 | 9.7412e-05 | 6.1267e-05 | 0.27566 | 0.27566 | 0.27566 | 0.98046 | -0.37421 | 0.97989 | -0.3854 | 15.146
40 | 0.01304 | 0.0032724 | -0.013034 | -0.0032692 | 5.8655e-06 | 3.2506e-06 | 0.019792 | 0.019792 | 0.019792 | 0.98046 | -0.37421 | 0.97998 | -0.38365 | 5.4374
41 | 0.070734 | 0.017839 | -0.070619 | -0.017766 | 0.00011572 | 7.3722e-05 | 0.10739 | 0.10739 | 0.10739 | 0.98046 | -0.37421 | 0.97871 | -0.40845 | 29.5032
42 | -0.26531 | -0.067017 | 0.26554 | 0.067165 | 0.00023358 | 0.00014828 | 0.40284 | 0.40284 | 0.40284 | 0.98046 | -0.37421 | 0.9814 | -0.35586 | 22.1341
43 | 0.17584 | 0.04444 | -0.17578 | -0.044402 | 6.0904e-05 | 3.8262e-05 | 0.26715 | 0.26715 | 0.26715 | 0.97989 | -0.3854 | 0.97952 | -0.39263 | 14.6787
44 | 0.013034 | 0.0032692 | -0.013026 | -0.0032646 | 8.2745e-06 | 4.5865e-06 | 0.019792 | 0.019792 | 0.019792 | 0.97998 | -0.38365 | 0.9793 | -0.39697 | 5.4374
45 | -0.27183 | -0.06874 | 0.272 | 0.06885 | 0.00017259 | 0.0001096 | 0.41237 | 0.41237 | 0.41237 | 0.9814 | -0.35586 | 0.98208 | -0.34263 | 22.6576
46 | 0.32426 | 0.082617 | -0.32404 | -0.082477 | 0.00022079 | 0.00014052 | 0.48869 | 0.48869 | 0.48869 | 0.98833 | -0.22198 | 0.9876 | -0.2361 | 26.8511
47 | 0.31585 | 0.080423 | -0.31554 | -0.080225 | 0.00031121 | 0.000198 | 0.47634 | 0.47634 | 0.47634 | 0.9876 | -0.2361 | 0.98653 | -0.25656 | 26.1727
48 | 0.035029 | 0.0087865 | -0.035025 | -0.0087842 | 3.7989e-06 | 2.3872e-06 | 0.053488 | 0.053488 | 0.053488 | 0.97454 | -0.49015 | 0.97442 | -0.49243 | 14.6944
49 | -0.13351 | -0.03354 | 0.13359 | 0.033586 | 7.3774e-05 | 4.574e-05 | 0.20389 | 0.20389 | 0.20389 | 0.97454 | -0.49015 | 0.97513 | -0.47858 | 11.2026
50 | 0.017274 | 0.004332 | -0.017268 | -0.0043287 | 5.6795e-06 | 3.3639e-06 | 0.026379 | 0.026379 | 0.026379 | 0.97442 | -0.49243 | 0.97407 | -0.49933 | 7.2471
51 | 0.017751 | 0.0044521 | -0.017746 | -0.0044492 | 4.9566e-06 | 2.9482e-06 | 0.027108 | 0.027108 | 0.027108 | 0.97442 | -0.49243 | 0.97413 | -0.49829 | 7.4473
52 | -0.13818 | -0.034739 | 0.13827 | 0.034795 | 9.067e-05 | 5.6332e-05 | 0.2109 | 0.2109 | 0.2109 | 0.97513 | -0.47858 | 0.97583 | -0.46485 | 11.588
53 | 0.066705 | 0.016741 | -0.066687 | -0.016731 | 1.7798e-05 | 9.978e-06 | 0.10207 | 0.10207 | 0.10207 | 0.97254 | -0.52956 | 0.97226 | -0.53516 | 5.6082
54 | 0.0066322 | 0.0016622 | -0.0066316 | -0.001662 | 5.3244e-07 | 1.6487e-07 | 0.010077 | 0.010077 | 0.010077 | 0.9793 | -0.39697 | 0.97921 | -0.39866 | 2.7685
55 | 0.0074787 | 0.0018743 | -0.007478 | -0.001874 | 6.6209e-07 | 2.3992e-07 | 0.011176 | 0.011177 | 0.011177 | 0.9957 | -0.08154 | 0.9956 | -0.083399 | 3.0705
56 | -0.0053399 | -0.0013383 | 0.0053407 | 0.0013384 | 8.1195e-07 | 1.115e-07 | 0.0081421 | 0.008142 | 0.0081421 | 0.97589 | -0.46382 | 0.97605 | -0.46062 | 2.2368
57 | 0.0053399 | 0.0013383 | -0.0053395 | -0.0013382 | 4.2663e-07 | 5.8648e-08 | 0.0081421 | 0.0081422 | 0.0081422 | 0.97589 | -0.46382 | 0.9758 | -0.46549 | 2.2369
58 | 0.022568 | 0.0056613 | -0.022559 | -0.0056561 | 8.5371e-06 | 5.2235e-06 | 0.034407 | 0.034407 | 0.034407 | 0.97605 | -0.46062 | 0.97565 | -0.46856 | 9.4526
59 | 0.059701 | 0.014977 | -0.059677 | -0.014964 | 2.4859e-05 | 1.3451e-05 | 0.091397 | 0.091398 | 0.091398 | 0.97205 | -0.5393 | 0.97161 | -0.54804 | 5.0218
60 | 0.0010356 | 0.00025943 | -0.0010356 | -0.00025955 | 9.6862e-09 | -1.212e-07 | 0.0015853 | 0.0015854 | 0.0015854 | 0.97205 | -0.5393 | 0.97204 | -0.5395 | 0.43554
61 | -0.060737 | -0.015237 | 0.060749 | 0.015243 | 1.2002e-05 | 6.5341e-06 | 0.092982 | 0.092982 | 0.092982 | 0.97205 | -0.5393 | 0.97226 | -0.53516 | 5.1089
62 | 0.050597 | 0.012688 | -0.050576 | -0.012678 | 2.0762e-05 | 1.0434e-05 | 0.077492 | 0.077493 | 0.077493 | 0.97161 | -0.54804 | 0.97117 | -0.55665 | 4.2578
63 | 0.0069825 | 0.0017499 | -0.0069818 | -0.0017496 | 6.9947e-07 | 2.4567e-07 | 0.010694 | 0.010694 | 0.010694 | 0.97161 | -0.54804 | 0.9715 | -0.55014 | 2.9378
64 | -0.2753 | -0.069862 | 0.2754 | 0.069927 | 0.00010206 | 6.4818e-05 | 0.41664 | 0.41664 | 0.41664 | 0.98396 | -0.30619 | 0.98436 | -0.29849 | 22.8922
65 | 0.2753 | 0.069862 | -0.27482 | -0.069556 | 0.00048153 | 0.00030584 | 0.41664 | 0.41664 | 0.41664 | 0.98396 | -0.30619 | 0.98208 | -0.34263 | 22.8923
66 | 0.023673 | 0.0059367 | -0.023668 | -0.0059333 | 5.5305e-06 | 3.3932e-06 | 0.035787 | 0.035787 | 0.035787 | 0.98436 | -0.29849 | 0.98411 | -0.30339 | 9.8317
67 | -0.29908 | -0.075864 | 0.2994 | 0.07607 | 0.00032415 | 0.00020611 | 0.45243 | 0.45243 | 0.45243 | 0.98436 | -0.29849 | 0.98553 | -0.27598 | 24.8586
68 | -0.0048346 | -0.0012117 | 0.0048349 | 0.0012117 | 3.0155e-07 | 2.2213e-09 | 0.0073143 | 0.0073142 | 0.0073143 | 0.98354 | -0.31447 | 0.98361 | -0.31316 | 2.0094
69 | -0.0095003 | -0.0023809 | 0.0095025 | 0.002382 | 2.2121e-06 | 1.0532e-06 | 0.014372 | 0.014372 | 0.014372 | 0.98361 | -0.31316 | 0.98386 | -0.30828 | 3.9484
70 | -0.0058708 | -0.0014714 | 0.0058718 | 0.0014716 | 9.9902e-07 | 2.2561e-07 | 0.0089609 | 0.0089607 | 0.0089609 | 0.97489 | -0.48353 | 0.97507 | -0.47996 | 2.4618
71 | 0.0058708 | 0.0014714 | -0.0058706 | -0.0014713 | 2.3359e-07 | 5.2776e-08 | 0.0089609 | 0.0089609 | 0.0089609 | 0.97489 | -0.48353 | 0.97485 | -0.48436 | 2.4618
72 | 0.0049246 | 0.0012342 | -0.0049245 | -0.0012342 | 4.822e-08 | 2.4626e-09 | 0.0075152 | 0.0075152 | 0.0075152 | 0.97507 | -0.47996 | 0.97506 | -0.48016 | 2.0646
73 | -0.010796 | -0.0027058 | 0.010799 | 0.0027073 | 2.9937e-06 | 1.549e-06 | 0.016476 | 0.016476 | 0.016476 | 0.97507 | -0.47996 | 0.97537 | -0.47414 | 4.5264
74 | 0.033867 | 0.0085235 | -0.033843 | -0.0085083 | 2.4297e-05 | 1.5226e-05 | 0.050792 | 0.050792 | 0.050792 | 0.99244 | -0.14407 | 0.99166 | -0.15909 | 13.9538
75 | 0.018081 | 0.0045341 | -0.018079 | -0.0045324 | 2.9409e-06 | 1.7444e-06 | 0.027111 | 0.027111 | 0.027111 | 0.99244 | -0.14407 | 0.99226 | -0.14748 | 7.4482
76 | 0.028764 | 0.0072149 | -0.02875 | -0.0072058 | 1.4657e-05 | 9.1081e-06 | 0.043092 | 0.043092 | 0.043092 | 0.99331 | -0.12736 | 0.99276 | -0.13806 | 11.8385
77 | 0.021935 | 0.0054997 | -0.021934 | -0.005499 | 1.0502e-06 | 6.4089e-07 | 0.033449 | 0.033449 | 0.033449 | 0.97583 | -0.46507 | 0.97577 | -0.46608 | 9.1894
78 | 0.17578 | 0.044402 | -0.17575 | -0.044383 | 2.9661e-05 | 1.8634e-05 | 0.26715 | 0.26715 | 0.26715 | 0.97952 | -0.39263 | 0.97934 | -0.39615 | 14.6787
79 | 0.3075 | 0.078209 | -0.30721 | -0.078027 | 0.00028743 | 0.00018282 | 0.46421 | 0.46421 | 0.46421 | 0.98653 | -0.25656 | 0.98553 | -0.27598 | 25.5063
80 | 0.012454 | 0.0031222 | -0.012452 | -0.003121 | 2.2258e-06 | 1.2204e-06 | 0.019026 | 0.019026 | 0.019026 | 0.97407 | -0.49933 | 0.97388 | -0.50308 | 5.2269
81 | 0.013527 | 0.0033917 | -0.013522 | -0.0033892 | 4.4991e-06 | 2.5298e-06 | 0.020663 | 0.020663 | 0.020663 | 0.97413 | -0.49829 | 0.97377 | -0.50527 | 5.6768
82 | -0.13827 | -0.034795 | 0.13832 | 0.034824 | 4.6548e-05 | 2.8919e-05 | 0.2109 | 0.2109 | 0.2109 | 0.97583 | -0.46485 | 0.97618 | -0.45781 | 11.588
83 | 0.0023185 | 0.00058093 | -0.0023184 | -0.00058105 | 4.9842e-08 | -1.1205e-07 | 0.0034651 | 0.0034651 | 0.0034651 | 0.9956 | -0.083399 | 0.99558 | -0.08385 | 0.95196
84 | 0.016018 | 0.0040167 | -0.016014 | -0.0040143 | 4.2549e-06 | 2.4858e-06 | 0.024431 | 0.024431 | 0.024431 | 0.97565 | -0.46856 | 0.97537 | -0.47414 | 6.7119
85 | 0.022853 | 0.0057299 | -0.02285 | -0.0057284 | 2.8435e-06 | 1.5138e-06 | 0.035015 | 0.035015 | 0.035015 | 0.97117 | -0.55665 | 0.97104 | -0.55926 | 4.8098
86 | 0.027723 | 0.0069478 | -0.027721 | -0.0069474 | 2.1957e-06 | 4.015e-07 | 0.042477 | 0.042478 | 0.042478 | 0.97117 | -0.55665 | 0.97109 | -0.55831 | 2.3339
87 | 0.0055042 | 0.0013793 | -0.005504 | -0.0013793 | 1.831e-07 | 3.2124e-08 | 0.0084305 | 0.0084306 | 0.0084306 | 0.9715 | -0.55014 | 0.97146 | -0.55084 | 2.3161
88 | -0.0047475 | -0.0011898 | 0.0047476 | 0.0011898 | 6.345e-08 | 6.2739e-10 | 0.0072553 | 0.0072553 | 0.0072553 | 0.97369 | -0.50693 | 0.9737 | -0.50665 | 1.9932
89 | -0.0079305 | -0.0019876 | 0.0079318 | 0.0019881 | 1.348e-06 | 5.5823e-07 | 0.012119 | 0.012119 | 0.012119 | 0.9737 | -0.50665 | 0.97388 | -0.50308 | 3.3295
90 | 0.015096 | 0.0037851 | -0.015093 | -0.0037831 | 3.5124e-06 | 2.0196e-06 | 0.022827 | 0.022827 | 0.022827 | 0.98411 | -0.30339 | 0.98386 | -0.30828 | 6.2712
91 | -0.0045832 | -0.0011487 | 0.0045832 | 0.0011487 | 1.8759e-09 | -6.7433e-11 | 0.0070044 | 0.0070044 | 0.0070044 | 0.97366 | -0.50747 | 0.97366 | -0.50746 | 1.9243
92 | -0.0092376 | -0.0023152 | 0.0092386 | 0.0023156 | 9.6499e-07 | 4.5699e-07 | 0.014118 | 0.014117 | 0.014118 | 0.97366 | -0.50746 | 0.97377 | -0.50527 | 3.8784
93 | -0.004295 | -0.0010764 | 0.0042952 | 0.0010764 | 1.6388e-07 | -2.3466e-08 | 0.0065357 | 0.0065357 | 0.0065357 | 0.97786 | -0.42501 | 0.9779 | -0.42421 | 1.7955
94 | 0.1658 | 0.041803 | -0.16574 | -0.041766 | 5.8998e-05 | 3.6984e-05 | 0.25237 | 0.25237 | 0.25237 | 0.9779 | -0.42421 | 0.97752 | -0.43165 | 13.8666
95 | -0.17009 | -0.042879 | 0.17032 | 0.043023 | 0.00022872 | 0.00014353 | 0.25891 | 0.25891 | 0.25891 | 0.9779 | -0.42421 | 0.97934 | -0.39615 | 14.2257
96 | 0.16107 | 0.040596 | -0.16104 | -0.040576 | 3.1505e-05 | 1.9726e-05 | 0.24527 | 0.24527 | 0.24527 | 0.97752 | -0.43165 | 0.97731 | -0.43574 | 13.4762
97 | -0.143 | -0.035996 | 0.143 | 0.035998 | 4.6278e-06 | 2.8807e-06 | 0.21803 | 0.21803 | 0.21803 | 0.97618 | -0.45781 | 0.97622 | -0.45713 | 11.9796
98 | -0.14763 | -0.037159 | 0.14768 | 0.037191 | 5.1647e-05 | 3.2204e-05 | 0.22509 | 0.22509 | 0.22509 | 0.97622 | -0.45713 | 0.97659 | -0.44981 | 12.3674
99 | -0.15195 | -0.038261 | 0.15205 | 0.03832 | 9.354e-05 | 5.841e-05 | 0.23159 | 0.23159 | 0.23159 | 0.97659 | -0.44981 | 0.97725 | -0.43695 | 12.7248
100 | -0.15672 | -0.039491 | 0.15673 | 0.039497 | 9.0651e-06 | 5.6687e-06 | 0.23871 | 0.23871 | 0.23871 | 0.97725 | -0.43695 | 0.97731 | -0.43574 | 13.1159
101 | 0.007387 | 0.0018514 | -0.0073865 | -0.0018512 | 4.7732e-07 | 1.8041e-07 | 0.01127 | 0.01127 | 0.01127 | 0.97537 | -0.47401 | 0.9753 | -0.47537 | 3.096
102 | -0.014369 | -0.0036013 | 0.014371 | 0.0036026 | 2.1285e-06 | 1.2148e-06 | 0.021922 | 0.021922 | 0.021922 | 0.97537 | -0.47401 | 0.97553 | -0.47091 | 6.0224
103 | -0.014371 | -0.0036026 | 0.014375 | 0.0036044 | 3.3079e-06 | 1.8878e-06 | 0.021922 | 0.021922 | 0.021922 | 0.97553 | -0.47091 | 0.97577 | -0.46608 | 6.0224
104 | -0.0055418 | -0.0013889 | 0.0055418 | 0.0013889 | 1.9817e-08 | 3.6365e-09 | 0.0084965 | 0.0084965 | 0.0084965 | 0.97055 | -0.56901 | 0.97055 | -0.56893 | 2.3342
105 | 0.0036925 | 0.00092539 | -0.0036925 | -0.00092541 | 5.8186e-08 | -2.2587e-08 | 0.0056613 | 0.0056613 | 0.0056613 | 0.97055 | -0.56901 | 0.97053 | -0.56934 | 1.5553
106 | -0.0076039 | -0.0019057 | 0.0076047 | 0.001906 | 8.1692e-07 | 3.2472e-07 | 0.011658 | 0.011658 | 0.011658 | 0.97055 | -0.56893 | 0.97066 | -0.56668 | 3.2028
107 | 0.0018621 | 0.00046667 | -0.0018621 | -0.00046668 | 2.6175e-09 | -8.9075e-09 | 0.002855 | 0.002855 | 0.002855 | 0.97053 | -0.56934 | 0.97053 | -0.56937 | 0.78433
108 | -0.0097257 | -0.0024376 | 0.0097258 | 0.0024376 | 8.0993e-08 | 3.9825e-08 | 0.014909 | 0.014909 | 0.014909 | 0.97066 | -0.56668 | 0.97067 | -0.5665 | 4.096
109 | -0.011787 | -0.0029541 | 0.011789 | 0.0029553 | 2.1657e-06 | 1.1674e-06 | 0.018069 | 0.018069 | 0.018069 | 0.97067 | -0.5665 | 0.97087 | -0.56265 | 4.964
110 | -0.01377 | -0.0034517 | 0.013771 | 0.0034522 | 1.2252e-06 | 4.2126e-07 | 0.021105 | 0.021105 | 0.021105 | 0.97087 | -0.56265 | 0.97096 | -0.56078 | 2.899
111 | -0.013771 | -0.0034522 | 0.013771 | 0.0034517 | 4.1425e-07 | -5.0181e-07 | 0.021105 | 0.021104 | 0.021105 | 0.97096 | -0.56078 | 0.97099 | -0.56015 | 1.1596
112 | -0.022689 | -0.0056869 | 0.022691 | 0.0056868 | 1.9448e-06 | -8.1934e-08 | 0.034771 | 0.03477 | 0.034771 | 0.97099 | -0.56015 | 0.97108 | -0.55835 | 1.9105
113 | 0.008918 | 0.0022353 | -0.0089172 | -0.0022349 | 7.8096e-07 | 3.6191e-07 | 0.013667 | 0.013667 | 0.013667 | 0.97099 | -0.56015 | 0.9709 | -0.56199 | 3.7546
114 | -0.0058729 | -0.0014718 | 0.0058729 | 0.0014718 | 1.5987e-08 | 3.7272e-09 | 0.0090019 | 0.0090019 | 0.0090019 | 0.97078 | -0.56433 | 0.97078 | -0.56428 | 2.4731
115 | 0.0034452 | 0.00086338 | -0.0034451 | -0.00086342 | 7.8825e-08 | -4.2746e-08 | 0.0052807 | 0.0052808 | 0.0052808 | 0.97078 | -0.56433 | 0.97076 | -0.56481 | 1.4508
116 | -0.0071376 | -0.0017888 | 0.0071383 | 0.0017891 | 7.7941e-07 | 2.841e-07 | 0.01094 | 0.01094 | 0.01094 | 0.97078 | -0.56428 | 0.9709 | -0.56199 | 3.0056
117 | -0.024312 | -0.006093 | 0.024312 | 0.006093 | 4.0941e-08 | 1.8727e-09 | 0.037254 | 0.037254 | 0.037254 | 0.97108 | -0.55835 | 0.97109 | -0.55831 | 2.0469
118 | -0.0019081 | -0.00047822 | 0.0019082 | 0.00047807 | 4.7287e-08 | -1.5197e-07 | 0.0029249 | 0.0029248 | 0.0029249 | 0.97075 | -0.56496 | 0.97078 | -0.56444 | 0.80354
119 | -0.003967 | -0.00099407 | 0.0039671 | 0.00099405 | 5.8176e-08 | -1.4644e-08 | 0.0060806 | 0.0060806 | 0.0060806 | 0.97078 | -0.56444 | 0.97079 | -0.56413 | 1.6705
120 | -0.0061292 | -0.0015359 | 0.0061292 | 0.0015359 | 7.4642e-09 | 1.9887e-09 | 0.0093947 | 0.0093947 | 0.0093947 | 0.97079 | -0.56413 | 0.97079 | -0.56411 | 2.581
121 | 0.012464 | 0.003125 | -0.012461 | -0.0031237 | 2.2558e-06 | 1.2398e-06 | 0.0191 | 0.0191 | 0.0191 | 0.97104 | -0.55926 | 0.97085 | -0.56306 | 5.2472
122 | 0.010386 | 0.0026034 | -0.010384 | -0.0026024 | 1.8806e-06 | 9.5874e-07 | 0.015916 | 0.015916 | 0.015916 | 0.97104 | -0.55926 | 0.97085 | -0.56306 | 4.3725
123 | 0.0045208 | 0.0011329 | -0.0045204 | -0.0011329 | 4.3247e-07 | -2.0969e-08 | 0.0069246 | 0.0069247 | 0.0069247 | 0.97146 | -0.55084 | 0.97136 | -0.55285 | 1.9024
124 | 0.010002 | 0.0025075 | -0.010002 | -0.0025071 | 6.8255e-07 | 3.4108e-07 | 0.015331 | 0.015331 | 0.015331 | 0.97085 | -0.56306 | 0.97077 | -0.56449 | 4.2118
125 | 0.008236 | 0.002064 | -0.0082356 | -0.0020638 | 4.1056e-07 | 1.7781e-07 | 0.012623 | 0.012623 | 0.012623 | 0.97085 | -0.56306 | 0.97079 | -0.56411 | 3.4679
126 | 0.0089836 | 0.002252 | -0.0089818 | -0.0022511 | 1.7906e-06 | 8.3473e-07 | 0.01377 | 0.01377 | 0.01377 | 0.97077 | -0.56449 | 0.97056 | -0.56868 | 3.7831
127 | 0.0032849 | 0.00082304 | -0.0032848 | -0.00082318 | 1.7725e-07 | -1.3746e-07 | 0.0049294 | 0.0049295 | 0.0049295 | 0.99159 | -0.16053 | 0.99153 | -0.16166 | 1.3543
128 | -0.0065635 | -0.0016447 | 0.0065636 | 0.0016448 | 1.1985e-07 | 3.4204e-08 | 0.0098493 | 0.0098493 | 0.0098493 | 0.99159 | -0.16053 | 0.99161 | -0.16015 | 2.7059
129 | 0.0020347 | 0.00050988 | -0.0020347 | -0.00050993 | 1.7651e-08 | -5.3816e-08 | 0.0030535 | 0.0030535 | 0.0030535 | 0.99153 | -0.16166 | 0.99152 | -0.16185 | 0.83887
130 | -0.0081218 | -0.0020353 | 0.0081235 | 0.002036 | 1.701e-06 | 6.9458e-07 | 0.012188 | 0.012187 | 0.012188 | 0.99161 | -0.16015 | 0.99184 | -0.15575 | 3.3482
131 | -0.011114 | -0.0027853 | 0.011116 | 0.0027864 | 1.9652e-06 | 1.0144e-06 | 0.016673 | 0.016673 | 0.016673 | 0.99184 | -0.15575 | 0.99203 | -0.15204 | 4.5806
132 | -0.013717 | -0.0034383 | 0.01372 | 0.0034399 | 2.9817e-06 | 1.6657e-06 | 0.020575 | 0.020575 | 0.020575 | 0.99203 | -0.15204 | 0.99226 | -0.14748 | 5.6524
133 | 0.0080088 | 0.0020073 | -0.0080083 | -0.0020071 | 4.2191e-07 | 1.778e-07 | 0.012279 | 0.012279 | 0.012279 | 0.97056 | -0.56868 | 0.97051 | -0.56978 | 3.3733
134 | 0.0064223 | 0.0016096 | -0.0064223 | -0.0016096 | 7.964e-10 | 2.385e-10 | 0.0098468 | 0.0098468 | 0.0098468 | 0.97051 | -0.56978 | 0.97051 | -0.56978 | 2.7052
135 | 0.0034474 | 0.00086397 | -0.0034473 | -0.00086399 | 3.4292e-08 | -1.8641e-08 | 0.005281 | 0.005281 | 0.005281 | 0.97136 | -0.55285 | 0.97135 | -0.55306 | 1.4508
136 | 0.022915 | 0.0057693 | -0.022882 | -0.0057496 | 3.2219e-05 | 1.9684e-05 | 0.034393 | 0.034394 | 0.034394 | 0.99166 | -0.15909 | 0.99014 | -0.18854 | 9.4488
137 | 0.022882 | 0.0057496 | -0.022867 | -0.0057403 | 1.5252e-05 | 9.3195e-06 | 0.034394 | 0.034394 | 0.034394 | 0.99014 | -0.18854 | 0.98942 | -0.20252 | 9.4488
138 | 0.022867 | 0.0057403 | -0.022841 | -0.0057246 | 2.5803e-05 | 1.5768e-05 | 0.034394 | 0.034394 | 0.034394 | 0.98942 | -0.20252 | 0.9882 | -0.2262 | 9.4489
139 | -0.0063102 | -0.0015815 | 0.0063108 | 0.0015816 | 6.5785e-07 | 1.6761e-07 | 0.0094598 | 0.0094597 | 0.0094598 | 0.99259 | -0.14135 | 0.9927 | -0.13917 | 2.5988
140 | -0.022272 | -0.005582 | 0.022273 | 0.0055827 | 1.1744e-06 | 7.1527e-07 | 0.033385 | 0.033385 | 0.033385 | 0.9927 | -0.13917 | 0.99276 | -0.13806 | 9.1718

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50496 | 0.12933

## res_load
| p_mw | q_mvar
0 | 0.0025021 | 0.00062709
1 | 0.0045848 | 0.0011491
2 | 0.0042219 | 0.0010581
3 | 0.0046777 | 0.0011723
4 | 0.0038184 | 0.00095699
5 | 0.0089098 | 0.002233
6 | 0.0031168 | 0.00078115
7 | 0.0043234 | 0.0010836
8 | 0.003877 | 0.00097167
9 | 0.012548 | 0.0031448
10 | 0.0027706 | 0.00069437
11 | 0.0057534 | 0.0014419
12 | 0.0056009 | 0.0014037
13 | 0.0057675 | 0.0014455
14 | 0.006284 | 0.0015749
15 | 0.0081954 | 0.002054
16 | 0.0045979 | 0.0011523
17 | 0.0080635 | 0.0020209
18 | 0.007998 | 0.0020045
19 | 0.0024877 | 0.00062347
20 | 0.0063936 | 0.0016024
21 | 0.0051571 | 0.0012925
22 | 0.0032979 | 0.00082653
23 | 0.0079368 | 0.0019892
24 | 0.0053395 | 0.0013382
25 | 0.0020973 | 0.00052564
26 | 0.0010356 | 0.00025955
27 | 0.0059383 | 0.0014883
28 | 0.0028196 | 0.00070666
29 | 0.0048346 | 0.0012117
30 | 0.0046654 | 0.0011693
31 | 0.0058706 | 0.0014713
32 | 0.019935 | 0.0049962
33 | 0.0058933 | 0.001477
34 | 0.0044974 | 0.0011272
35 | 0.0063266 | 0.0015856
36 | 0.0080413 | 0.0020153
37 | 0.0048137 | 0.0012064
38 | 0.0042192 | 0.0010574
39 | 0.0066316 | 0.001662
40 | 0.0051596 | 0.0012931
41 | 0.0065411 | 0.0016394
42 | 0.0014776 | 0.00037032
43 | 0.0047475 | 0.0011898
44 | 0.0031829 | 0.00079771
45 | 0.0085714 | 0.0021482
46 | 0.0078082 | 0.0019569
47 | 0.0049245 | 0.0012342
48 | 0.0052147 | 0.0013069
49 | 0.0045832 | 0.0011487
50 | 0.0046544 | 0.0011665
51 | 0.0042837 | 0.0010736
52 | 0.004295 | 0.0010764
53 | 0.004668 | 0.0011699
54 | 0.005427 | 0.0013601
55 | 0.0046755 | 0.0011718
56 | 0.0046307 | 0.0011606
57 | 0.0042688 | 0.0010699
58 | 0.0023184 | 0.00058105
59 | 0.0045204 | 0.0011329
60 | 0.0055904 | 0.0014011
61 | 0.0046759 | 0.0011719
62 | 0.0043064 | 0.0010793
63 | 0.0069823 | 0.0017499
64 | 0.0073865 | 0.0018512
65 | 0.0075594 | 0.0018946
66 | 0.0018493 | 0.00046347
67 | 0.0020621 | 0.00051682
68 | 0.0018304 | 0.00045874
69 | 0.002121 | 0.00053157
70 | 0.0018621 | 0.00046668
71 | 0.0020609 | 0.00051651
72 | 0.0019809 | 0.00049645
73 | 0.0024277 | 0.00060845
74 | 0.0012647 | 0.00031695
75 | 0.0034451 | 0.00086342
76 | 0.0017789 | 0.00044583
77 | 0.0016208 | 0.00040621
78 | 0.0019081 | 0.00047822
79 | 0.0020588 | 0.00051599
80 | 0.0034091 | 0.0008544
81 | 0.0021621 | 0.00054188
82 | 0.0009832 | 0.00024641
83 | 0.0024589 | 0.00061626
84 | 0.0021483 | 0.00053841
85 | 0.0010182 | 0.00025517
86 | 0.0021064 | 0.0005279
87 | 0.0032786 | 0.00082168
88 | 0.0012501 | 0.0003133
89 | 0.0015582 | 0.00039051
90 | 0.0020347 | 0.00050993
91 | 0.00299 | 0.00074938
92 | 0.0026012 | 0.00065191
93 | 0.0043589 | 0.0010924
94 | 0.00097306 | 0.00024387
95 | 0.0015861 | 0.00039751
96 | 0.0064223 | 0.0016096
97 | 0.001073 | 0.00026892
98 | 0.0034473 | 0.00086399
99 | 0.010928 | 0.0027389
100 | 0.0063102 | 0.0015815
101 | 0.015961 | 0.0040003
102 | 0.0064762 | 0.0016231
103 | 0.022841 | 0.0057246

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1